## Sheet1
AssetID | AssetCategory | AssetName | AssetDescription | SiteName | FacilityName | InstallYear | LocationName | CoF | TempComments1 | TempComments2 | TempComments3 | VisualCondition | PoF | AvgESL
1 | Process Mechanical | Water Pump No.1 | Pump, Water, No.1 (Maley) - A 01 Pumps | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | Fair | The pump is still working but it already exceeded its expected service life |  | 3 | 3 | 30
2 | Process Mechanical | Water Pump No.2 | Pump, Water, No.2 (Maley) - A 01 Pumps | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | Fair | The pump is still working but it already exceeded its expected service life |  | 3 | 3 | 30
3 | Process Mechanical | High Flow Pump | High Flow (Maley) - A 01 Pumps | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | Poor | The pump is beyond its expected service life. The missing pump suggest that it has been sent for repair |  | 3 | 3 | 30
4 | Process Mechanical | Piping | Piping, Water Pumping - A 05 Piping & Valves | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
5 | Process Mechanical | Coupon Rack (To be removed) | Coupon Rack (Maley) - A 05 Piping & Valves | Maley Booster Station |  | 1992 |  | 2 | This is not process mechanical equipment. |  |  | 2 | 2 | 30
7 | Process Instrumentation | Ethernet Swith | Switch (Maley) | Maley Booster Station | Booster Station | 2020 | Pump Room | 1 | Good |  |  | 2 | 2 | 15
8 | Process Instrumentation | UPS | Power Supply(Maley) | Maley Booster Station | Booster Station | 2020 | Pump Room | 1 | Good |  |  | 2 | 2 | 15
9 | Process Electrical | Standby Generator | Generator (Maley) - A 17 Generator | Maley Booster Station | Booster Station | 1992 | Generator Room | 3 | good |  |  | 2 | 2 | 25
10 | Building Mechanical | Unit Heater 1 | Gas fired unit heater | Maley Booster Station | Booster Station | 1992 | Pump Room | 1 | Good |  |  | 2 | 2 | 30
11 | Process Instrumentation | Control System (Place holder) | Control System, DG (Maley) - A 27 Inst. & Controls | Maley Booster Station | Booster Station | 1992 | Pump Room | 1 |  |  |  | 3 | 3 | 15
12 | Process Instrumentation | Flow Recorder #1 | FLOW RECORDER (Maley) | Maley Booster Station | Booster Station | 2011 | Pump Room | 2 | Aging, Wear and Tear | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 3 | 3 | 15
13 | Process Instrumentation | Flow Recorder #2 | FLOW RECORDER (Maley) | Maley Booster Station | Booster Station | 2011 | Pump Room | 2 | Aging, Wear and Tear | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 3 | 3 | 15
14 | Process Instrumentation | Low Temperature Alarm Thermostat 1 | Low Temperature Alarm Thermostat (Maley) | Maley Booster Station | Booster Station | 2011 | Pump Room | 1 | Aging | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 3 | 3 | 15
15 | Site Works | Asphalt Pavement | Asphalt Pavement (approx. 130 sq. m) | Maley Booster Station | Booster Station | 1992 | Site | 1 | Fair | Minor craks were noted. |  | 3 | 3 | 20
16 | Process Instrumentation | Network Switch | Network Switch (Maley) | Maley Booster Station | Booster Station | 2020 | Pump Room | 1 | Good |  |  | 2 | 2 | 15
17 | Building Structural | Pump Room Monorail Crane Beam | Monorail, 1Ton (Maley) - A 49 Lifting Appliances | Maley Booster Station | Booster Station | 1992 | Pump Room | 1 | Good |  |  | 2 | 2 | 60
18 | Process Instrumentation | PLC | PLC (Maley) | Maley Booster Station | Booster Station | 2020 | Pump Room | 3 | Good |  |  | 2 | 2 | 15
20 |  | MALEY BOOSTER | Maley Booster - A 78 (Reserved) | Maley Booster Station |  | 2005 |  | 2 |  |  |  | 3 | 3 | 30
21 | Building Mechanical | Safety Equipment (Placeholder) | Safety Equipment (Maley) - A 79 Safety Equipment | Maley Booster Station | Booster Station | 2005 | Pump Room | 2 |  |  |  | 3 | 3 | 30
22 | Process Mechanical | Booster Pump #3 | Pump, Booster #3 (Sunrise) - A 01 Pumps | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
23 | Process Mechanical | Booster Pump #2 | Pump, Booster #2 (Sunrise) - A 01 Pumps | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
24 | Process Mechanical | Booster Pump #1 | Pump, Booster #1(Sunrise) - A 01 Pumps | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
25 | Process Mechanical | Pressure Relief Valve | Valve, Pressure Relief 6",A 05 Piping & Valves | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
26 | Process Mechanical | Pressure Relief Valve | Valve, Pressure Relief 2",A 05 Piping & Valves | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | This valve is a component of the bigger 6" pressure relief valve | Good |  | 3 | 3 | 30
27 | Building Mechanical | P-Trap Primer | P-Trap Primer (Sunrise) - A 05 Piping & Valves | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 1 | Assume to be good |  |  | 2 | 2 | 30
28 | Process Mechanical | Process Piping | Piping - A 05 Piping & Valves | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Very Good |  |  | 1 | 1 | 30
30 | Process Instrumentation | Ethernet Switch | Ethernet Switch(SUNRISE BOOSTER) | Sunrise Ridge Booster Station | Booster Station | 2016 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
31 | Process Instrumentation | UPS | UPS (Sunrise Booster) | Sunrise Ridge Booster Station | Booster Station | 2018 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
32 | Process Electrical | Standby Generator | Gen, Stby(Sunrise Booster) - A 17 Generator | Sunrise Ridge Booster Station | Booster Station | 2005 | Generator Room | 3 | Good | The generator includes a sub-base fuel tank; no containment for the fuel; |  | 2 | 2 | 25
33 | Building Mechanical | Unit Heater 1 | Unit Heater UH-1 | Sunrise Ridge Booster Station | Booster Station | 2021 | Pump Room | 1 | Good |  |  | 2 | 2 | 30
34 | Process Instrumentation | Instrumentation & Control (Placeholder) | Inst. & CTRL (Sunrise Booster) - A 27 Inst. & Controls | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 |  |  |  | 3 | 3 | 15
35 | Site Works | Asphalt Pavement | Asphalt Pavement on 96sq. M - A 32 Building & Grounds | Sunrise Ridge Booster Station | Booster Station | 2005 | Site | 1 | Good | Localized depressions in front of the building was observed. |  | 3 | 3 | 20
36 | Building Structural | Pump Room 1/2 Ton Bridge Crane | Monorail & 1/2 Ton Hoist - A 49 Lifting Appliances | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 1 | Good |  |  | 2 | 2 | 60
37 |  | SUNRISE BOOSTER | Sunrise Booster - A 78 (Reserved) | Sunrise Ridge Booster Station |  | 2004 |  | 2 |  |  |  | 3 | 3 | 30
38 | Process Mechanical | CL2 #1 Booster Pump | Booster Pump CL2 #1 - A 01 Pumps | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
39 | Process Mechanical | CL2 #2 Booster Pump | Booster Pump CL2 #2 - A 01 Pumps | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
40 | Process Mechanical | Deep Well #7 Pump | Pump, Deep Well #7 - A 01 Pumps | Falconbridge Wells | Well Building | 2004 | Well #7 | 2 | Good |  |  | 2 | 2 | 30
41 | Process Mechanical | Deep Well #6 Pump | Pump, Deep Well #6 - A 01 Pumps | Falconbridge Wells | Site | 2004 | Well #6 | 2 | Good |  |  | 2 | 2 | 30
42 | Process Mechanical | Deep Well #5 Pump | Pump, Deep Well #5 - A 01 Pumps | Falconbridge Wells | Site | 2004 | Well #5 | 2 | Good |  |  | 2 | 2 | 30
43 | Process Mechanical | Poly #1 Pump | Pump, Poly #1 - A 01 Pumps | Falconbridge Wells | Well Building | 2019 | Fluoride Room | 2 | Very Good |  |  | 1 | 1 | 30
44 | Process Mechanical | Poly #2 Pump | Pump, Poly #2 - A 01 Pumps | Falconbridge Wells | Well Building | 2019 | Fluoride Room | 2 | Very Good |  |  | 1 | 1 | 30
45 | Process Mechanical | West Main Booster Pump | Booster Pump, West Main - A 01 Pumps | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
46 | Process Mechanical | Pump #7 Control Vavle | Control Valve Pump #7 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Fair | Minor corrosion was observed on the surface of the valve |  | 3 | 3 | 30
47 | Process Mechanical | Pump #7 Distrubtion Valve | Distrubtion Valve Pump #7 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
48 | Process Mechanical | Pump #7 Bypass Valve | Bypass Valve Pump #7 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
49 | Process Mechanical | Pump #6 Control Valve | Control Valve Pump #6 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Fair | Corrosion was observed on the top of the valve |  | 3 | 3 | 30
50 | Process Mechanical | Pump #6 Distrubtion Valve | Distrubtion Valve Pump #6 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
51 | Process Mechanical | Pump #6 Bypass Valve | Bypass Valve Pump #6 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
52 | Process Mechanical | Pump #5 Control Valve | Control Valve Pump #5 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good | Minor corrosion was observed on the pump |  | 3 | 3 | 30
53 | Process Mechanical | Pump #5 Distrubtion Valve | Distrubtion Valve Pump #5 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
54 | Process Mechanical | Pump #5 Bypass Valve | Bypass Valve Pump #5 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2014 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
55 | Process Mechanical | Tank Pressure Relief Valve | Pressure Relief, Tank - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
56 | Process Mechanical | Waste Pressure Relief Valve | Pressure Relief, Waste - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2014 | Pump Room | 2 | Fair | Minor deterioration and corrosion service on the valve |  | 3 | 3 | 30
57 | Process Mechanical | Piping & Valves (Placeholder) | Piping & Valves, Gen. - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2005 | Pump Room | 2 |  |  |  | 3 | 3 | 30
61 | Process Instrumentation | Temperature Sensor | Temperature Sensor | Falconbridge Wells | Well Building | 2015 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
62 | Process Instrumentation | Ethernet Switch | Ethernet Switch(Falconbridge) | Falconbridge Wells | Well Building | 2015 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
63 | Process Instrumentation | Fiber Patch Panel | Fiber Patch Panel(Falconbridge) | Falconbridge Wells | Well Building | 2015 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
64 | Building Mechanical | Fuel Tank | Diesel Tank and Piping | Falconbridge Wells | Well Building | 2018 | Generator Room | 2 | Good | Cc: There was no containment for diesel fuel lines. TSSA requires all equipment containing or carrying fuel to be contained per CSA B139.1.1-15 Section 6.5.1.4. |  | 4 | 4 | 30
65 | Building Mechanical | Surge Tank | Surge Tank | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 2 | Good |  |  | 2 | 2 | 30
66 | Process Instrumentation | MODEM | MODEM(Falconbridge) | Falconbridge Wells | Well Building | 2015 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
67 | Process Instrumentation | PLC Panel 6812-4 | PLC RPU ENCLOSURE(Falconbridge) | Falconbridge Wells | Well Building | 2015 | Pump Room | 3 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
68 | Process Instrumentation | Operator Interface Terminal | Operator Interface Terminal(Falconbridge) | Falconbridge Wells | Well Building | 2015 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
69 | Process Electrical | Standby Generator | Generator - A 17 Generator | Falconbridge Wells | Well Building | 2004 | Generator Room | 3 | Good |  |  | 2 | 2 | 25
70 | Building Mechanical | Intake Dampers for Generator Room | Intake dampers (Total of 2) | Falconbridge Wells | Well Building | 2004 | Generator Room | 2 | Good |  |  | 2 | 2 | 30
71 | Process Electrical | Automatic Transfer Switch | Transfer Switch - A 27 Inst. & Controls | Falconbridge Wells | Well Building | 2004 | Pump Room | 3 | Good | Cc: Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the transfer switch which may require examination, adjustment, servicing, or mainte |  | 3 | 3 | 25
72 | Process Instrumentation | FALCONBRIDGE WELLS (Placeholder) | Inst & Ctrls, Cl2 - A 27 Inst. & Controls | Falconbridge Wells |  | 2004 |  | 2 |  |  |  | 3 | 3 | 15
73 | Process Instrumentation | pH-Chlorine Analyzer AIT-1791 | pH-Chlorine Analyzer(Falconbridge) | Falconbridge Wells | Well Building | 2010 | Pump Room | 2 | Aging | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 3 | 3 | 15
75 | Process Instrumentation | Colorimetric Chlorine Analyzer #1 | Colorimetric Chlorine Analyzer1 | Falconbridge Wells | Well Building | 2021 | Pump Room | 2 | Very Good |  |  | 3 | 3 | 15
76 | Process Instrumentation | FALCONBRIDGE WELLS (Placeholder) | Inst & Controls, Pump #5 - A 27 Inst. & Controls | Falconbridge Wells |  | 2004 |  | 2 |  |  |  | 3 | 3 | 15
77 | Process Instrumentation | By Pass Turbidimeter | By Pass Turbidity(Falconbridge). AE-17944-2 | Falconbridge Wells | Well Building | 2015 | Pump Room | 2 | Aging | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 3 | 3 | 15
78 | Process Instrumentation | Ambient Chlorine Remote Sensor 1 | Ambient Chlorine Remote Sensor 1(Falconbridge) | Falconbridge Wells | Well Building | 2015 | Chlorine Room | 2 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
79 | Process Instrumentation | Ambient Chlorine Remote Sensor 2 | Ambient Chlorine Remote Sensor 2(Falconbridge) | Falconbridge Wells | Well Building | 2015 | Chlorine Room | 2 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
80 | Process Instrumentation | Thermostat | Thermostat | Falconbridge Wells | Well Building | 2018 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
81 | Process Instrumentation | Chlorinator #1 | CHLORINATOR(Falconbridge) | Falconbridge Wells | Well Building | 2015 | Chlorine Room | 2 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
82 | Process Instrumentation | Chlorinator #2 | CHLORINATOR(Falconbridge) | Falconbridge Wells | Well Building | 2015 | Chlorine Room | 2 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
83 | Site Works | Gravel Parking Lots & Driveway | Gravel Parking Lots & Driveway, approx. 830 sq. m | Falconbridge Wells | Site | 2004 | Site | 1 | Good | Weed and plant growing on gravel driveway and parking lot |  | 2 | 2 | 20
84 | Process Instrumentation | CL2 Scale | Scale CL2 - A 53 Scales | Falconbridge Wells | Well Building | 2015 | Chlorine Room | 1 | Aging, Wear and Tear | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 3 | 3 | 15
86 | Process Instrumentation | Poly Tank Level Transmitter | Poly Tank Level Transmitter(Falconbridge) | Falconbridge Wells | Well Building | 2010 | Fluoride Room | 2 | Aging, Wear and Tear | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 3 | 3 | 15
87 | Process Instrumentation | UPS | Power Supply(Falconbridge) | Falconbridge Wells | Well Building | 2010 | Pump Room | 1 | Aging | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 3 | 3 | 15
88 | Process Instrumentation | PLC | PLC(Falconbridge) | Falconbridge Wells | Well Building | 2015 | Pump Room | 3 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
89 | Building Mechanical | Temperature Switch | Temperature Switch(Falconbridge) | Falconbridge Wells | Well Building | 2004 | Pump Room | 1 | Good |  |  | 2 | 2 | 30
90 | Process Instrumentation | Turbidity Analyzer | Tubidity Analyzer - Genernal Purpose Analyzer Controller(Falconbridge) | Falconbridge Wells | Well Building | 2015 | Pump Room | 2 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
91 | Process Instrumentation | Weight Transmitter | Weight Transmitter(Falconbridge) | Falconbridge Wells | Well Building | 2018 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
92 |  | FALCONBRIDGE WELLS | Falconbridge Wells - A 78 (Reserved) | Falconbridge Wells |  | 2004 |  | 3 |  |  |  | 3 | 3 | 30
94 | Building Mechanical | Eye Wash Station | Eye Wash station - A 79 Safety Equipment | Falconbridge Wells | Well Building | 2004 | Generator Room | 1 | Good |  |  | 2 | 2 | 30
96 | Building Electrical | Outdoor Lighting | 4 Wallpack Fixtures | Sunrise Ridge Booster Station | Booster Station | 2005 | Site | 1 | Good | to be replaced with LED fixtures in next upgrade |  | 2 | 2 | 25
97 | Process Electrical | Hydro Meter | Hydro Meter | Sunrise Ridge Booster Station | Booster Station | 2005 | Site | 1 | Good |  |  | 2 | 2 | 25
98 | Building Electrical | Indoor Lighting | 24 linear fluroscent Fixtures | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 1 | Good | to be replaced with LED fixtures in next upgrade |  | 2 | 2 | 25
99 | Building Electrical | Emergency Lighting | 2 combination exit signs | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good |  |  | 2 | 2 | 25
101 | Process Electrical | MCC #1 | MCC | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 3 | Good | Cc: Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the MCC which may require examination, adjustment, servicing, or maintenance while |  | 3 | 3 | 25
102 | Process Electrical | Power Meter | Power Meter | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good |  |  | 2 | 2 | 25
103 | Process Electrical | Main Circuit Breaker | Main Circuit Breaker | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 3 | Good | Cc: Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the main circuit breaker which may require examination, adjustment, servicing, or m |  | 3 | 3 | 25
104 | Process Electrical | Automatic Transfer Switch | Automatic Transfer Switch | Sunrise Ridge Booster Station | Booster Station | 2005 | Generator Room | 3 | Good | Cc: Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the auotmatic transfer switch which may require examination, adjustment, servicing, |  | 3 | 3 | 25
105 | Process Electrical | Surge Suppressor | Surge Suppressor | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good | Cc: Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the surge suppressor which may require examination, adjustment, servicing, or maint |  | 3 | 3 | 25
106 | Process Electrical | Pump #1 VFD | VFD | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good |  |  | 2 | 2 | 25
107 | Process Electrical | Pump #2 VFD | VFD | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good |  |  | 2 | 2 | 25
108 | Process Electrical | Pump #3 VFD | VFD | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good |  |  | 2 | 2 | 25
109 | Building Electrical | Lighting Panel A | Lighting Panel | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 1 | Good |  |  | 2 | 2 | 25
110 | Process Electrical | Transformer | Transformer | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good |  |  | 2 | 2 | 25
111 | Building Electrical | Outdoor Lighting | 2 wall pack lights | Maley Booster Station | Booster Station | 1992 | Site | 1 | good | to be replaced with LED fixtures in next upgrade |  | 2 | 2 | 25
112 | Building Electrical | Pump Room Lighting | 8 linear flurescent lights | Maley Booster Station | Booster Station | 1992 | Pump Room | 1 | good | to be replaced with LED fixtures in next upgrade |  | 2 | 2 | 25
113 | Building Electrical | Generator Room Lighting | 4 linear flurescent lights | Maley Booster Station | Booster Station | 1992 | Generator Room | 1 | good | to be replaced with LED fixtures in next upgrade |  | 2 | 2 | 25
114 | Process Electrical | Generator Transfer Panel | Generator Transfer Panel | Maley Booster Station | Booster Station | 1992 | Pump Room | 3 | good | Cc: Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the generator transfer panel which may require examination, adjustment, servicing, |  | 3 | 3 | 25
115 | Process Electrical | Lighting Transformer Disconnect Switch | Disconnect Switch | Maley Booster Station | Booster Station | 1992 | Pump Room | 1 | good |  |  | 2 | 2 | 25
116 | Process Electrical | Lighting Panel | Lighting Panel | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | good |  |  | 2 | 2 | 25
117 | Building Electrical | Generator Room Heating Disconnect Switch | Disconnect Switch | Maley Booster Station | Booster Station | 1992 | Pump Room | 1 | good |  |  | 2 | 2 | 25
118 | Process Electrical | Splitter | Splitter | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | good | Cc: Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the splitter which may require examination, adjustment, servicing, or maintenance w |  | 3 | 3 | 25
119 | Process Electrical | Phase Loss Relay Disconnect Switch | Disconnect Switch | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | good |  |  | 2 | 2 | 25
120 | Process Electrical | Pump Control Panel | Pump Control Panel | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | good | Cc: Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the pump control panel which may require examination, adjustment, servicing, or mai |  | 3 | 3 | 25
121 | Process Electrical | Incoming Power Enclosure | Incoming Power Enclosure | Maley Booster Station | Booster Station | 1992 | Pump Room | 1 | good | Cc: Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the incoming power enclosure which may require examination, adjustment, servicing, |  | 3 | 3 | 25
122 | Process Electrical | Main Disconnect Switch | Main Disconnect Switch | Maley Booster Station | Booster Station | 1992 | Pump Room | 3 | good | Cc: Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the main disconnect switch which may require examination, adjustment, servicing, or |  | 3 | 3 | 25
123 | Process Electrical | Transformer | Transformer | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | good |  |  | 2 | 2 | 25
124 | Process Electrical | VFD#1 | VFD | Maley Booster Station | Booster Station | 2010 | Pump Room | 2 | good |  |  | 2 | 2 | 25
125 | Process Electrical | VFD#2 | VFD | Maley Booster Station | Booster Station | 2010 | Pump Room | 2 | good |  |  | 2 | 2 | 25
126 | Process Electrical | Duplex Pump Control Panel (CP-4000) | duplex pump control panel | Maley Booster Station | Booster Station | 2010 | Pump Room | 2 | good |  |  | 2 | 2 | 25
127 | Process Electrical | Load #1 Output Filter | output filter | Maley Booster Station | Booster Station | 2010 | Pump Room | 2 | good |  |  | 2 | 2 | 25
128 | Process Electrical | Load #2 Output Filter | output filter | Maley Booster Station | Booster Station | 2010 | Pump Room | 2 | good |  |  | 2 | 2 | 25
129 | Process Electrical | Load #2 Input Filter | output filter | Maley Booster Station | Booster Station | 2010 | Pump Room | 2 | good |  |  | 2 | 2 | 25
130 | Process Electrical | Load #1 Input Filter | output filter | Maley Booster Station | Booster Station | 2010 | Pump Room | 2 | good |  |  | 2 | 2 | 25
131 | Process Electrical | Pump #1 Disconnect Switch | Disconnect Switch | Maley Booster Station | Booster Station | 2010 | Pump Room | 2 | good |  |  | 2 | 2 | 25
132 | Process Electrical | Pump #2 Disconnect Switch | Disconnect Switch | Maley Booster Station | Booster Station | 2010 | Pump Room | 2 | good |  |  | 2 | 2 | 25
133 | Building Electrical | Pump Room Exit Sign | 1 combination exit sign | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | good |  |  | 2 | 2 | 25
134 | Process Electrical | Battery Charger | Battery Charger | Maley Booster Station | Booster Station | 1992 | Generator Room | 2 | good |  |  | 2 | 2 | 25
135 | Process Electrical | Hydro Meter | Hydro Meter | Maley Booster Station | Booster Station | 1992 | Site | 1 | poor | severe corrosion | graffiti on the enclosure | 4 | 4 | 25
136 | Process Electrical | Hydro Meter | Hydro Meter | Falconbridge Wells | Site | 2004 | Site | 1 | fair | pump room outer wall | The enclosure for Hydrometer was in fair condtion. The latch was corrode and discolouration on the panel was noted. | 3 | 3 | 25
137 | Building Electrical | Outdoor Lighting | 4 wall pack LEDs | Falconbridge Wells | Site | 2004 | Site | 1 | good | photosensor for one of the fixtures did not work |  | 3 | 3 | 25
138 | Building Electrical | Generator Room Lights | 4 linear flurescent | Falconbridge Wells | Well Building | 2004 | Generator Room | 1 | good | to be replaced with LED fixtures in next upgrade |  | 2 | 2 | 25
139 | Building Electrical | Unit Heater #3 Disconnect Switch | disconnect switch | Falconbridge Wells | Well Building | 2004 | Generator Room | 1 | good |  |  | 2 | 2 | 25
140 | Building Electrical | T775 Control Panel | T775 Control Panel | Falconbridge Wells | Well Building | 2004 | Generator Room | 1 | Good |  |  | 2 | 2 | 25
141 | Building Electrical | Generator Room Exhuast Fan Control Panel | Control Panel | Falconbridge Wells | Well Building | 2004 | Generator Room | 2 | good |  |  | 2 | 2 | 25
142 | Building Electrical | Pump Room Lights | 9 linear flurescent | Falconbridge Wells | Well Building | 2004 | Pump Room | 1 | good | to be replaced with LED fixtures in next upgrade |  | 2 | 2 | 25
143 | Building Electrical | Pump Room Exit Signs | 2 exit signs | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | good |  |  | 2 | 2 | 25
144 | Process Electrical | MCC12-1A | MCC | Falconbridge Wells | Well Building | 2004 | Pump Room | 3 | good | Cc: Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the MCC which may require examination, adjustment, servicing, or maintenance while |  | 3 | 3 | 25
145 | Process Electrical | Main Circuit Breaker | Main Circuit Breaker | Falconbridge Wells | Well Building | 2004 | Pump Room | 3 | good | Cc: Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the main circuit breaker which may require examination, adjustment, servicing, or m |  | 3 | 3 | 25
146 | Process Electrical | Power Meter | Power Meter | Falconbridge Wells | Well Building | 2004 | Pump Room | 1 | good |  |  | 2 | 2 | 25
147 | Process Electrical | Well Pump #5 Starter | starter | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | good | Cc: Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the starter which may require examination, adjustment, servicing, or maintenance wh |  | 3 | 3 | 25
148 | Process Electrical | Spare Starters | starter | Falconbridge Wells | Well Building | 2004 | Pump Room | 1 | good |  |  | 2 | 2 | 25
149 | Process Electrical | Booster Pump #2 Starter | starter | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | good |  |  | 2 | 2 | 25
150 | Process Electrical | Booster Pump #1 Starter | starter | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | good |  |  | 2 | 2 | 25
151 | Process Electrical | Western Main Booster Pump Starter | starter | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | good |  |  | 2 | 2 | 25
152 | Process Electrical | Well Pump #6 Starter | starter | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | good |  |  | 2 | 2 | 25
153 | Process Electrical | Well Pump #7 Starter | starter | Falconbridge Wells | Well Building | 2018 | Pump Room | 2 | Good |  |  | 2 | 2 | 25
154 | Process Electrical | Transient Voltage Surge Suppressor | Transient Voltage Surge Suppressor | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | good |  |  | 2 | 2 | 25
155 | Process Electrical | Pump #5 Deepwell Distribution Shutoff Motorized Valve Actuator | Motorized Valve Actuator | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | good |  |  | 2 | 2 | 25
156 | Process Electrical | Pump #5 Deepwell Bypass Shutoff Motorized Valve Actuator | Motorized Valve Actuator | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | good |  |  | 2 | 2 | 25
157 | Process Electrical | Pump #6 Distribution Shutoff Motorized Valve Actuator | Motorized Valve Actuator | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | good |  |  | 2 | 2 | 25
158 | Process Electrical | Pump #6 Deepwell Bypass Shutoff Motorized Valve Actuator | Motorized Valve | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | good |  |  | 2 | 2 | 25
159 | Process Electrical | Pump #7 Distribution Shutoff Motorized Valve Actuator | Motorized Valve Actuator | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | good |  |  | 2 | 2 | 25
160 | Process Electrical | Pump #7 Deepwell Bypass Shutoff Motorized Valve Actuator | Motorized Valve | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | good |  |  | 2 | 2 | 25
161 | Building Electrical | Chlorine Room Exhuast Fan Control Panel | Control Panel | Falconbridge Wells | Well Building | 2004 | Chlorine Room | 2 | good |  |  | 2 | 2 | 25
162 | Process Electrical | Transformer | Transformer | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | good |  |  | 2 | 2 | 25
163 | Building Electrical | LP6811 Lighting Panel | Lighting Panel | Falconbridge Wells | Well Building | 2004 | Pump Room | 1 | good |  |  | 2 | 2 | 25
164 | Process Electrical | Transformer | Transformer | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | good |  |  | 2 | 2 | 25
165 | Building Electrical | UP6812 Lighting Panel | Lighting Panel | Falconbridge Wells | Well Building | 2004 | Pump Room | 1 | good |  |  | 2 | 2 | 25
166 | Building Electrical | Fluoride Room Exhuast Fan Control Panel | Control Panel | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 2 | good |  |  | 2 | 2 | 25
167 | Building Electrical | Process Room Exhuast Fan Control Panel | Control Panel | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | good |  |  | 2 | 2 | 25
168 | Building Electrical | Fluoride Room Light | 1 linear flurescent | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 1 | good | to be replaced with LED fixtures in next upgrade |  | 2 | 2 | 25
169 | Building Electrical | Chlorine Room Light | 1 linear flurescent | Falconbridge Wells | Well Building | 2004 | Chlorine Room | 1 | good | to be replaced with LED fixtures in next upgrade |  | 2 | 2 | 25
170 | Building Electrical | Fluoride Room Exit Sign | exit sign | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 2 | good |  |  | 2 | 2 | 25
171 | Building Electrical | Chlorine Room Emergency Light | battery unit | Falconbridge Wells | Well Building | 2004 | Chlorine Room | 2 | good |  |  | 2 | 2 | 25
172 | Building Electrical | Pump Room Emergency Light | 2 battery unit | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | good |  |  | 2 | 2 | 25
173 |  | PLC Panel | PLC Panel |  |  | 2004 |  | 3 | Good |  |  | 2 | 2 | 30
174 | Building Electrical | T775 Control Panel | CONTROL PANEL (SUNRISE BOOSTER) | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 1 | Aging |  |  | 3 | 3 | 25
175 | Process Instrumentation | Temperature Transmitter | Thermostat (SUNRISE BOOSTER) | Sunrise Ridge Booster Station | Booster Station | 2018 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
176 | Process Instrumentation | Gauge Pressure Cerabar 1 | Gauge Pressure Cerabar (SUNRISE BOOSTER) | Sunrise Ridge Booster Station | Booster Station | 2018 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
177 | Process Instrumentation | Pressure Gauge 1 | Pressure Gauge (SUNRISE BOOSTER) | Sunrise Ridge Booster Station | Booster Station | 2018 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
178 | Process Instrumentation | Gauge Pressure Cerabar 2 | Gauge Pressure Cerabar (SUNRISE BOOSTER) | Sunrise Ridge Booster Station | Booster Station | 2018 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
179 | Process Instrumentation | Pressure Gauge 2 | Pressure Gauge (SUNRISE BOOSTER) | Sunrise Ridge Booster Station | Booster Station | 2018 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
180 | Process Instrumentation | Low Temp T-STAT | Low Temp T-STAT(SUNRISE BOOSTER) | Sunrise Ridge Booster Station | Booster Station | 2016 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
182 | Process Instrumentation | MODEM | Modem(SUNRISE BOOSTER) | Sunrise Ridge Booster Station | Booster Station | 2016 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
183 | Process Instrumentation | PLC | PLC(SUNRISE BOOSTER) | Sunrise Ridge Booster Station | Booster Station | 2006 | Pump Room | 3 | Aging | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 3 | 3 | 15
184 | Process Instrumentation | Thermostat | Thermostat(SUNRISE BOOSTER) | Sunrise Ridge Booster Station | Booster Station | 2016 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
186 | Process Instrumentation | MODEM | MODEM(Maley) | Maley Booster Station | Booster Station | 2020 | Pump Room | 1 | Good |  |  | 2 | 2 | 15
187 | Process Instrumentation | Temperature Transmitter | Temperature Transmitter(Maley) | Maley Booster Station | Booster Station | 2016 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
188 | Process Instrumentation | Low Temperature Alarm Thermostat 2 | Low temperature alarm thermostat with diesel louvres(Maley) | Maley Booster Station | Booster Station | 2011 | Pump Room | 1 | Wear and Tear | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 3 | 3 | 15
189 | Process Instrumentation | Thermostat | Thermostat(Maley) | Maley Booster Station | Booster Station | 2011 | Pump Room | 1 | Wear and Tear | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 3 | 3 | 15
190 | Process Instrumentation | RPU Control Cabinet | RPU Control Cabinet | Maley Booster Station | Booster Station | 2020 | Pump Room | 1 | Good |  |  | 2 | 2 | 15
191 | Process Instrumentation | Flow Switch | Flow Switch (Maley) | Maley Booster Station | Booster Station | 2008 | Pump Room | 1 | Aging | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 3 | 3 | 15
192 |  | MALEY BOOSTER ALTOMETER 2 | Altometer Signal Converter(Maley) |  |  | 2008 |  | 3 |  |  |  | 3 | 3 | 30
193 | Process Instrumentation | Flowmeter #1 | FLOWMETER | Maley Booster Station | Booster Station | 2008 | Pump Room | 2 | Aging | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 3 | 3 | 15
194 |  | MALEY BOOSTER Pressure Guage |  |  |  | 2004 |  | 3 |  |  |  | 3 | 3 | 30
195 | Process Instrumentation | Pressure Gauge 1 | Pressure Gauge (Maley) | Maley Booster Station | Booster Station | 2018 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
196 | Process Instrumentation | Suction Pressure Transducer 1 | Gauge Pressure Cerabar (Maley) | Maley Booster Station | Booster Station | 2020 | Pump Room | 1 | Very Good |  |  | 1 | 1 | 15
197 | Process Instrumentation | Pressure Gauge 2 | Pressure Gauge (Maley) | Maley Booster Station | Booster Station | 2018 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
198 | Process Instrumentation | Suction Pressure Transducer 2 | Gauge Pressure Cerabar (Maley) | Maley Booster Station | Booster Station | 2020 | Pump Room | 1 | Very Good |  |  | 1 | 1 | 15
199 | Process Instrumentation | Gas Detector Transmitter #2 | Gas Deterctor Transmitter | Falconbridge Wells | Well Building | 2015 | Chlorine Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
200 | Process Instrumentation | Gas Detector Transmitter #1 | Gas Deterctor Transmitter | Falconbridge Wells | Well Building | 2015 | Chlorine Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
201 | Process Instrumentation | Treated Water Turbidimeter | Treated Turbidity (Falconbridge) | Falconbridge Wells | Well Building | 2015 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
202 | Process Instrumentation | Colorimetric Chlorine Analyzer #2 | Colorimetric Chlorine Analyzer2 | Falconbridge Wells | Well Building | 2021 | Pump Room | 2 | Very Good |  |  | 1 | 1 | 15
203 | Process Instrumentation | pH-Chlorine Analyzer AIT-17942 | pH-Chlorine Analyzer(Falconbridge) | Falconbridge Wells | Well Building | 2015 | Pump Room | 2 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
204 | Process Instrumentation | Free Chlorine Transmitter | Universal Controller(Falconbridge) | Falconbridge Wells | Well Building | 2018 | Pump Room | 2 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
205 | Process Instrumentation | Raw Water Gauge (qty:7) | Raw Water Gauge | Falconbridge Wells | Well Building | 2015 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
206 | Process Instrumentation | Booster Pump #6 Flowmeter | FLOW Transmitter, FIT-17946 | Falconbridge Wells | Well Building | 2018 | Pump Room | 2 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
207 | Process Instrumentation | Flowmeter #2 | FLOWMETER | Maley Booster Station | Booster Station | 2008 | Pump Room | 2 | Aging | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 3 | 3 | 15
208 | Process Instrumentation | Booster Pump #5 Flowmeter | FLOW Transmitter, FIT-17945 | Falconbridge Wells | Well Building | 2018 | Pump Room | 2 | Good | Condensation on the flowmeter was observed; Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
209 | Process Instrumentation | Treated Water Flowmeter | FLOW Transmitter | Falconbridge Wells | Well Building | 2018 | Pump Room | 2 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
210 | Process Instrumentation | Western Main Flowmeter | FLOW Transmitter, FIT17948 | Falconbridge Wells | Well Building | 2018 | Pump Room | 2 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
211 | Process Instrumentation | Booster Pump #7 Flowmeter | FLOW Transmitter, FIT-17947 | Falconbridge Wells | Well Building | 2018 | Pump Room | 2 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
212 | Process Instrumentation | Treated Water Pressure Transmitter | Treated Water Pressure Transmitter | Falconbridge Wells | Well Building | 2018 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
213 | Process Mechanical | Suction Header Butterfly Valve | Butterfly Valve | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good | Minor corrosion was observed |  | 3 | 3 | 30
214 | Process Mechanical | Booster Pump #3 Suction Butterfly Valve | Butterfly Valve | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good | Minor corrosion was observed |  | 3 | 3 | 30
215 | Process Mechanical | Booster Pump #3 Discharge Check Valve | Swing Check Valve | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
216 | Process Mechanical | Booster Pump #3 Discharge Butterfly Valve | Butterfly Valve | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good | Minor corrosion was observed |  | 3 | 3 | 30
217 | Process Mechanical | Pressure Relief Line Butterfly Valve 1 | Butterfly Valve | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good | Minor corrosion was observed |  | 3 | 3 | 30
218 | Process Mechanical | Pressure Relief Line Burrerfly Valve 2 | Butterfly Valve | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good | Minor corrosion was observed |  | 3 | 3 | 30
219 | Process Mechanical | Booster Pump #2 Suction Butterfly Valve | Butterfly Valve | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good | Minor corrosion was observed |  | 3 | 3 | 30
220 | Process Mechanical | Booster Pump # 2 Discharge Check Valve | Swing Check Valve | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
221 | Process Mechanical | Booster Pump #2 Discharge Butterfly Valve | Butterfly Valve | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Fair | Minor corrosion was observed at the connection |  | 3 | 3 | 30
222 | Process Mechanical | Bosster Pump #1 Suction Butterfly Valve | Butterfly Valve | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good | Minor corrosion was observed |  | 3 | 3 | 30
223 | Process Mechanical | Booster Pump #1 Discharge Check Valve | Swing Check Valve | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
224 | Process Mechanical | Booster Pump #1 Discharge Butterfly Valve | Butterfly Valve | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good | Minor corrosion was observed |  | 3 | 3 | 30
225 | Process Mechanical | Station Inflow Butterfly Valve | Inflow Butterfly Valve | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | Fair | The valve is still working but it is beyond its expected service life. |  | 3 | 3 | 30
226 | Process Mechanical | Pump 1 Inlet Butterfly Valve | Inlet Butterfly Valve No.1 | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | fair | The valve is still working but it is beyond its expected service life. |  | 3 | 3 | 30
227 | Process Mechanical | Pump 1 Check Valve | Check Valve No.1 | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | fair | The valve is still working but it is beyond its expected service life. |  | 3 | 3 | 30
228 | Process Mechanical | Pump 1 Outlet Butterfly Valve | Outlet Butterfly Valve No.1 | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | Fair | The valve is still working but it is beyond its expected service life. |  | 3 | 3 | 30
229 | Process Mechanical | Pump 2 Inlet Butterfly Valve | Inlet Butterfly Valve No.2 | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | Fair | The valve is still working but it is beyond its expected service life. |  | 3 | 3 | 30
230 | Process Mechanical | Pump 2 Check Valve | Check Valve No.2 | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | Fair | The valve is still working but it is beyond its expected service life. |  | 3 | 3 | 30
231 | Process Mechanical | Pump 2 Outlet Butterfly Valve | Outlet Butterfly Valve No.2 | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | Fair | The valve is still working but it is beyond its expected service life. |  | 3 | 3 | 30
232 | Process Mechanical | Pump 3 Inlet Butterfly Valve | Inlet Butterfly Valve | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | Fair | The valve is still working but it is beyond its expected service life. |  | 3 | 3 | 30
233 | Process Mechanical | Pump 3 Pressure Reducing Valve | Pressure Reducing Valve | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | Fair | The valve is still working but it is beyond its expected service life. |  | 3 | 3 | 30
234 | Process Mechanical | Pump 3 Outlet Butterfly Valve | Outlet Butterfly Valve | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | Fair | The valve is still working but it is beyond its expected service life. |  | 3 | 3 | 30
235 | Process Mechanical | Pump #7 Distrubtion Valve Actuator | Distrubtion Valve Actuator Pump #7 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
236 | Process Mechanical | Pump #7 Bypass Valve Actuator | Bypass Valve Actuator Pump #7 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
237 | Process Mechanical | Pump #7 Inlet Gate Valve | Inlet Gate Valve Pump #7 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
238 | Process Mechanical | Pump #7 Bypass Gate Valve | Bypass Gate Valve Pump #7 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
239 | Process Mechanical | Pump #7 Check Valve | Check Valve Pump #7 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2020 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
240 | Process Mechanical | Pump #7 Air Release Valve | Air Release Valve Pump #7 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
241 | Process Mechanical | Pump #6 Distribution Valve Actuator | Distrubtion Valve Actuator Pump #6 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
242 | Process Mechanical | Pump #6 Bypass Valve Actuator | Bypass Valve Actuator Pump #6 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
243 | Process Mechanical | Pump #5 Distrubtion Valve Actuator | Distrubtion Actuator Valve Pump #5 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
244 | Process Mechanical | Pump #5 Bypass Valve Actuator | Bypass Valve Actuator Pump #5 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
245 | Process Mechanical | Pump #6 Inlet Gate Valve | Inlet Gate Valve Pump #6 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good | Minor deterioration was observed on the valve. |  | 3 | 3 | 30
246 | Process Mechanical | Pump #6 Bypass Gate Valve | Bypass Gate Valve Pump #6 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good | Minor deterioration was observed on the valve. |  | 3 | 3 | 30
247 | Process Mechanical | Pump #6 Check Valve | Check Valve Pump #6 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Fair | Minor deterioration was observed on the valve. |  | 3 | 3 | 30
248 | Process Mechanical | Pump #6 Air Release Valve | Air Release Valve Pump #6 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
249 | Process Mechanical | Pump #5 Inlet Gate Valve | Inlet Gate Valve Pump #5 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
250 | Process Mechanical | Pump #5 Bypass Gate Valve | Bypass Gate Valve Pump #5 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
251 | Process Mechanical | Pump #5 Check Valve | Check Valve Pump #5 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2020 | Pump Room | 2 | Very Good |  |  | 1 | 1 | 30
252 | Process Mechanical | Pump#5 Air Release Valve | Air Release Valve Pump #5 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
253 | Process Mechanical | Treated Water Bypass Gate Valve | Treated Water Bypass Gate Valve - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
254 | Process Mechanical | Treated Tanker Fill Connection Check Valve | Treated Tanker Fill Connection Check Valve - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Fair | Minor deterioration on the surface of the pump | This valve and its 100 mm dia pipe is missing on the existing drawing. | 3 | 3 | 30
255 | Process Mechanical | Treated Tanker Fill Connection Gate Valve | Treated Tanker Fill Connection Gate Valve - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good | This valve and its associated piping is missing on the existing drawing. |  | 3 | 3 | 30
256 | Process Mechanical | Flow Meter Gate Valve #1 | Flow Meter Gate Valve #1 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
257 | Process Mechanical | Flow Meter Gate Valve #2 | Flow Meter Gate Valve #2 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Fair | Minor deteroiration on the turning stem and wheel of the valve |  | 3 | 3 | 30
258 | Process Mechanical | Booster Pump Suction Gate Valve #1 | Booster Pump Suction Gate Valve 1 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
259 | Process Mechanical | Treated Water Butterfly Valve #1 | Treated Water Butterfly Valve #1 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Fair | Minor corrosion was observed on the surface of the valve |  | 3 | 3 | 30
260 | Process Mechanical | Waste Line Air Release Valve | Waste Line Air Release Valve - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Very Good | This valve is missing on the existing drawing |  | 1 | 1 | 30
261 | Process Mechanical | Treated Water Air Release Valve | Treated Water Air Release Valve - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Very Good | The valve is missing on the as built drawing. |  | 1 | 1 | 30
262 | Process Mechanical | Poly #1 Storage Tank | Storage Tank, Poly #1 | Falconbridge Wells | Well Building | 2010 | Fluoride Room | 1 | Very Good |  |  | 1 | 1 | 30
263 | Process Mechanical | Poly #2 Storage Tank | Storage Tank, Poly #2 | Falconbridge Wells | Well Building | 2010 | Fluoride Room | 1 | Very Good |  |  | 1 | 1 | 30
264 | Process Mechanical | Process Piping | Process Piping - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Very Good |  |  | 1 | 1 | 30
265 | Process Mechanical | West Main Booster Pump Small Valves | Valves that are smaller than 100 mm dia - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Fair | Minor corrosion on the check valve was observed |  | 3 | 3 | 30
266 | Building Structural | Pump Room Concrete Foundation |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good |  |  | 2 | 2 | 60
267 | Building Structural | Pump Room Concrete Floor Slab |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good |  |  | 2 | 2 | 60
268 | Building Structural | Pump Room Masonry Blockwall |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good |  |  | 2 | 2 | 60
269 | Building Structural | Generator Room Concrete Foundation |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Generator Room | 2 | Good |  |  | 2 | 2 | 60
270 | Building Structural | Generator Room Concrete Floor Slab |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Generator Room | 2 | Good |  |  | 2 | 2 | 60
271 | Building Structural | Generator Room Masonry Blockwalls |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Generator Room | 2 | Good |  |  | 2 | 2 | 60
272 | Building Structural | Booster Station Wood Truss Roof |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Site | 3 | Good | Hidden under plywood ceiling |  | 2 | 2 | 60
273 | Building Architectural | Asphalt Shingle Roof |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Site | 3 | Poor | Shingles observed to be curling |  | 3 | 3 | 30
274 | Building Architectural | Exterior Brick Veneer |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Site | 2 | Good |  |  | 2 | 2 | 30
275 | Building Architectural | Pump Room Wall and Ceiling Paint |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 1 | Good |  |  | 2 | 2 | 30
276 | Building Architectural | Pump Room Floor Coating |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 1 | Good |  |  | 2 | 2 | 30
277 | Building Architectural | Pump Room Access Door (Double) |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 1 | Fair | Minor corrosion at bottom of door frame. Weathered exterior paint |  | 3 | 3 | 30
278 | Building Architectural | Generator Room Access Door (Double) |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Generator Room | 1 | Fair | Cc: Minor corrosion at bottom of door frame. Weathered exterior paint; door height need to be adjusted to address the code compliance issue associated with the diesel fuel tank |  | 3 | 3 | 30
279 | Building Architectural | Generator Room Wall and Ceiling Paint |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Generator Room | 1 | Good |  |  | 2 | 2 | 30
280 | Building Architectural | Generator Room Floor Coating |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Generator Room | 1 | Good |  |  | 2 | 2 | 30
281 | Building Architectural | Exterior Brick Veneer |  | Maley Booster Station | Booster Station | 1992 | Site | 2 | Fair | Localized erosion of brick. Grafitti typically noted |  | 3 | 3 | 30
282 | Building Architectural | Asphalt Shingle Roof |  | Maley Booster Station | Booster Station | 1992 | Site | 3 | Fair | Aging |  | 3 | 3 | 30
283 | Building Architectural | Pump Room Access Door (Double) |  | Maley Booster Station | Booster Station | 1992 | Pump Room | 1 | Fair | Weathered exterior paint |  | 3 | 3 | 30
284 | Building Architectural | Pump Room Access Door (Single) |  | Maley Booster Station | Booster Station | 1992 | Pump Room | 1 | Fair | Weathered exterior paint. Grafitti on exterior |  | 3 | 3 | 30
285 | Building Architectural | Pump Room Floor Coating |  | Maley Booster Station | Booster Station | 1992 | Pump Room | 1 | Good |  |  | 2 | 2 | 30
286 | Building Architectural | Pump Room Wall and Ceiling Paint |  | Maley Booster Station | Booster Station | 1992 | Pump Room | 1 | Good |  |  | 2 | 2 | 30
287 | Building Architectural | Generator Room Access Door (Double) |  | Maley Booster Station | Booster Station | 1992 | Generator Room | 1 | Fair | Weathered exterior paint; door height need to be adjusted to address the code compliance issue associated with the diesel fuel tank |  | 3 | 3 | 30
288 | Building Architectural | Generator Room Wall and Ceiling Paint |  | Maley Booster Station | Booster Station | 1992 | Generator Room | 1 | Good |  |  | 2 | 2 | 30
289 | Building Architectural | Generator Room Floor Coating |  | Maley Booster Station | Booster Station | 1992 | Generator Room | 1 | Good |  |  | 2 | 2 | 30
290 | Building Architectural | Generator Room Plywood Ceiling Covering |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Generator Room | 1 | Good |  |  | 2 | 2 | 30
291 | Building Architectural | Pump Room Plywood Ceiling Covering |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 1 | Good |  |  | 2 | 2 | 30
292 | Building Structural | Pump Room Concrete Foundation |  | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | Fair | Minor cracking/spalling at exterior corner |  | 3 | 3 | 60
293 | Building Structural | Pump Room Concrete Floor Slab |  | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | Fair | Minor hairline cracking throughout |  | 3 | 3 | 60
294 | Building Structural | Pump Room Masonry Blockwall |  | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | Good |  |  | 2 | 2 | 60
295 | Building Architectural | Generator Room Plywood Ceiling |  | Maley Booster Station | Booster Station | 1992 | Generator Room | 1 | Good |  |  | 2 | 2 | 30
296 | Building Architectural | Pump Room Plywood Covering |  | Maley Booster Station | Booster Station | 1992 | Pump Room | 1 | Good |  |  | 2 | 2 | 30
297 | Building Structural | Generator Room Concrete Foundation |  | Maley Booster Station | Booster Station | 1992 | Generator Room | 2 | Fair | Aging |  | 3 | 3 | 60
298 | Building Structural | Generator Room Concrete Floor Slab |  | Maley Booster Station | Booster Station | 1992 | Generator Room | 2 | Good |  |  | 2 | 2 | 60
299 | Building Structural | Generator Room Masonry Blockwall |  | Maley Booster Station | Booster Station | 1992 | Generator Room | 2 | Good | Containment wall for diesel tank have been removed. The surrounding area should be patched and repainted. |  | 2 | 2 | 60
300 | Building Structural | Booster Station Wood Truss Roof |  | Maley Booster Station | Booster Station | 1992 | Site | 3 | Good | Hidden under finishes |  | 2 | 2 | 60
301 | Building Structural | Pump Room Concrete Foundation |  | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good |  |  | 2 | 2 | 60
302 | Building Structural | Pump Room Masonry Blockwall |  | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good |  |  | 2 | 2 | 60
303 | Building Structural | Pump Room Precast Concrete Roof |  | Falconbridge Wells | Well Building | 2004 | Pump Room | 3 | Good |  |  | 2 | 2 | 60
304 | Building Structural | Generator Room Concrete Foundation |  | Falconbridge Wells | Well Building | 2004 | Generator Room | 2 | Good |  |  | 2 | 2 | 60
305 | Building Structural | Generator Room Concrete Floor Slab |  | Falconbridge Wells | Well Building | 2004 | Generator Room | 2 | Good |  |  | 2 | 2 | 60
306 | Building Structural | Generator Room Masonry Blockwall |  | Falconbridge Wells | Well Building | 2004 | Generator Room | 2 | Good |  |  | 2 | 2 | 60
307 | Building Structural | Generator Room Precast Concrete Roof |  | Falconbridge Wells | Well Building | 2004 | Generator Room | 3 | Good |  |  | 2 | 2 | 60
308 | Building Structural | Pump Room Concrete Floor Slab |  | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good | Gap observed between floor slab and wall footing |  | 2 | 2 | 60
309 | Building Structural | Chlorine Room Concrete Foundation |  | Falconbridge Wells | Well Building | 2004 | Chlorine Room | 2 | Good |  |  | 2 | 2 | 60
310 | Building Structural | Chlorine Room Concrete Floor Slab |  | Falconbridge Wells | Well Building | 2004 | Chlorine Room | 2 | Good |  |  | 2 | 2 | 60
311 | Building Structural | Chlorine Room Masonry Blockwall |  | Falconbridge Wells | Well Building | 2004 | Chlorine Room | 2 | Good |  |  | 2 | 2 | 60
312 | Building Structural | Chlorine Room Precast Concrete Roof |  | Falconbridge Wells | Well Building | 2004 | Chlorine Room | 3 | Good |  |  | 2 | 2 | 60
313 | Building Structural | Flouride Room Concrete Foundation |  | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 2 | Good |  |  | 2 | 2 | 60
314 | Building Structural | Flouride Room Concrete Floor Slab |  | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 2 |  |  |  | 3 | 3 | 60
315 | Building Structural | Flouride Room Masonry Blockwall |  | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 2 | Good |  |  | 2 | 2 | 60
316 | Building Structural | Flouride Room Precast Concrete Roof |  | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 3 | Good |  |  | 2 | 2 | 60
317 | Building Structural | Vestibule Concrete Foundation |  | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 2 | Good |  |  | 2 | 2 | 60
318 | Building Structural | Vestibule Concrete Floor Slab |  | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 2 | Good |  |  | 2 | 2 | 60
319 | Building Structural | Vestibule Masonry Blockwall |  | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 2 | Good |  |  | 2 | 2 | 60
320 | Building Structural | Vestibule Precast Concrete Roof |  | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 3 | Good |  |  | 2 | 2 | 60
321 | Building Architectural | Exterior Block Veneer |  | Falconbridge Wells | Well Building | 2004 | Site | 2 | Fair | Cracked block/mortar above generator door. Cracked/debonded block expansion joint sealant |  | 3 | 3 | 30
322 | Building Architectural | Roofing System |  | Falconbridge Wells | Well Building | 2004 | Site | 3 | Good |  |  | 2 | 2 | 30
323 | Building Architectural | Pump Room Access Door (Double) |  | Falconbridge Wells | Well Building | 2004 | Pump Room | 1 | fair | Corrosion at bottom of door frame, weathered exterior paint |  | 3 | 3 | 30
324 | Building Architectural | Pump Room Access Door (Single) |  | Falconbridge Wells | Well Building | 2004 | Pump Room | 1 | fair | Corrosion at bottom of door frame, weathered exterior paint |  | 3 | 3 | 30
325 | Building Architectural | Pump Room Access Door (Single) | Interior | Falconbridge Wells | Well Building | 2004 | Pump Room | 1 | Good | Door height need to be adjusted to address the code compliance issue associated with the diesel fuel tank |  | 3 | 3 | 30
326 | Building Architectural | Pump Room Wall Paint |  | Falconbridge Wells | Well Building | 2004 | Pump Room | 1 | good |  |  | 2 | 2 | 30
327 | Building Architectural | Generator Room Access Door (Double) |  | Falconbridge Wells | Well Building | 2004 | Generator Room | 1 | Fair | Corrosion at bottom of door frame, weathered exterior paint; Door height need to be adjusted to address the code compliance issue associated with the diesel fuel tank |  | 3 | 3 | 30
328 | Building Architectural | Generator Room Wall Paint |  | Falconbridge Wells | Well Building | 2004 | Generator Room | 1 | Good |  |  | 2 | 2 | 30
329 | Building Architectural | Pump Room Roof Hatch |  | Falconbridge Wells | Well Building | 2004 | Pump Room | 1 | Good |  |  | 2 | 2 | 30
330 | Building Architectural | Vestibule Access Door (Single) |  | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 1 | Fair | Corrosion at bottom of door frame, weathered exterrior paint |  | 3 | 3 | 30
331 | Building Architectural | Vestibule Wall Paint |  | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 1 | Good |  |  | 2 | 2 | 30
332 | Building Architectural | Chlorine Room Wall Paint |  | Falconbridge Wells | Well Building | 2004 | Chlorine Room | 1 | Good |  |  | 2 | 2 | 30
333 | Building Architectural | Chlorine Room Access Door (Single) |  | Falconbridge Wells | Well Building | 2004 | Chlorine Room | 1 | fair | Typical corrosion |  | 3 | 3 | 30
334 | Building Architectural | Chlorine Room Interior Window |  | Falconbridge Wells | Well Building | 2004 | Chlorine Room | 1 | Good |  |  | 2 | 2 | 30
335 | Building Architectural | Fluoride Room Interior Window |  | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 1 | Good |  |  | 2 | 2 | 30
336 | Building Architectural | Fluoride Room Wall Paint |  | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 1 | Good |  |  | 2 | 2 | 30
337 | Building Architectural | Fluoride Room Access Door (Single) |  | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 1 | fair | Typical corrosion |  | 3 | 3 | 30
338 | Building Architectural | Pump Room Lab Cainbets |  | Falconbridge Wells | Well Building | 2004 | Pump Room | 1 | Good |  |  | 2 | 2 | 30
339 | Site Works | Curbing around the building and parking lot | Curbing (approx. 40m total, surrounding the building and parking lot) | Sunrise Ridge Booster Station | Booster Station | 2005 | Site | 1 | Good | Minor cracking was found on the site |  | 3 | 3 | 20
340 | Site Works | Concrete Sidewalk | Concrete Sidewalk (approx. 5m by 1.5m) | Sunrise Ridge Booster Station | Booster Station | 2005 | Site | 1 | Good |  |  | 2 | 2 | 20
341 | Site Works | Bollard | 1 bollard for the protection of gas service line and meter | Sunrise Ridge Booster Station | Booster Station | 2005 | Site | 1 | Fair | Minor corrosion was observed |  | 3 | 3 | 20
342 | Site Works | Gas Piping | Gas distribution pipe at the southeast corner of the building (no information, assumed to exist, distance estimated by measuring the length from gas meter to gas heaters, total 19m) | Sunrise Ridge Booster Station | Booster Station | 2005 | Site | 1 | Fair | Surface corrosion was observed |  | 3 | 3 | 20
343 | Site Works | Sanitary Sewer Piping | Sanitary sewer piping (assumed to be PVC size 150mm approximately 5m long) | Sunrise Ridge Booster Station | Booster Station | 2005 | Site | 2 | Good |  |  | 2 | 2 | 20
344 | Site Works | Interlocking Pavement | Interlocking Pavement (appox. 180 sq. m, on driveway and surrounding the building) | Maley Booster Station | Booster Station | 1992 | Site | 1 | Fair | Cracking, separation, and depression were observed on the site |  | 3 | 3 | 20
345 | Site Works | Bollard | Gas meter bollard at the southeast corner of the building | Maley Booster Station | Booster Station | 1992 | Site | 1 | Good |  |  | 2 | 2 | 20
347 | Site Works | Gas Distribution Piping | Gas piping; distance estimated by measuring the length from gas meter to gas heaters, total 20m | Maley Booster Station | Booster Station | 1992 | Site | 2 | Good |  |  | 2 | 2 | 20
348 | Site Works | Sanitary Sewer | Sanitary sewer piping, 100mm, assumed to be pvc, approx. 25m | Maley Booster Station | Booster Station | 1992 | Site | 2 | Good |  |  | 2 | 2 | 20
349 | Site Works | Double Swing Gate (East Side) | One approx. 6m wide opening double swing at the east side, with barbed wire | Falconbridge Wells | Site | 2004 | Site | 1 | Fair | Corrosion of the gates and barbed wires was observed; Corrosion at bottom of gate |  | 3 | 3 | 20
350 | Site Works | Site Gates (Well 6) | One swing gate (approx. 4m wide opening double swing) | Falconbridge Wells | Site | 2004 | Well #6 | 1 | Good |  |  | 2 | 2 | 20
351 | Site Works | Site Gates (Well 5) | One swing gate (approx. 4m wide opening double swing) | Falconbridge Wells | Site | 2004 | Well #5 | 1 | Good |  |  | 2 | 2 | 20
352 | Site Works | Chain-link Fence | Chain-link fence with barbed wire (1.8m tall, approx. 70m long) | Falconbridge Wells | Site | 2004 | Site | 1 | Fair | The fence and barbed wire was broken and distorted at several locations. Corrosion on the fence and barbed wire was also observed. |  | 3 | 3 | 20
353 | Site Works | Chain-link Fence (Well #5) | Chain-link fence (2.4m tall, approx. 6m long) | Falconbridge Wells | Site | 2004 | Well #5 | 1 | Good |  |  | 2 | 2 | 20
354 | Site Works | Chain-link Fence (Well #6) | Chain-link fence (2.4m tall, approx. 6m long) | Falconbridge Wells | Site | 2004 | Well #6 | 1 | Good |  |  | 2 | 2 | 20
355 | Site Works | Concrete Sidewalk | Concrete sidewalk (approx. 80 sq. m) | Falconbridge Wells | Site | 2004 | Site | 1 | Good | Weed growing around concrete sidewalk patches |  | 3 | 3 | 20
356 | Site Works | Drain Pipe | 125mm PVC Drain Pipe (approx. 5.5m) | Falconbridge Wells | Site | 2004 | Site | 1 | Assume to be in good condition |  |  | 2 | 2 | 20
357 | Building Architectural | Louvre |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Generator Room | 1 | Good |  |  | 2 | 2 | 30
361 | Process Instrumentation | Pressure Gauges | Pressure Gauges (qty:7) | Falconbridge Wells | Well Building | 2015 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
362 | Process Electrical | Phase Loss Disconnect |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good |  |  | 2 | 2 | 25
363 |  | intake damper |  | Sunrise Ridge Booster Station |  | 2005 |  | 2 |  |  |  | 3 | 3 | 30
364 | Building Mechanical | Generator Dampers | 2 motorized dampers and louver | Sunrise Ridge Booster Station | Booster Station | 2005 | Generator Room | 2 | Good |  |  | 2 | 2 | 30
365 | Building Mechanical | Diesel Engine Silencer and Exhaust Flue | Diesel Engine Silencer and Exhaust Flue | Sunrise Ridge Booster Station | Booster Station | 2005 | Generator Room | 2 | Good |  |  | 2 | 2 | 30
367 | Building Mechanical | Diesel Fuel Tank | diesel tank and piping | Maley Booster Station | Booster Station | 2018 | Generator Room | 2 | Good | Cc: There was no containment for diesel fuel lines. TSSA requires all equipment containing or carrying fuel to be contained per CSA B139.1.1-15 Section 6.5.1.4. |  | 4 | 4 | 30
368 | Building Mechanical | Generator Room Heater | electrical unit heater | Maley Booster Station | Booster Station | 2018 | Generator Room | 1 | Good |  |  | 2 | 2 | 30
372 | Building Mechanical | Recircculation Damper | Recirc damper | Falconbridge Wells | Well Building | 2004 | Generator Room | 2 | Good |  |  | 2 | 2 | 30
373 | Building Mechanical | Unit Heater 1 | unit heater | Falconbridge Wells | Well Building | 2004 | Pump Room | 1 | Good |  |  | 2 | 2 | 30
374 | Building Mechanical | Unit Heater 2 | unit heater | Falconbridge Wells | Well Building | 2004 | Generator Room | 1 | Good |  |  | 2 | 2 | 30
375 | Building Mechanical | Unit Heater 3 | unit heater | Falconbridge Wells | Well Building | 2004 | Pump Room | 1 | Good |  |  | 2 | 2 | 30
377 | Building Mechanical | Pump Room Motorized Damper | louver and damper | Falconbridge Wells | Well Building | 2004 | Pump Room | 1 | Good |  |  | 2 | 2 | 30
378 | Building Mechanical | Emergency Shower | emergency shower, Safety Equipment - A 79 Safety Equipment | Falconbridge Wells | Well Building | 2004 |  | 1 | Good |  |  | 2 | 2 | 30
379 | Building Mechanical | Shower Area Unit Heater | unit heater | Falconbridge Wells | Well Building | 2004 |  | 1 | Good |  |  | 2 | 2 | 30
380 | Building Mechanical | Exhaust Fan 5 | exhaust fan | Falconbridge Wells | Well Building | 2004 |  | 2 | Good |  |  | 2 | 2 | 30
381 | Building Mechanical | Exhaust Fan 3 | exhaust fan | Falconbridge Wells | Well Building | 2004 | Chlorine Room | 2 | Good |  |  | 2 | 2 | 30
382 | Building Mechanical | Chlorine Room Unit Heater |  | Falconbridge Wells | Well Building | 2016 | Chlorine Room | 1 | Very Good |  |  | 1 | 1 | 30
383 | Building Mechanical | Chlorine Room Mororized damper | damper | Falconbridge Wells | Well Building | 2004 | Chlorine Room | 2 | Good |  |  | 2 | 2 | 30
384 | Building Mechanical | Fluoride Room Motorized Damper |  | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 2 | Good |  |  | 2 | 2 | 30
385 | Building Mechanical | Exhaust Fan 1 | exhaust fan | Falconbridge Wells | Well Building | 2004 | Generator Room | 2 | Good |  |  | 2 | 2 | 30
386 | Building Mechanical | Exhaust Fan 2 | exhaust fan | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
387 | Building Mechanical | Exhaust Fan 4 | exhaust fan | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 2 | Good |  |  | 2 | 2 | 30
388 | Building Mechanical | Themostatic Mixing Valve | Themostatic Mixing Valve for Emergency Eyewash | Falconbridge Wells | Well Building | 2004 |  | 1 | Good | Minor corrosion on the valve was observed. |  | 3 | 3 | 30
389 | Building Mechanical | Diesel Engine Silencer and Exhaust Flue |  | Falconbridge Wells | Well Building | 2004 | Generator Room | 2 | Good |  |  | 2 | 2 | 30
390 | Building Electrical | Smoke Detectors |  | Falconbridge Wells | Well Building | 2004 | Generator Room | 2 | Good |  |  | 2 | 2 | 25
392 | Building Mechanical | Unit Heater 2 | Unit Heater UH-1 | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 1 | Good |  |  | 2 | 2 | 30
395 | Building Electrical | Smoke Detectors | Smoke Detector | Sunrise Ridge Booster Station | Booster Station | 2023 |  | 2 | There were no smoke detectors installed at the station. A smoke detection system in accordance with the requirements of NFPA 820 and OBC is required. |  |  | 4 | 4 | 25
396 | Building Mechanical | Electric Heater | Electric Heater | Sunrise Ridge Booster Station | Booster Station | 2021 | Generator Room | 1 | Good |  |  | 2 | 2 | 30
397 | Building Architectural | Monorail Chain Hoist | Monorail Chain Hoist 0.5 Ton | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
399 | Building Mechanical | Generator Air Intake Damper | Intake motorized damper and louver | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
400 | Building Mechanical | Unit Heater 2 | Gas fired unit heater | Maley Booster Station | Booster Station | 1992 | Pump Room | 1 | Good |  |  | 2 | 2 | 30
401 | Building Mechanical | Chain Hoist | Chain Hoist (1 ton) | Maley Booster Station | Booster Station | 1992 | Pump Room | 1 | Good |  |  | 2 | 2 | 30
402 | Building Electrical | Smoke Detector |  | Maley Booster Station | Booster Station | 2023 |  | 2 | There were no smoke detectors installed at the station. A smoke detection system in accordance with the requirements of NFPA 820 and OBC is required. |  |  | 4 | 4 | 25
403 | Building Mechanical | Diesel Engine Silencer and Exhaust Flue |  | Maley Booster Station | Booster Station | 1992 | Generator Room | 2 | Good |  |  | 2 | 2 | 30
406 | Process Mechanical | Tank Gate Valve |  | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
407 | Process Mechanical | Deep Well #7 Pressure Reducing Valve | Pressure reducing valve | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
408 | Process Mechanical | Deep Well #6 Pressure Reducing Valve | Pressure reducing valve | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
409 | Process Mechanical | Deep Well #5 Pressure Reducing Valve | Pressure reducing valve | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
410 | Process Mechanical | Misc Small Valves | Approx. 33 small valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good |  |  | 2 | 2 | 30
411 | Process Instrumentation | Western Main Booster Pump Discharge Pressure Transmitter | Pressure transmitter | Falconbridge Wells | Well Building | 2018 | Pump Room | 1 | Aging | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 3 | 3 | 15
412 | Process Instrumentation | Control Valve Pump #5 Switch | Pump switch | Falconbridge Wells | Well Building | 2020 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
413 | Process Instrumentation | Control Valve Pump #6 Switch | Pump switch | Falconbridge Wells | Well Building | 2020 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
414 | Process Instrumentation | Control Valve Pump #7 Switch | Pump switch | Falconbridge Wells | Well Building | 2020 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
416 | Process Instrumentation | CL2 Detector #1 | Chlorine Detector | Falconbridge Wells | Well Building | 2015 | Pump Room | 1 | Aging, Wear and Tear | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 3 | 3 | 15
417 | Process Instrumentation | CL2 Detector #2 | Chlorine Detector | Falconbridge Wells | Well Building | 2015 | Pump Room | 1 | Aging, Wear and Tear | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 3 | 3 | 15
418 | Process Instrumentation | Discharge Pressure Transducer | Discharge Pressure Transducer | Maley Booster Station | Booster Station | 2020 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 2 | 2 | 15
420 | Site Works | Double Swing Gate 1 (South Side) | One approx. 4m wide opening double swing at the south side with barbed wire | Falconbridge Wells | Site | 2004 | Site | 1 | Fair | Corrosion of the gates and barbed wires was observed; Corrosion at bottom of gate |  | 3 | 3 | 20
421 | Site Works | Double Swing Gate 2 (South Side) | One approx. 4m wide opening double swing at the south side with barbed wire | Falconbridge Wells | Site | 2004 | Site | 1 | Fair | Corrosion of the gates and barbed wires was observed; Corrosion at bottom of gate |  | 3 | 3 | 20
423 | Site Works | Well #5 | Well #5, located outside the treatment building to the west, with a depth of appoximately 40m, 100mm dia | Falconbridge Wells | Site | 2004 | Site | 3 | Assumed to be in good condition |  |  | 2 | 2 | 20
424 | Site Works | Well #6 | Well #6, located to the south across Nickel Rim Road, with a depth of approximately 40m, 100mm dia | Falconbridge Wells | Site | 2004 | Site | 3 | Assumed to be in good condition |  |  | 2 | 2 | 20
425 | Site Works | Well #7 | Well #7, located underneath the building, with a depth of appoximately 40m, 100mm dia | Falconbridge Wells | Site | 2004 | Site | 3 | Assumed to be in good condition |  |  | 2 | 2 | 20
426 | Building Structural | Monorail Beam | 0.5 Ton | Sunrise Ridge Booster Station | Booster Station | 2005 | Site | 1 | Good |  |  | 2 | 2 | 60
427 | Building Electrical | Generator Room Emergency Light | battery unit | Falconbridge Wells | Well Building | 2004 | Generator Room | 2 | Good |  |  | 2 | 2 | 25
428 | Building Electrical | Generator Room Exit Sign | exit sign | Falconbridge Wells | Well Building | 2004 | Generator Room | 2 | Good |  |  | 2 | 2 | 25
429 | Building Electrical | Shower Exhuast Fan Control Panel | Control Panel | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good |  |  | 2 | 2 | 25
430 | Building Electrical | Generator Room Exit Sign | exit sign | Maley Booster Station | Booster Station | 2021 | Generator Room | 2 | Very Good |  |  | 1 | 1 | 25
432 | Process Electrical | Battery Charger | Battery Charger | Sunrise Ridge Booster Station | Booster Station | 2005 | Generator Room | 3 | Good |  |  | 2 | 2 | 25
433 | Process Electrical | Battery Charger | Battery Charger | Falconbridge Wells | Well Building | 2004 | Generator Room | 3 | Good |  |  | 2 | 2 | 25
434 | Process Instrumentation | Pump #5 Three Phase Pump Monitor/Protector | Three Phase Pump Monitor/Protector | Falconbridge Wells | Well Building | 2011 | Pump Room | 1 | Aging, Wear and Tear | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 3 | 3 | 15
435 | Process Instrumentation | Pump #6 Three Phase Pump Monitor/Protector | Three Phase Pump Monitor/Protector | Falconbridge Wells | Well Building | 2011 | Pump Room | 1 | Aging, Wear and Tear | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 3 | 3 | 15
436 | Process Instrumentation | Pump #7 Three Phase Pump Monitor/Protector | Three Phase Pump Monitor/Protector | Falconbridge Wells | Well Building | 2011 | Pump Room | 1 | Aging, Wear and Tear | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 3 | 3 | 15
437 | Process Instrumentation | Poly Tank Level Indicator | Poly Tank Level Indicator | Falconbridge Wells | Well Building | 2011 | Fluoride Room | 1 | Aging, Wear and Tear | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age |  | 3 | 3 | 15
438 | Process Instrumentation | Corrosion Inhibitor Calibration Unit | Corrosion Inhibitor Calibration Unit | Falconbridge Wells | Well Building | 2019 | Fluoride Room | 1 | Good |  |  | 2 | 2 | 15

## Sheet2
AssetID | VisualCondition | PoF
1 | 3 | 3
2 | 3 | 3
3 | 3 | 3
4 | 2 | 2
5 | 2 | 2
7 | 2 | 2
8 | 2 | 2
9 | 2 | 2
10 | 2 | 2
11 | 3 | 3
12 | 3 | 3
13 | 3 | 3
14 | 3 | 3
15 | 3 | 3
16 | 2 | 2
17 | 2 | 2
18 | 2 | 2
20 | 3 | 3
21 | 3 | 3
22 | 2 | 2
23 | 2 | 2
24 | 2 | 2
25 | 2 | 2
26 | 3 | 3
27 | 2 | 2
28 | 1 | 1
30 | 2 | 2
31 | 2 | 2
32 | 2 | 2
33 | 2 | 2
34 | 3 | 3
35 | 3 | 3
36 | 2 | 2
37 | 3 | 3
38 | 2 | 2
39 | 2 | 2
40 | 2 | 2
41 | 2 | 2
42 | 2 | 2
43 | 1 | 1
44 | 1 | 1
45 | 2 | 2
46 | 3 | 3
47 | 2 | 2
48 | 2 | 2
49 | 3 | 3
50 | 2 | 2
51 | 2 | 2
52 | 3 | 3
53 | 2 | 2
54 | 2 | 2
55 | 2 | 2
56 | 3 | 3
57 | 3 | 3
61 | 2 | 2
62 | 2 | 2
63 | 2 | 2
64 | 4 | 4
65 | 2 | 2
66 | 2 | 2
67 | 2 | 2
68 | 2 | 2
69 | 2 | 2
70 | 2 | 2
71 | 3 | 3
72 | 3 | 3
73 | 3 | 3
75 | 3 | 3
76 | 3 | 3
77 | 3 | 3
78 | 2 | 2
79 | 2 | 2
80 | 2 | 2
81 | 2 | 2
82 | 2 | 2
83 | 2 | 2
84 | 3 | 3
86 | 3 | 3
87 | 3 | 3
88 | 2 | 2
89 | 2 | 2
90 | 2 | 2
91 | 2 | 2
92 | 3 | 3
94 | 2 | 2
96 | 2 | 2
97 | 2 | 2
98 | 2 | 2
99 | 2 | 2
101 | 3 | 3
102 | 2 | 2
103 | 3 | 3
104 | 3 | 3
105 | 3 | 3
106 | 2 | 2
107 | 2 | 2
108 | 2 | 2
109 | 2 | 2
110 | 2 | 2
111 | 2 | 2
112 | 2 | 2
113 | 2 | 2
114 | 3 | 3
115 | 2 | 2
116 | 2 | 2
117 | 2 | 2
118 | 3 | 3
119 | 2 | 2
120 | 3 | 3
121 | 3 | 3
122 | 3 | 3
123 | 2 | 2
124 | 2 | 2
125 | 2 | 2
126 | 2 | 2
127 | 2 | 2
128 | 2 | 2
129 | 2 | 2
130 | 2 | 2
131 | 2 | 2
132 | 2 | 2
133 | 2 | 2
134 | 2 | 2
135 | 4 | 4
136 | 3 | 3
137 | 3 | 3
138 | 2 | 2
139 | 2 | 2
140 | 2 | 2
141 | 2 | 2
142 | 2 | 2
143 | 2 | 2
144 | 3 | 3
145 | 3 | 3
146 | 2 | 2
147 | 3 | 3
148 | 2 | 2
149 | 2 | 2
150 | 2 | 2
151 | 2 | 2
152 | 2 | 2
153 | 2 | 2
154 | 2 | 2
155 | 2 | 2
156 | 2 | 2
157 | 2 | 2
158 | 2 | 2
159 | 2 | 2
160 | 2 | 2
161 | 2 | 2
162 | 2 | 2
163 | 2 | 2
164 | 2 | 2
165 | 2 | 2
166 | 2 | 2
167 | 2 | 2
168 | 2 | 2
169 | 2 | 2
170 | 2 | 2
171 | 2 | 2
172 | 2 | 2
173 | 2 | 2
174 | 3 | 3
175 | 2 | 2
176 | 2 | 2
177 | 2 | 2
178 | 2 | 2
179 | 2 | 2
180 | 2 | 2
182 | 2 | 2
183 | 3 | 3
184 | 2 | 2
186 | 2 | 2
187 | 2 | 2
188 | 3 | 3
189 | 3 | 3
190 | 2 | 2
191 | 3 | 3
192 | 3 | 3
193 | 3 | 3
194 | 3 | 3
195 | 2 | 2
196 | 1 | 1
197 | 2 | 2
198 | 1 | 1
199 | 2 | 2
200 | 2 | 2
201 | 2 | 2
202 | 1 | 1
203 | 2 | 2
204 | 2 | 2
205 | 2 | 2
206 | 2 | 2
207 | 3 | 3
208 | 2 | 2
209 | 2 | 2
210 | 2 | 2
211 | 2 | 2
212 | 2 | 2
213 | 3 | 3
214 | 3 | 3
215 | 2 | 2
216 | 3 | 3
217 | 3 | 3
218 | 3 | 3
219 | 3 | 3
220 | 2 | 2
221 | 3 | 3
222 | 3 | 3
223 | 2 | 2
224 | 3 | 3
225 | 3 | 3
226 | 3 | 3
227 | 3 | 3
228 | 3 | 3
229 | 3 | 3
230 | 3 | 3
231 | 3 | 3
232 | 3 | 3
233 | 3 | 3
234 | 3 | 3
235 | 2 | 2
236 | 2 | 2
237 | 2 | 2
238 | 2 | 2
239 | 2 | 2
240 | 2 | 2
241 | 2 | 2
242 | 2 | 2
243 | 2 | 2
244 | 2 | 2
245 | 3 | 3
246 | 3 | 3
247 | 3 | 3
248 | 2 | 2
249 | 2 | 2
250 | 2 | 2
251 | 1 | 1
252 | 2 | 2
253 | 2 | 2
254 | 3 | 3
255 | 3 | 3
256 | 2 | 2
257 | 3 | 3
258 | 2 | 2
259 | 3 | 3
260 | 1 | 1
261 | 1 | 1
262 | 1 | 1
263 | 1 | 1
264 | 1 | 1
265 | 3 | 3
266 | 2 | 2
267 | 2 | 2
268 | 2 | 2
269 | 2 | 2
270 | 2 | 2
271 | 2 | 2
272 | 2 | 2
273 | 3 | 3
274 | 2 | 2
275 | 2 | 2
276 | 2 | 2
277 | 3 | 3
278 | 3 | 3
279 | 2 | 2
280 | 2 | 2
281 | 3 | 3
282 | 3 | 3
283 | 3 | 3
284 | 3 | 3
285 | 2 | 2
286 | 2 | 2
287 | 3 | 3
288 | 2 | 2
289 | 2 | 2
290 | 2 | 2
291 | 2 | 2
292 | 3 | 3
293 | 3 | 3
294 | 2 | 2
295 | 2 | 2
296 | 2 | 2
297 | 3 | 3
298 | 2 | 2
299 | 2 | 2
300 | 2 | 2
301 | 2 | 2
302 | 2 | 2
303 | 2 | 2
304 | 2 | 2
305 | 2 | 2
306 | 2 | 2
307 | 2 | 2
308 | 2 | 2
309 | 2 | 2
310 | 2 | 2
311 | 2 | 2
312 | 2 | 2
313 | 2 | 2
314 | 3 | 3
315 | 2 | 2
316 | 2 | 2
317 | 2 | 2
318 | 2 | 2
319 | 2 | 2
320 | 2 | 2
321 | 3 | 3
322 | 2 | 2
323 | 3 | 3
324 | 3 | 3
325 | 3 | 3
326 | 2 | 2
327 | 3 | 3
328 | 2 | 2
329 | 2 | 2
330 | 3 | 3
331 | 2 | 2
332 | 2 | 2
333 | 3 | 3
334 | 2 | 2
335 | 2 | 2
336 | 2 | 2
337 | 3 | 3
338 | 2 | 2
339 | 3 | 3
340 | 2 | 2
341 | 3 | 3
342 | 3 | 3
343 | 2 | 2
344 | 3 | 3
345 | 2 | 2
347 | 2 | 2
348 | 2 | 2
349 | 3 | 3
350 | 2 | 2
351 | 2 | 2
352 | 3 | 3
353 | 2 | 2
354 | 2 | 2
355 | 3 | 3
356 | 2 | 2
357 | 2 | 2
361 | 2 | 2
362 | 2 | 2
363 | 3 | 3
364 | 2 | 2
365 | 2 | 2
367 | 4 | 4
368 | 2 | 2
372 | 2 | 2
373 | 2 | 2
374 | 2 | 2
375 | 2 | 2
377 | 2 | 2
378 | 2 | 2
379 | 2 | 2
380 | 2 | 2
381 | 2 | 2
382 | 1 | 1
383 | 2 | 2
384 | 2 | 2
385 | 2 | 2
386 | 2 | 2
387 | 2 | 2
388 | 3 | 3
389 | 2 | 2
390 | 2 | 2
392 | 2 | 2
395 | 4 | 4
396 | 2 | 2
397 | 2 | 2
399 | 2 | 2
400 | 2 | 2
401 | 2 | 2
402 | 4 | 4
403 | 2 | 2
406 | 2 | 2
407 | 2 | 2
408 | 2 | 2
409 | 2 | 2
410 | 2 | 2
411 | 3 | 3
412 | 2 | 2
413 | 2 | 2
414 | 2 | 2
416 | 3 | 3
417 | 3 | 3
418 | 2 | 2
420 | 3 | 3
421 | 3 | 3
423 | 2 | 2
424 | 2 | 2
425 | 2 | 2
426 | 2 | 2
427 | 2 | 2
428 | 2 | 2
429 | 2 | 2
430 | 1 | 1
432 | 2 | 2
433 | 2 | 2
434 | 3 | 3
435 | 3 | 3
436 | 3 | 3
437 | 3 | 3
438 | 2 | 2

## comment
ParentID | AssetName | Comment Type | Comment
1 | Water Pump No.1 | Condition Comment | The asset was observed to be in fair condition. The pump is still working but it already exceeded its expected service life was observed.
2 | Water Pump No.2 | Condition Comment | The asset was observed to be in fair condition. The pump is still working but it already exceeded its expected service life was observed.
3 | High Flow Pump | Condition Comment | The asset was observed to be in fair condition. The pump is beyond its expected service life. Missing pump suggest that it has been sent for repair.
4 | Piping | Condition Comment | The asset was observed to be in good condition.
5 | Coupon Rack (To be removed) | Condition Comment | The asset was observed to be in good condition.
7 | Ethernet Swith | Condition Comment | The asset was observed to be in good condition.
8 | UPS | Condition Comment | The asset was observed to be in good condition.
9 | Standby Generator | Condition Comment | The asset was observed to be in good condition.
10 | Unit Heater 1 | Condition Comment | The asset was observed to be in good condition.
11 | Control System (Place holder) | Condition Comment | The asset was assumed to be in fair condition.
12 | Flow Recorder #1 | Condition Comment | The asset was observed to be in fair condition. Aging, wear and tear were noted.
13 | Flow Recorder #2 | Condition Comment | The asset was observed to be in fair condition. Aging, wear and tear were noted.
14 | Low Temperature Alarm Thermostat 1 | Condition Comment | The asset was observed to be in fair condition. Aging, wear and tear were noted.
15 | Asphalt Pavement | Condition Comment | The asset was observed to be in fair condition. Minor cracks were noted.
16 | Network Switch | Condition Comment | The asset was observed to be in good condition.
17 | Pump Room Monorail Crane Beam | Condition Comment | The asset was observed to be in good condition.
18 | PLC | Condition Comment | The asset was observed to be in good condition.
20 | MALEY BOOSTER | Condition Comment | The asset was assumed to be in fair condition.
21 | Safety Equipment (Placeholder) | Condition Comment | The asset was assumed to be in fair condition.
22 | Booster Pump #3 | Condition Comment | The asset was observed to be in good condition.
23 | Booster Pump #2 | Condition Comment | The asset was observed to be in good condition.
24 | Booster Pump #1 | Condition Comment | The asset was observed to be in good condition.
25 | Pressure Relief Valve | Condition Comment | The asset was observed to be in good condition.
26 | Pressure Relief Valve | Condition Comment | The asset was observed to be in fair condition. This valve was a component of the bigger 6" pressure relief valve.
27 | P-Trap Primer | Condition Comment | The asset was assumed in good condition.
28 | Process Piping | Condition Comment | The asset was observed to be in very good condition.
30 | Ethernet Switch | Condition Comment | The asset was observed to be in good condition.
31 | UPS | Condition Comment | The asset was observed to be in good condition.
32 | Standby Generator | Condition Comment | The asset was observed to be in good condition. The generator includes a sub-base fuel tank. No containment for the fuel was observed.
33 | Unit Heater 1 | Condition Comment | The asset was observed to be in good condition.
34 | Instrumentation & Control (Placeholder) | Condition Comment | The asset was assumed to be in fair condition.
35 | Asphalt Pavement | Condition Comment | The asset was observed to be in fair condition. Localized depressions in front of the building was observed.
36 | Pump Room 1/2 Ton Bridge Crane | Condition Comment | The asset was observed to be in good condition.
37 | SUNRISE BOOSTER | Condition Comment | The asset was assumed to be in fair condition.
38 | CL2 #1 Booster Pump | Condition Comment | The asset was observed to be in good condition.
39 | CL2 #2 Booster Pump | Condition Comment | The asset was observed to be in good condition.
40 | Deep Well #7 Pump | Condition Comment | The asset was observed to be in good condition.
41 | Deep Well #6 Pump | Condition Comment | The asset was observed to be in good condition.
42 | Deep Well #5 Pump | Condition Comment | The asset was observed to be in good condition.
43 | Poly #1 Pump | Condition Comment | The asset was observed to be in very good condition.
44 | Poly #2 Pump | Condition Comment | The asset was observed to be in very good condition.
45 | West Main Booster Pump | Condition Comment | The asset was observed to be in good condition.
46 | Pump #7 Control Vavle | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed on the surface of the valve.
47 | Pump #7 Distrubtion Valve | Condition Comment | The asset was observed to be in good condition.
48 | Pump #7 Bypass Valve | Condition Comment | The asset was observed to be in good condition.
49 | Pump #6 Control Valve | Condition Comment | The asset was observed to be in fair condition. Corrosion was observed on the top of the valve.
50 | Pump #6 Distrubtion Valve | Condition Comment | The asset was observed to be in good condition.
51 | Pump #6 Bypass Valve | Condition Comment | The asset was observed to be in good condition.
52 | Pump #5 Control Valve | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed on the pump.
53 | Pump #5 Distrubtion Valve | Condition Comment | The asset was observed to be in good condition.
54 | Pump #5 Bypass Valve | Condition Comment | The asset was observed to be in good condition.
55 | Tank Pressure Relief Valve | Condition Comment | The asset was observed to be in good condition.
56 | Waste Pressure Relief Valve | Condition Comment | The asset was observed to be in fair condition. Minor deterioration and corrosion service on the valve was observed.
57 | Piping & Valves (Placeholder) | Condition Comment | The asset was assumed to be in fair condition.
61 | Temperature Sensor | Condition Comment | The asset was observed to be in good condition.
62 | Ethernet Switch | Condition Comment | The asset was observed to be in good condition.
63 | Fiber Patch Panel | Condition Comment | The asset was observed to be in good condition.
64 | Fuel Tank | Condition Comment | The asset was observed to be in poor condition due to TSSA violation. TSSA requires all equipment containing or carrying fuel to be contained per csa b139.1.1-15 section 6.5.1.4.
64 | Fuel Tank | Code Concern Comment | There was no containment for diesel fuel lines. TSSA requires all equipment containing or carrying fuel to be contained per csa b139.1.1-15 section 6.5.1.4.
65 | Surge Tank | Condition Comment | The asset was observed to be in good condition.
66 | MODEM | Condition Comment | The asset was observed to be in good condition.
67 | PLC Panel 6812-4 | Condition Comment | The asset was observed to be in good condition.
68 | Operator Interface Terminal | Condition Comment | The asset was observed to be in good condition.
69 | Standby Generator | Condition Comment | The asset was observed to be in good condition.
70 | Intake Dampers for Generator Room | Condition Comment | The asset was observed to be in good condition.
71 | Automatic Transfer Switch | Condition Comment | The asset was observed to be in fair condition due to conde concern.
71 | Automatic Transfer Switch | Code Concern Comment | Shock and arc flash hazard as no arc flash label was installed. as per (ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the transfer switch which may require examination, adjustment, servicing, or maintenance while energized.
72 | FALCONBRIDGE WELLS (Placeholder) | Condition Comment | The asset was assumed to be in fair condition.
73 | pH-Chlorine Analyzer AIT-1791 | Condition Comment | The asset was observed to be in fair condition as it was aging.
75 | Colorimetric Chlorine Analyzer #1 | Condition Comment | The asset was observed to be in fair condition. Very good was observed.
76 | FALCONBRIDGE WELLS (Placeholder) | Condition Comment | The asset was assumed to be in fair condition.
77 | By Pass Turbidimeter | Condition Comment | The asset was observed to be in fair condition as it was aging.
78 | Ambient Chlorine Remote Sensor 1 | Condition Comment | The asset was observed to be in good condition.
79 | Ambient Chlorine Remote Sensor 2 | Condition Comment | The asset was observed to be in good condition.
80 | Thermostat | Condition Comment | The asset was observed to be in good condition.
81 | Chlorinator #1 | Condition Comment | The asset was observed to be in good condition.
82 | Chlorinator #2 | Condition Comment | The asset was observed to be in good condition.
83 | Gravel Parking Lots & Driveway | Condition Comment | The asset was observed to be in good condition. Weed and plant growing on gravel driveway and parking lot were observed.
84 | CL2 Scale | Condition Comment | The asset was observed to be in fair condition. Aging, wear and tear were noted.
86 | Poly Tank Level Transmitter | Condition Comment | The asset was observed to be in fair condition. Aging, wear and tear were noted.
87 | UPS | Condition Comment | The asset was observed to be in fair condition due to aging.
88 | PLC | Condition Comment | The asset was observed to be in good condition.
89 | Temperature Switch | Condition Comment | The asset was observed to be in good condition.
90 | Turbidity Analyzer | Condition Comment | The asset was observed to be in good condition.
91 | Weight Transmitter | Condition Comment | The asset was observed to be in good condition.
92 | FALCONBRIDGE WELLS | Condition Comment | The asset was assumed to be in fair condition.
94 | Eye Wash Station | Condition Comment | The asset was observed to be in good condition.
96 | Outdoor Lighting | Condition Comment | The asset was observed to be in good condition. To be replaced with LED fixtures in next upgrade.
97 | Hydro Meter | Condition Comment | The asset was observed to be in good condition.
98 | Indoor Lighting | Condition Comment | The asset was observed to be in good condition. To be replaced with LED fixtures in next upgrade.
99 | Emergency Lighting | Condition Comment | The asset was observed to be in good condition.
101 | MCC #1 | Condition Comment | The asset was observed to be in fair condition due to code concern. Shock and arc flash hazard as no arc flash label was installed. as per (ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the mcc which may require examination, adjustment, servicing, or maintenance while energized.
101 | MCC #1 | Code Concern Comment | Shock and arc flash hazard as no arc flash label was installed. as per (ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the mcc which may require examination, adjustment, servicing, or maintenance while energized.
102 | Power Meter | Condition Comment | The asset was observed to be in good condition.
103 | Main Circuit Breaker | Condition Comment | The asset was observed to be in fair condition due to code concern. Shock and arc flash hazard as no arc flash label was installed. as per (ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the mcc which may require examination, adjustment, servicing, or maintenance while energized.
103 | Main Circuit Breaker | Code Concern Comment | Shock and arc flash hazard as no arc flash label was installed. as per (ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the main circuit breaker which may require examination, adjustment, servicing, or maintenance while energized.
104 | Automatic Transfer Switch | Condition Comment | The asset was observed to be in fair condition due to code concern. Shock and arc flash hazard as no arc flash label was installed. as per (ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the mcc which may require examination, adjustment, servicing, or maintenance while energized.
104 | Automatic Transfer Switch | Code Concern Comment | Shock and arc flash hazard as no arc flash label was installed. as per (ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the auotmatic transfer switch which may require examination, adjustment, servicing, maintenance while energized.
105 | Surge Suppressor | Condition Comment | The asset was observed to be in fair condition due to code concern. Shock and arc flash hazard as no arc flash label was installed. as per (ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the mcc which may require examination, adjustment, servicing, or maintenance while energized.
105 | Surge Suppressor | Code Concern Comment | Shock and arc flash hazard as no arc flash label was installed. as per (ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the surge suppressor which may require examination, adjustment, servicing, or maintenance while energized.
106 | Pump #1 VFD | Condition Comment | The asset was observed to be in good condition.
107 | Pump #2 VFD | Condition Comment | The asset was observed to be in good condition.
108 | Pump #3 VFD | Condition Comment | The asset was observed to be in good condition.
109 | Lighting Panel A | Condition Comment | The asset was observed to be in good condition.
110 | Transformer | Condition Comment | The asset was observed to be in good condition.
111 | Outdoor Lighting | Condition Comment | The asset was observed to be in good condition. To be replaced with led fixtures in next upgrade was observed.
112 | Pump Room Lighting | Condition Comment | The asset was observed to be in good condition. To be replaced with led fixtures in next upgrade was observed.
113 | Generator Room Lighting | Condition Comment | The asset was observed to be in good condition. To be replaced with led fixtures in next upgrade was observed.
114 | Generator Transfer Panel | Condition Comment | The asset was observed to be in fair condition due to code concern. Shock and arc flash hazard as no arc flash label was installed. as per (ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the mcc which may require examination, adjustment, servicing, or maintenance while energized.
114 | Generator Transfer Panel | Code Concern Comment | Shock and arc flash hazard as no arc flash label was installed. as per (ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the generator transfer panel which may require examination, adjustment, servicing, or maintenance while energized.
115 | Lighting Transformer Disconnect Switch | Condition Comment | The asset was observed to be in good condition.
116 | Lighting Panel | Condition Comment | The asset was observed to be in good condition.
117 | Generator Room Heating Disconnect Switch | Condition Comment | The asset was observed to be in good condition.
118 | Splitter | Condition Comment | The asset was observed to be in fair condition due to code concern. Shock and arc flash hazard as no arc flash label was installed. as per (ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the mcc which may require examination, adjustment, servicing, or maintenance while energized.
118 | Splitter | Code Concern Comment | Shock and arc flash hazard as no arc flash label was installed. as per (ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the splitter which may require examination, adjustment, servicing, or maintenance while energized.
119 | Phase Loss Relay Disconnect Switch | Condition Comment | The asset was observed to be in good condition.
120 | Pump Control Panel | Condition Comment | The asset was observed to be in fair condition due to code concern. Shock and arc flash hazard as no arc flash label was installed. as per (ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the mcc which may require examination, adjustment, servicing, or maintenance while energized.
120 | Pump Control Panel | Code Concern Comment | Shock and arc flash hazard as no arc flash label was installed. as per (ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the pump control panel which may require examination, adjustment, servicing, or maintenance while energized.
121 | Incoming Power Enclosure | Condition Comment | The asset was observed to be in fair condition due to code concern. Shock and arc flash hazard as no arc flash label was installed. as per (ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the mcc which may require examination, adjustment, servicing, or maintenance while energized.
121 | Incoming Power Enclosure | Code Concern Comment | Shock and arc flash hazard as no arc flash label was installed. as per (ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the incoming power enclosure which may require examination, adjustment, servicing, or maintenance while energized.
122 | Main Disconnect Switch | Condition Comment | The asset was observed to be in fair condition due to code concern. Shock and arc flash hazard as no arc flash label was installed. as per (ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the mcc which may require examination, adjustment, servicing, or maintenance while energized.
122 | Main Disconnect Switch | Code Concern Comment | Shock and arc flash hazard as no arc flash label was installed. as per (ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the main disconnect switch which may require examination, adjustment, servicing, or maintenance while energized.
123 | Transformer | Condition Comment | The asset was observed to be in good condition.
124 | VFD#1 | Condition Comment | The asset was observed to be in good condition.
125 | VFD#2 | Condition Comment | The asset was observed to be in good condition.
126 | Duplex Pump Control Panel (CP-4000) | Condition Comment | The asset was observed to be in good condition.
127 | Load #1 Output Filter | Condition Comment | The asset was observed to be in good condition.
128 | Load #2 Output Filter | Condition Comment | The asset was observed to be in good condition.
129 | Load #2 Input Filter | Condition Comment | The asset was observed to be in good condition.
130 | Load #1 Input Filter | Condition Comment | The asset was observed to be in good condition.
131 | Pump #1 Disconnect Switch | Condition Comment | The asset was observed to be in good condition.
132 | Pump #2 Disconnect Switch | Condition Comment | The asset was observed to be in good condition.
133 | Pump Room Exit Sign | Condition Comment | The asset was observed to be in good condition.
134 | Battery Charger | Condition Comment | The asset was observed to be in good condition.
135 | Hydro Meter | Condition Comment | The asset was observed to be in poor condition.
136 | Hydro Meter | Condition Comment | The asset was observed to be in fair condition. Pump room outer wall and the enclosure for hydrometer was in fair condtion. The latch was corrode and discolouration on the panel was noted.
137 | Outdoor Lighting | Condition Comment | The asset was observed to be in fair condition. Photosensor for one of the fixtures did not work.
138 | Generator Room Lights | Condition Comment | The asset was observed to be in good condition. To be replaced with LED fixtures in next upgrade.
139 | Unit Heater #3 Disconnect Switch | Condition Comment | The asset was observed to be in good condition.
140 | T775 Control Panel | Condition Comment | The asset was observed to be in good condition.
141 | Generator Room Exhuast Fan Control Panel | Condition Comment | The asset was observed to be in good condition.
142 | Pump Room Lights | Condition Comment | The asset was observed to be in good condition. To be replaced with LED fixtures in next upgrade.
143 | Pump Room Exit Signs | Condition Comment | The asset was observed to be in good condition.
144 | MCC12-1A | Condition Comment | The asset was observed to be in fair condition due to code concern. Shock and arc flash hazard as no arc flash label was installed. as per (ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the mcc which may require examination, adjustment, servicing, or maintenance while energized.
144 | MCC12-1A | Code Concern Comment | Shock and arc flash hazard as no arc flash label was installed. as per (ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the mcc which may require examination, adjustment, servicing, or maintenance while energized.
145 | Main Circuit Breaker | Condition Comment | The asset was observed to be in fair condition due to code concern. Shock and arc flash hazard as no arc flash label was installed. as per (ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the mcc which may require examination, adjustment, servicing, or maintenance while energized.
145 | Main Circuit Breaker | Code Concern Comment | Shock and arc flash hazard as no arc flash label was installed. as per (ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the main circuit breaker which may require examination, adjustment, servicing, or maintenance while energized.
146 | Power Meter | Condition Comment | The asset was observed to be in good condition.
147 | Well Pump #5 Starter | Condition Comment | The asset was observed to be in fair condition due to code concern. Shock and arc flash hazard as no arc flash label was installed. as per (ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the mcc which may require examination, adjustment, servicing, or maintenance while energized.
147 | Well Pump #5 Starter | Code Concern Comment | Shock and arc flash hazard as no arc flash label was installed. as per (ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the starter which may require examination, adjustment, servicing, or maintenance while energized.
148 | Spare Starters | Condition Comment | The asset was observed to be in good condition.
149 | Booster Pump #2 Starter | Condition Comment | The asset was observed to be in good condition.
150 | Booster Pump #1 Starter | Condition Comment | The asset was observed to be in good condition.
151 | Western Main Booster Pump Starter | Condition Comment | The asset was observed to be in good condition.
152 | Well Pump #6 Starter | Condition Comment | The asset was observed to be in good condition.
153 | Well Pump #7 Starter | Condition Comment | The asset was observed to be in good condition.
154 | Transient Voltage Surge Suppressor | Condition Comment | The asset was observed to be in good condition.
155 | Pump #5 Deepwell Distribution Shutoff Motorized Valve Actuator | Condition Comment | The asset was observed to be in good condition.
156 | Pump #5 Deepwell Bypass Shutoff Motorized Valve Actuator | Condition Comment | The asset was observed to be in good condition.
157 | Pump #6 Distribution Shutoff Motorized Valve Actuator | Condition Comment | The asset was observed to be in good condition.
158 | Pump #6 Deepwell Bypass Shutoff Motorized Valve Actuator | Condition Comment | The asset was observed to be in good condition.
159 | Pump #7 Distribution Shutoff Motorized Valve Actuator | Condition Comment | The asset was observed to be in good condition.
160 | Pump #7 Deepwell Bypass Shutoff Motorized Valve Actuator | Condition Comment | The asset was observed to be in good condition.
161 | Chlorine Room Exhuast Fan Control Panel | Condition Comment | The asset was observed to be in good condition.
162 | Transformer | Condition Comment | The asset was observed to be in good condition.
163 | LP6811 Lighting Panel | Condition Comment | The asset was observed to be in good condition.
164 | Transformer | Condition Comment | The asset was observed to be in good condition.
165 | UP6812 Lighting Panel | Condition Comment | The asset was observed to be in good condition.
166 | Fluoride Room Exhuast Fan Control Panel | Condition Comment | The asset was observed to be in good condition.
167 | Process Room Exhuast Fan Control Panel | Condition Comment | The asset was observed to be in good condition.
168 | Fluoride Room Light | Condition Comment | The asset was observed to be in good condition. To be replaced with LED fixtures in next upgrade.
169 | Chlorine Room Light | Condition Comment | The asset was observed to be in good condition. To be replaced with LED fixtures in next upgrade.
170 | Fluoride Room Exit Sign | Condition Comment | The asset was observed to be in good condition.
171 | Chlorine Room Emergency Light | Condition Comment | The asset was observed to be in good condition.
172 | Pump Room Emergency Light | Condition Comment | The asset was observed to be in good condition.
173 | PLC Panel | Condition Comment | The asset was observed to be in good condition.
174 | T775 Control Panel | Condition Comment | The asset was observed to be in fair condition due to aging.
175 | Temperature Transmitter | Condition Comment | The asset was observed to be in good condition.
176 | Gauge Pressure Cerabar 1 | Condition Comment | The asset was observed to be in good condition.
177 | Pressure Gauge 1 | Condition Comment | The asset was observed to be in good condition.
178 | Gauge Pressure Cerabar 2 | Condition Comment | The asset was observed to be in good condition.
179 | Pressure Gauge 2 | Condition Comment | The asset was observed to be in good condition.
180 | Low Temp T-STAT | Condition Comment | The asset was observed to be in good condition.
182 | MODEM | Condition Comment | The asset was observed to be in good condition.
183 | PLC | Condition Comment | The asset was observed to be in fair condition due to aging.
184 | Thermostat | Condition Comment | The asset was observed to be in good condition.
186 | MODEM | Condition Comment | The asset was observed to be in good condition.
187 | Temperature Transmitter | Condition Comment | The asset was observed to be in good condition.
188 | Low Temperature Alarm Thermostat 2 | Condition Comment | The asset was observed to be in fair condition. Wear and tear were observed.
189 | Thermostat | Condition Comment | The asset was observed to be in fair condition. Wear and tear were observed.
190 | RPU Control Cabinet | Condition Comment | The asset was observed to be in good condition.
191 | Flow Switch | Condition Comment | The asset was observed to be in fair condition due to aging.
192 | MALEY BOOSTER ALTOMETER 2 | Condition Comment | The asset was assumed to be in fair condition.
193 | Flowmeter #1 | Condition Comment | The asset was observed to be in fair condition due to aging.
194 | MALEY BOOSTER Pressure Guage | Condition Comment | The asset was assumed to be in fair condition.
195 | Pressure Gauge 1 | Condition Comment | The asset was observed to be in good condition.
196 | Suction Pressure Transducer 1 | Condition Comment | The asset was observed to be in very good.
197 | Pressure Gauge 2 | Condition Comment | The asset was observed to be in good condition.
198 | Suction Pressure Transducer 2 | Condition Comment | The asset was observed to be in very good.
199 | Gas Detector Transmitter #2 | Condition Comment | The asset was observed to be in good condition.
200 | Gas Detector Transmitter #1 | Condition Comment | The asset was observed to be in good condition.
201 | Treated Water Turbidimeter | Condition Comment | The asset was observed to be in good condition.
202 | Colorimetric Chlorine Analyzer #2 | Condition Comment | The asset was observed to be in very good.
203 | pH-Chlorine Analyzer AIT-17942 | Condition Comment | The asset was observed to be in good condition.
204 | Free Chlorine Transmitter | Condition Comment | The asset was observed to be in good condition.
205 | Raw Water Gauge (qty:7) | Condition Comment | The asset was observed to be in good condition.
206 | Booster Pump #6 Flowmeter | Condition Comment | The asset was observed to be in good condition.
207 | Flowmeter #2 | Condition Comment | The asset was observed to be in fair condition due to aging.
208 | Booster Pump #5 Flowmeter | Condition Comment | The asset was observed to be in good condition. Condensation on the flowmeter was observed.
209 | Treated Water Flowmeter | Condition Comment | The asset was observed to be in good condition.
210 | Western Main Flowmeter | Condition Comment | The asset was observed to be in good condition.
211 | Booster Pump #7 Flowmeter | Condition Comment | The asset was observed to be in good condition.
212 | Treated Water Pressure Transmitter | Condition Comment | The asset was observed to be in good condition.
213 | Suction Header Butterfly Valve | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed.
214 | Booster Pump #3 Suction Butterfly Valve | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed.
215 | Booster Pump #3 Discharge Check Valve | Condition Comment | The asset was observed to be in good condition.
216 | Booster Pump #3 Discharge Butterfly Valve | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed.
217 | Pressure Relief Line Butterfly Valve 1 | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed.
218 | Pressure Relief Line Burrerfly Valve 2 | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed.
219 | Booster Pump #2 Suction Butterfly Valve | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed.
220 | Booster Pump # 2 Discharge Check Valve | Condition Comment | The asset was observed to be in good condition.
221 | Booster Pump #2 Discharge Butterfly Valve | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed at the connection.
222 | Bosster Pump #1 Suction Butterfly Valve | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed.
223 | Booster Pump #1 Discharge Check Valve | Condition Comment | The asset was observed to be in good condition.
224 | Booster Pump #1 Discharge Butterfly Valve | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed.
225 | Station Inflow Butterfly Valve | Condition Comment | The asset was observed to be in fair condition. The valve is still working but it is beyond its expected service life was observed.
226 | Pump 1 Inlet Butterfly Valve | Condition Comment | The asset was observed to be in fair condition. The valve is still working but it is beyond its expected service life was observed.
227 | Pump 1 Check Valve | Condition Comment | The asset was observed to be in fair condition. The valve is still working but it is beyond its expected service life was observed.
228 | Pump 1 Outlet Butterfly Valve | Condition Comment | The asset was observed to be in fair condition. The valve is still working but it is beyond its expected service life was observed.
229 | Pump 2 Inlet Butterfly Valve | Condition Comment | The asset was observed to be in fair condition. The valve is still working but it is beyond its expected service life was observed.
230 | Pump 2 Check Valve | Condition Comment | The asset was observed to be in fair condition. The valve is still working but it is beyond its expected service life was observed.
231 | Pump 2 Outlet Butterfly Valve | Condition Comment | The asset was observed to be in fair condition. The valve is still working but it is beyond its expected service life was observed.
232 | Pump 3 Inlet Butterfly Valve | Condition Comment | The asset was observed to be in fair condition. The valve is still working but it is beyond its expected service life was observed.
233 | Pump 3 Pressure Reducing Valve | Condition Comment | The asset was observed to be in fair condition. The valve is still working but it is beyond its expected service life was observed.
234 | Pump 3 Outlet Butterfly Valve | Condition Comment | The asset was observed to be in fair condition. The valve is still working but it is beyond its expected service life was observed.
235 | Pump #7 Distrubtion Valve Actuator | Condition Comment | The asset was observed to be in good condition.
236 | Pump #7 Bypass Valve Actuator | Condition Comment | The asset was observed to be in good condition.
237 | Pump #7 Inlet Gate Valve | Condition Comment | The asset was observed to be in good condition.
238 | Pump #7 Bypass Gate Valve | Condition Comment | The asset was observed to be in good condition.
239 | Pump #7 Check Valve | Condition Comment | The asset was observed to be in good condition.
240 | Pump #7 Air Release Valve | Condition Comment | The asset was observed to be in good condition.
241 | Pump #6 Distribution Valve Actuator | Condition Comment | The asset was observed to be in good condition.
242 | Pump #6 Bypass Valve Actuator | Condition Comment | The asset was observed to be in good condition.
243 | Pump #5 Distrubtion Valve Actuator | Condition Comment | The asset was observed to be in good condition.
244 | Pump #5 Bypass Valve Actuator | Condition Comment | The asset was observed to be in good condition.
245 | Pump #6 Inlet Gate Valve | Condition Comment | The asset was observed to be in fair condition. Minor deterioration was observed on the valve.
246 | Pump #6 Bypass Gate Valve | Condition Comment | The asset was observed to be in fair condition. Minor deterioration was observed on the valve.
247 | Pump #6 Check Valve | Condition Comment | The asset was observed to be in fair condition. Minor deterioration was observed on the valve.
248 | Pump #6 Air Release Valve | Condition Comment | The asset was observed to be in good condition.
249 | Pump #5 Inlet Gate Valve | Condition Comment | The asset was observed to be in good condition.
250 | Pump #5 Bypass Gate Valve | Condition Comment | The asset was observed to be in good condition.
251 | Pump #5 Check Valve | Condition Comment | The asset was observed to be in very good condition.
252 | Pump#5 Air Release Valve | Condition Comment | The asset was observed to be in good condition.
253 | Treated Water Bypass Gate Valve | Condition Comment | The asset was observed to be in good condition.
254 | Treated Tanker Fill Connection Check Valve | Condition Comment | The asset was assumed to be in fair condition. The valve and its 100 mm dia pipe was missing on the existing drawing.
255 | Treated Tanker Fill Connection Gate Valve | Condition Comment | The asset was observed to be in fair condition. This valve and its associated piping was missing on the existing drawing.
256 | Flow Meter Gate Valve #1 | Condition Comment | The asset was observed to be in good condition.
257 | Flow Meter Gate Valve #2 | Condition Comment | The asset was observed to be in fair condition. Minor deteroiration on the turning stem and wheel of the valve were observed.
258 | Booster Pump Suction Gate Valve #1 | Condition Comment | The asset was observed to be in good condition.
259 | Treated Water Butterfly Valve #1 | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed was observed on the surface of the valve.
260 | Waste Line Air Release Valve | Condition Comment | The asset was observed to be in very good condition; however this valve was missing on the existing drawing.
261 | Treated Water Air Release Valve | Condition Comment | The asset was observed to be in very good condition; however this valve was missing on the existing drawing.
262 | Poly #1 Storage Tank | Condition Comment | The asset was observed to be in very good condition.
263 | Poly #2 Storage Tank | Condition Comment | The asset was observed to be in very good condition.
264 | Process Piping | Condition Comment | The asset was observed to be in very good condition.
265 | West Main Booster Pump Small Valves | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed on the check valve.
266 | Pump Room Concrete Foundation | Condition Comment | The asset was observed to be in good condition.
267 | Pump Room Concrete Floor Slab | Condition Comment | The asset was observed to be in good condition.
268 | Pump Room Masonry Blockwall | Condition Comment | The asset was observed to be in good condition.
269 | Generator Room Concrete Foundation | Condition Comment | The asset was observed to be in good condition.
270 | Generator Room Concrete Floor Slab | Condition Comment | The asset was observed to be in good condition.
271 | Generator Room Masonry Blockwalls | Condition Comment | The asset was observed to be in good condition.
272 | Booster Station Wood Truss Roof | Condition Comment | The asset was observed to be in good condition. The asset was hidden under plywood ceiling.
273 | Asphalt Shingle Roof | Condition Comment | The asset was observed to be in fair condition. Poor and shingles was observed to be curling.
274 | Exterior Brick Veneer | Condition Comment | The asset was observed to be in good condition.
275 | Pump Room Wall and Ceiling Paint | Condition Comment | The asset was observed to be in good condition.
276 | Pump Room Floor Coating | Condition Comment | The asset was observed to be in good condition.
277 | Pump Room Access Door (Double) | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed at bottom of door frame. Weathered exterior paint was also noted.
278 | Generator Room Access Door (Double) | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed at bottom of door frame. Weathered exterior paint was also noted. Door height need to be adjusted to address the code compliance issue associated with the diesel fuel tank.
278 | Generator Room Access Door (Double) | Code Concern Comment | Minor corrosion at bottom of door frame. weathered exterior paint; Door height need to be adjusted to address the code compliance issue associated with the diesel fuel tank.
279 | Generator Room Wall and Ceiling Paint | Condition Comment | The asset was observed to be in good condition.
280 | Generator Room Floor Coating | Condition Comment | The asset was observed to be in good condition.
281 | Exterior Brick Veneer | Condition Comment | The asset was observed to be in fair condition. Localized erosion of brick was noted. Grafitti was noted.
282 | Asphalt Shingle Roof | Condition Comment | The asset was observed to be in fair condition due to aging.
283 | Pump Room Access Door (Double) | Condition Comment | The asset was observed to be in fair condition. Weathered exterior paint was observed.
284 | Pump Room Access Door (Single) | Condition Comment | The asset was observed to be in fair condition. Weathered exterior paint was noted. Grafitti on exterior was observed.
285 | Pump Room Floor Coating | Condition Comment | The asset was observed to be in good condition.
286 | Pump Room Wall and Ceiling Paint | Condition Comment | The asset was observed to be in good condition.
287 | Generator Room Access Door (Double) | Condition Comment | The asset was observed to be in fair condition. Weathered exterior paint; door height need to be adjusted to address the code compliance issue associated with the diesel fuel tank was observed.
288 | Generator Room Wall and Ceiling Paint | Condition Comment | The asset was observed to be in good condition.
289 | Generator Room Floor Coating | Condition Comment | The asset was observed to be in good condition.
290 | Generator Room Plywood Ceiling Covering | Condition Comment | The asset was observed to be in good condition.
291 | Pump Room Plywood Ceiling Covering | Condition Comment | The asset was observed to be in good condition.
292 | Pump Room Concrete Foundation | Condition Comment | The asset was observed to be in fair condition. Minor cracking/spalling at exterior corner was observed.
293 | Pump Room Concrete Floor Slab | Condition Comment | The asset was observed to be in fair condition. Minor hairline cracking was observed throughout.
294 | Pump Room Masonry Blockwall | Condition Comment | The asset was observed to be in good condition.
295 | Generator Room Plywood Ceiling | Condition Comment | The asset was observed to be in good condition.
296 | Pump Room Plywood Covering | Condition Comment | The asset was observed to be in good condition.
297 | Generator Room Concrete Foundation | Condition Comment | The asset was observed to be in fair condition due to aging.
298 | Generator Room Concrete Floor Slab | Condition Comment | The asset was observed to be in good condition.
299 | Generator Room Masonry Blockwall | Condition Comment | The asset was observed to be in good condition; however, containment wall for diesel tank have been removed and the surrounding area should be patched and repainted.
300 | Booster Station Wood Truss Roof | Condition Comment | The asset was observed to be in good condition. It was hidden under finishes was observed.
301 | Pump Room Concrete Foundation | Condition Comment | The asset was observed to be in good condition.
302 | Pump Room Masonry Blockwall | Condition Comment | The asset was observed to be in good condition.
303 | Pump Room Precast Concrete Roof | Condition Comment | The asset was observed to be in good condition.
304 | Generator Room Concrete Foundation | Condition Comment | The asset was observed to be in good condition.
305 | Generator Room Concrete Floor Slab | Condition Comment | The asset was observed to be in good condition.
306 | Generator Room Masonry Blockwall | Condition Comment | The asset was observed to be in good condition.
307 | Generator Room Precast Concrete Roof | Condition Comment | The asset was observed to be in good condition.
308 | Pump Room Concrete Floor Slab | Condition Comment | The asset was observed to be in good condition. Gap was observed between floor slab and wall footing.
309 | Chlorine Room Concrete Foundation | Condition Comment | The asset was observed to be in good condition.
310 | Chlorine Room Concrete Floor Slab | Condition Comment | The asset was observed to be in good condition.
311 | Chlorine Room Masonry Blockwall | Condition Comment | The asset was observed to be in good condition.
312 | Chlorine Room Precast Concrete Roof | Condition Comment | The asset was observed to be in good condition.
313 | Flouride Room Concrete Foundation | Condition Comment | The asset was observed to be in good condition.
314 | Flouride Room Concrete Floor Slab | Condition Comment | The asset was assumed to be in fair condition.
315 | Flouride Room Masonry Blockwall | Condition Comment | The asset was observed to be in good condition.
316 | Flouride Room Precast Concrete Roof | Condition Comment | The asset was observed to be in good condition.
317 | Vestibule Concrete Foundation | Condition Comment | The asset was observed to be in good condition.
318 | Vestibule Concrete Floor Slab | Condition Comment | The asset was observed to be in good condition.
319 | Vestibule Masonry Blockwall | Condition Comment | The asset was observed to be in good condition.
320 | Vestibule Precast Concrete Roof | Condition Comment | The asset was observed to be in good condition.
321 | Exterior Block Veneer | Condition Comment | The asset was observed to be in fair condition. Cracked block/mortar above generator door was noted. Cracked/debonded block expansion joint sealant was observed.
322 | Roofing System | Condition Comment | The asset was observed to be in good condition.
323 | Pump Room Access Door (Double) | Condition Comment | The asset was observed to be in fair condition. Corrosion was observed at bottom of door frame. Weathered exterior paint was noted.
324 | Pump Room Access Door (Single) | Condition Comment | The asset was observed to be in fair condition. Corrosion was observed at bottom of door frame. Weathered exterior paint was noted.
325 | Pump Room Access Door (Single) | Condition Comment | The asset was observed to be in fair condition. Door height need to be adjusted to address the code compliance issue associated with the diesel fuel tank.
326 | Pump Room Wall Paint | Condition Comment | The asset was observed to be in good condition.
327 | Generator Room Access Door (Double) | Condition Comment | The asset was observed to be in fair condition. Corrosion was observed at bottom of door frame. Weathered exterior paint was noted; Door height need to be adjusted to address the code compliance issue associated with the diesel fuel tank.
328 | Generator Room Wall Paint | Condition Comment | The asset was observed to be in good condition.
329 | Pump Room Roof Hatch | Condition Comment | The asset was observed to be in good condition.
330 | Vestibule Access Door (Single) | Condition Comment | The asset was observed to be in fair condition. Corrosion was observed at bottom of door frame. Weathered exterior paint was not noted.
331 | Vestibule Wall Paint | Condition Comment | The asset was observed to be in good condition.
332 | Chlorine Room Wall Paint | Condition Comment | The asset was observed to be in good condition.
333 | Chlorine Room Access Door (Single) | Condition Comment | The asset was observed to be in fair condition. Typical corrosion was observed.
334 | Chlorine Room Interior Window | Condition Comment | The asset was observed to be in good condition.
335 | Fluoride Room Interior Window | Condition Comment | The asset was observed to be in good condition.
336 | Fluoride Room Wall Paint | Condition Comment | The asset was observed to be in good condition.
337 | Fluoride Room Access Door (Single) | Condition Comment | The asset was observed to be in fair condition. Typical corrosion was observed.
338 | Pump Room Lab Cainbets | Condition Comment | The asset was observed to be in good condition.
339 | Curbing around the building and parking lot | Condition Comment | The asset was observed to be in fair condition. Minor cracking was observed on the site.
340 | Concrete Sidewalk | Condition Comment | The asset was observed to be in good condition.
341 | Bollard | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed
342 | Gas Piping | Condition Comment | The asset was observed to be in fair condition. Surface corrosion was observed.
343 | Sanitary Sewer Piping | Condition Comment | The asset was observed to be in good condition.
344 | Interlocking Pavement | Condition Comment | The asset was observed to be in fair condition. Cracking, separation, and depression were observed on the site.
345 | Bollard | Condition Comment | The asset was observed to be in good condition.
347 | Gas Distribution Piping | Condition Comment | The asset was observed to be in good condition.
348 | Sanitary Sewer | Condition Comment | The asset was observed to be in good condition.
349 | Double Swing Gate (East Side) | Condition Comment | The asset was observed to be in fair condition. Corrosion of the gates and barbed wires was observed. Corrosion at bottom of gate was observed.
350 | Site Gates (Well 6) | Condition Comment | The asset was observed to be in good condition.
351 | Site Gates (Well 5) | Condition Comment | The asset was observed to be in good condition.
352 | Chain-link Fence | Condition Comment | The asset was observed to be in fair condition. The fence and barbed wire was broken and distorted at several locations. Corrosion on the fence and barbed wire were also observed.
353 | Chain-link Fence (Well #5) | Condition Comment | The asset was observed to be in good condition.
354 | Chain-link Fence (Well #6) | Condition Comment | The asset was observed to be in good condition.
355 | Concrete Sidewalk | Condition Comment | The asset was observed to be in fair condition. Weed growing around concrete sidewalk patches was observed.
356 | Drain Pipe | Condition Comment | The asset was assumed to be in good condition.
357 | Louvre | Condition Comment | The asset was observed to be in good condition.
361 | Pressure Gauges | Condition Comment | The asset was observed to be in good condition.
362 | Phase Loss Disconnect | Condition Comment | The asset was observed to be in good condition.
363 | intake damper | Condition Comment | The asset was assumed to be in fair condition.
364 | Generator Dampers | Condition Comment | The asset was observed to be in good condition.
365 | Diesel Engine Silencer and Exhaust Flue | Condition Comment | The asset was observed to be in good condition.
367 | Diesel Fuel Tank | Condition Comment | The asset was observed to be in poor condition due to TSSA code concern. TSSA requires all equipment containing or carrying fuel to be contained per csa b139.1.1-15 section 6.5.1.4.
367 | Diesel Fuel Tank | Code Concern Comment | There was no containment for diesel fuel lines. TSSA requires all equipment containing or carrying fuel to be contained per csa b139.1.1-15 section 6.5.1.4.
368 | Generator Room Heater | Condition Comment | The asset was observed to be in good condition.
372 | Recircculation Damper | Condition Comment | The asset was observed to be in good condition.
373 | Unit Heater 1 | Condition Comment | The asset was observed to be in good condition.
374 | Unit Heater 2 | Condition Comment | The asset was observed to be in good condition.
375 | Unit Heater 3 | Condition Comment | The asset was observed to be in good condition.
377 | Pump Room Motorized Damper | Condition Comment | The asset was observed to be in good condition.
378 | Emergency Shower | Condition Comment | The asset was observed to be in good condition.
379 | Shower Area Unit Heater | Condition Comment | The asset was observed to be in good condition.
380 | Exhaust Fan 5 | Condition Comment | The asset was observed to be in good condition.
381 | Exhaust Fan 3 | Condition Comment | The asset was observed to be in good condition.
382 | Chlorine Room Unit Heater | Condition Comment | The asset was observed to be in very good condition.
383 | Chlorine Room Mororized damper | Condition Comment | The asset was observed to be in good condition.
384 | Fluoride Room Motorized Damper | Condition Comment | The asset was observed to be in good condition.
385 | Exhaust Fan 1 | Condition Comment | The asset was observed to be in good condition.
386 | Exhaust Fan 2 | Condition Comment | The asset was observed to be in good condition.
387 | Exhaust Fan 4 | Condition Comment | The asset was observed to be in good condition.
388 | Themostatic Mixing Valve | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed on the valve.
389 | Diesel Engine Silencer and Exhaust Flue | Condition Comment | The asset was observed to be in good condition.
390 | Smoke Detectors | Condition Comment | The asset was observed to be in good condition.
392 | Unit Heater 2 | Condition Comment | The asset was observed to be in good condition.
395 | Smoke Detectors | Condition Comment | The asset was observed to be in poor condition. There were no smoke detectors installed at the station. A smoke detection system in accordance with the requirements of nfpa 820 and obc is required.
396 | Electric Heater | Condition Comment | The asset was observed to be in good condition.
397 | Monorail Chain Hoist | Condition Comment | The asset was observed to be in good condition.
399 | Generator Air Intake Damper | Condition Comment | The asset was observed to be in good condition.
400 | Unit Heater 2 | Condition Comment | The asset was observed to be in good condition.
401 | Chain Hoist | Condition Comment | The asset was observed to be in good condition.
402 | Smoke Detector | Condition Comment | The asset was observed to be in poor condition. There were no smoke detectors installed at the station. A smoke detection system in accordance with the requirements of nfpa 820 and obc is required.
403 | Diesel Engine Silencer and Exhaust Flue | Condition Comment | The asset was observed to be in good condition.
406 | Tank Gate Valve | Condition Comment | The asset was observed to be in good condition.
407 | Deep Well #7 Pressure Reducing Valve | Condition Comment | The asset was observed to be in good condition.
408 | Deep Well #6 Pressure Reducing Valve | Condition Comment | The asset was observed to be in good condition.
409 | Deep Well #5 Pressure Reducing Valve | Condition Comment | The asset was observed to be in good condition.
410 | Misc Small Valves | Condition Comment | The asset was observed to be in good condition.
411 | Western Main Booster Pump Discharge Pressure Transmitter | Condition Comment | The asset was observed to be in fair condition due to aging.
412 | Control Valve Pump #5 Switch | Condition Comment | The asset was observed to be in good condition.
413 | Control Valve Pump #6 Switch | Condition Comment | The asset was observed to be in good condition.
414 | Control Valve Pump #7 Switch | Condition Comment | The asset was observed to be in good condition.
416 | CL2 Detector #1 | Condition Comment | The asset was observed to be in fair condition due to aging.
417 | CL2 Detector #2 | Condition Comment | The asset was observed to be in fair condition due to aging.
418 | Discharge Pressure Transducer | Condition Comment | The asset was observed to be in good condition.
420 | Double Swing Gate 1 (South Side) | Condition Comment | The asset was observed to be in fair condition. Corrosion of the gates and barbed wires was observed. Corrosion at bottom of gate was noted.
421 | Double Swing Gate 2 (South Side) | Condition Comment | The asset was observed to be in fair condition. Corrosion of the gates and barbed wires was observed. Corrosion at bottom of gate was noted.
423 | Well #5 | Condition Comment | The asset was assumed to be in good condition.
424 | Well #6 | Condition Comment | The asset was assumed to be in good condition.
425 | Well #7 | Condition Comment | The asset was assumed to be in good condition.
426 | Monorail Beam | Condition Comment | The asset was observed to be in good condition.
427 | Generator Room Emergency Light | Condition Comment | The asset was observed to be in good condition.
428 | Generator Room Exit Sign | Condition Comment | The asset was observed to be in good condition.
429 | Shower Exhuast Fan Control Panel | Condition Comment | The asset was observed to be in good condition.
430 | Generator Room Exit Sign | Condition Comment | The asset was observed to be in very good condition.
432 | Battery Charger | Condition Comment | The asset was observed to be in good condition.
433 | Battery Charger | Condition Comment | The asset was observed to be in good condition.
434 | Pump #5 Three Phase Pump Monitor/Protector | Condition Comment | The asset was observed to be in fair condition. Aging, wear and tear were observed.
435 | Pump #6 Three Phase Pump Monitor/Protector | Condition Comment | The asset was observed to be in fair condition. Aging, wear and tear were observed.
436 | Pump #7 Three Phase Pump Monitor/Protector | Condition Comment | The asset was observed to be in fair condition. Aging, wear and tear were observed.
437 | Poly Tank Level Indicator | Condition Comment | The asset was observed to be in fair condition. Aging, wear and tear were observed.
438 | Corrosion Inhibitor Calibration Unit | Condition Comment | The asset was observed to be in good condition.

## replacement
| 0 | 1 | 3 | 4
0 | ParentID | AssetName | Recurring | WorkFrequency
1 | 1 | Water Pump No.1 | True | 30
2 | 2 | Water Pump No.2 | True | 30
3 | 3 | High Flow Pump | True | 30
4 | 4 | Piping | True | 30
5 | 5 | Coupon Rack (To be removed) | True | 30
6 | 7 | Ethernet Swith | True | 15
7 | 8 | UPS | True | 15
8 | 9 | Standby Generator | True | 25
9 | 10 | Unit Heater 1 | True | 30
10 | 11 | Control System (Place holder) | True | 15
11 | 12 | Flow Recorder #1 | True | 15
12 | 13 | Flow Recorder #2 | True | 15
13 | 14 | Low Temperature Alarm Thermostat 1 | True | 15
14 | 15 | Asphalt Pavement | True | 20
15 | 16 | Network Switch | True | 15
16 | 17 | Pump Room Monorail Crane Beam | True | 60
17 | 18 | PLC | True | 15
18 | 20 | MALEY BOOSTER | True | 30
19 | 21 | Safety Equipment (Placeholder) | True | 30
20 | 22 | Booster Pump #3 | True | 30
21 | 23 | Booster Pump #2 | True | 30
22 | 24 | Booster Pump #1 | True | 30
23 | 25 | Pressure Relief Valve | True | 30
24 | 26 | Pressure Relief Valve | True | 30
25 | 27 | P-Trap Primer | True | 30
26 | 28 | Process Piping | True | 30
27 | 30 | Ethernet Switch | True | 15
28 | 31 | UPS | True | 15
29 | 32 | Standby Generator | True | 25
30 | 33 | Unit Heater 1 | True | 30
31 | 34 | Instrumentation & Control (Placeholder) | True | 15
32 | 35 | Asphalt Pavement | True | 20
33 | 36 | Pump Room 1/2 Ton Bridge Crane | True | 60
34 | 37 | SUNRISE BOOSTER | True | 30
35 | 38 | CL2 #1 Booster Pump | True | 30
36 | 39 | CL2 #2 Booster Pump | True | 30
37 | 40 | Deep Well #7 Pump | True | 30
38 | 41 | Deep Well #6 Pump | True | 30
39 | 42 | Deep Well #5 Pump | True | 30
40 | 43 | Poly #1 Pump | True | 30
41 | 44 | Poly #2 Pump | True | 30
42 | 45 | West Main Booster Pump | True | 30
43 | 46 | Pump #7 Control Vavle | True | 30
44 | 47 | Pump #7 Distrubtion Valve | True | 30
45 | 48 | Pump #7 Bypass Valve | True | 30
46 | 49 | Pump #6 Control Valve | True | 30
47 | 50 | Pump #6 Distrubtion Valve | True | 30
48 | 51 | Pump #6 Bypass Valve | True | 30
49 | 52 | Pump #5 Control Valve | True | 30
50 | 53 | Pump #5 Distrubtion Valve | True | 30
51 | 54 | Pump #5 Bypass Valve | True | 30
52 | 55 | Tank Pressure Relief Valve | True | 30
53 | 56 | Waste Pressure Relief Valve | True | 30
54 | 57 | Piping & Valves (Placeholder) | True | 30
55 | 61 | Temperature Sensor | True | 15
56 | 62 | Ethernet Switch | True | 15
57 | 63 | Fiber Patch Panel | True | 15
58 | 64 | Fuel Tank | True | 30
59 | 65 | Surge Tank | True | 30
60 | 66 | MODEM | True | 15
61 | 67 | PLC Panel 6812-4 | True | 15
62 | 68 | Operator Interface Terminal | True | 15
63 | 69 | Standby Generator | True | 25
64 | 70 | Intake Dampers for Generator Room | True | 30
65 | 71 | Automatic Transfer Switch | True | 25
66 | 72 | FALCONBRIDGE WELLS (Placeholder) | True | 15
67 | 73 | pH-Chlorine Analyzer AIT-1791 | True | 15
68 | 75 | Colorimetric Chlorine Analyzer #1 | True | 15
69 | 76 | FALCONBRIDGE WELLS (Placeholder) | True | 15
70 | 77 | By Pass Turbidimeter | True | 15
71 | 78 | Ambient Chlorine Remote Sensor 1 | True | 15
72 | 79 | Ambient Chlorine Remote Sensor 2 | True | 15
73 | 80 | Thermostat | True | 15
74 | 81 | Chlorinator #1 | True | 15
75 | 82 | Chlorinator #2 | True | 15
76 | 83 | Gravel Parking Lots & Driveway | True | 20
77 | 84 | CL2 Scale | True | 15
78 | 86 | Poly Tank Level Transmitter | True | 15
79 | 87 | UPS | True | 15
80 | 88 | PLC | True | 15
81 | 89 | Temperature Switch | True | 30
82 | 90 | Turbidity Analyzer | True | 15
83 | 91 | Weight Transmitter | True | 15
84 | 92 | FALCONBRIDGE WELLS | True | 30
85 | 94 | Eye Wash Station | True | 30
86 | 96 | Outdoor Lighting | True | 25
87 | 97 | Hydro Meter | True | 25
88 | 98 | Indoor Lighting | True | 25
89 | 99 | Emergency Lighting | True | 25
90 | 101 | MCC #1 | True | 25
91 | 102 | Power Meter | True | 25
92 | 103 | Main Circuit Breaker | True | 25
93 | 104 | Automatic Transfer Switch | True | 25
94 | 105 | Surge Suppressor | True | 25
95 | 106 | Pump #1 VFD | True | 25
96 | 107 | Pump #2 VFD | True | 25
97 | 108 | Pump #3 VFD | True | 25
98 | 109 | Lighting Panel A | True | 25
99 | 110 | Transformer | True | 25
100 | 111 | Outdoor Lighting | True | 25
101 | 112 | Pump Room Lighting | True | 25
102 | 113 | Generator Room Lighting | True | 25
103 | 114 | Generator Transfer Panel | True | 25
104 | 115 | Lighting Transformer Disconnect Switch | True | 25
105 | 116 | Lighting Panel | True | 25
106 | 117 | Generator Room Heating Disconnect Switch | True | 25
107 | 118 | Splitter | True | 25
108 | 119 | Phase Loss Relay Disconnect Switch | True | 25
109 | 120 | Pump Control Panel | True | 25
110 | 121 | Incoming Power Enclosure | True | 25
111 | 122 | Main Disconnect Switch | True | 25
112 | 123 | Transformer | True | 25
113 | 124 | VFD#1 | True | 25
114 | 125 | VFD#2 | True | 25
115 | 126 | Duplex Pump Control Panel (CP-4000) | True | 25
116 | 127 | Load #1 Output Filter | True | 25
117 | 128 | Load #2 Output Filter | True | 25
118 | 129 | Load #2 Input Filter | True | 25
119 | 130 | Load #1 Input Filter | True | 25
120 | 131 | Pump #1 Disconnect Switch | True | 25
121 | 132 | Pump #2 Disconnect Switch | True | 25
122 | 133 | Pump Room Exit Sign | True | 25
123 | 134 | Battery Charger | True | 25
124 | 135 | Hydro Meter | True | 25
125 | 136 | Hydro Meter | True | 25
126 | 137 | Outdoor Lighting | True | 25
127 | 138 | Generator Room Lights | True | 25
128 | 139 | Unit Heater #3 Disconnect Switch | True | 25
129 | 140 | T775 Control Panel | True | 25
130 | 141 | Generator Room Exhuast Fan Control Panel | True | 25
131 | 142 | Pump Room Lights | True | 25
132 | 143 | Pump Room Exit Signs | True | 25
133 | 144 | MCC12-1A | True | 25
134 | 145 | Main Circuit Breaker | True | 25
135 | 146 | Power Meter | True | 25
136 | 147 | Well Pump #5 Starter | True | 25
137 | 148 | Spare Starters | True | 25
138 | 149 | Booster Pump #2 Starter | True | 25
139 | 150 | Booster Pump #1 Starter | True | 25
140 | 151 | Western Main Booster Pump Starter | True | 25
141 | 152 | Well Pump #6 Starter | True | 25
142 | 153 | Well Pump #7 Starter | True | 25
143 | 154 | Transient Voltage Surge Suppressor | True | 25
144 | 155 | Pump #5 Deepwell Distribution Shutoff Motorized Valve Actuator | True | 25
145 | 156 | Pump #5 Deepwell Bypass Shutoff Motorized Valve Actuator | True | 25
146 | 157 | Pump #6 Distribution Shutoff Motorized Valve Actuator | True | 25
147 | 158 | Pump #6 Deepwell Bypass Shutoff Motorized Valve Actuator | True | 25
148 | 159 | Pump #7 Distribution Shutoff Motorized Valve Actuator | True | 25
149 | 160 | Pump #7 Deepwell Bypass Shutoff Motorized Valve Actuator | True | 25
150 | 161 | Chlorine Room Exhuast Fan Control Panel | True | 25
151 | 162 | Transformer | True | 25
152 | 163 | LP6811 Lighting Panel | True | 25
153 | 164 | Transformer | True | 25
154 | 165 | UP6812 Lighting Panel | True | 25
155 | 166 | Fluoride Room Exhuast Fan Control Panel | True | 25
156 | 167 | Process Room Exhuast Fan Control Panel | True | 25
157 | 168 | Fluoride Room Light | True | 25
158 | 169 | Chlorine Room Light | True | 25
159 | 170 | Fluoride Room Exit Sign | True | 25
160 | 171 | Chlorine Room Emergency Light | True | 25
161 | 172 | Pump Room Emergency Light | True | 25
162 | 173 | PLC Panel | True | 30
163 | 174 | T775 Control Panel | True | 25
164 | 175 | Temperature Transmitter | True | 15
165 | 176 | Gauge Pressure Cerabar 1 | True | 15
166 | 177 | Pressure Gauge 1 | True | 15
167 | 178 | Gauge Pressure Cerabar 2 | True | 15
168 | 179 | Pressure Gauge 2 | True | 15
169 | 180 | Low Temp T-STAT | True | 15
170 | 182 | MODEM | True | 15
171 | 183 | PLC | True | 15
172 | 184 | Thermostat | True | 15
173 | 186 | MODEM | True | 15
174 | 187 | Temperature Transmitter | True | 15
175 | 188 | Low Temperature Alarm Thermostat 2 | True | 15
176 | 189 | Thermostat | True | 15
177 | 190 | RPU Control Cabinet | True | 15
178 | 191 | Flow Switch | True | 15
179 | 192 | MALEY BOOSTER ALTOMETER 2 | True | 30
180 | 193 | Flowmeter #1 | True | 15
181 | 194 | MALEY BOOSTER Pressure Guage | True | 30
182 | 195 | Pressure Gauge 1 | True | 15
183 | 196 | Suction Pressure Transducer 1 | True | 15
184 | 197 | Pressure Gauge 2 | True | 15
185 | 198 | Suction Pressure Transducer 2 | True | 15
186 | 199 | Gas Detector Transmitter #2 | True | 15
187 | 200 | Gas Detector Transmitter #1 | True | 15
188 | 201 | Treated Water Turbidimeter | True | 15
189 | 202 | Colorimetric Chlorine Analyzer #2 | True | 15
190 | 203 | pH-Chlorine Analyzer AIT-17942 | True | 15
191 | 204 | Free Chlorine Transmitter | True | 15
192 | 205 | Raw Water Gauge (qty:7) | True | 15
193 | 206 | Booster Pump #6 Flowmeter | True | 15
194 | 207 | Flowmeter #2 | True | 15
195 | 208 | Booster Pump #5 Flowmeter | True | 15
196 | 209 | Treated Water Flowmeter | True | 15
197 | 210 | Western Main Flowmeter | True | 15
198 | 211 | Booster Pump #7 Flowmeter | True | 15
199 | 212 | Treated Water Pressure Transmitter | True | 15
200 | 213 | Suction Header Butterfly Valve | True | 30
201 | 214 | Booster Pump #3 Suction Butterfly Valve | True | 30
202 | 215 | Booster Pump #3 Discharge Check Valve | True | 30
203 | 216 | Booster Pump #3 Discharge Butterfly Valve | True | 30
204 | 217 | Pressure Relief Line Butterfly Valve 1 | True | 30
205 | 218 | Pressure Relief Line Burrerfly Valve 2 | True | 30
206 | 219 | Booster Pump #2 Suction Butterfly Valve | True | 30
207 | 220 | Booster Pump # 2 Discharge Check Valve | True | 30
208 | 221 | Booster Pump #2 Discharge Butterfly Valve | True | 30
209 | 222 | Bosster Pump #1 Suction Butterfly Valve | True | 30
210 | 223 | Booster Pump #1 Discharge Check Valve | True | 30
211 | 224 | Booster Pump #1 Discharge Butterfly Valve | True | 30
212 | 225 | Station Inflow Butterfly Valve | True | 30
213 | 226 | Pump 1 Inlet Butterfly Valve | True | 30
214 | 227 | Pump 1 Check Valve | True | 30
215 | 228 | Pump 1 Outlet Butterfly Valve | True | 30
216 | 229 | Pump 2 Inlet Butterfly Valve | True | 30
217 | 230 | Pump 2 Check Valve | True | 30
218 | 231 | Pump 2 Outlet Butterfly Valve | True | 30
219 | 232 | Pump 3 Inlet Butterfly Valve | True | 30
220 | 233 | Pump 3 Pressure Reducing Valve | True | 30
221 | 234 | Pump 3 Outlet Butterfly Valve | True | 30
222 | 235 | Pump #7 Distrubtion Valve Actuator | True | 30
223 | 236 | Pump #7 Bypass Valve Actuator | True | 30
224 | 237 | Pump #7 Inlet Gate Valve | True | 30
225 | 238 | Pump #7 Bypass Gate Valve | True | 30
226 | 239 | Pump #7 Check Valve | True | 30
227 | 240 | Pump #7 Air Release Valve | True | 30
228 | 241 | Pump #6 Distribution Valve Actuator | True | 30
229 | 242 | Pump #6 Bypass Valve Actuator | True | 30
230 | 243 | Pump #5 Distrubtion Valve Actuator | True | 30
231 | 244 | Pump #5 Bypass Valve Actuator | True | 30
232 | 245 | Pump #6 Inlet Gate Valve | True | 30
233 | 246 | Pump #6 Bypass Gate Valve | True | 30
234 | 247 | Pump #6 Check Valve | True | 30
235 | 248 | Pump #6 Air Release Valve | True | 30
236 | 249 | Pump #5 Inlet Gate Valve | True | 30
237 | 250 | Pump #5 Bypass Gate Valve | True | 30
238 | 251 | Pump #5 Check Valve | True | 30
239 | 252 | Pump#5 Air Release Valve | True | 30
240 | 253 | Treated Water Bypass Gate Valve | True | 30
241 | 254 | Treated Tanker Fill Connection Check Valve | True | 30
242 | 255 | Treated Tanker Fill Connection Gate Valve | True | 30
243 | 256 | Flow Meter Gate Valve #1 | True | 30
244 | 257 | Flow Meter Gate Valve #2 | True | 30
245 | 258 | Booster Pump Suction Gate Valve #1 | True | 30
246 | 259 | Treated Water Butterfly Valve #1 | True | 30
247 | 260 | Waste Line Air Release Valve | True | 30
248 | 261 | Treated Water Air Release Valve | True | 30
249 | 262 | Poly #1 Storage Tank | True | 30
250 | 263 | Poly #2 Storage Tank | True | 30
251 | 264 | Process Piping | True | 30
252 | 265 | West Main Booster Pump Small Valves | True | 30
253 | 266 | Pump Room Concrete Foundation | True | 60
254 | 267 | Pump Room Concrete Floor Slab | True | 60
255 | 268 | Pump Room Masonry Blockwall | True | 60
256 | 269 | Generator Room Concrete Foundation | True | 60
257 | 270 | Generator Room Concrete Floor Slab | True | 60
258 | 271 | Generator Room Masonry Blockwalls | True | 60
259 | 272 | Booster Station Wood Truss Roof | True | 60
260 | 273 | Asphalt Shingle Roof | True | 30
261 | 274 | Exterior Brick Veneer | True | 30
262 | 275 | Pump Room Wall and Ceiling Paint | True | 30
263 | 276 | Pump Room Floor Coating | True | 30
264 | 277 | Pump Room Access Door (Double) | True | 30
265 | 278 | Generator Room Access Door (Double) | True | 30
266 | 279 | Generator Room Wall and Ceiling Paint | True | 30
267 | 280 | Generator Room Floor Coating | True | 30
268 | 281 | Exterior Brick Veneer | True | 30
269 | 282 | Asphalt Shingle Roof | True | 30
270 | 283 | Pump Room Access Door (Double) | True | 30
271 | 284 | Pump Room Access Door (Single) | True | 30
272 | 285 | Pump Room Floor Coating | True | 30
273 | 286 | Pump Room Wall and Ceiling Paint | True | 30
274 | 287 | Generator Room Access Door (Double) | True | 30
275 | 288 | Generator Room Wall and Ceiling Paint | True | 30
276 | 289 | Generator Room Floor Coating | True | 30
277 | 290 | Generator Room Plywood Ceiling Covering | True | 30
278 | 291 | Pump Room Plywood Ceiling Covering | True | 30
279 | 292 | Pump Room Concrete Foundation | True | 60
280 | 293 | Pump Room Concrete Floor Slab | True | 60
281 | 294 | Pump Room Masonry Blockwall | True | 60
282 | 295 | Generator Room Plywood Ceiling | True | 30
283 | 296 | Pump Room Plywood Covering | True | 30
284 | 297 | Generator Room Concrete Foundation | True | 60
285 | 298 | Generator Room Concrete Floor Slab | True | 60
286 | 299 | Generator Room Masonry Blockwall | True | 60
287 | 300 | Booster Station Wood Truss Roof | True | 60
288 | 301 | Pump Room Concrete Foundation | True | 60
289 | 302 | Pump Room Masonry Blockwall | True | 60
290 | 303 | Pump Room Precast Concrete Roof | True | 60
291 | 304 | Generator Room Concrete Foundation | True | 60
292 | 305 | Generator Room Concrete Floor Slab | True | 60
293 | 306 | Generator Room Masonry Blockwall | True | 60
294 | 307 | Generator Room Precast Concrete Roof | True | 60
295 | 308 | Pump Room Concrete Floor Slab | True | 60
296 | 309 | Chlorine Room Concrete Foundation | True | 60
297 | 310 | Chlorine Room Concrete Floor Slab | True | 60
298 | 311 | Chlorine Room Masonry Blockwall | True | 60
299 | 312 | Chlorine Room Precast Concrete Roof | True | 60
300 | 313 | Flouride Room Concrete Foundation | True | 60
301 | 314 | Flouride Room Concrete Floor Slab | True | 60
302 | 315 | Flouride Room Masonry Blockwall | True | 60
303 | 316 | Flouride Room Precast Concrete Roof | True | 60
304 | 317 | Vestibule Concrete Foundation | True | 60
305 | 318 | Vestibule Concrete Floor Slab | True | 60
306 | 319 | Vestibule Masonry Blockwall | True | 60
307 | 320 | Vestibule Precast Concrete Roof | True | 60
308 | 321 | Exterior Block Veneer | True | 30
309 | 322 | Roofing System | True | 30
310 | 323 | Pump Room Access Door (Double) | True | 30
311 | 324 | Pump Room Access Door (Single) | True | 30
312 | 325 | Pump Room Access Door (Single) | True | 30
313 | 326 | Pump Room Wall Paint | True | 30
314 | 327 | Generator Room Access Door (Double) | True | 30
315 | 328 | Generator Room Wall Paint | True | 30
316 | 329 | Pump Room Roof Hatch | True | 30
317 | 330 | Vestibule Access Door (Single) | True | 30
318 | 331 | Vestibule Wall Paint | True | 30
319 | 332 | Chlorine Room Wall Paint | True | 30
320 | 333 | Chlorine Room Access Door (Single) | True | 30
321 | 334 | Chlorine Room Interior Window | True | 30
322 | 335 | Fluoride Room Interior Window | True | 30
323 | 336 | Fluoride Room Wall Paint | True | 30
324 | 337 | Fluoride Room Access Door (Single) | True | 30
325 | 338 | Pump Room Lab Cainbets | True | 30
326 | 339 | Curbing around the building and parking lot | True | 20
327 | 340 | Concrete Sidewalk | True | 20
328 | 341 | Bollard | True | 20
329 | 342 | Gas Piping | True | 20
330 | 343 | Sanitary Sewer Piping | True | 20
331 | 344 | Interlocking Pavement | True | 20
332 | 345 | Bollard | True | 20
333 | 347 | Gas Distribution Piping | True | 20
334 | 348 | Sanitary Sewer | True | 20
335 | 349 | Double Swing Gate (East Side) | True | 20
336 | 350 | Site Gates (Well 6) | True | 20
337 | 351 | Site Gates (Well 5) | True | 20
338 | 352 | Chain-link Fence | True | 20
339 | 353 | Chain-link Fence (Well #5) | True | 20
340 | 354 | Chain-link Fence (Well #6) | True | 20
341 | 355 | Concrete Sidewalk | True | 20
342 | 356 | Drain Pipe | True | 20
343 | 357 | Louvre | True | 30
344 | 361 | Pressure Gauges | True | 15
345 | 362 | Phase Loss Disconnect | True | 25
346 | 363 | intake damper | True | 30
347 | 364 | Generator Dampers | True | 30
348 | 365 | Diesel Engine Silencer and Exhaust Flue | True | 30
349 | 367 | Diesel Fuel Tank | True | 30
350 | 368 | Generator Room Heater | True | 30
351 | 372 | Recircculation Damper | True | 30
352 | 373 | Unit Heater 1 | True | 30
353 | 374 | Unit Heater 2 | True | 30
354 | 375 | Unit Heater 3 | True | 30
355 | 377 | Pump Room Motorized Damper | True | 30
356 | 378 | Emergency Shower | True | 30
357 | 379 | Shower Area Unit Heater | True | 30
358 | 380 | Exhaust Fan 5 | True | 30
359 | 381 | Exhaust Fan 3 | True | 30
360 | 382 | Chlorine Room Unit Heater | True | 30
361 | 383 | Chlorine Room Mororized damper | True | 30
362 | 384 | Fluoride Room Motorized Damper | True | 30
363 | 385 | Exhaust Fan 1 | True | 30
364 | 386 | Exhaust Fan 2 | True | 30
365 | 387 | Exhaust Fan 4 | True | 30
366 | 388 | Themostatic Mixing Valve | True | 30
367 | 389 | Diesel Engine Silencer and Exhaust Flue | True | 30
368 | 390 | Smoke Detectors | True | 25
369 | 392 | Unit Heater 2 | True | 30
370 | 395 | Smoke Detectors | True | 25
371 | 396 | Electric Heater | True | 30
372 | 397 | Monorail Chain Hoist | True | 30
373 | 399 | Generator Air Intake Damper | True | 30
374 | 400 | Unit Heater 2 | True | 30
375 | 401 | Chain Hoist | True | 30
376 | 402 | Smoke Detector | True | 25
377 | 403 | Diesel Engine Silencer and Exhaust Flue | True | 30
378 | 406 | Tank Gate Valve | True | 30
379 | 407 | Deep Well #7 Pressure Reducing Valve | True | 30
380 | 408 | Deep Well #6 Pressure Reducing Valve | True | 30
381 | 409 | Deep Well #5 Pressure Reducing Valve | True | 30
382 | 410 | Misc Small Valves | True | 30
383 | 411 | Western Main Booster Pump Discharge Pressure Transmitter | True | 15
384 | 412 | Control Valve Pump #5 Switch | True | 15
385 | 413 | Control Valve Pump #6 Switch | True | 15
386 | 414 | Control Valve Pump #7 Switch | True | 15
387 | 416 | CL2 Detector #1 | True | 15
388 | 417 | CL2 Detector #2 | True | 15
389 | 418 | Discharge Pressure Transducer | True | 15
390 | 420 | Double Swing Gate 1 (South Side) | True | 20
391 | 421 | Double Swing Gate 2 (South Side) | True | 20
392 | 423 | Well #5 | True | 20
393 | 424 | Well #6 | True | 20
394 | 425 | Well #7 | True | 20
395 | 426 | Monorail Beam | True | 60
396 | 427 | Generator Room Emergency Light | True | 25
397 | 428 | Generator Room Exit Sign | True | 25
398 | 429 | Shower Exhuast Fan Control Panel | True | 25
399 | 430 | Generator Room Exit Sign | True | 25
400 | 432 | Battery Charger | True | 25
401 | 433 | Battery Charger | True | 25
402 | 434 | Pump #5 Three Phase Pump Monitor/Protector | True | 15
403 | 435 | Pump #6 Three Phase Pump Monitor/Protector | True | 15
404 | 436 | Pump #7 Three Phase Pump Monitor/Protector | True | 15
405 | 437 | Poly Tank Level Indicator | True | 15
406 | 438 | Corrosion Inhibitor Calibration Unit | True | 15

## rehab
| 0 | 1 | 2 | 3 | 4
0 | ParentID | AssetName | RehabComment | Rehabyear | RehabUnitMaterialCost