## Sheet1
AssetID | AssetCategory | AssetName | AssetDescription | SiteName | FacilityName | InstallYear | LocationName | CoF | TempComments1 | TempComments2 | TempComments3
1 | Process Mechanical | Water Pump No.1 | Pump, Water, No.1 (Maley) - A 01 Pumps | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | Fair | The pump is still working but it already exceeded its expected service life
2 | Process Mechanical | Water Pump No.2 | Pump, Water, No.2 (Maley) - A 01 Pumps | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | Fair | The pump is still working but it already exceeded its expected service life
3 | Process Mechanical | High Flow Pump | High Flow (Maley) - A 01 Pumps | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | Poor | The pump is beyond its expected service life. The missing pump suggest that it has been sent for repair
4 | Process Mechanical | Piping | Piping, Water Pumping - A 05 Piping & Valves | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | Good
5 | Process Mechanical | Coupon Rack (To be removed) | Coupon Rack (Maley) - A 05 Piping & Valves | Maley Booster Station |  | 1992 |  | 2 | This is not process mechanical equipment.
7 | Process Instrumentation | Ethernet Swith | Switch (Maley) | Maley Booster Station | Booster Station | 2020 | Pump Room | 1 | Good
8 | Process Instrumentation | UPS | Power Supply(Maley) | Maley Booster Station | Booster Station | 2020 | Pump Room | 1 | Good
9 | Process Electrical | Standby Generator | Generator (Maley) - A 17 Generator | Maley Booster Station | Booster Station | 1992 | Generator Room | 3 | good
10 | Building Mechanical | Unit Heater 1 | Gas fired unit heater | Maley Booster Station | Booster Station | 1992 | Pump Room | 1 | Good
11 | Process Instrumentation | Control System (Place holder) | Control System, DG (Maley) - A 27 Inst. & Controls | Maley Booster Station | Booster Station | 1992 | Pump Room | 1
12 | Process Instrumentation | Flow Recorder #1 | FLOW RECORDER (Maley) | Maley Booster Station | Booster Station | 2011 | Pump Room | 2 | Aging, Wear and Tear | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
13 | Process Instrumentation | Flow Recorder #2 | FLOW RECORDER (Maley) | Maley Booster Station | Booster Station | 2011 | Pump Room | 2 | Aging, Wear and Tear | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
14 | Process Instrumentation | Low Temperature Alarm Thermostat 1 | Low Temperature Alarm Thermostat (Maley) | Maley Booster Station | Booster Station | 2011 | Pump Room | 1 | Aging | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
15 | Site Works | Asphalt Pavement | Asphalt Pavement (approx. 130 sq. m) | Maley Booster Station | Booster Station | 1992 | Site | 1 | Fair | Minor craks were noted.
16 | Process Instrumentation | Network Switch | Network Switch (Maley) | Maley Booster Station | Booster Station | 2020 | Pump Room | 1 | Good
17 | Building Structural | Pump Room Monorail Crane Beam | Monorail, 1Ton (Maley) - A 49 Lifting Appliances | Maley Booster Station | Booster Station | 1992 | Pump Room | 1 | Good
18 | Process Instrumentation | PLC | PLC (Maley) | Maley Booster Station | Booster Station | 2020 | Pump Room | 3 | Good
20 |  | MALEY BOOSTER | Maley Booster - A 78 (Reserved) | Maley Booster Station |  | 2005 |  | 2
21 | Building Mechanical | Safety Equipment (Placeholder) | Safety Equipment (Maley) - A 79 Safety Equipment | Maley Booster Station | Booster Station | 2005 | Pump Room | 2
22 | Process Mechanical | Booster Pump #3 | Pump, Booster #3 (Sunrise) - A 01 Pumps | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good
23 | Process Mechanical | Booster Pump #2 | Pump, Booster #2 (Sunrise) - A 01 Pumps | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good
24 | Process Mechanical | Booster Pump #1 | Pump, Booster #1(Sunrise) - A 01 Pumps | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good
25 | Process Mechanical | Pressure Relief Valve | Valve, Pressure Relief 6",A 05 Piping & Valves | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good
26 | Process Mechanical | Pressure Relief Valve | Valve, Pressure Relief 2",A 05 Piping & Valves | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | This valve is a component of the bigger 6" pressure relief valve | Good
27 | Building Mechanical | P-Trap Primer | P-Trap Primer (Sunrise) - A 05 Piping & Valves | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 1 | Assume to be good
28 | Process Mechanical | Process Piping | Piping - A 05 Piping & Valves | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Very Good
30 | Process Instrumentation | Ethernet Switch | Ethernet Switch(SUNRISE BOOSTER) | Sunrise Ridge Booster Station | Booster Station | 2016 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
31 | Process Instrumentation | UPS | UPS (Sunrise Booster) | Sunrise Ridge Booster Station | Booster Station | 2018 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
32 | Process Electrical | Standby Generator | Gen, Stby(Sunrise Booster) - A 17 Generator | Sunrise Ridge Booster Station | Booster Station | 2005 | Generator Room | 3 | Good | The generator includes a sub-base fuel tank; no containment for the fuel;
33 | Building Mechanical | Unit Heater 1 | Unit Heater UH-1 | Sunrise Ridge Booster Station | Booster Station | 2021 | Pump Room | 1 | Good
34 | Process Instrumentation | Instrumentation & Control (Placeholder) | Inst. & CTRL (Sunrise Booster) - A 27 Inst. & Controls | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2
35 | Site Works | Asphalt Pavement | Asphalt Pavement on 96sq. M - A 32 Building & Grounds | Sunrise Ridge Booster Station | Booster Station | 2005 | Site | 1 | Good | Localized depressions in front of the building was observed.
36 | Building Structural | Pump Room 1/2 Ton Bridge Crane | Monorail & 1/2 Ton Hoist - A 49 Lifting Appliances | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 1 | Good
37 |  | SUNRISE BOOSTER | Sunrise Booster - A 78 (Reserved) | Sunrise Ridge Booster Station |  | 2004 |  | 2
38 | Process Mechanical | CL2 #1 Booster Pump | Booster Pump CL2 #1 - A 01 Pumps | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good
39 | Process Mechanical | CL2 #2 Booster Pump | Booster Pump CL2 #2 - A 01 Pumps | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good
40 | Process Mechanical | Deep Well #7 Pump | Pump, Deep Well #7 - A 01 Pumps | Falconbridge Wells | Well Building | 2004 | Well #7 | 2 | Good
41 | Process Mechanical | Deep Well #6 Pump | Pump, Deep Well #6 - A 01 Pumps | Falconbridge Wells | Site | 2004 | Well #6 | 2 | Good
42 | Process Mechanical | Deep Well #5 Pump | Pump, Deep Well #5 - A 01 Pumps | Falconbridge Wells | Site | 2004 | Well #5 | 2 | Good
43 | Process Mechanical | Poly #1 Pump | Pump, Poly #1 - A 01 Pumps | Falconbridge Wells | Well Building | 2019 | Fluoride Room | 2 | Very Good
44 | Process Mechanical | Poly #2 Pump | Pump, Poly #2 - A 01 Pumps | Falconbridge Wells | Well Building | 2019 | Fluoride Room | 2 | Very Good
45 | Process Mechanical | West Main Booster Pump | Booster Pump, West Main - A 01 Pumps | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good
46 | Process Mechanical | Pump #7 Control Vavle | Control Valve Pump #7 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Fair | Minor corrosion was observed on the surface of the valve
47 | Process Mechanical | Pump #7 Distrubtion Valve | Distrubtion Valve Pump #7 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good
48 | Process Mechanical | Pump #7 Bypass Valve | Bypass Valve Pump #7 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good
49 | Process Mechanical | Pump #6 Control Valve | Control Valve Pump #6 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Fair | Corrosion was observed on the top of the valve
50 | Process Mechanical | Pump #6 Distrubtion Valve | Distrubtion Valve Pump #6 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good
51 | Process Mechanical | Pump #6 Bypass Valve | Bypass Valve Pump #6 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good
52 | Process Mechanical | Pump #5 Control Valve | Control Valve Pump #5 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good | Minor corrosion was observed on the pump
53 | Process Mechanical | Pump #5 Distrubtion Valve | Distrubtion Valve Pump #5 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good
54 | Process Mechanical | Pump #5 Bypass Valve | Bypass Valve Pump #5 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2014 | Pump Room | 2 | Good
55 | Process Mechanical | Tank Pressure Relief Valve | Pressure Relief, Tank - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good
56 | Process Mechanical | Waste Pressure Relief Valve | Pressure Relief, Waste - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2014 | Pump Room | 2 | Fair | Minor deterioration and corrosion service on the valve
57 | Process Mechanical | Piping & Valves (Placeholder) | Piping & Valves, Gen. - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2005 | Pump Room | 2
61 | Process Instrumentation | Temperature Sensor | Temperature Sensor | Falconbridge Wells | Well Building | 2015 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
62 | Process Instrumentation | Ethernet Switch | Ethernet Switch(Falconbridge) | Falconbridge Wells | Well Building | 2015 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
63 | Process Instrumentation | Fiber Patch Panel | Fiber Patch Panel(Falconbridge) | Falconbridge Wells | Well Building | 2015 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
64 | Building Mechanical | Fuel Tank | Diesel Tank and Piping | Falconbridge Wells | Well Building | 2018 | Generator Room | 2 | Good | Cc: There was no containment for diesel fuel lines. TSSA requires all equipment containing or carrying fuel to be contained per CSA B139.1.1-15 Section 6.5.1.4.
65 | Building Mechanical | Surge Tank | Surge Tank | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 2 | Good
66 | Process Instrumentation | MODEM | MODEM(Falconbridge) | Falconbridge Wells | Well Building | 2015 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
67 | Process Instrumentation | PLC Panel 6812-4 | PLC RPU ENCLOSURE(Falconbridge) | Falconbridge Wells | Well Building | 2015 | Pump Room | 3 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
68 | Process Instrumentation | Operator Interface Terminal | Operator Interface Terminal(Falconbridge) | Falconbridge Wells | Well Building | 2015 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
69 | Process Electrical | Standby Generator | Generator - A 17 Generator | Falconbridge Wells | Well Building | 2004 | Generator Room | 3 | Good
70 | Building Mechanical | Intake Dampers for Generator Room | Intake dampers (Total of 2) | Falconbridge Wells | Well Building | 2004 | Generator Room | 2 | Good
71 | Process Electrical | Automatic Transfer Switch | Transfer Switch - A 27 Inst. & Controls | Falconbridge Wells | Well Building | 2004 | Pump Room | 3 | Good | Cc: Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the transfer switch which may require examination, adjustment, servicing, or mainte
72 | Process Instrumentation | FALCONBRIDGE WELLS (Placeholder) | Inst & Ctrls, Cl2 - A 27 Inst. & Controls | Falconbridge Wells |  | 2004 |  | 2
73 | Process Instrumentation | pH-Chlorine Analyzer AIT-1791 | pH-Chlorine Analyzer(Falconbridge) | Falconbridge Wells | Well Building | 2010 | Pump Room | 2 | Aging | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
75 | Process Instrumentation | Colorimetric Chlorine Analyzer #1 | Colorimetric Chlorine Analyzer1 | Falconbridge Wells | Well Building | 2021 | Pump Room | 2 | Very Good
76 | Process Instrumentation | FALCONBRIDGE WELLS (Placeholder) | Inst & Controls, Pump #5 - A 27 Inst. & Controls | Falconbridge Wells |  | 2004 |  | 2
77 | Process Instrumentation | By Pass Turbidimeter | By Pass Turbidity(Falconbridge). AE-17944-2 | Falconbridge Wells | Well Building | 2015 | Pump Room | 2 | Aging | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
78 | Process Instrumentation | Ambient Chlorine Remote Sensor 1 | Ambient Chlorine Remote Sensor 1(Falconbridge) | Falconbridge Wells | Well Building | 2015 | Chlorine Room | 2 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
79 | Process Instrumentation | Ambient Chlorine Remote Sensor 2 | Ambient Chlorine Remote Sensor 2(Falconbridge) | Falconbridge Wells | Well Building | 2015 | Chlorine Room | 2 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
80 | Process Instrumentation | Thermostat | Thermostat | Falconbridge Wells | Well Building | 2018 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
81 | Process Instrumentation | Chlorinator #1 | CHLORINATOR(Falconbridge) | Falconbridge Wells | Well Building | 2015 | Chlorine Room | 2 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
82 | Process Instrumentation | Chlorinator #2 | CHLORINATOR(Falconbridge) | Falconbridge Wells | Well Building | 2015 | Chlorine Room | 2 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
83 | Site Works | Gravel Parking Lots & Driveway | Gravel Parking Lots & Driveway, approx. 830 sq. m | Falconbridge Wells | Site | 2004 | Site | 1 | Good | Weed and plant growing on gravel driveway and parking lot
84 | Process Instrumentation | CL2 Scale | Scale CL2 - A 53 Scales | Falconbridge Wells | Well Building | 2015 | Chlorine Room | 1 | Aging, Wear and Tear | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
86 | Process Instrumentation | Poly Tank Level Transmitter | Poly Tank Level Transmitter(Falconbridge) | Falconbridge Wells | Well Building | 2010 | Fluoride Room | 2 | Aging, Wear and Tear | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
87 | Process Instrumentation | UPS | Power Supply(Falconbridge) | Falconbridge Wells | Well Building | 2010 | Pump Room | 1 | Aging | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
88 | Process Instrumentation | PLC | PLC(Falconbridge) | Falconbridge Wells | Well Building | 2015 | Pump Room | 3 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
89 | Building Mechanical | Temperature Switch | Temperature Switch(Falconbridge) | Falconbridge Wells | Well Building | 2004 | Pump Room | 1 | Good
90 | Process Instrumentation | Turbidity Analyzer | Tubidity Analyzer - Genernal Purpose Analyzer Controller(Falconbridge) | Falconbridge Wells | Well Building | 2015 | Pump Room | 2 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
91 | Process Instrumentation | Weight Transmitter | Weight Transmitter(Falconbridge) | Falconbridge Wells | Well Building | 2018 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
92 |  | FALCONBRIDGE WELLS | Falconbridge Wells - A 78 (Reserved) | Falconbridge Wells |  | 2004 |  | 3
94 | Building Mechanical | Eye Wash Station | Eye Wash station - A 79 Safety Equipment | Falconbridge Wells | Well Building | 2004 | Generator Room | 1 | Good
96 | Building Electrical | Outdoor Lighting | 4 Wallpack Fixtures | Sunrise Ridge Booster Station | Booster Station | 2005 | Site | 1 | Good | to be replaced with LED fixtures in next upgrade
97 | Process Electrical | Hydro Meter | Hydro Meter | Sunrise Ridge Booster Station | Booster Station | 2005 | Site | 1 | Good
98 | Building Electrical | Indoor Lighting | 24 linear fluroscent Fixtures | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 1 | Good | to be replaced with LED fixtures in next upgrade
99 | Building Electrical | Emergency Lighting | 2 combination exit signs | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good
101 | Process Electrical | MCC #1 | MCC | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 3 | Good | Cc: Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the MCC which may require examination, adjustment, servicing, or maintenance while
102 | Process Electrical | Power Meter | Power Meter | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good
103 | Process Electrical | Main Circuit Breaker | Main Circuit Breaker | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 3 | Good | Cc: Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the main circuit breaker which may require examination, adjustment, servicing, or m
104 | Process Electrical | Automatic Transfer Switch | Automatic Transfer Switch | Sunrise Ridge Booster Station | Booster Station | 2005 | Generator Room | 3 | Good | Cc: Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the auotmatic transfer switch which may require examination, adjustment, servicing,
105 | Process Electrical | Surge Suppressor | Surge Suppressor | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good | Cc: Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the surge suppressor which may require examination, adjustment, servicing, or maint
106 | Process Electrical | Pump #1 VFD | VFD | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good
107 | Process Electrical | Pump #2 VFD | VFD | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good
108 | Process Electrical | Pump #3 VFD | VFD | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good
109 | Building Electrical | Lighting Panel A | Lighting Panel | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 1 | Good
110 | Process Electrical | Transformer | Transformer | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good
111 | Building Electrical | Outdoor Lighting | 2 wall pack lights | Maley Booster Station | Booster Station | 1992 | Site | 1 | good | to be replaced with LED fixtures in next upgrade
112 | Building Electrical | Pump Room Lighting | 8 linear flurescent lights | Maley Booster Station | Booster Station | 1992 | Pump Room | 1 | good | to be replaced with LED fixtures in next upgrade
113 | Building Electrical | Generator Room Lighting | 4 linear flurescent lights | Maley Booster Station | Booster Station | 1992 | Generator Room | 1 | good | to be replaced with LED fixtures in next upgrade
114 | Process Electrical | Generator Transfer Panel | Generator Transfer Panel | Maley Booster Station | Booster Station | 1992 | Pump Room | 3 | good | Cc: Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the generator transfer panel which may require examination, adjustment, servicing,
115 | Process Electrical | Lighting Transformer Disconnect Switch | Disconnect Switch | Maley Booster Station | Booster Station | 1992 | Pump Room | 1 | good
116 | Process Electrical | Lighting Panel | Lighting Panel | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | good
117 | Building Electrical | Generator Room Heating Disconnect Switch | Disconnect Switch | Maley Booster Station | Booster Station | 1992 | Pump Room | 1 | good
118 | Process Electrical | Splitter | Splitter | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | good | Cc: Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the splitter which may require examination, adjustment, servicing, or maintenance w
119 | Process Electrical | Phase Loss Relay Disconnect Switch | Disconnect Switch | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | good
120 | Process Electrical | Pump Control Panel | Pump Control Panel | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | good | Cc: Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the pump control panel which may require examination, adjustment, servicing, or mai
121 | Process Electrical | Incoming Power Enclosure | Incoming Power Enclosure | Maley Booster Station | Booster Station | 1992 | Pump Room | 1 | good | Cc: Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the incoming power enclosure which may require examination, adjustment, servicing,
122 | Process Electrical | Main Disconnect Switch | Main Disconnect Switch | Maley Booster Station | Booster Station | 1992 | Pump Room | 3 | good | Cc: Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the main disconnect switch which may require examination, adjustment, servicing, or
123 | Process Electrical | Transformer | Transformer | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | good
124 | Process Electrical | VFD#1 | VFD | Maley Booster Station | Booster Station | 2010 | Pump Room | 2 | good
125 | Process Electrical | VFD#2 | VFD | Maley Booster Station | Booster Station | 2010 | Pump Room | 2 | good
126 | Process Electrical | Duplex Pump Control Panel (CP-4000) | duplex pump control panel | Maley Booster Station | Booster Station | 2010 | Pump Room | 2 | good
127 | Process Electrical | Load #1 Output Filter | output filter | Maley Booster Station | Booster Station | 2010 | Pump Room | 2 | good
128 | Process Electrical | Load #2 Output Filter | output filter | Maley Booster Station | Booster Station | 2010 | Pump Room | 2 | good
129 | Process Electrical | Load #2 Input Filter | output filter | Maley Booster Station | Booster Station | 2010 | Pump Room | 2 | good
130 | Process Electrical | Load #1 Input Filter | output filter | Maley Booster Station | Booster Station | 2010 | Pump Room | 2 | good
131 | Process Electrical | Pump #1 Disconnect Switch | Disconnect Switch | Maley Booster Station | Booster Station | 2010 | Pump Room | 2 | good
132 | Process Electrical | Pump #2 Disconnect Switch | Disconnect Switch | Maley Booster Station | Booster Station | 2010 | Pump Room | 2 | good
133 | Building Electrical | Pump Room Exit Sign | 1 combination exit sign | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | good
134 | Process Electrical | Battery Charger | Battery Charger | Maley Booster Station | Booster Station | 1992 | Generator Room | 2 | good
135 | Process Electrical | Hydro Meter | Hydro Meter | Maley Booster Station | Booster Station | 1992 | Site | 1 | poor | severe corrosion | graffiti on the enclosure
136 | Process Electrical | Hydro Meter | Hydro Meter | Falconbridge Wells | Site | 2004 | Site | 1 | fair | pump room outer wall | The enclosure for Hydrometer was in fair condtion. The latch was corrode and discolouration on the panel was noted.
137 | Building Electrical | Outdoor Lighting | 4 wall pack LEDs | Falconbridge Wells | Site | 2004 | Site | 1 | good | photosensor for one of the fixtures did not work
138 | Building Electrical | Generator Room Lights | 4 linear flurescent | Falconbridge Wells | Well Building | 2004 | Generator Room | 1 | good | to be replaced with LED fixtures in next upgrade
139 | Building Electrical | Unit Heater #3 Disconnect Switch | disconnect switch | Falconbridge Wells | Well Building | 2004 | Generator Room | 1 | good
140 | Building Electrical | T775 Control Panel | T775 Control Panel | Falconbridge Wells | Well Building | 2004 | Generator Room | 1 | Good
141 | Building Electrical | Generator Room Exhuast Fan Control Panel | Control Panel | Falconbridge Wells | Well Building | 2004 | Generator Room | 2 | good
142 | Building Electrical | Pump Room Lights | 9 linear flurescent | Falconbridge Wells | Well Building | 2004 | Pump Room | 1 | good | to be replaced with LED fixtures in next upgrade
143 | Building Electrical | Pump Room Exit Signs | 2 exit signs | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | good
144 | Process Electrical | MCC12-1A | MCC | Falconbridge Wells | Well Building | 2004 | Pump Room | 3 | good | Cc: Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the MCC which may require examination, adjustment, servicing, or maintenance while
145 | Process Electrical | Main Circuit Breaker | Main Circuit Breaker | Falconbridge Wells | Well Building | 2004 | Pump Room | 3 | good | Cc: Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the main circuit breaker which may require examination, adjustment, servicing, or m
146 | Process Electrical | Power Meter | Power Meter | Falconbridge Wells | Well Building | 2004 | Pump Room | 1 | good
147 | Process Electrical | Well Pump #5 Starter | starter | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | good | Cc: Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the starter which may require examination, adjustment, servicing, or maintenance wh
148 | Process Electrical | Spare Starters | starter | Falconbridge Wells | Well Building | 2004 | Pump Room | 1 | good
149 | Process Electrical | Booster Pump #2 Starter | starter | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | good
150 | Process Electrical | Booster Pump #1 Starter | starter | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | good
151 | Process Electrical | Western Main Booster Pump Starter | starter | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | good
152 | Process Electrical | Well Pump #6 Starter | starter | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | good
153 | Process Electrical | Well Pump #7 Starter | starter | Falconbridge Wells | Well Building | 2018 | Pump Room | 2 | Good
154 | Process Electrical | Transient Voltage Surge Suppressor | Transient Voltage Surge Suppressor | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | good
155 | Process Electrical | Pump #5 Deepwell Distribution Shutoff Motorized Valve Actuator | Motorized Valve Actuator | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | good
156 | Process Electrical | Pump #5 Deepwell Bypass Shutoff Motorized Valve Actuator | Motorized Valve Actuator | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | good
157 | Process Electrical | Pump #6 Distribution Shutoff Motorized Valve Actuator | Motorized Valve Actuator | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | good
158 | Process Electrical | Pump #6 Deepwell Bypass Shutoff Motorized Valve Actuator | Motorized Valve | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | good
159 | Process Electrical | Pump #7 Distribution Shutoff Motorized Valve Actuator | Motorized Valve Actuator | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | good
160 | Process Electrical | Pump #7 Deepwell Bypass Shutoff Motorized Valve Actuator | Motorized Valve | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | good
161 | Building Electrical | Chlorine Room Exhuast Fan Control Panel | Control Panel | Falconbridge Wells | Well Building | 2004 | Chlorine Room | 2 | good
162 | Process Electrical | Transformer | Transformer | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | good
163 | Building Electrical | LP6811 Lighting Panel | Lighting Panel | Falconbridge Wells | Well Building | 2004 | Pump Room | 1 | good
164 | Process Electrical | Transformer | Transformer | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | good
165 | Building Electrical | UP6812 Lighting Panel | Lighting Panel | Falconbridge Wells | Well Building | 2004 | Pump Room | 1 | good
166 | Building Electrical | Fluoride Room Exhuast Fan Control Panel | Control Panel | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 2 | good
167 | Building Electrical | Process Room Exhuast Fan Control Panel | Control Panel | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | good
168 | Building Electrical | Fluoride Room Light | 1 linear flurescent | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 1 | good | to be replaced with LED fixtures in next upgrade
169 | Building Electrical | Chlorine Room Light | 1 linear flurescent | Falconbridge Wells | Well Building | 2004 | Chlorine Room | 1 | good | to be replaced with LED fixtures in next upgrade
170 | Building Electrical | Fluoride Room Exit Sign | exit sign | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 2 | good
171 | Building Electrical | Chlorine Room Emergency Light | battery unit | Falconbridge Wells | Well Building | 2004 | Chlorine Room | 2 | good
172 | Building Electrical | Pump Room Emergency Light | 2 battery unit | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | good
173 |  | PLC Panel | PLC Panel |  |  | 2004 |  | 3 | Good
174 | Building Electrical | T775 Control Panel | CONTROL PANEL (SUNRISE BOOSTER) | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 1 | Aging
175 | Process Instrumentation | Temperature Transmitter | Thermostat (SUNRISE BOOSTER) | Sunrise Ridge Booster Station | Booster Station | 2018 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
176 | Process Instrumentation | Gauge Pressure Cerabar 1 | Gauge Pressure Cerabar (SUNRISE BOOSTER) | Sunrise Ridge Booster Station | Booster Station | 2018 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
177 | Process Instrumentation | Pressure Gauge 1 | Pressure Gauge (SUNRISE BOOSTER) | Sunrise Ridge Booster Station | Booster Station | 2018 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
178 | Process Instrumentation | Gauge Pressure Cerabar 2 | Gauge Pressure Cerabar (SUNRISE BOOSTER) | Sunrise Ridge Booster Station | Booster Station | 2018 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
179 | Process Instrumentation | Pressure Gauge 2 | Pressure Gauge (SUNRISE BOOSTER) | Sunrise Ridge Booster Station | Booster Station | 2018 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
180 | Process Instrumentation | Low Temp T-STAT | Low Temp T-STAT(SUNRISE BOOSTER) | Sunrise Ridge Booster Station | Booster Station | 2016 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
182 | Process Instrumentation | MODEM | Modem(SUNRISE BOOSTER) | Sunrise Ridge Booster Station | Booster Station | 2016 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
183 | Process Instrumentation | PLC | PLC(SUNRISE BOOSTER) | Sunrise Ridge Booster Station | Booster Station | 2006 | Pump Room | 3 | Aging | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
184 | Process Instrumentation | Thermostat | Thermostat(SUNRISE BOOSTER) | Sunrise Ridge Booster Station | Booster Station | 2016 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
186 | Process Instrumentation | MODEM | MODEM(Maley) | Maley Booster Station | Booster Station | 2020 | Pump Room | 1 | Good
187 | Process Instrumentation | Temperature Transmitter | Temperature Transmitter(Maley) | Maley Booster Station | Booster Station | 2016 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
188 | Process Instrumentation | Low Temperature Alarm Thermostat 2 | Low temperature alarm thermostat with diesel louvres(Maley) | Maley Booster Station | Booster Station | 2011 | Pump Room | 1 | Wear and Tear | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
189 | Process Instrumentation | Thermostat | Thermostat(Maley) | Maley Booster Station | Booster Station | 2011 | Pump Room | 1 | Wear and Tear | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
190 | Process Instrumentation | RPU Control Cabinet | RPU Control Cabinet | Maley Booster Station | Booster Station | 2020 | Pump Room | 1 | Good
191 | Process Instrumentation | Flow Switch | Flow Switch (Maley) | Maley Booster Station | Booster Station | 2008 | Pump Room | 1 | Aging | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
192 |  | MALEY BOOSTER ALTOMETER 2 | Altometer Signal Converter(Maley) |  |  | 2008 |  | 3
193 | Process Instrumentation | Flowmeter #1 | FLOWMETER | Maley Booster Station | Booster Station | 2008 | Pump Room | 2 | Aging | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
194 |  | MALEY BOOSTER Pressure Guage |  |  |  | 2004 |  | 3
195 | Process Instrumentation | Pressure Gauge 1 | Pressure Gauge (Maley) | Maley Booster Station | Booster Station | 2018 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
196 | Process Instrumentation | Suction Pressure Transducer 1 | Gauge Pressure Cerabar (Maley) | Maley Booster Station | Booster Station | 2020 | Pump Room | 1 | Very Good
197 | Process Instrumentation | Pressure Gauge 2 | Pressure Gauge (Maley) | Maley Booster Station | Booster Station | 2018 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
198 | Process Instrumentation | Suction Pressure Transducer 2 | Gauge Pressure Cerabar (Maley) | Maley Booster Station | Booster Station | 2020 | Pump Room | 1 | Very Good
199 | Process Instrumentation | Gas Detector Transmitter #2 | Gas Deterctor Transmitter | Falconbridge Wells | Well Building | 2015 | Chlorine Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
200 | Process Instrumentation | Gas Detector Transmitter #1 | Gas Deterctor Transmitter | Falconbridge Wells | Well Building | 2015 | Chlorine Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
201 | Process Instrumentation | Treated Water Turbidimeter | Treated Turbidity (Falconbridge) | Falconbridge Wells | Well Building | 2015 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
202 | Process Instrumentation | Colorimetric Chlorine Analyzer #2 | Colorimetric Chlorine Analyzer2 | Falconbridge Wells | Well Building | 2021 | Pump Room | 2 | Very Good
203 | Process Instrumentation | pH-Chlorine Analyzer AIT-17942 | pH-Chlorine Analyzer(Falconbridge) | Falconbridge Wells | Well Building | 2015 | Pump Room | 2 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
204 | Process Instrumentation | Free Chlorine Transmitter | Universal Controller(Falconbridge) | Falconbridge Wells | Well Building | 2018 | Pump Room | 2 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
205 | Process Instrumentation | Raw Water Gauge (qty:7) | Raw Water Gauge | Falconbridge Wells | Well Building | 2015 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
206 | Process Instrumentation | Booster Pump #6 Flowmeter | FLOW Transmitter, FIT-17946 | Falconbridge Wells | Well Building | 2018 | Pump Room | 2 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
207 | Process Instrumentation | Flowmeter #2 | FLOWMETER | Maley Booster Station | Booster Station | 2008 | Pump Room | 2 | Aging | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
208 | Process Instrumentation | Booster Pump #5 Flowmeter | FLOW Transmitter, FIT-17945 | Falconbridge Wells | Well Building | 2018 | Pump Room | 2 | Good | Condensation on the flowmeter was observed; Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
209 | Process Instrumentation | Treated Water Flowmeter | FLOW Transmitter | Falconbridge Wells | Well Building | 2018 | Pump Room | 2 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
210 | Process Instrumentation | Western Main Flowmeter | FLOW Transmitter, FIT17948 | Falconbridge Wells | Well Building | 2018 | Pump Room | 2 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
211 | Process Instrumentation | Booster Pump #7 Flowmeter | FLOW Transmitter, FIT-17947 | Falconbridge Wells | Well Building | 2018 | Pump Room | 2 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
212 | Process Instrumentation | Treated Water Pressure Transmitter | Treated Water Pressure Transmitter | Falconbridge Wells | Well Building | 2018 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
213 | Process Mechanical | Suction Header Butterfly Valve | Butterfly Valve | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good | Minor corrosion was observed
214 | Process Mechanical | Booster Pump #3 Suction Butterfly Valve | Butterfly Valve | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good | Minor corrosion was observed
215 | Process Mechanical | Booster Pump #3 Discharge Check Valve | Swing Check Valve | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good
216 | Process Mechanical | Booster Pump #3 Discharge Butterfly Valve | Butterfly Valve | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good | Minor corrosion was observed
217 | Process Mechanical | Pressure Relief Line Butterfly Valve 1 | Butterfly Valve | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good | Minor corrosion was observed
218 | Process Mechanical | Pressure Relief Line Burrerfly Valve 2 | Butterfly Valve | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good | Minor corrosion was observed
219 | Process Mechanical | Booster Pump #2 Suction Butterfly Valve | Butterfly Valve | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good | Minor corrosion was observed
220 | Process Mechanical | Booster Pump # 2 Discharge Check Valve | Swing Check Valve | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good
221 | Process Mechanical | Booster Pump #2 Discharge Butterfly Valve | Butterfly Valve | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Fair | Minor corrosion was observed at the connection
222 | Process Mechanical | Bosster Pump #1 Suction Butterfly Valve | Butterfly Valve | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good | Minor corrosion was observed
223 | Process Mechanical | Booster Pump #1 Discharge Check Valve | Swing Check Valve | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good
224 | Process Mechanical | Booster Pump #1 Discharge Butterfly Valve | Butterfly Valve | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good | Minor corrosion was observed
225 | Process Mechanical | Station Inflow Butterfly Valve | Inflow Butterfly Valve | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | Fair | The valve is still working but it is beyond its expected service life.
226 | Process Mechanical | Pump 1 Inlet Butterfly Valve | Inlet Butterfly Valve No.1 | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | fair | The valve is still working but it is beyond its expected service life.
227 | Process Mechanical | Pump 1 Check Valve | Check Valve No.1 | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | fair | The valve is still working but it is beyond its expected service life.
228 | Process Mechanical | Pump 1 Outlet Butterfly Valve | Outlet Butterfly Valve No.1 | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | Fair | The valve is still working but it is beyond its expected service life.
229 | Process Mechanical | Pump 2 Inlet Butterfly Valve | Inlet Butterfly Valve No.2 | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | Fair | The valve is still working but it is beyond its expected service life.
230 | Process Mechanical | Pump 2 Check Valve | Check Valve No.2 | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | Fair | The valve is still working but it is beyond its expected service life.
231 | Process Mechanical | Pump 2 Outlet Butterfly Valve | Outlet Butterfly Valve No.2 | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | Fair | The valve is still working but it is beyond its expected service life.
232 | Process Mechanical | Pump 3 Inlet Butterfly Valve | Inlet Butterfly Valve | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | Fair | The valve is still working but it is beyond its expected service life.
233 | Process Mechanical | Pump 3 Pressure Reducing Valve | Pressure Reducing Valve | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | Fair | The valve is still working but it is beyond its expected service life.
234 | Process Mechanical | Pump 3 Outlet Butterfly Valve | Outlet Butterfly Valve | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | Fair | The valve is still working but it is beyond its expected service life.
235 | Process Mechanical | Pump #7 Distrubtion Valve Actuator | Distrubtion Valve Actuator Pump #7 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good
236 | Process Mechanical | Pump #7 Bypass Valve Actuator | Bypass Valve Actuator Pump #7 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good
237 | Process Mechanical | Pump #7 Inlet Gate Valve | Inlet Gate Valve Pump #7 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good
238 | Process Mechanical | Pump #7 Bypass Gate Valve | Bypass Gate Valve Pump #7 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good
239 | Process Mechanical | Pump #7 Check Valve | Check Valve Pump #7 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2020 | Pump Room | 2 | Good
240 | Process Mechanical | Pump #7 Air Release Valve | Air Release Valve Pump #7 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good
241 | Process Mechanical | Pump #6 Distribution Valve Actuator | Distrubtion Valve Actuator Pump #6 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good
242 | Process Mechanical | Pump #6 Bypass Valve Actuator | Bypass Valve Actuator Pump #6 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good
243 | Process Mechanical | Pump #5 Distrubtion Valve Actuator | Distrubtion Actuator Valve Pump #5 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good
244 | Process Mechanical | Pump #5 Bypass Valve Actuator | Bypass Valve Actuator Pump #5 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good
245 | Process Mechanical | Pump #6 Inlet Gate Valve | Inlet Gate Valve Pump #6 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good | Minor deterioration was observed on the valve.
246 | Process Mechanical | Pump #6 Bypass Gate Valve | Bypass Gate Valve Pump #6 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good | Minor deterioration was observed on the valve.
247 | Process Mechanical | Pump #6 Check Valve | Check Valve Pump #6 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Fair | Minor deterioration was observed on the valve.
248 | Process Mechanical | Pump #6 Air Release Valve | Air Release Valve Pump #6 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good
249 | Process Mechanical | Pump #5 Inlet Gate Valve | Inlet Gate Valve Pump #5 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good
250 | Process Mechanical | Pump #5 Bypass Gate Valve | Bypass Gate Valve Pump #5 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good
251 | Process Mechanical | Pump #5 Check Valve | Check Valve Pump #5 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2020 | Pump Room | 2 | Very Good
252 | Process Mechanical | Pump#5 Air Release Valve | Air Release Valve Pump #5 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good
253 | Process Mechanical | Treated Water Bypass Gate Valve | Treated Water Bypass Gate Valve - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good
254 | Process Mechanical | Treated Tanker Fill Connection Check Valve | Treated Tanker Fill Connection Check Valve - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Fair | Minor deterioration on the surface of the pump | This valve and its 100 mm dia pipe is missing on the existing drawing.
255 | Process Mechanical | Treated Tanker Fill Connection Gate Valve | Treated Tanker Fill Connection Gate Valve - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good | This valve and its associated piping is missing on the existing drawing.
256 | Process Mechanical | Flow Meter Gate Valve #1 | Flow Meter Gate Valve #1 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good
257 | Process Mechanical | Flow Meter Gate Valve #2 | Flow Meter Gate Valve #2 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Fair | Minor deteroiration on the turning stem and wheel of the valve
258 | Process Mechanical | Booster Pump Suction Gate Valve #1 | Booster Pump Suction Gate Valve 1 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good
259 | Process Mechanical | Treated Water Butterfly Valve #1 | Treated Water Butterfly Valve #1 - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Fair | Minor corrosion was observed on the surface of the valve
260 | Process Mechanical | Waste Line Air Release Valve | Waste Line Air Release Valve - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Very Good | This valve is missing on the existing drawing
261 | Process Mechanical | Treated Water Air Release Valve | Treated Water Air Release Valve - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Very Good | The valve is missing on the as built drawing.
262 | Process Mechanical | Poly #1 Storage Tank | Storage Tank, Poly #1 | Falconbridge Wells | Well Building | 2010 | Fluoride Room | 1 | Very Good
263 | Process Mechanical | Poly #2 Storage Tank | Storage Tank, Poly #2 | Falconbridge Wells | Well Building | 2010 | Fluoride Room | 1 | Very Good
264 | Process Mechanical | Process Piping | Process Piping - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Very Good
265 | Process Mechanical | West Main Booster Pump Small Valves | Valves that are smaller than 100 mm dia - A 05 Piping & Valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Fair | Minor corrosion on the check valve was observed
266 | Building Structural | Pump Room Concrete Foundation |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good
267 | Building Structural | Pump Room Concrete Floor Slab |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good
268 | Building Structural | Pump Room Masonry Blockwall |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good
269 | Building Structural | Generator Room Concrete Foundation |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Generator Room | 2 | Good
270 | Building Structural | Generator Room Concrete Floor Slab |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Generator Room | 2 | Good
271 | Building Structural | Generator Room Masonry Blockwalls |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Generator Room | 2 | Good
272 | Building Structural | Booster Station Wood Truss Roof |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Site | 3 | Good | Hidden under plywood ceiling
273 | Building Architectural | Asphalt Shingle Roof |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Site | 3 | Poor | Shingles observed to be curling
274 | Building Architectural | Exterior Brick Veneer |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Site | 2 | Good
275 | Building Architectural | Pump Room Wall and Ceiling Paint |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 1 | Good
276 | Building Architectural | Pump Room Floor Coating |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 1 | Good
277 | Building Architectural | Pump Room Access Door (Double) |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 1 | Fair | Minor corrosion at bottom of door frame. Weathered exterior paint
278 | Building Architectural | Generator Room Access Door (Double) |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Generator Room | 1 | Fair | Cc: Minor corrosion at bottom of door frame. Weathered exterior paint; door height need to be adjusted to address the code compliance issue associated with the diesel fuel tank
279 | Building Architectural | Generator Room Wall and Ceiling Paint |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Generator Room | 1 | Good
280 | Building Architectural | Generator Room Floor Coating |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Generator Room | 1 | Good
281 | Building Architectural | Exterior Brick Veneer |  | Maley Booster Station | Booster Station | 1992 | Site | 2 | Fair | Localized erosion of brick. Grafitti typically noted
282 | Building Architectural | Asphalt Shingle Roof |  | Maley Booster Station | Booster Station | 1992 | Site | 3 | Fair | Aging
283 | Building Architectural | Pump Room Access Door (Double) |  | Maley Booster Station | Booster Station | 1992 | Pump Room | 1 | Fair | Weathered exterior paint
284 | Building Architectural | Pump Room Access Door (Single) |  | Maley Booster Station | Booster Station | 1992 | Pump Room | 1 | Fair | Weathered exterior paint. Grafitti on exterior
285 | Building Architectural | Pump Room Floor Coating |  | Maley Booster Station | Booster Station | 1992 | Pump Room | 1 | Good
286 | Building Architectural | Pump Room Wall and Ceiling Paint |  | Maley Booster Station | Booster Station | 1992 | Pump Room | 1 | Good
287 | Building Architectural | Generator Room Access Door (Double) |  | Maley Booster Station | Booster Station | 1992 | Generator Room | 1 | Fair | Weathered exterior paint; door height need to be adjusted to address the code compliance issue associated with the diesel fuel tank
288 | Building Architectural | Generator Room Wall and Ceiling Paint |  | Maley Booster Station | Booster Station | 1992 | Generator Room | 1 | Good
289 | Building Architectural | Generator Room Floor Coating |  | Maley Booster Station | Booster Station | 1992 | Generator Room | 1 | Good
290 | Building Architectural | Generator Room Plywood Ceiling Covering |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Generator Room | 1 | Good
291 | Building Architectural | Pump Room Plywood Ceiling Covering |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 1 | Good
292 | Building Structural | Pump Room Concrete Foundation |  | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | Fair | Minor cracking/spalling at exterior corner
293 | Building Structural | Pump Room Concrete Floor Slab |  | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | Fair | Minor hairline cracking throughout
294 | Building Structural | Pump Room Masonry Blockwall |  | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | Good
295 | Building Architectural | Generator Room Plywood Ceiling |  | Maley Booster Station | Booster Station | 1992 | Generator Room | 1 | Good
296 | Building Architectural | Pump Room Plywood Covering |  | Maley Booster Station | Booster Station | 1992 | Pump Room | 1 | Good
297 | Building Structural | Generator Room Concrete Foundation |  | Maley Booster Station | Booster Station | 1992 | Generator Room | 2 | Fair | Aging
298 | Building Structural | Generator Room Concrete Floor Slab |  | Maley Booster Station | Booster Station | 1992 | Generator Room | 2 | Good
299 | Building Structural | Generator Room Masonry Blockwall |  | Maley Booster Station | Booster Station | 1992 | Generator Room | 2 | Good | Containment wall for diesel tank have been removed. The surrounding area should be patched and repainted.
300 | Building Structural | Booster Station Wood Truss Roof |  | Maley Booster Station | Booster Station | 1992 | Site | 3 | Good | Hidden under finishes
301 | Building Structural | Pump Room Concrete Foundation |  | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good
302 | Building Structural | Pump Room Masonry Blockwall |  | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good
303 | Building Structural | Pump Room Precast Concrete Roof |  | Falconbridge Wells | Well Building | 2004 | Pump Room | 3 | Good
304 | Building Structural | Generator Room Concrete Foundation |  | Falconbridge Wells | Well Building | 2004 | Generator Room | 2 | Good
305 | Building Structural | Generator Room Concrete Floor Slab |  | Falconbridge Wells | Well Building | 2004 | Generator Room | 2 | Good
306 | Building Structural | Generator Room Masonry Blockwall |  | Falconbridge Wells | Well Building | 2004 | Generator Room | 2 | Good
307 | Building Structural | Generator Room Precast Concrete Roof |  | Falconbridge Wells | Well Building | 2004 | Generator Room | 3 | Good
308 | Building Structural | Pump Room Concrete Floor Slab |  | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good | Gap observed between floor slab and wall footing
309 | Building Structural | Chlorine Room Concrete Foundation |  | Falconbridge Wells | Well Building | 2004 | Chlorine Room | 2 | Good
310 | Building Structural | Chlorine Room Concrete Floor Slab |  | Falconbridge Wells | Well Building | 2004 | Chlorine Room | 2 | Good
311 | Building Structural | Chlorine Room Masonry Blockwall |  | Falconbridge Wells | Well Building | 2004 | Chlorine Room | 2 | Good
312 | Building Structural | Chlorine Room Precast Concrete Roof |  | Falconbridge Wells | Well Building | 2004 | Chlorine Room | 3 | Good
313 | Building Structural | Flouride Room Concrete Foundation |  | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 2 | Good
314 | Building Structural | Flouride Room Concrete Floor Slab |  | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 2
315 | Building Structural | Flouride Room Masonry Blockwall |  | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 2 | Good
316 | Building Structural | Flouride Room Precast Concrete Roof |  | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 3 | Good
317 | Building Structural | Vestibule Concrete Foundation |  | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 2 | Good
318 | Building Structural | Vestibule Concrete Floor Slab |  | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 2 | Good
319 | Building Structural | Vestibule Masonry Blockwall |  | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 2 | Good
320 | Building Structural | Vestibule Precast Concrete Roof |  | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 3 | Good
321 | Building Architectural | Exterior Block Veneer |  | Falconbridge Wells | Well Building | 2004 | Site | 2 | Fair | Cracked block/mortar above generator door. Cracked/debonded block expansion joint sealant
322 | Building Architectural | Roofing System |  | Falconbridge Wells | Well Building | 2004 | Site | 3 | Good
323 | Building Architectural | Pump Room Access Door (Double) |  | Falconbridge Wells | Well Building | 2004 | Pump Room | 1 | fair | Corrosion at bottom of door frame, weathered exterior paint
324 | Building Architectural | Pump Room Access Door (Single) |  | Falconbridge Wells | Well Building | 2004 | Pump Room | 1 | fair | Corrosion at bottom of door frame, weathered exterior paint
325 | Building Architectural | Pump Room Access Door (Single) | Interior | Falconbridge Wells | Well Building | 2004 | Pump Room | 1 | Good | Door height need to be adjusted to address the code compliance issue associated with the diesel fuel tank
326 | Building Architectural | Pump Room Wall Paint |  | Falconbridge Wells | Well Building | 2004 | Pump Room | 1 | good
327 | Building Architectural | Generator Room Access Door (Double) |  | Falconbridge Wells | Well Building | 2004 | Generator Room | 1 | Fair | Corrosion at bottom of door frame, weathered exterior paint; Door height need to be adjusted to address the code compliance issue associated with the diesel fuel tank
328 | Building Architectural | Generator Room Wall Paint |  | Falconbridge Wells | Well Building | 2004 | Generator Room | 1 | Good
329 | Building Architectural | Pump Room Roof Hatch |  | Falconbridge Wells | Well Building | 2004 | Pump Room | 1 | Good
330 | Building Architectural | Vestibule Access Door (Single) |  | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 1 | Fair | Corrosion at bottom of door frame, weathered exterrior paint
331 | Building Architectural | Vestibule Wall Paint |  | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 1 | Good
332 | Building Architectural | Chlorine Room Wall Paint |  | Falconbridge Wells | Well Building | 2004 | Chlorine Room | 1 | Good
333 | Building Architectural | Chlorine Room Access Door (Single) |  | Falconbridge Wells | Well Building | 2004 | Chlorine Room | 1 | fair | Typical corrosion
334 | Building Architectural | Chlorine Room Interior Window |  | Falconbridge Wells | Well Building | 2004 | Chlorine Room | 1 | Good
335 | Building Architectural | Fluoride Room Interior Window |  | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 1 | Good
336 | Building Architectural | Fluoride Room Wall Paint |  | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 1 | Good
337 | Building Architectural | Fluoride Room Access Door (Single) |  | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 1 | fair | Typical corrosion
338 | Building Architectural | Pump Room Lab Cainbets |  | Falconbridge Wells | Well Building | 2004 | Pump Room | 1 | Good
339 | Site Works | Curbing around the building and parking lot | Curbing (approx. 40m total, surrounding the building and parking lot) | Sunrise Ridge Booster Station | Booster Station | 2005 | Site | 1 | Good | Minor cracking was found on the site
340 | Site Works | Concrete Sidewalk | Concrete Sidewalk (approx. 5m by 1.5m) | Sunrise Ridge Booster Station | Booster Station | 2005 | Site | 1 | Good
341 | Site Works | Bollard | 1 bollard for the protection of gas service line and meter | Sunrise Ridge Booster Station | Booster Station | 2005 | Site | 1 | Fair | Minor corrosion was observed
342 | Site Works | Gas Piping | Gas distribution pipe at the southeast corner of the building (no information, assumed to exist, distance estimated by measuring the length from gas meter to gas heaters, total 19m) | Sunrise Ridge Booster Station | Booster Station | 2005 | Site | 1 | Fair | Surface corrosion was observed
343 | Site Works | Sanitary Sewer Piping | Sanitary sewer piping (assumed to be PVC size 150mm approximately 5m long) | Sunrise Ridge Booster Station | Booster Station | 2005 | Site | 2 | Good
344 | Site Works | Interlocking Pavement | Interlocking Pavement (appox. 180 sq. m, on driveway and surrounding the building) | Maley Booster Station | Booster Station | 1992 | Site | 1 | Fair | Cracking, separation, and depression were observed on the site
345 | Site Works | Bollard | Gas meter bollard at the southeast corner of the building | Maley Booster Station | Booster Station | 1992 | Site | 1 | Good
347 | Site Works | Gas Distribution Piping | Gas piping; distance estimated by measuring the length from gas meter to gas heaters, total 20m | Maley Booster Station | Booster Station | 1992 | Site | 2 | Good
348 | Site Works | Sanitary Sewer | Sanitary sewer piping, 100mm, assumed to be pvc, approx. 25m | Maley Booster Station | Booster Station | 1992 | Site | 2 | Good
349 | Site Works | Double Swing Gate (East Side) | One approx. 6m wide opening double swing at the east side, with barbed wire | Falconbridge Wells | Site | 2004 | Site | 1 | Fair | Corrosion of the gates and barbed wires was observed; Corrosion at bottom of gate
350 | Site Works | Site Gates (Well 6) | One swing gate (approx. 4m wide opening double swing) | Falconbridge Wells | Site | 2004 | Well #6 | 1 | Good
351 | Site Works | Site Gates (Well 5) | One swing gate (approx. 4m wide opening double swing) | Falconbridge Wells | Site | 2004 | Well #5 | 1 | Good
352 | Site Works | Chain-link Fence | Chain-link fence with barbed wire (1.8m tall, approx. 70m long) | Falconbridge Wells | Site | 2004 | Site | 1 | Fair | The fence and barbed wire was broken and distorted at several locations. Corrosion on the fence and barbed wire was also observed.
353 | Site Works | Chain-link Fence (Well #5) | Chain-link fence (2.4m tall, approx. 6m long) | Falconbridge Wells | Site | 2004 | Well #5 | 1 | Good
354 | Site Works | Chain-link Fence (Well #6) | Chain-link fence (2.4m tall, approx. 6m long) | Falconbridge Wells | Site | 2004 | Well #6 | 1 | Good
355 | Site Works | Concrete Sidewalk | Concrete sidewalk (approx. 80 sq. m) | Falconbridge Wells | Site | 2004 | Site | 1 | Good | Weed growing around concrete sidewalk patches
356 | Site Works | Drain Pipe | 125mm PVC Drain Pipe (approx. 5.5m) | Falconbridge Wells | Site | 2004 | Site | 1 | Assume to be in good condition
357 | Building Architectural | Louvre |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Generator Room | 1 | Good
361 | Process Instrumentation | Pressure Gauges | Pressure Gauges (qty:7) | Falconbridge Wells | Well Building | 2015 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
362 | Process Electrical | Phase Loss Disconnect |  | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good
363 |  | intake damper |  | Sunrise Ridge Booster Station |  | 2005 |  | 2
364 | Building Mechanical | Generator Dampers | 2 motorized dampers and louver | Sunrise Ridge Booster Station | Booster Station | 2005 | Generator Room | 2 | Good
365 | Building Mechanical | Diesel Engine Silencer and Exhaust Flue | Diesel Engine Silencer and Exhaust Flue | Sunrise Ridge Booster Station | Booster Station | 2005 | Generator Room | 2 | Good
367 | Building Mechanical | Diesel Fuel Tank | diesel tank and piping | Maley Booster Station | Booster Station | 2018 | Generator Room | 2 | Good | Cc: There was no containment for diesel fuel lines. TSSA requires all equipment containing or carrying fuel to be contained per CSA B139.1.1-15 Section 6.5.1.4.
368 | Building Mechanical | Generator Room Heater | electrical unit heater | Maley Booster Station | Booster Station | 2018 | Generator Room | 1 | Good
372 | Building Mechanical | Recircculation Damper | Recirc damper | Falconbridge Wells | Well Building | 2004 | Generator Room | 2 | Good
373 | Building Mechanical | Unit Heater 1 | unit heater | Falconbridge Wells | Well Building | 2004 | Pump Room | 1 | Good
374 | Building Mechanical | Unit Heater 2 | unit heater | Falconbridge Wells | Well Building | 2004 | Generator Room | 1 | Good
375 | Building Mechanical | Unit Heater 3 | unit heater | Falconbridge Wells | Well Building | 2004 | Pump Room | 1 | Good
377 | Building Mechanical | Pump Room Motorized Damper | louver and damper | Falconbridge Wells | Well Building | 2004 | Pump Room | 1 | Good
378 | Building Mechanical | Emergency Shower | emergency shower, Safety Equipment - A 79 Safety Equipment | Falconbridge Wells | Well Building | 2004 |  | 1 | Good
379 | Building Mechanical | Shower Area Unit Heater | unit heater | Falconbridge Wells | Well Building | 2004 |  | 1 | Good
380 | Building Mechanical | Exhaust Fan 5 | exhaust fan | Falconbridge Wells | Well Building | 2004 |  | 2 | Good
381 | Building Mechanical | Exhaust Fan 3 | exhaust fan | Falconbridge Wells | Well Building | 2004 | Chlorine Room | 2 | Good
382 | Building Mechanical | Chlorine Room Unit Heater |  | Falconbridge Wells | Well Building | 2016 | Chlorine Room | 1 | Very Good
383 | Building Mechanical | Chlorine Room Mororized damper | damper | Falconbridge Wells | Well Building | 2004 | Chlorine Room | 2 | Good
384 | Building Mechanical | Fluoride Room Motorized Damper |  | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 2 | Good
385 | Building Mechanical | Exhaust Fan 1 | exhaust fan | Falconbridge Wells | Well Building | 2004 | Generator Room | 2 | Good
386 | Building Mechanical | Exhaust Fan 2 | exhaust fan | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good
387 | Building Mechanical | Exhaust Fan 4 | exhaust fan | Falconbridge Wells | Well Building | 2004 | Fluoride Room | 2 | Good
388 | Building Mechanical | Themostatic Mixing Valve | Themostatic Mixing Valve for Emergency Eyewash | Falconbridge Wells | Well Building | 2004 |  | 1 | Good | Minor corrosion on the valve was observed.
389 | Building Mechanical | Diesel Engine Silencer and Exhaust Flue |  | Falconbridge Wells | Well Building | 2004 | Generator Room | 2 | Good
390 | Building Electrical | Smoke Detectors |  | Falconbridge Wells | Well Building | 2004 | Generator Room | 2 | Good
392 | Building Mechanical | Unit Heater 2 | Unit Heater UH-1 | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 1 | Good
395 | Building Electrical | Smoke Detectors | Smoke Detector | Sunrise Ridge Booster Station | Booster Station | 2023 |  | 2 | There were no smoke detectors installed at the station. A smoke detection system in accordance with the requirements of NFPA 820 and OBC is required.
396 | Building Mechanical | Electric Heater | Electric Heater | Sunrise Ridge Booster Station | Booster Station | 2021 | Generator Room | 1 | Good
397 | Building Architectural | Monorail Chain Hoist | Monorail Chain Hoist 0.5 Ton | Sunrise Ridge Booster Station | Booster Station | 2005 | Pump Room | 2 | Good
399 | Building Mechanical | Generator Air Intake Damper | Intake motorized damper and louver | Maley Booster Station | Booster Station | 1992 | Pump Room | 2 | Good
400 | Building Mechanical | Unit Heater 2 | Gas fired unit heater | Maley Booster Station | Booster Station | 1992 | Pump Room | 1 | Good
401 | Building Mechanical | Chain Hoist | Chain Hoist (1 ton) | Maley Booster Station | Booster Station | 1992 | Pump Room | 1 | Good
402 | Building Electrical | Smoke Detector |  | Maley Booster Station | Booster Station | 2023 |  | 2 | There were no smoke detectors installed at the station. A smoke detection system in accordance with the requirements of NFPA 820 and OBC is required.
403 | Building Mechanical | Diesel Engine Silencer and Exhaust Flue |  | Maley Booster Station | Booster Station | 1992 | Generator Room | 2 | Good
406 | Process Mechanical | Tank Gate Valve |  | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good
407 | Process Mechanical | Deep Well #7 Pressure Reducing Valve | Pressure reducing valve | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good
408 | Process Mechanical | Deep Well #6 Pressure Reducing Valve | Pressure reducing valve | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good
409 | Process Mechanical | Deep Well #5 Pressure Reducing Valve | Pressure reducing valve | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good
410 | Process Mechanical | Misc Small Valves | Approx. 33 small valves | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good
411 | Process Instrumentation | Western Main Booster Pump Discharge Pressure Transmitter | Pressure transmitter | Falconbridge Wells | Well Building | 2018 | Pump Room | 1 | Aging | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
412 | Process Instrumentation | Control Valve Pump #5 Switch | Pump switch | Falconbridge Wells | Well Building | 2020 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
413 | Process Instrumentation | Control Valve Pump #6 Switch | Pump switch | Falconbridge Wells | Well Building | 2020 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
414 | Process Instrumentation | Control Valve Pump #7 Switch | Pump switch | Falconbridge Wells | Well Building | 2020 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
416 | Process Instrumentation | CL2 Detector #1 | Chlorine Detector | Falconbridge Wells | Well Building | 2015 | Pump Room | 1 | Aging, Wear and Tear | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
417 | Process Instrumentation | CL2 Detector #2 | Chlorine Detector | Falconbridge Wells | Well Building | 2015 | Pump Room | 1 | Aging, Wear and Tear | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
418 | Process Instrumentation | Discharge Pressure Transducer | Discharge Pressure Transducer | Maley Booster Station | Booster Station | 2020 | Pump Room | 1 | Good | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
420 | Site Works | Double Swing Gate 1 (South Side) | One approx. 4m wide opening double swing at the south side with barbed wire | Falconbridge Wells | Site | 2004 | Site | 1 | Fair | Corrosion of the gates and barbed wires was observed; Corrosion at bottom of gate
421 | Site Works | Double Swing Gate 2 (South Side) | One approx. 4m wide opening double swing at the south side with barbed wire | Falconbridge Wells | Site | 2004 | Site | 1 | Fair | Corrosion of the gates and barbed wires was observed; Corrosion at bottom of gate
423 | Site Works | Well #5 | Well #5, located outside the treatment building to the west, with a depth of appoximately 40m, 100mm dia | Falconbridge Wells | Site | 2004 | Site | 3 | Assumed to be in good condition
424 | Site Works | Well #6 | Well #6, located to the south across Nickel Rim Road, with a depth of approximately 40m, 100mm dia | Falconbridge Wells | Site | 2004 | Site | 3 | Assumed to be in good condition
425 | Site Works | Well #7 | Well #7, located underneath the building, with a depth of appoximately 40m, 100mm dia | Falconbridge Wells | Site | 2004 | Site | 3 | Assumed to be in good condition
426 | Building Structural | Monorail Beam | 0.5 Ton | Sunrise Ridge Booster Station | Booster Station | 2005 | Site | 1 | Good
427 | Building Electrical | Generator Room Emergency Light | battery unit | Falconbridge Wells | Well Building | 2004 | Generator Room | 2 | Good
428 | Building Electrical | Generator Room Exit Sign | exit sign | Falconbridge Wells | Well Building | 2004 | Generator Room | 2 | Good
429 | Building Electrical | Shower Exhuast Fan Control Panel | Control Panel | Falconbridge Wells | Well Building | 2004 | Pump Room | 2 | Good
430 | Building Electrical | Generator Room Exit Sign | exit sign | Maley Booster Station | Booster Station | 2021 | Generator Room | 2 | Very Good
432 | Process Electrical | Battery Charger | Battery Charger | Sunrise Ridge Booster Station | Booster Station | 2005 | Generator Room | 3 | Good
433 | Process Electrical | Battery Charger | Battery Charger | Falconbridge Wells | Well Building | 2004 | Generator Room | 3 | Good
434 | Process Instrumentation | Pump #5 Three Phase Pump Monitor/Protector | Three Phase Pump Monitor/Protector | Falconbridge Wells | Well Building | 2011 | Pump Room | 1 | Aging, Wear and Tear | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
435 | Process Instrumentation | Pump #6 Three Phase Pump Monitor/Protector | Three Phase Pump Monitor/Protector | Falconbridge Wells | Well Building | 2011 | Pump Room | 1 | Aging, Wear and Tear | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
436 | Process Instrumentation | Pump #7 Three Phase Pump Monitor/Protector | Three Phase Pump Monitor/Protector | Falconbridge Wells | Well Building | 2011 | Pump Room | 1 | Aging, Wear and Tear | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
437 | Process Instrumentation | Poly Tank Level Indicator | Poly Tank Level Indicator | Falconbridge Wells | Well Building | 2011 | Fluoride Room | 1 | Aging, Wear and Tear | Installation year and remaining service life estimation based on asset condition of the field device, which is not directly correlated to its age
438 | Process Instrumentation | Corrosion Inhibitor Calibration Unit | Corrosion Inhibitor Calibration Unit | Falconbridge Wells | Well Building | 2019 | Fluoride Room | 1 | Good