## Sheet1
AssetID | ClientAssetID0 | ClientAssetID1 | ClientAssetID2 | UniformatL0 | UniformatL1 | UniformatL2 | UniformatL3 | UniformatL4 | UniformatL5 | MasterFormatX | MasterFormatX2 | FlagAsProcess | FlagAsSubProcess | FlagAsAssembly | FlagAsParent | ParentID | AssetName | CoF | AssetDescription | Owner | Status | SiteName | FacilityName | LocationName | AssetCategory | CustomClientCategory | AssetType | CustomClientAssetType | Manufacturer | Model | SerialNumber | InspectionType | AssessmentYear | InstallYear | AvgESL | ReplaceYear | PhotoName | DrawingName | VisualCondition | PerformanceCondition | PoF | RedundancyFactor | CostID | MaterialUnitCost | Quantity | UnitOfQuantity | CostYear | CostSource | MarkupEquipment | MarkupLabour | MarkupAncillary | MarkupRemoval | MarkupEngineering | MarkupAdministration | MarkupContractor | MarkupContingency | TotalReplacementMarkup | LastEditor | LastEditTime | PlannerReviewer | PlannerReviewTime | DisciplineReview | DisciplineReviewTime | PMReview | PMReviewTime | TempProcess | TempSubProcess | TempSubProcessInstance | SizeCapacity | DBNotes | CountCapex | CountOpex | CountComments | CountDrawings | PreventDeletion | PreventEdit
5 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE |  | Chancery Lane PS |  |  | Halton |  | Chancery Lane PS | WWPS |  | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5947e+18 | [8 empty] | 1 |  | 5_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
6 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE |  | Chartwell Rd. PS |  |  | Halton |  | Chartwell Rd. PS | WWPS |  | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 1.5944e+18 | [8 empty] | 1 |  | 6_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
7 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE |  | Cumnock PS |  |  | Halton |  | Cumnock PS | WWPS |  | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 1.5944e+18 | [8 empty] | 1 |  | 7_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
8 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE |  | Ennisclaire Drive PS |  |  | Halton |  | Ennisclaire Drive PS | WWPS |  | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.596e+18 | [8 empty] | 1 |  | 8_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
9 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE |  | First Street PS |  |  | Halton |  | First Street PS | WWPS |  | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1977 |  |  | HR-FRST-006 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 1.5966e+18 | [8 empty] | 1 |  | 9_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
10 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE |  | Garlock Gdns PS |  |  | Halton |  | Garlock Gdns PS | WWPS |  | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 1.5944e+18 | [8 empty] | 1 |  | 10_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
11 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE |  | Morrison Heights PS |  |  | Halton |  | Morrison Heights PS | WWPS |  | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 1.5944e+18 | [8 empty] | 1 |  | 11_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
12 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE |  | Raymar Pl PS |  |  | Halton |  | Raymar Pl PS | WWPS |  | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 1.5944e+18 | [8 empty] | 1 |  | 12_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
24 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Dry Well Structure | 2 | Chancery Lane PS Dry Well | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Tank, Steel | [5 empty] | 1975 | 60 |  | HR-CNRY-004 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Building | Substructure | 1 |  | 24_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
25 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 5 | Site |  | Chancery Lane PS Site | Halton |  | Chancery Lane PS | WWPS | Site | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 1.5944e+18 | [8 empty] | 1 |  | 25_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
26 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Dry Well Structure | 2 | Chartwell Rd. PS Dry Well | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Building Structural | Building and Process Structural |  | Tank, Steel | [5 empty] | 1983 | 60 |  | HR-CTWL-073 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Building | Substructure | 1 |  | 26_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
27 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 6 | Site |  | Chartwell Rd. PS Site | Halton |  | Chartwell Rd. PS | WWPS | Site | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 1.5944e+18 | [8 empty] | 1 |  | 27_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
28 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 633 | Wet Well Concrete Structure | 2 | Chartwell Rd. PS Wet Well | Halton | In Service | Chartwell Rd. PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Tank, Concrete | [5 empty] | 1983 | 60 |  | HR-CTWL-024 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.5986e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 28_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
29 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Dry Well Structure | 2 | Cumnock PS Dry Well | Halton | In Service | Cumnock PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Tank, Steel | [5 empty] | 1974 | 60 |  | HR-CMNK-122 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Building | Substructure | 1 |  | 29_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
30 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 7 | Site |  | Cumnock PS Site | Halton |  | Cumnock PS | WWPS | Site | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 1.5944e+18 | [8 empty] | 1 |  | 30_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
31 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 641 | Wet Well Concrete Structure | 2 | Cumnock PS Wet Well | Halton | In Service | Cumnock PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Tank, Concrete | [5 empty] | 1974 | 60 |  | HR-CMNK-138 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 31_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
33 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 8 | Site |  | Ennisclaire Drive PS Site | Halton |  | Ennisclaire Drive PS | WWPS | Site | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 1.5944e+18 | [8 empty] | 1 |  | 33_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
34 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 642 | Wet Well Concrete Structure | 2 | Ennisclaire Drive PS Wet Well | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Tank, Concrete | [5 empty] | 1977 | 60 |  | HR-ENIS-002 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 34_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
35 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 9 |  |  | First Street PS | Halton |  | First Street PS | WWPS |  | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 1.5944e+18 | [8 empty] | 1 |  | 35_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
36 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 9 | Dry Well | 2 | First Street PS Dry Well | Halton | In Service | First Street PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Tank, Steel | [5 empty] | 1986 | 60 |  | HR-FRST-065 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Building | Substructure | 1 |  | 36_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
37 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 9 | Site |  | First Street PS Site | Halton |  | First Street PS | WWPS | Site | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1986 | [10 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 1.5944e+18 | Maira Rafiq | 1.6007e+18 | [6 empty] | 1 |  | 37_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
38 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 9 | Wet Well Concrete Structure | 2 | First Street PS Wet Well | Halton | In Service | First Street PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Tank, Concrete | [5 empty] | 1986 | 60 |  | HR-FRST-094 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 38_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
40 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 10 | Site |  | Garlock Gdns PS Site | Halton |  | Garlock Gdns PS | WWPS | Site | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 1.5944e+18 | [8 empty] | 1 |  | 40_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
41 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 10 | Wet Well Concrete Structure | 2 | Garlock Gdns PS Wet Well | Halton | In Service | Garlock Gdns PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Tank, Concrete | [5 empty] | 1977 | 60 |  | HR-GGDN-088 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 41_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
42 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 11 | Dry Well Structure | 2 | Morrison Heights PS Dry Well | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Tank, Steel | [5 empty] | 1973 | 60 | 2033 | HR-MORI-098 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Building | Substructure | 1 |  | 42_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
43 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 11 | Site |  | Morrison Heights PS Site | Halton |  | Morrison Heights PS | WWPS | Site | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 1.5944e+18 | [8 empty] | 1 |  | 43_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
44 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 11 | Wet Well Concrete Structure | 2 | Morrison Heights PS Wet Well | Halton | In Service | Morrison Heights PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Tank, Concrete | [5 empty] | 1973 | 60 | 2033 | HR-MORI-124 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 44_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
45 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 12 | Site |  | Raymar Pl PS Site | Halton |  | Raymar Pl PS | WWPS | Site | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 1.5944e+18 | [8 empty] | 1 |  | 45_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
46 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Wet Well Concrete Structure | 2 | Raymar Pl PS Wet Well | Halton | In Service | Raymar Pl PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Tank, Concrete | [5 empty] | 1985 | 60 |  | HR-RAYM-054 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 46_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
53 |  |  | 201575 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 645 | Sewage Lift Pump #1 | 2 | Sewage Lift Pump #1;Flygt;CP3085.183;;8 L/s at 8m TDH 3 hp | Halton | In Service | Garlock Gdns PS | Garlock Gdns PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | FLYGT | C3085-183-4438 | 3085-183-0710219 |  | 2020 | 1977 | 30 |  | HR-GGDN-015 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 53_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
54 |  |  | 201576 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 53 | Sewage Lift Pump #1 Check Valve | 2 | Check Valve #1;;;;100 mm dia | Halton | In Service | Garlock Gdns PS | Garlock Gdns PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Valve | VALMATIC | SWING FLEX |  |  | 2020 | 1977 | 30 |  | HR-GGDN-006 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 54_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
55 |  |  | 211093 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 53 | Sewage Lift Pump #1 Discharge Valve | 2 | Knife Gate Valve #1;;;;100 mm dia | Halton | In Service | Garlock Gdns PS | Garlock Gdns PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Valve | STAFSJO | NW100 |  |  | 2020 | 1977 | 30 |  | HR-GGDN-005 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 55_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
56 |  |  | 219156 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 41 | Variable Frequency Drive Pump # 1 | 2 | 26.1 AMPS | Halton |  | Garlock Gdns PS | Garlock Gdns PS | Wet Well | Process Electrical | Process Electrical |  | VFD | ALLEN BRADLEY | POWERFLEX-40 | BB024NOW6350010 |  | 2020 | 1977 | 25 |  |  |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 56_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
57 |  |  | 201577 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 645 | Sewage Lift Pump #2 | 2 | Sewage Lift Pump #1;Flygt;CP3085.183;;8 L/s at 8m TDH 3 hp | Halton | Not In Service | Garlock Gdns PS | Garlock Gdns PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | FLYGT | 3085-183-4438 | 3085-183-0710220 |  | 2020 | 1977 | 30 |  | HR-GGDN-016 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 57_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
58 |  |  | 201578 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 57 | Sewage Lift Pump #2 Check Valve | 2 | Check Valve #2;;;;100 mm dia | Halton | In Service | Garlock Gdns PS | Garlock Gdns PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Valve | VALMATIC | SWING FLEX |  |  | 2020 | 1977 | 30 |  | HR-GGDN-010 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 58_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
59 |  |  | 211094 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 57 | Sewage Lift Pump #2 Discharge Valve | 2 | Knife Gate Valve #1;;;;100 mm dia | Halton | In Service | Garlock Gdns PS | Garlock Gdns PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Valve | STAFSJO | NW100 |  |  | 2020 | 1977 | 30 |  | HR-GGDN-012 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 59_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
60 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 40 | Forcemain | 4 | 100mm diameter, approx. 237m ductile forcemain | Halton | In Service | Garlock Gdns PS | Garlock Gdns PS | Site | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 2020 | 1977 | 60 |  |  |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Discharge Header |  |  | 60_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
61 |  |  | 201546 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 648 | Wet Well Exhaust Fan | 1 | 115 VOLTS/PHASE 1, capacity: 325 cfm | Halton |  | Raymar Pl PS | Raymar Pl PS | Wet Well | Building Mechanical | Building Services |  | Fan |  |  |  |  | 2020 | 1985 | 30 |  | HR-RAYM-001 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 1.5961e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | HVAC - Distribution Systems |  |  | 61_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
62 |  |  | 201547 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 648 | Sewage Lift Pump #1 | 2 | Sewage Lift Pump #1;Flygt;CP3101;;6.6 L/s at 11.4 m TDH 5 HP | Halton | In Service | Raymar Pl PS | Raymar Pl PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | FLYGT | 3101 MT | 10534 |  | 2020 | 1985 | 30 |  | HR-RAYM-025 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 62_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
63 |  |  | 211079 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 62 | Sewage Lift Pump #1 Check Valve | 2 | Check Valve #1;Flygt;;;100 mm dia | Halton | In Service | Raymar Pl PS | Raymar Pl PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Valve | HILLEN DE LELIE | BALL CHECK |  |  | 2020 | 1985 | 30 |  | HR-RAYM-009 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 63_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
64 |  |  | 211080 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 62 | Sewage Lift Pump #1 Discharge Valve | 2 | Gate Valve #1;;;;100 mm dia | Halton | In Service | Raymar Pl PS | Raymar Pl PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Valve | JENKINS | GATE VALVE |  |  | 2020 | 1985 | 30 |  | HR-RAYM-010 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 64_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
65 |  |  | 201548 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 648 | Sewage Lift Pump #2 | 2 | Sewage Lift Pump #2;Flygt;CP3101;;6.6 L/s at 11.4 m TDH 5 HP | Halton | In Service | Raymar Pl PS | Raymar Pl PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | FLYGT | C3102-180 | 355048-433 |  | 2020 | 1985 | 30 |  | HR-RAYM-012 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 65_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
66 |  |  | 211081 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 65 | Sewage Lift Pump #1 Check Valve | 2 | Check Valve #1;Flygt;;;100 mm dia | Halton | In Service | Raymar Pl PS | Raymar Pl PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Valve | HILLEN DE LELIE | BALL CHECK |  |  | 2020 | 1985 | 30 |  | HR-RAYM-007 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 66_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
67 |  |  | 211082 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 65 | Sewage Lift Pump #1 Discharge Valve | 2 | Gate Valve #2;;;;100 mm dia | Halton | In Service | Raymar Pl PS | Raymar Pl PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Valve | JENKINS | GATE VALVE |  |  | 2020 | 1985 | 30 |  | HR-RAYM-006 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 67_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
68 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 45 | Forcemain | 4 | 100mm diameter, approx. 165m PVC SDR 35 pipe | Halton | In Service | Raymar Pl PS | Raymar Pl PS | Site | Process Mechanical | Process Piping |  | Piping, PVC |  |  |  |  | 2020 | 1985 | 60 |  |  |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Discharge Header |  |  | 68_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
69 |  |  | 201661 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 646 | Dry Well Sump Pump | 1 | 1/4" | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Pump, Centrifugal |  | SE-CIA-SFS |  |  | 2020 | 1973 | 30 |  | HR-MORI-024 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 1.5961e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly |  |  | 69_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
70 |  |  | 201662 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 647 | TRANSMITTER LEVEL WET WELL #1 | 2 | 72" Wet Well Level Transmitter; Siemens Milltronics; Multiranger 100; ; ; | Halton | In Service | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Instrumentation | Process Instrumentation |  | Transmitter | MILLTRONICS | MULTIRANGER 100 | 012105122XB |  | 2020 | 2008 | 15 | 2030 | HR-MORI-009 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 1.5966e+18 | Maira Rafiq | 1.5983e+18 |  |  |  |  | Pumping | Wet Well |  |  | 70_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
71 |  |  | 201653 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 646 | Dry Wall Exhaust Fan | 1 |  | Halton |  | Morrison Heights PS | Morrison Heights PS | Dry Well | Building Mechanical | Building Services |  | Fan | FASCO | D112 | 7108-0195 |  | 2020 | 1973 | 30 |  | HR-MORI-115 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 1.5961e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | HVAC - Distribution Systems |  |  | 71_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
72 |  |  | 201654 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 646 | Sewage Lift Pump #1 | 2 | Sewage Lift Pump #1;Clow Pumps;N4310;;12 L/s 7.5 hp | Halton | In Service | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | CLOW | N 4310 | 918126 |  | 2020 | 1973 | 30 |  | HR-MORI-020 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 72_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
73 |  |  | 217113 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 72 | Sewage Lift Pump #1 Check Valve | 2 | Check Valve #1;Swing-Flex;Model 504A;;100 mm dia | Halton | In Service | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | EDDY IOWA |  |  |  | 2020 | 1973 | 30 |  | HR-MORI-019 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 73_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
74 |  |  | 201656 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 72 | Sewage Lift Pump #1 Motor Drive | 2 | 7.5 HP | Halton |  | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Electrical | Process Electrical |  | Motor | U.S. MOTORS | TYPE 1 | 9204320-901 |  | 2020 | 1973 | 25 |  | HR-MORI-012 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 74_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
75 |  |  | 211145 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 72 | Sewage Lift Pump #1 Inlet Valve | 2 | Inlet Knife Gate Valve #1;Trueline;;;100 mm dia | Halton | In Service | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | IOWA |  |  |  | 2020 | 1973 | 30 |  | HR-MORI-022 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 75_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
76 |  |  | 211146 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 72 | Sewage Lift Pump #1 Discharge Valve | 2 | Discharge Knife Gate Valve #1;Trueline;;;100 mm dia | Halton | In Service | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | IOWA |  |  |  | 2020 | 1973 | 30 |  | HR-MORI-018 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 76_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
78 |  |  | 201657 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 646 | Sewage Lift Pump #2 | 2 | Sewage Lift Pump #2;Clow Pumps;N4310;;12 L/s 7.5 hp | Halton | In Service | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | CLOW | N 4310 | 918126 |  | 2020 | 1973 | 30 |  | HR-MORI-012 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 78_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
79 |  |  | 201658 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 78 | Sewage Lift Pump #2 Check Valve | 2 | Check Valve #2;Swing-Flex;Model 504A;;100 mm dia | Halton | In Service | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | EDDY IOWA |  |  |  | 2020 | 1973 | 30 |  | HR-MORI-014 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 79_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
80 |  |  | 201659 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 78 | Sewage Lift Pump #2 Motor Drive | 2 | 7.5 HP | Halton |  | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Electrical | Process Electrical |  | Motor | U.S. ELECTRIC MOTORS |  | 9204320-901 |  | 2020 | 1973 | 25 |  | HR-MORI-020 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 80_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
81 |  |  | 211147 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 78 | Sewage Lift Pump #2 Inlet Valve | 2 | Inlet Knife Gate Valve #1;Trueline;;;100 mm dia | Halton | In Service | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | IOWA |  |  |  | 2020 | 1973 | 30 |  | HR-MORI-011 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 81_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
82 |  |  | 211148 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 78 | Sewage Lift Pump #2 Discharge Valve | 2 | Discharge Knife Gate Valve #1;Trueline;;;100 mm dia | Halton | In Service | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | IOWA |  |  |  | 2020 | 1973 | 30 |  | HR-MORI-015 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 82_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
83 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 43 | Forcemain | 5 | 150mm diameter, approx. 254m PVC series 125 pipe | Halton | In Service | Morrison Heights PS | Morrison Heights PS | Site | Process Mechanical | Process Piping |  | Piping, PVC |  |  |  |  | 2020 | 1973 | 60 |  |  |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Discharge Header |  |  | 83_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
129 |  |  | 201612 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 24 | PUMP #1 SUMP | 1 | Sump Pump;;;; | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Building Mechanical | Building Services |  | Pump | HYDROMATIC |  |  |  | 2020 | 1975 | 30 |  | HR-CNRY-010 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5952e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Pumping | Pump Assembly |  |  | 129_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
130 |  |  | 211126 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 638 | TRANSMITTER LEVEL WET WELL | 2 | 94.5" Wet Well Level Transmitter; Siemens Milltronics; MultiRanger 200; ; ; | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Instrumentation | Process Instrumentation |  | Transmitter | MILLTRONICS | MULTIRANGER PLUS | 082191 012-19 |  | 2020 | 2009 | 15 | 2030 | HR-CNRY-008 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 1.5966e+18 | Maira Rafiq | 1.5983e+18 |  |  |  |  | Pumping | Wet Well |  |  | 130_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
131 |  |  | 201605 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 638 | FAN EXHAUST #1 | 1 | 115 VOLTS/PHASE 1 | Halton | Missing | Chancery Lane PS | Chancery Lane PS | Dry Well | Building Mechanical | Building Services |  | Fan |  |  |  |  | 2020 | 1975 | 30 |  |  |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 1.5961e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Building | HVAC - Distribution Systems |  |  | 131_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
132 |  |  | 201606 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 638 | Sewage Lift Pump #1 | 2 | Sewage Lift Pump #1;Smith & Loveless;4B2A;;16.7 L/s at 11.6 m TDH 5HP | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Pump | SMITH AND LOVELESS | 4B2A | 9750232 |  | 2020 | 1975 | 30 |  | HR-CNRY-012 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5952e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 132_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
133 |  |  | 201607 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 132 | Sewage Lift Pump #1 Check Valve | 2 | Check Valve #1;Smith & Loveless;;150 mm dia | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | SMITH AND LOVELESS |  |  |  | 2020 | 1975 | 30 |  | HR-CNRY-014 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5952e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 133_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
134 |  |  | 201608 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 638 | MOTOR DRIVE SEWAGE LIFT PUMP #1 | 2 | 5 HP/1160 RPM | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Electrical | Process Electrical |  | Motor | ROBBIN & MYERS | S & L - N-BPM1 | CF50232 |  | 2020 | 1975 | 25 |  | HR-CNRY-116 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.6004e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 134_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
135 |  |  | 211127 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 132 | Sewage Lift Pump #1 Inlet Valve | 2 | Inlet Gate Valve No.1;Smith & Loveless;;;150 mm dia | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | STOCKHAM |  |  |  | 2020 | 1975 | 30 |  | HR-CNRY-011 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5952e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 135_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
136 |  |  | 211128 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 132 | Sewage Lift Pump #1 Discharge Valve | 2 | Discharge Gate Valve No.1;Smith & Loveless;;;150 mm dia | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | STOCKHAM |  |  |  | 2020 | 1975 | 30 |  | HR-CNRY-015 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5952e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 136_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
137 |  |  | 201609 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 638 | Sewage Lift Pump #2 | 2 | Sewage Lift Pump #2;Smith & Loveless;4B2A;;16.7 L/s at 11.6 m TDH 5HP | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | SMITH AND LOVELESS | 4B2A | 9750232 |  | 2020 | 1975 | 30 |  | HR-CNRY-022 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5952e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 137_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
138 |  |  | 201610 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 137 | Sewage Lift Pump #2 Check Valve | 2 | Check Valve #2;Smith & Loveless;;150 mm dia | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | SMITH AND LOVELESS |  |  |  | 2020 | 1975 | 30 |  | HR-CNRY-021 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5952e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 138_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
139 |  |  | 201611 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 24 | MOTOR DRIVE SEWAGE LIFT PUMP #2 | 2 | 5 HP/1160 RPM | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Electrical | Process Electrical |  | Motor | ROBBIN & MYERS | S&L- N-BPMII | CB50231 |  | 2020 | 1975 | 25 |  | HR-CNRY-116 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.6004e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 139_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
140 |  |  | 211129 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 137 | Sewage Lift Pump #2 Inlet Valve | 2 | Inlet Gate Valve No.2;Smith & Loveless;;;150 mm dia | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | STOCKHAM |  |  |  | 2020 | 1975 | 30 |  | HR-CNRY-020 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5952e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 140_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
141 |  |  | 211130 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 137 | Sewage Lift Pump #1 Discharge Valve | 2 | Discharge Gate Valve No.2;Smith & Loveless;;;150 mm dia | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | STOCKHAM |  |  |  | 2020 | 1975 | 30 |  | HR-CNRY-023 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5952e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 141_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
142 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 25 | Forcemain | 4 | 150mm diameter, approx. 350 m ductile Iron forcemain piping | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Site | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 2020 | 1975 | 60 |  |  |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5952e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Pumping | Discharge Header |  |  | 142_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
143 |  |  | 201557 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 26 | PUMP #1 SUMP | 1 | Sump Pump;;;; | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Building Mechanical | Building Services |  | Pump, Centrifugal | SMITH AND LOVELESS |  |  |  | 2020 | 1983 | 30 |  | HR-CTWL-019 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5952e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Pumping | Pump Assembly |  |  | 143_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
144 |  |  | 201558 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 633 | WET WELL LEVEL TRANSMITTER #1 | 2 | 80" Wet Well Level Transmitter; Siemens Milltronics; Multiranger Plus; ; ; | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation |  | Transmitter | MILLTRONICS | MULTIRANGER PLUS | 061489 186-07 |  | 2020 | 2009 | 15 | 2025 | HR-CTWL-005 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 1.5966e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Pumping | Wet Well |  |  | 144_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
145 |  |  | 201550 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 632 | FAN EXHAUST #1 | 1 | 115 VOLTS/PHASE 1 | Halton | Missing | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Building Mechanical | Building Services |  | Fan |  |  |  |  | 2020 | 1983 | 30 | 2021 |  |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 1.5961e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Building | HVAC - Distribution Systems |  |  | 145_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
146 |  |  | 201551 | 0 | [7 empty] | FALSE | FALSE | FALSE | TRUE | 632 | Sewage Lift Pump #1 | 2 | Sewage Lift Pump #1;Smith & Loveless;4B2;;;16.5 L/s at 10.1 m TDH 5 HP | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | SMITH AND LOVELESS | 4B2 | 6537098 |  | 2020 | 1983 | 30 |  | HR-CTWL-017 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5952e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 146_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
147 |  |  | 201552 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 146 | Sewage Lift Pump #1 Check Valve | 2 | Discharge Check Valve #1;Smith and Loveless;;;150 mm dia | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | SMITH AND LOVELESS |  |  |  | 2020 | 1983 | 30 |  | HR-CTWL-016 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5952e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 147_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
148 |  |  | 201553 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 146 | Sewage Lift Pump #1 Motor Drive | 2 | 5 HP/1160 RPM | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Motor | ROBIN MYERS |  | ABM3U7098 |  | 2020 | 1983 | 30 |  | HR-CTWL-017 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.6006e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 148_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
149 |  |  | 211083 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 26 | Sewage Lift Pum #1 Inlet Valve | 2 | Inlet Gate Valve #1;Clow;;;150 mm dia | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | EDDY IOWA |  |  |  | 2020 | 1983 | 30 | 0 | HR-CTWL-018 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5952e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 149_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
150 |  |  | 211084 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 146 | Sewage Lift Pump #1 Discharge Valve | 2 | Discharge Gate Valve #1;Clow;;;150 mm dia | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | CLOW |  |  |  | 2020 | 1983 | 30 |  | HR-CTWL-015 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5952e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 150_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
151 |  |  | 201554 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 632 | Sewage Lift Pump #2 | 2 | Sewage Lift Pump #2;Smith & Loveless;4B2;;;16.5 L/s at 10.1 m TDH 5 HP | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | SMITH AND LOVELESS | 4B2 | 6537097 |  | 2020 | 1983 | 30 |  | HR-CTWL-010 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5952e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 151_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
152 |  |  | 201555 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 151 | Sewage Lift Pump #2 Check Valve | 2 | Discharge Check Valve #2;Smith and Loveless;;;150 mm dia | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | SMITH AND LOVELESS |  |  |  | 2020 | 1983 | 30 |  | HR-CTWL-012 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5952e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 152_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
153 |  |  | 201556 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 151 | Sewage Lift Pump #2 Motor Drive | 2 | 5 HP/1160 RPM | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Motor | ROBIN MYERS |  | ABM3U7097 |  | 2020 | 1983 | 30 |  | HR-CTWL-027 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.6006e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 153_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
154 |  |  | 211085 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 151 | Sewage Lift Pump #2 Inlet Valve | 2 | Inlet Gate Valve #2;Clow;;;150 mm dia | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | EDDY IOWA |  |  |  | 2020 | 1983 | 30 |  | HR-CTWL-009 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5952e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 154_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
155 |  |  | 211086 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 151 | Sewage Lift Pump #2 Discharge Valve | 2 | Discharge Gate Valve #2;Clow;;;150 mm dia | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | CLOW |  |  |  | 2020 | 1983 | 30 |  | HR-CTWL-013 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5952e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 155_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
156 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 27 | Forcemain | 4 | 200mm diameter, approx. 40m ductile iron forcemain | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Site | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 2020 | 1983 | 60 |  |  |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Pumping | Discharge Header |  |  | 156_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
157 |  |  | 201649 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 29 | PUMP SUMP | 1 | Sump Pump;;;; | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Building Mechanical | Building Services |  | Pump, Centrifugal |  |  |  |  | 2020 | 1974 | 30 |  | HR-CMNK-021 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly |  |  | 157_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
158 |  |  | 201651 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 641 | TRANSMITTER LEVEL WET WELL #1 | 2 | 76.25" Wet Well Level Transmitter; Siemens Milltronics; Multiranger Plus; ; ; | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Process Instrumentation | Process Instrumentation |  | Transmitter | MILLTRONICS | MULTIRANGER PLUS | 05-25-94 118-6D |  | 2020 | 2009 | 15 | 2030 | HR-CMNK-005 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 1.5966e+18 | Maira Rafiq | 1.5983e+18 |  |  |  |  | Pumping | Wet Well |  |  | 158_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
159 |  |  | 201640 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 640 | Dry Well Exhaust Fan | 1 | 115 VOLTS, installation year assumed to be 1974 | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Building Mechanical | Building Services |  | Fan |  |  |  |  | 2020 | 1974 | 30 |  | HR-CMNK-121 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 1.5961e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Building | HVAC - Distribution Systems |  |  | 159_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
160 |  |  | 201641 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 640 | Sewage Lift Pump #1 | 2 | Sewage Lift Pump #1;Clow;N4310;;6.3 L/s 3 hp | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | CLOW | N4310 | 918126 |  | 2020 | 1974 | 30 |  | HR-CMNK-013 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 160_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
161 |  |  | 201642 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 160 | Sewage Lift Pump #1 Check Valve | 2 | Check Valve #1;Crow;;;100 mm dia | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | IOWA |  |  |  | 2020 | 1974 | 30 |  | HR-CMNK-014 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 161_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
162 |  |  | 201643 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 29 | Sewage Lift Pump #1 Motor Drive | 2 | 7.9HP | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Process Electrical | Process Electrical |  | Motor | U.S. MOTORS | AV-9 | R2071304 |  | 2020 | 1974 | 25 |  | HR-CMNK-013 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 162_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
163 |  |  | 211141 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 160 | Sewage Lift Pump #1 Inlet Valve | 2 | Inlet Gate Valve #1;Crow;;;100 mm dia | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | IOWA |  |  |  | 2020 | 1974 | 30 |  | HR-CMNK-011 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 163_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
164 |  |  | 211142 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 160 | Sewage Lift Pump #1 Discharge Valve | 2 | Discharge Gate Valve #1;Crow;;;100 mm dia | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | IOWA |  |  |  | 2020 | 1974 | 30 |  | HR-CMNK-015 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 164_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
165 |  |  | 201645 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 640 | Sewage Lift Pump #2 | 2 | Sewage Lift Pump #2;Clow;N4310;;6.3 L/s 3 hp | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | CLOW | N4310 | 918127 |  | 2020 | 1974 | 30 |  | HR-CMNK-019 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 165_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
166 |  |  | 201646 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 165 | Sewage Lift Pump #2 Check Valve | 2 | Check Valve #1;Crow;;;100 mm dia | Halton | 20 | Cumnock PS | Cumnock PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | IOWA |  |  |  | 2020 | 1974 | 30 |  | HR-CMNK-018 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 166_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
167 |  |  | 201647 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 29 | Sewage Lift Pump #2 Motor Drive | 2 | 7.5P | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Process Electrical | Process Electrical |  | Motor | U.S. MOTORS | AV-9 | R2071304 |  | 2020 | 1974 | 25 |  | HR-CMNK-019 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 167_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
168 |  |  | 211143 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 165 | Sewage Lift Pump #2 Inlet Valve | 2 | Inlet Gate Valve #2;Crow;;;100 mm dia | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | IOWA |  |  |  | 2020 | 1974 | 30 |  | HR-CMNK-020 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 168_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
169 |  |  | 211144 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 165 | Sewage Lift Pump #2 Discharge Valve | 2 | Discharge Gate Valve #2;Crow;;;100 mm dia | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | IOWA (CLOW) |  |  |  | 2020 | 1974 | 30 |  | HR-CMNK-017 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 169_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
170 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 30 | Forcemain | 4 | 150mm diameter, approx. 79 m ductile iron pipe | Halton | In Service | Cumnock PS | Cumnock PS | Site | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 2020 | 1974 | 60 |  |  |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Discharge Header |  |  | 170_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
172 |  |  | 211126 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 642 | TRANSMITTER LEVEL WET WELL | 2 | 94.5" Wet Well Level Transmitter; Siemens Milltronics; Multiranger 200; ; ; | Halton | In Service | Ennisclaire Drive PS | WWPS | Site | Process Instrumentation | Process Instrumentation |  | Transmitter | MILLTRONICS | MULTIRANGER PLUS | 082191 012-19 |  | 2020 | 2019 | 15 | 2035 | HR-ENIS-030 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 1.5966e+18 | Maira Rafiq | 1.5983e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 172_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
174 |  |  | 201606 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 642 | Sewage Lift Pump #1 | 2 | Sewage Pump #1;Flygt;C3082MT;;7.8 L/s at 7.2 m TDH 2hp | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | SMITH AND LOVELESS | 4B2A | 9750232 |  | 2020 | 1977 | 30 |  | HR-ENIS-009 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 174_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
175 |  |  | 201607 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 174 | Sewage Lift Pump #1 Check Valve | 2 | Check Valve #1;;;;100 mm dia | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | SMITH AND LOVELESS |  |  |  | 2020 | 1977 | 30 |  | HR-ENIS-010 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 175_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
177 |  |  | 211127 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 174 | Sewage Lift Pump #1 Knife Gate Valve | 2 | Knife Gate Valve #1;;;;100 mm dia | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | STOCKHAM |  |  |  | 2020 | 1977 | 30 |  | HR-ENIS-012 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 177_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
178 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 33 | Forcemain | 3 | 100mm diameter, approx. 290m Ductile Iron forcemain | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Site | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 2020 | 1977 | 60 |  |  |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Discharge Header |  |  | 178_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
179 |  |  | 201543 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 643 | Sump Pump #1 | 1 | Sump Pump;;;; | Halton | In Service | First Street PS | First Street PS | Dry Well | Building Mechanical | Building Services |  | Pump, Submersible | HYDROMATIC | SV-25A |  |  | 2020 | 1986 | 30 |  | HR-FRST-009 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Building | Plumbing - Sanitary Waste |  |  | 179_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
180 |  |  | 201545 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 644 | TRANSMITTER LEVEL WET WELL #1 | 2 | 18.5" Wet Well Level Transmitter; Siemens Milltronics; Multiranger Plus; ; ; | Halton | In Service | First Street PS | First Street PS | Dry Well | Process Instrumentation | Process Instrumentation |  | Transmitter | MILLTRONICS | MULTIRANGER PLUS | 05-17-94 211GE |  | 2020 | 2009 | 15 | 2030 | HR-FRST-006 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 1.5966e+18 | Maira Rafiq | 1.5983e+18 |  |  |  |  | Pumping | Wet Well |  |  | 180_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
181 |  |  | 201536 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 643 | Dry Well Exhaust Fan | 1 | 115 V./60 HZ., Installation year assumed to be 1985 | Halton |  | First Street PS | First Street PS | Dry Well | Building Mechanical | Building Services |  | Fan | DAYTON | 40 |  |  | 2020 | 1986 | 30 |  | HR-FRST-018 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 1.5961e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | HVAC - Distribution Systems |  |  | 181_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
182 |  |  | 201537 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 643 | Sewage Lift Pump #1 | 2 | Sewage Lift Pump #1;Clow;Model 4310;;15.8 L/s at 12.2 m TDH 7.5hp | Halton | In Service | First Street PS | First Street PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Pump | CLOW | 431O | 261755 |  | 2020 | 1986 | 30 |  | HR-FRST-016 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 182_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
183 |  |  | 201538 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 182 | Sewage Lift Pump #1 Check Valve | 2 | Check Valve #1;Kennedy;;;100 mm dia | Halton | In Service | First Street PS | First Street PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | KENNEDY | FIG 106 | 11071 |  | 2020 | 1986 | 30 |  | HR-FRST-015 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 183_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
184 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 36 | Sewage Lift Pump #2 Motor Drive | 2 | 7.5 HP/1755 RPM | Halton |  | First Street PS | First Street PS | Dry Well | Process Electrical | Process Electrical |  | Motor | RELIANCE ELECTRIC | P | 1YAB31452A1 |  | 2020 | 1986 | 25 |  |  |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 184_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
185 |  |  | 211075 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 182 | Sewage Lift Pump #1 Inlet Valve | 2 | Inlet Gate Valve #1;Kennedy;;;100 mm dia | Halton | In Service | First Street PS | First Street PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | CLOW | EDDY IOWA |  |  | 2020 | 1986 | 30 |  | HR-FRST-014 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 185_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
186 |  |  | 211076 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 182 | Sewage Lift Pump #1 Discharge Valve | 2 | Discharge Gate Valve #1;Kennedy;;;100 mm dia | Halton | In Service | First Street PS | First Street PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | CLOW | EDDY IOWA |  |  | 2020 | 1986 | 30 |  | HR-FRST-017 |  | 5 |  | 5 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 186_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
187 |  |  | 201540 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 643 | Sewage Lift Pump #2 | 2 | Sewage Lift Pump #2;Clow;Model 4310;;15.8 L/s at 12.2 m TDH 7.5hp | Halton | In Service | First Street PS | First Street PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Pump | CLOW | 431O | 261755 |  | 2020 | 1986 | 30 |  | HR-FRST-010 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 187_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
188 |  |  | 201541 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 187 | Sewage Lift Pump #2 Check Valve | 2 | Check Valve #1;;;;100 mm dia | Halton | In Service | First Street PS | First Street PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | KENNEDY | FIG 106 | 11071 |  | 2020 | 1986 | 30 |  | HR-FRST-011 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 188_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
189 |  |  | 201542 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 36 | Sewage Lift Pump #2 Motor Drive | 2 | 7.5 HP/1755 RPM | Halton | In Service | First Street PS | First Street PS | Dry Well | Process Electrical | Process Electrical |  | Motor | RELIANCE ELECTRIC | P | 1YAB31452A2UK |  | 2020 | 1986 | 25 |  | HR-FRST-023 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 189_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
190 |  |  | 211077 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 187 | Sewage Lift Pump #2 Inlet Valve | 2 | Inlet Gate Valve #1;;;;100 mm dia | Halton | In Service | First Street PS | First Street PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | CLOW | EDDY IOWA |  |  | 2020 | 1986 | 30 |  | HR-FRST-030 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 190_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
191 |  |  | 211078 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 187 | Sewage Lift Pump #2 Disccharge Valve | 2 | Discharge Gate Valve #1;;;;100 mm dia | Halton | In Service | First Street PS | First Street PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | CLOW | EDDY IOWA |  |  | 2020 | 1986 | 30 |  | HR-FRST-012 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 191_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
192 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 37 | Forcemain | 4 | 150mm diameter, approx. 150 m PVC pipe | Halton | In Service | First Street PS | First Street PS | Site | Process Mechanical | Process Piping |  | Piping, PVC |  |  |  |  | 2020 | 1986 | 60 |  |  |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Discharge Header |  |  | 192_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
237 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 25 | Overflow Piping | 3 | 250mm diameter, approx. 147 m concrete pipe | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Site | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1975 | 60 |  | HR-CNRY-043 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5952e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Pumping | Wet Well |  |  | 237_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
238 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 638 | Discharge Header | 3 | 150mm diameter, approx. 5 m cast iron piping | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1975 | 60 |  | HR-CNRY-031 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5952e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Pumping | Discharge Header |  |  | 238_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
240 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 132 | Pump 1 Piping | 3 | 150mm diameter, approx. 4.5m ductile piping | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1975 | 60 | 0 | HR-CNRY-116 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.6004e+18 |  |  |  |  | Pumping | Discharge Header | 1 |  | 240_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
241 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 137 | Pump 2 Piping | 3 | 150mm diameter, approx. 4.5m ductile piping | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1975 | 60 | 0 | HR-CNRY-116 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.6004e+18 |  |  |  |  | Pumping | Discharge Header | 2 |  | 241_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
242 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 27 | Overflow Piping | 3 | 250mm diameter, approx. 10.5 m (4.5 m PVC pipe, 6 m CMP pipe) | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Site | Process Mechanical | Process Piping |  | Piping, PVC |  |  |  |  | 0 | 1983 | 60 |  |  |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | [6 empty] | Pumping | Wet Well |  |  | 242_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
243 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 146 | Pump 1 Piping | 3 | 150mm diameter, approx. 5m ductile iron pipe | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1983 | 60 |  | HR-CTWL-033 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Pumping | Pump Assembly |  |  | 243_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
244 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 633 | Bar Screen | 2 | Bar Screen;;;; | Halton |  | Chartwell Rd. PS | Chartwell Rd. PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Screen |  |  |  |  | 0 | 1983 | 30 |  | HR-CTWL-054 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Pumping | Wet Well |  |  | 244_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
247 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 30 | Overflow Piping | 3 | 300mm diameter, approx. 2.5m CMP pipe | Halton | In Service | Cumnock PS | Cumnock PS | Site | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1974 | 60 |  | HR-CMNK-147 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Wet Well |  |  | 247_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
248 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 160 | Pump 1 Piping | 3 | 100mm diameter, approx. 5m ductile pipe | Halton | In Service | Cumnock PS | Cumnock PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1974 | 60 |  | HR-CMNK-010 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 248_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
249 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 641 | Bar Screen | 2 | Bar Screen | Halton | In Service | Cumnock PS | Cumnock PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1974 | 30 |  | HR-CMNK-136 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Wet Well |  |  | 249_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
250 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 640 | Discharge Header | 3 | 100mm diameter, approx. 5m, ductile iron stand pipe | Halton |  | Cumnock PS | Cumnock PS | Dry Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1974 | 60 | 0 |  |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Discharge Header |  |  | 250_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
251 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 33 | Overflow Piping | 3 | 200mm diameter, approx. 22m | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Site | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1977 | 60 |  |  |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Wet Well |  |  | 251_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
252 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 174 | Pump 1 Piping | 3 | 100mm diameter, approx. 5 m | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1977 | 60 |  | HR-ENIS-013 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 252_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
253 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 399 | Pump 2 Piping | 3 | 100mm diameter, approx. 5m | Halton |  | Ennisclaire Drive PS | WWPS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1977 | 60 | 0 | HR-ENIS-013 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 253_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
254 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 38 | Overflow Piping | 3 | 250mm diameter, approx. 3.5 m connect to storm sewer | Halton | In Service | First Street PS | First Street PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1986 | 60 |  | HR-FRST-012 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Suction |  |  | 254_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
255 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 35 | Emergency Pumping Riser | 3 | 100mm diameter, approx. 1.6m | Halton |  | First Street PS | First Street PS |  | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1986 | 60 |  |  |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [18 empty] | Pumping | Discharge Header |  |  | 255_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
256 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 182 | Pump 1 Piping | 3 | 100mm diameter, approx. 5 m ductile iron pipe | Halton | In Service | First Street PS | First Street PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1986 | 60 |  | HR-FRST-013 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Suction |  |  | 256_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
257 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 187 | Pump 2 Piping | 3 | 100mm diameter, approx. 3m ductile iron pipe | Halton | In Service | First Street PS | First Street PS |  | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1986 | 60 | 0 |  |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly |  |  | 257_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
258 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 643 | Discharge Header | 3 | 100mm diameter, approx. 7m ductile iron | Halton | In Service | First Street PS | First Street PS | Dry Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1986 | 60 | 0 |  |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Discharge Header |  |  | 258_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
259 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 40 | Overflow Piping | 3 | 300mm diameter, approx. 6m | Halton |  | Garlock Gdns PS | Garlock Gdns PS | Site | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1977 | 60 |  |  |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | [6 empty] | Pumping | Wet Well |  |  | 259_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
260 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 53 | Pump 1 Discharge Piping | 3 | 100mm diameter, approx. 5m ductile pipe | Halton | In Service | Garlock Gdns PS | Garlock Gdns PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1977 | 60 |  | HR-GGDN-014 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 260_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
261 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 57 | Pump 2 Discharge Piping | 3 | 100mm diameter, approx. 5m ductile pipe | Halton | In Service | Garlock Gdns PS | Garlock Gdns PS | Dry Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1977 | 60 | 0 |  |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 261_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
262 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 43 | Overflow Piping | 3 | 150mm diameter, approx. 9 m overflow piping | Halton | In Service | Morrison Heights PS | Morrison Heights PS | Site | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1973 | 60 |  | HR-MORI-123 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Wet Well |  |  | 262_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
263 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 72 | Pump 1 Piping | 3 | Ductile Iron, 100mm dia, 5 m length | Halton |  | Morrison Heights PS | Morrison Heights PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1973 | 60 |  | HR-MORI-115 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Suction | 1 |  | 263_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
264 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 78 | Pump 2 Piping | 3 | Ductile Iron, 100mm dia, 5 m length | Halton |  | Morrison Heights PS | Morrison Heights PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1973 | 60 | 0 | HR-MORI-115 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 264_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
265 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 646 | Discharge Piping | 3 | Ductile Iron, 100mm dia, 5 m length | Halton |  | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1973 | 60 | 0 | HR-MORI-115 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Wet Well |  |  | 265_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
266 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 648 | Overflow Piping | 3 | 100mm diameter, approx. 4.5m | Halton | In Service | Raymar Pl PS | Raymar Pl PS | Wetwell | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1985 | 60 |  |  |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Wet Well |  |  | 266_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
267 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 62 | Pump 1 Discharge Piping | 3 | 100mm diameter, approx. 5m ductile pipe | Halton |  | Raymar Pl PS | Raymar Pl PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1985 | 60 | 0 | HR-RAYM-040 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 267_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
268 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 65 | Pump 2 Discharge Piping | 3 | 100mm diameter, approx. 8.6 m ductile iron pipe | Halton | In Service | Raymar Pl PS | Raymar Pl PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1985 | 60 |  | HR-RAYM-040 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Wet Well | 2 |  | 268_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
301 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 639 | Wet Well Concrete Structure | 2 |  | Halton | In Service | Chancery Lane PS | WWPS | Process Structural | Process Structural | Building and Process Structural |  | Tank, Concrete | [5 empty] | 1975 | 60 |  | HR-CNRY-033 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 302_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
302 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Dry Well Access Hatch | 1 | Chancery Lane PS Dry Well | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1975 | 60 | 2035 | HR-CNRY-037 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Building | Substructure | 1 |  | 303_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
303 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Dry Well Access Ladder | 2 | Chancery Lane PS Dry Well | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1975 | 60 | 2035 | HR-CNRY-004 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Building | Substructure | 1 |  | 304_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
304 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Protective Paint | 1 | Chancery Lane PS Dry Well | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Misc. Structural | [5 empty] | 1975 | 60 | 2035 | HR-CNRY-041 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Building | Interior Finishes | 1 |  | 305_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
305 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 639 | Manhole Frame and Cover | 1 |  | Halton | In Service | Chancery Lane PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Misc. Structural | [5 empty] | 1975 | 60 |  | HR-CNRY-035 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 307_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
306 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 639 | Wet Well Access Ladder | 2 |  | Halton | In Service | Chancery Lane PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1975 | 60 | 2035 | HR-CNRY-033 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 308_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
307 |  |  |  | 0 |  |  |  |  | 0 |  |  | TRUE | FALSE | FALSE | FALSE | 639 | Wet Well Aluminum Platform | 2 |  | Halton | In Service | Chancery Lane PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1975 | 60 | 2035 | HR-CNRY-033 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 309_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
308 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 639 | Wet Well Aluminum Guardrail | 2 |  | Halton | In Service | Chancery Lane PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1975 | 60 | 2035 | HR-CNRY-033 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 310_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
309 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Davit Socket Base | 2 |  | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Misc. Structural | [5 empty] | 1975 | 60 | 2035 | HR-CNRY-037 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Building |  | 1 |  | 312_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
317 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Dry Well Access Ladder | 2 | Chartwell Rd. PS Dry Well | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1983 | 60 | 2046 | HR-CTWL-024 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Building | Interior Construction | 1 |  | 320_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
318 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Dry Well Access Hatch | 1 | Chartwell Rd. PS Dry Well | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1983 | 60 | 2046 | HR-CTWL-023 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Building | Interior Construction | 1 |  | 321_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
319 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Dry Well Davit Socket Base | 2 |  | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1983 | 60 | 2046 | HR-CTWL-023 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Building | Conveying (Elevators, Cranes) | 1 |  | 322_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
320 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 633 | Wet Well Access Hatch | 1 |  | Halton | In Service | Chartwell Rd. PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1983 | 60 | 2046 | HR-CTWL-025 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 323_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
321 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 633 | Wet Well Davit Socket Base | 2 |  | Halton | In Service | Chartwell Rd. PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1983 | 60 | 2046 | HR-CTWL-025 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Building |  | 1 |  | 324_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
322 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 633 | Wet Well Access Ladder | 2 |  | Halton | In Service | Chartwell Rd. PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1983 | 60 | 2046 | HR-CTWL-073 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 325_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
323 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 633 | Checker Plate Platform | 2 |  | Halton | In Service | Chartwell Rd. PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1983 | 60 | 2036 | HR-CTWL-073 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 326_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
324 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Dry Well Protective Paint | 1 |  | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Misc. Structural | [5 empty] | 1983 | 60 | 2046 | HR-CTWL-024 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Building | Interior Finishes | 1 |  | 327_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
325 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 31 | Wet Well Access Ladder | 2 | Cumnock PS Wet Well | Halton | In Service | Cumnock PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1974 | 60 | 2034 | HR-CMNK-156 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 328_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
326 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 641 | Wet Well Checker Plate Platform | 2 | Cumnock PS Wet Well | Halton | In Service | Cumnock PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1974 | 60 | 2034 | HR-CMNK-157 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 329_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
327 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 641 | Manhole Frame and Cover | 1 | Cumnock PS Wet Well | Halton | In Service | Cumnock PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1974 | 60 | 2034 | HR-CMNK-095 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 330_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
328 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Dry Well Access Hatch | 1 | Cumnock PS Dry Well | Halton | In Service | Cumnock PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1974 | 60 | 2034 | HR-CMNK-033 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Building | Substructure | 1 |  | 331_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
329 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Dry Well Access Ladder | 2 | Cumnock PS Dry Well | Halton | In Service | Cumnock PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1974 | 60 | 2034 | HR-CMNK-128 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Building | Substructure | 1 |  | 332_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
330 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | TRUE | FALSE | FALSE | 640 | Dry Aluminum Grating | 2 | Cumnock PS Dry Well | Halton | In Service | Cumnock PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1974 | 60 | 2034 | HR-CMNK-126 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Building | Substructure | 1 |  | 333_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
331 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Protective Paint | 1 | Cumnock PS Dry Well | Halton | In Service | Cumnock PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Misc. Architectural | [5 empty] | 1974 | 60 | 2034 | HR-CMNK-126 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Building | Interior Finishes | 1 |  | 334_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
332 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Davit Socket Base | 2 | Cumnock PS Dry Well | Halton | In Service | Cumnock PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Misc. Structural | [5 empty] | 1974 | 60 | 2034 | HR-CMNK-035 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Building |  | 1 |  | 335_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
333 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 642 | Wet Well Access Hatch | 1 | Ennisclaire Drive PS Wet Well | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1977 | 60 |  | HR-ENIS-001 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 336_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
334 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 642 | Wet Well Access Ladder | 2 | Ennisclaire Drive PS Wet Well | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1977 | 60 | 2036 | HR-ENIS-002 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 337_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
335 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 642 | Wet Well Aluminum Platform | 2 | Ennisclaire Drive PS Wet Well | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1977 | 60 |  | HR-ENIS-004 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 338_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
336 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 642 | Wet Well Aluminum Guardrail | 2 | Ennisclaire Drive PS Wet Well | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1977 | 60 | 2036 | HR-ENIS-002 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 339_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
337 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 642 | Davit Socket Base | 2 | Ennisclaire Drive PS Wet Well | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1977 | 60 |  | HR-ENIS-001 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Building |  | 1 |  | 340_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
338 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 644 | Wet Well Access Ladder | 2 | First Street PS Wet Well | Halton | In Service | First Street PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1986 | 60 | 2046 | HR-FRST-094 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 341_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
339 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 644 | Wet Well Aluminum Platform | 2 | First Street PS Wet Well | Halton | In Service | First Street PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1986 | 60 | 2046 | HR-FRST-094 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 342_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
340 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 644 | Manhole Frame and Cover | 1 | First Street PS Wet Well | Halton | In Service | First Street PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1986 | 60 |  | HR-FRST-097 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 343_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
341 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 644 | Davit Socket Base | 2 | First Street PS Wet Well | Halton | In Service | First Street PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Misc. Structural | [5 empty] | 1986 | 60 | 2046 | HR-FRST-098 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 344_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
342 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 643 | Dry Well Access Hatch | 1 | First Street PS Dry Well | Halton | In Service | First Street PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1986 | 60 | 2046 | HR-FRST-029 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Building | Substructure | 1 |  | 345_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
343 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 643 | Dry Well Access Ladder | 2 | First Street PS Dry Well | Halton |  | First Street PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1986 | 60 | 2046 | HR-FRST-019 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Building | Substructure | 1 |  | 346_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
344 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 643 | Protective Paint | 1 | First Street PS Dry Well | Halton | In Service | First Street PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Misc. Architectural | [5 empty] | 1986 | 60 |  | HR-FRST-019 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Building | Interior Finishes | 1 |  | 347_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
345 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 643 | Dry Well Davit Socket Base | 2 | First Street PS Dry Well | Halton | In Service | First Street PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1986 | 60 | 2046 | HR-FRST-029 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Building |  | 1 |  | 348_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
346 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 645 | Wet Well Access Hatch | 1 | Garlock Gdns PS Wet Well | Halton | In Service | Garlock Gdns PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1977 | 60 |  | HR-GGDN-023 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 349_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
347 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 645 | Wet Well Access Ladder | 2 | Garlock Gdns PS Wet Well | Halton | In Service | Garlock Gdns PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1977 | 60 | 2040 | HR-GGDN-088 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 350_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
348 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 645 | Wet Well Davit Socket Base | 2 | Garlock Gdns PS Wet Well | Halton | In Service | Garlock Gdns PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1977 | 60 |  | HR-GGDN-023 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 351_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
349 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 645 | Wet Well Aluminum Platform | 2 | Garlock Gdns PS Wet Well | Halton | In Service | Garlock Gdns PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1977 | 60 | 2040 | HR-GGDN-088 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 352_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
350 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 646 | Dry Well Access Hatch | 1 | Morrison Heights PS Dry Well | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1973 | 60 | 2033 | HR-MORI-096 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Building | Substructure | 1 |  | 353_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
351 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 646 | Dry Well Access Ladder | 2 | Morrison Heights PS Dry Well | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1973 | 60 | 2033 | HR-MORI-097 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Building | Substructure | 1 |  | 354_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
352 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 42 | Dry Well Davit Socket Base | 2 | Morrison Heights PS Dry Well | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1973 | 60 | 2033 | HR-MORI-096 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Building | Substructure | 1 |  | 355_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
353 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 646 | Protective Paint | 1 | Morrison Heights PS Dry Well | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Misc. Architectural | [5 empty] | 1973 | 60 | 2033 | HR-MORI-097 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Building | Interior Finishes | 1 |  | 356_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
354 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 647 | Manhole Frame and Cover | 1 | Morrison Heights PS Wet Well | Halton | In Service | Morrison Heights PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1973 | 60 | 2033 | HR-MORI-001 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 357_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
355 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 647 | Wet Well Access Ladder | 2 | Morrison Heights PS Wet Well | Halton | In Service | Morrison Heights PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1973 | 60 | 2033 | HR-MORI-001 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 358_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
356 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 647 | Wet Well Davit Socket Base | 2 | Morrison Heights PS Wet Well | Halton | In Service | Morrison Heights PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1973 | 60 | 2033 | HR-MORI-001 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 359_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
357 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Wet Well Access Hatch | 1 | Raymar Pl PS Wet Well | Halton | In Service | Raymar Pl PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1985 | 60 |  | HR-RAYM-029 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 360_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
358 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Pump Hatch 1 | 1 | Raymar Pl PS Wet Well | Halton | In Service | Raymar Pl PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1985 | 60 |  | HR-RAYM-029 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 361_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
359 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Pump Hatch 2 | 1 | Raymar Pl PS Wet Well | Halton |  | Raymar Pl PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1985 | 60 |  | HR-RAYM-029 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Wet Well | 2 |  | 362_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
360 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Wet Well Access Ladder | 2 | Exterior to platform | Halton |  | Raymar Pl PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1985 | 60 |  | HR-RAYM-054 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 363_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
361 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | We Well Access Ladder | 2 | Platform to base | Halton | In Service | Raymar Pl PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1985 | 60 |  | HR-RAYM-054 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 364_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
362 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Wet Well Aluminum Platform | 2 | Raymar Pl PS Wet Well | Halton | In Service | Raymar Pl PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1985 | 60 |  | HR-RAYM-054 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 365_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
363 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Wet Well Davit Socket Base | 2 | Raymar Pl PS Wet Well | Halton |  | Raymar Pl PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1985 | 60 |  | HR-RAYM-029 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 366_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
382 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 643 | Dry Well Concrete Foundation | 2 | First Street PS Dry Well | Halton | In Service | First Street PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Tank, Concrete | [5 empty] | 1986 | 60 |  |  |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5948e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Building | Superstructure | 1 |  | 385_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
383 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Dry Well Concrete Foundation | 2 | Cumnock PS Dry Well | Halton | In Service | Cumnock PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Misc. Structural | [5 empty] | 1974 | 60 |  |  |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5948e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Building | Superstructure | 1 |  | 386_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
384 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Dry Well Concrete Foundation | 2 | Chartwell Rd. PS Dry Well | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Misc. Structural | [5 empty] | 1983 | 60 | 2043 |  |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5948e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Building | Substructure | 1 |  | 387_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
385 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Dry Well Concrete Foundation | 2 | Chancery Lane PS Dry Well | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Building Structural | Building and Process Structural |  | Reinforced Concrete | [5 empty] | 1975 | 60 |  |  |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5948e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Building | Substructure | 1 |  | 388_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
387 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 41 | Grab Bar |  | Garlock Gdns PS Wet Well | Halton | In Service | Garlock Gdns PS | WWPS | Wet Well | Building Structural | Building and Process Structural | [7 empty] | 1977 | 60 | 2036 | HR-GGDN-023 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | David Ip | 1.5949e+18 | [8 empty] | 1 |  | 390_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
392 |  |  | 211127 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 32 | VALVE KNIFE GATE SEWAGE LIFT PUMP #2 | 2 | Knife Gate Valve #2;;;;100 mm dia | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Dry Well |  | Process Mechanical Equipment |  | Valve | [5 empty] | 1977 | 30 |  | HR-ENIS-013 |  | 5 |  | 5 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | [8 empty] | 1 |  | 279_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
393 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 32 | PUMP #2 SEWAGE LIFT | 2 | Sewage Pump #2;Flygt;C3082MT;;7.8 L/s at 7.2 m TDH 2hp | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Dry Well |  | Process Mechanical Equipment |  | Pump, Centrifugal | [5 empty] | 1977 | 30 |  | HR-ENIS-009 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | [8 empty] | 1 |  | 280_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
394 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 32 | VALVE CHECK SEWAGE LIFT PUMP #2 | 2 | Check Valve #2;;;;100 mm dia | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Dry Well |  | Process Mechanical Equipment |  | Valve | [5 empty] | 1977 | 30 |  | HR-ENIS-014 |  | 5 |  | 5 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | [8 empty] | 1 |  | 281_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
395 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 32 | VALVE KNIFE GATE SEWAGE LIFT PUMP #2 | 2 | Knife Gate Valve #2;;;;100 mm dia | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Dry Well |  | Process Mechanical Equipment |  | Valve | [5 empty] | 1977 | 30 |  | HR-ENIS-013 |  | 5 |  | 5 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | [8 empty] | 1 |  | 282_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
396 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 32 | Bar Screen | 2 | Bar Screen;;;;6.5'X3.25' | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Dry Well |  | Process Mechanical Equipment |  | Valve | [5 empty] | 1977 | 30 |  | HR-ENIS-015 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | [8 empty] | 1 |  | 283_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
397 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 32 | PUMP #2 SEWAGE LIFT | 2 | Sewage Pump #2;Flygt;C3082MT;;7.8 L/s at 7.2 m TDH 2hp | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Dry Well |  | Process Mechanical Equipment |  | Pump, Centrifugal | [5 empty] | 1977 | 30 |  | HR-ENIS-009 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | [8 empty] | 1 |  | 284_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
399 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 642 | Sewage Lift Pump #2 | 2 | Sewage Pump #1;Flygt;C3082MT;;7.8 L/s at 7.2 m TDH 2hp | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | pump | [5 empty] | 1977 | 30 |  | HR-ENIS-009 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 286_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
400 |  |  | 201607 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 32 | VALVE CHECK SEWAGE LIFT PUMP #2 | 2 | Check Valve #2;;;;100 mm dia | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Dry Well |  | Process Mechanical Equipment |  | Valve | [5 empty] | 1977 | 30 |  | HR-ENIS-014 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | [8 empty] | 1 |  | 287_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
401 |  |  | 211127 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 32 | VALVE KNIFE GATE SEWAGE LIFT PUMP #1 | 2 | Knife Gate Valve #1;;;;100 mm dia | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Dry Well |  | Process Mechanical Equipment |  | Valve | [5 empty] | 1977 | 30 |  | HR-ENIS-012 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | [8 empty] | 1 |  | 288_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
402 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 399 | Sewage Lift Pump #2 Check Valve | 2 | Check Valve #1;;;;100 mm dia | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Valve | [5 empty] | 1977 | 30 |  | HR-ENIS-014 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 289_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
403 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 399 | Sewage Lift Pump #2 Knife Gate Valve | 2 | Knife Gate Valve #2;;;;100 mm dia | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Valve | [5 empty] | 1977 | 30 |  | HR-ENIS-013 |  | 5 |  | 5 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Wet Well | 2 |  | 290_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
404 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 645 | Bar Screen | 2 | Bar Screen;;;; | Halton | In Service | Garlock Gdns PS | Garlock Gdns PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Piping, DI/CPP/Steel/SS | [5 empty] | 1977 | 30 |  | HR-GGDN-013 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 292_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
405 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 46 | VALVE DISCHARGE #3 | 2 | Gate Valve #3;;;;100 mm dia | Halton | In Service | Raymar Pl PS | Raymar Pl PS | Wet Well |  | Process Mechanical Equipment |  | Valve | [5 empty] | 1985 | 30 |  | HR-RAYM-017 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | [8 empty] | 1 |  | 293_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
406 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Discharge Valve #3 | 2 | Gate Valve #3;;;;100 mm dia | Halton | In Service | Raymar Pl PS | WWPS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Valve | [5 empty] | 1985 | 30 |  | HR-RAYM-017 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Adrian Li | 1.5953e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Discharge Header | 1 |  | 294_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
422 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Remote Signal Telephone Transmitter | 1 | Remote Signal Telephone Transmitter; Pribusin; IUC-X9-TXC; ; ; | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation |  | Transmitter | [5 empty] | 2009 | 15 | 2009 | HR-CNRY-108 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 1.5966e+18 | Maira Rafiq | 1.5983e+18 |  |  |  |  | Communications | Telephone/IT | 1 |  | 288_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
423 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 639 | Wet Well Floats | 2 | Wet Well Floats; ; ; ; ; | Halton | In Service | Chancery Lane PS | WWPS | Wet Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2009 | 15 | 2030 | HR-CNRY-064 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 1.5966e+18 | Maira Rafiq | 1.5983e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 289_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
424 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Sump Float | 2 | Sump Float; ; ; ; ; | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2009 | 15 |  | HR-CNRY-132 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 1.5966e+18 | Maira Rafiq | 1.5983e+18 |  |  |  |  | Building | Plumbing - Sanitary Waste | 1 |  | 290_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
429 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 633 | Wet Well Float | 2 | Wet Well Float; ; ; ; ; | Halton | In Service | Chartwell Rd. PS | WWPS | Wet Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2019 | 15 | 2025 | HR-CTWL-065 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 1.5966e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Pumping | Suction Header | 1 |  | 295_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
430 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Sump Float | 1 | Sump Float; ; ; ; ; | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2019 | 15 | 2025 | HR-CTWL-016 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 1.5966e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Building | Plumbing - Sanitary Waste | 1 |  | 296_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
431 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Remote Signals Telephone Transmitter | 1 | Remote Signals Telephone Transmitter; Pribusin; IUC-X9-TXC; ; ; | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation |  | Transmitter | [5 empty] | 2016 | 15 | 2030 | HR-CTWL-128 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 1.5966e+18 | Maira Rafiq | 1.598e+18 |  |  |  |  | Communications | Telephone/IT | 1 |  | 297_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
432 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Sump Float | 2 | Sump Float; ; ; ; ; | Halton | In Service | Cumnock PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2009 | 15 | 2030 | HR-CMNK-023 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 1.5966e+18 | Maira Rafiq | 1.5983e+18 |  |  |  |  | Building | Plumbing - Sanitary Waste | 1 |  | 298_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
433 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Remote Signals Telephone Transmitter | 1 | Remote Signals Telephone Transmitter; Pribusin; IUC-X9-TXC; ; ; | Halton | In Service | Cumnock PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation |  | Transmitter | [5 empty] | 2016 | 15 |  | HR-CMNK-079 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 1.5966e+18 | Maira Rafiq | 1.5983e+18 |  |  |  |  | Communications | Telephone/IT | 1 |  | 299_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
434 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 641 | Wet Well Floats | 2 | Wet Well Floats; ; ; ; ; | Halton | In Service | Cumnock PS | WWPS | Wet Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2009 | 15 | 2030 | HR-CMNK-152 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 1.5966e+18 | Maira Rafiq | 1.5983e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 300_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
435 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 33 | Remote Signals Telephone Transmitter | 1 | Remote Signals Telephone Transmitter; Pribusin; IUC-X9-TXC; ; ; | Halton | In Service | Ennisclaire Drive PS | WWPS | Site | Process Instrumentation | Process Instrumentation |  | Transmitter | [5 empty] | 2009 | 15 | 2030 | HR-ENIS-038 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 1.5966e+18 | Maira Rafiq | 1.5983e+18 |  |  |  |  | Communications | Telephone/IT | 1 |  | 301_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
436 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 642 | Wet Well Floats | 2 | Wet Well Floats; ; ; ; ; | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2009 | 15 | 2030 | HR-ENIS-081 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 1.5966e+18 | Maira Rafiq | 1.5983e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 302_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
437 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 643 | Sump Float | 2 | Sump Float; ; ; ; ; | Halton | In Service | First Street PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2009 | 15 | 2030 | HR-FRST-024 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 1.5966e+18 | Maira Rafiq | 1.5983e+18 |  |  |  |  | Building | Plumbing - Sanitary Waste | 1 |  | 303_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
438 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 643 | Remote Signals Telephone Transmitter | 1 | Remote Signals Telephone Transmitter; Pribusin; IUC-X9-TXC; ; ; | Halton | In Service | First Street PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation |  | Transmitter | [5 empty] | 2016 | 15 | 2030 | HR-FRST-153 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 1.5966e+18 | Maira Rafiq | 1.5983e+18 |  |  |  |  | Communications | Telephone/IT | 1 |  | 304_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
439 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 644 | Wet Well Float | 2 | Wet Well Float; ; ; ; ; | Halton | In Service | First Street PS | WWPS | Wet Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2019 | 15 | 2030 | HR-FRST-088 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 1.5966e+18 | Maira Rafiq | 1.5983e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 305_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
440 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 645 | Wet Well Level Transmitter | 2 | Wet Well Level Transmitter; Siemens Milltronics; Multiranger 100; ; ; | Halton | In Service | Garlock Gdns PS | WWPS | Site | Process Instrumentation | Process Instrumentation |  | Transmitter | [5 empty] | 2009 | 15 | 2030 | HR-GGDN-039 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 1.5966e+18 | Maira Rafiq | 1.5983e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 306_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
441 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 40 | Remote Signals Telephone Transmitter | 1 | Remote Signals Telephone Transmitter; Pribusin; IUC-X9-TXC; ; ; | Halton | In Service | Garlock Gdns PS | WWPS | Site | Process Instrumentation | Process Instrumentation |  | Transmitter | [5 empty] | 2016 | 15 | 2030 | HR-GGDN-076 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 1.5966e+18 | Maira Rafiq | 1.5983e+18 |  |  |  |  | Communications | Telephone/IT | 1 |  | 307_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
442 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 645 | Wet Well Floats | 2 | Wet Well Floats; ; ; ; ; | Halton | In Service | Garlock Gdns PS | WWPS | Wet Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2009 | 15 | 2030 | HR-GGDN-004 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 1.5966e+18 | Maira Rafiq | 1.5983e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 308_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
443 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 646 | Sump Float | 2 | Sump Float; ; ; ; ; | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2008 | 15 | 2030 | HR-MORI-027 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 1.5966e+18 | Maira Rafiq | 1.5983e+18 |  |  |  |  | Building | Plumbing - Sanitary Waste | 1 |  | 309_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
444 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 43 | Remote Signals Telephone Transmitter | 2 | Remote Signals Telephone Transmitter; Pribusin; IUC-X9-TXC; ; ; | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation |  | Transmitter | [5 empty] | 2016 | 15 | 2030 | HR-MORI-031 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 1.5966e+18 | Maira Rafiq | 1.5983e+18 |  |  |  |  | Communications | Telephone/IT | 1 |  | 310_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
445 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 647 | Wet Well Float | 2 | Wet Well Float; ; ; ; ; | Halton | In Service | Morrison Heights PS | WWPS | Wet Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2009 | 15 | 2030 | HR-MORI-124 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 1.5966e+18 | Maira Rafiq | 1.5983e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 311_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
446 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Wet Well Level Transmitter | 2 | Wet Well Level Transmitter; Siemens Milltronics; Multiranger Plus; ; ; | Halton | In Service | Raymar Pl PS | WWPS | Site | Process Instrumentation | Process Instrumentation |  | Transmitter | [5 empty] | 2009 | 15 | 2030 | HR-RAYM-080 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 1.5966e+18 | Maira Rafiq | 1.5983e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 312_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
447 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 45 | Remote Signals Telephone Transmitter | 1 | Remote Signals Telephone Transmitter; Pribusin; IUC-X9-TXC; ; ; | Halton | In Service | Raymar Pl PS | WWPS | Site | Process Instrumentation | Process Instrumentation |  | Transmitter | [5 empty] | 2016 | 15 | 2030 | HR-RAYM-132 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 1.5966e+18 | Maira Rafiq | 1.5983e+18 |  |  |  |  | Communications | Telephone/IT | 1 |  | 313_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
448 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Wet Well Floats | 2 | Wet Well Floats; ; ; ; ; | Halton | In Service | Raymar Pl PS | WWPS | Wet Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2009 | 15 | 2030 | HR-RAYM-011 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 1.5966e+18 | Maira Rafiq | 1.5983e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 314_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
485 |  |  | 201611 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 25 | Main Disconnect Switch | 2 | Main Disconnect Switch; Square D; ; ;600V, 60A, fused | Halton | In Service | Chancery Lane PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2010 | 25 | 2040 | HR-CNRY-076 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5959e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Primary Power | MCC | 1 |  | 307_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
486 |  |  | 201611 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 25 | Power Meter | 2 | Power Meter; ; ; ; | Halton | In Service | Chancery Lane PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2010 | 25 | 2040 | HR-CNRY-080 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5959e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Primary Power | MCC | 1 |  | 309_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
487 |  |  | 201611 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 25 | Manual Transfer Switch | 2 | Manual Transfer Switch; Square D; ; ;600V, 60A | Halton | In Service | Chancery Lane PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2010 | 25 | 2040 | HR-CNRY-081 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5959e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Primary Power | Transfer Switch | 1 |  | 310_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
488 |  |  | 201611 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 25 | Generator Connection Receptacle | 2 | Generator Connection Receptacle; ; ; ;600V | Halton | In Service | Chancery Lane PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2010 | 25 | 2040 | HR-CNRY-072 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5959e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Primary Power | Standby Generator | 1 |  | 311_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
489 |  |  | 201611 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Dry Well Lights | 1 | Dry Well Lights; ; ; ;2 Fluorescent | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Process Electrical | Process Electrical |  | Lighting | [5 empty] | 1975 | 25 | 2025 | HR-CNRY-086 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5959e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Building | Electrical - Lighting | 1 |  | 312_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
490 |  |  | 201611 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 25 | Outdoor Enclosure | 2 | Outdoor Enclosure; ; ; ; | Halton | In Service | Chancery Lane PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2010 | 25 | 2040 | HR-CNRY-071 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5959e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Primary Power | MCC | 1 |  | 314_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
491 |  |  | 201611 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Pump Control Panel | 3 | Pump Control Panel; S&L; ; ; | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Process Electrical | Process Electrical |  | Panel, Breaker | [5 empty] | 1975 | 25 | 2025 | IMG_20200629_140353 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5959e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 315_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
492 |  |  | 201556 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 27 | Outdoor Electrical Enclosure | 2 | Outdoor Electrical Enclosure; ; ; ; | Halton | In Service | Chartwell Rd. PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 1965 | 25 | 2025 | HR-CTWL-023 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5959e+18 | Maira Rafiq | 1.5986e+18 |  |  |  |  | Primary Power | MCC | 1 |  | 316_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
493 |  |  | 201556 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 27 | Main Disconnect Switch | 2 | Main Disconnect Switch; Square D; ; ;600V, 60A, fused | Halton | In Service | Chartwell Rd. PS | WWPS | Site | Process Electrical | Process Electrical |  | MCC | [5 empty] | 2010 | 25 | 2040 | HR-CTWL-079 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5959e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Primary Power | MCC | 1 |  | 317_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
494 |  |  | 201556 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 27 | Power Meter | 2 | Power Meter; Elster; ; ; | Halton | In Service | Chartwell Rd. PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2010 | 25 | 2040 | HR-CTWL-084 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5959e+18 | Maira Rafiq | 1.5986e+18 |  |  |  |  | Primary Power | MCC | 1 |  | 318_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
495 |  |  | 201556 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 27 | Manual Transfer Switch | 2 | Manual Transfer Switch; Square D; ; ; 600V, 60A | Halton | In Service | Chartwell Rd. PS | WWPS | Site | Process Electrical | Process Electrical |  | Panel, Breaker | [5 empty] | 2010 | 25 | 2040 | HR-CTWL-085 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5959e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Primary Power | Transfer Switch | 1 |  | 319_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
496 |  |  | 201556 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Dry Well Lighting | 1 | Dry Well Lighting; ; ; ; 2 fluorescent lights | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Building Electrical | Building Services |  | Lighting | [5 empty] | 1965 | 30 | 2025 | HR-CTWL-085 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5959e+18 | Maira Rafiq | 1.5986e+18 |  |  |  |  | Building | Electrical - Lighting | 1 |  | 320_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
497 |  |  | 201556 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Control Panel | 3 | Control Panel; S&L; ; ; | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Process Electrical | Process Electrical |  | Panel, Breaker | [5 empty] | 1965 | 25 | 2025 | HR-CTWL-002 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Primary Power | MCC | 1 |  | 321_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
498 |  |  | 201556 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Generator Connection Receptacle | 2 | Generator Connection Receptacle; ; ; ; 600V, 60A | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Process Electrical | Process Electrical |  | Generator | [5 empty] | 1965 | 25 | 2025 | HR-CTWL-002 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5959e+18 | Maira Rafiq | 1.5986e+18 |  |  |  |  | Primary Power | Standby Generator | 1 |  | 322_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
499 |  |  | 201647 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 30 | Outdoor Enclosure | 2 | Outdoor Enclosure | Halton | In Service | Cumnock PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 1993 | 25 | 2030 | HR-CMNK-036 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.596e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Primary Power | MCC | 1 |  | 323_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
500 |  |  | 201647 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 7 | Main Disconnect Switch | 2 | Main Disconnect Switch; Square D; ; ;600V, 60A | Halton | In Service | Cumnock PS | WWPS | Site | Process Electrical | Process Electrical |  | MCC | [5 empty] | 1993 | 25 | 2035 | HR-CMNK-038 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.596e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Primary Power | MCC | 1 |  | 324_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
501 |  |  | 201647 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 7 | Power Meter | 2 | Power Meter; elster; ; ; | Halton | In Service | Cumnock PS | WWPS | Site | Process Electrical | Process Electrical |  | MCC | [5 empty] | 1993 | 25 | 2035 | HR-CMNK-041 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.596e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Primary Power | MCC | 1 |  | 325_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
502 |  |  | 201647 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 7 | Manual Transfer Switch | 2 | Manual Transfer Switch; square D; ; ;600V, 60A | Halton | In Service | Cumnock PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 1993 | 25 | 2035 | HR-CMNK-042 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.596e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Primary Power | Transfer Switch | 1 |  | 326_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
503 |  |  | 201647 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Drywell Lighting | 1 | Drywell Lighting; ; ; ;2 fluorescent fixtures | Halton | In Service | Cumnock PS | WWPS | Dry Well | Process Electrical | Process Electrical |  | Lighting | [5 empty] | 1974 | 25 | 2025 | HR-CMNK-051 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.596e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Building | Electrical - Lighting | 1 |  | 327_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
504 |  |  | 201647 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Control Panel | 3 | Control Panel; S&L; ; ; | Halton | In Service | Cumnock PS | WWPS | Dry Well | Process Electrical | Process Electrical |  | Panel, Breaker | [5 empty] | 1974 | 25 | 2025 | HR-CMNK-0003 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.596e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 328_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
505 |  |  | 201608 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 33 | outdoor enclosure | 2 | outdoor enclosure | Halton | In Service | Ennisclaire Drive PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 1972 | 25 | 2025 | HR-ENIS-028 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5965e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Primary Power | MCC | 1 |  | 329_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
506 |  |  | 201608 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 33 | Control Panel with Main DS | 3 | Control Panel with Main DS; | Halton | In Service | Ennisclaire Drive PS | WWPS | Site | Process Electrical | Process Electrical |  | Panel, Breaker | [5 empty] | 1972 | 25 | 2025 | HR-ENIS-029 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 330_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
507 |  |  | 201608 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 33 | Pump #1 VFD with Breaker | 2 | Pump #1 VFD with Breaker; PowerFlex 40; Series A; ; ; Size 1, 7.5HP | Halton | In Service | Ennisclaire Drive PS | WWPS | Site | Process Electrical | Process Electrical |  | VFD | [5 empty] | 2007 | 25 | 2037 | HR-ENIS-053 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5965e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 331_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
508 |  |  | 201608 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 33 | Pump #2 VFD with Breaker | 2 | Pump #2 VFD with Breaker; PowerFlex 40; Series A; ; ; Size 1, 7.5HP | Halton | In Service | Ennisclaire Drive PS | WWPS | Site | Process Electrical | Process Electrical |  | VFD | [5 empty] | 2007 | 25 | 2037 | HR-ENIS-047 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5965e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 332_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
509 |  |  | 201608 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 33 | Generator Connection Receptacle | 2 | Generator Connection Receptacle; ; ; ; ; 240V, 60A | Halton | In Service | Ennisclaire Drive PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2007 | 25 | 2037 | HR-ENIS-060 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Primary Power | Standby Generator | 1 |  | 333_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
510 |  |  | 201608 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 33 | Manual Transfer Switch | 2 | Manual Transfer Switch; Moeller; ; ; ; 600V, 63A | Halton | In Service | Ennisclaire Drive PS | WWPS | Site | Process Electrical | Process Electrical |  | MCC | [5 empty] | 2007 | 25 | 2037 | HR-ENIS-061 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Primary Power | Transfer Switch | 1 |  | 334_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
511 |  |  | 201608 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 642 | Wet Well Light | 1 | Wet Well Light; ; ; ; ; class 1, div 1 rated | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Process Electrical | Process Electrical |  | Lighting | [5 empty] | 2007 | 25 | 2025 | HR-ENIS-061 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Building | Electrical - Lighting | 1 |  | 335_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
512 |  |  | 201542 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 37 | Outdoor Enclosure | 2 | Outdoor Enclosure | Halton | In Service | First Street PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2010 | 25 | 2040 | HR-FRST-099 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Primary Power | MCC | 1 |  | 336_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
513 |  |  | 201542 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 37 | Main Fused Disconnect Switch | 2 | Main Fused Disconnect Switch; Square D; ; ; 600V, 60A | Halton | In Service | First Street PS | WWPS | Site | Process Electrical | Process Electrical |  | MCC | [5 empty] | 2010 | 25 | 2040 | HR-FRST-100 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Primary Power | MCC | 1 |  | 337_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
514 |  |  | 201542 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 37 | Power Meter | 2 | Power Meter; Elster; ; ; | Halton | In Service | First Street PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2010 | 25 | 2040 | HR-FRST-107 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Primary Power | MCC | 1 |  | 338_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
515 |  |  | 201542 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 37 | Manual Transfer Switch | 2 | Manual Transfer Switch; Square D; ; ;600V, 60A | Halton | In Service | First Street PS | WWPS | Site | Process Electrical | Process Electrical |  | MCC | [5 empty] | 2010 | 25 | 2040 | HR-FRST-109 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Primary Power | Transfer Switch | 1 |  | 339_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
516 |  |  | 201542 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 643 | Control Panel | 3 | Control Panel; Clow; AER-O-FLO; ;600V | Halton | In Service | First Street PS | WWPS | Dry Well | Process Electrical | Process Electrical |  | Panel, Breaker | [5 empty] | 1983 | 25 | 2025 | HR-FRST-001 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 340_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
517 |  |  | 201542 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 37 | Generator Connection Receptacle | 2 | Generator Connection Receptacle; ; ; ;600V, 60A | Halton | In Service | First Street PS | WWPS | Site | Process Electrical | Process Electrical |  | Generator | [5 empty] | 2010 | 25 | 2040 | HR-FRST-122 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Primary Power | Standby Generator | 1 |  | 341_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
518 |  |  | 201542 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 643 | Dry Well Lights | 1 | Dry Well Lights; ; ; rated for class 1, div 2 | Halton | In Service | First Street PS | WWPS | Site | Process Electrical | Process Electrical |  | Lighting | [5 empty] | 2000 | 25 | 2030 | HR-FRST-126 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Building | Electrical - Lighting | 1 |  | 342_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
519 |  |  | 219156 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 645 | Wet Well Light | 1 | Wet Well Light; ; ; ; florescent, class 1, div 1 rated | Halton | In Service | Garlock Gdns PS | WWPS | Wet Well | Process Electrical | Process Electrical |  | Lighting | [5 empty] | 1977 | 25 | 2025 | HR-GGDN-022 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Building | Electrical - Lighting | 1 |  | 343_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
520 |  |  | 219156 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 40 | Enclosure Light | 1 | Enclosure Light; ; ; ; florescent | Halton | In Service | Garlock Gdns PS | WWPS | Site | Process Electrical | Process Electrical |  | Lighting | [5 empty] | 1977 | 25 | 2025 | HR-GGDN-028 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Building | Electrical - Lighting | 1 |  | 344_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
521 |  |  | 219156 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 40 | Power Meter | 2 | Power Meter; ; ; ; | Halton | In Service | Garlock Gdns PS | WWPS | Site | Process Electrical | Process Electrical |  | MCC | [5 empty] | 2003 | 25 | 2033 | HR-GGDN-027 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Primary Power | MCC | 1 |  | 345_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
522 |  |  | 219156 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 40 | Control Panel with Main DS and MTS | 3 | Control Panel with Main DS; ; ; ; 240V, 30A | Halton | In Service | Garlock Gdns PS | WWPS | Site | Process Electrical | Process Electrical |  | Panel, Breaker | [5 empty] | 1977 | 25 | 2025 | HR-GGDN-037 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Primary Power | MCC | 1 |  | 346_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
523 |  |  | 219156 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 40 | Generator Connect Recept. | 2 | Generator Connect Recept.; ; ; ; 240V, 30A | Halton | In Service | Garlock Gdns PS | WWPS | Site | Process Electrical | Process Electrical |  | Generator | [5 empty] | 1977 | 25 | 2025 | HR-GGDN-056 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Primary Power | Standby Generator | 1 |  | 347_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
524 |  |  | 219156 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 41 | Pump #1 VFD with Breaker | 2 | Pump #1 VFD with Breaker; PowerFlex 40; Series A; ; 240V, 30A, size 1 | Halton | In Service | Garlock Gdns PS | WWPS | Site | Process Electrical | Process Electrical |  | VFD | [5 empty] | 2003 | 25 | 2033 | HR-GGDN-057 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 348_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
525 |  |  | 219156 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 40 | Pump #2 VFD with Breaker | 2 | Pump #2 VFD with Breaker; PowerFlex 40; Series A; ; 240V, 30A, size 1 | Halton | In Service | Garlock Gdns PS | WWPS | Site | Process Electrical | Process Electrical |  | VFD | [5 empty] | 2003 | 25 | 2033 | HR-GGDN-057 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 349_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
526 |  |  | 201659 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 43 | Outdoor Enclosure | 2 | Outdoor Enclosure | Halton | In Service | Morrison Heights PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2010 | 25 | 2040 | HR-MORI-040 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Primary Power | MCC | 1 |  | 350_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
527 |  |  | 201659 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 43 | Generator Connect Recept. | 2 | Generator Connect Recept. ; ; ; ; 600V, 60A | Halton | In Service | Morrison Heights PS | WWPS | Site | Process Electrical | Process Electrical |  | Generator | [5 empty] | 2010 | 25 | 2040 | HR-MORI-041 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Primary Power | Standby Generator | 1 |  | 351_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
528 |  |  | 201659 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 43 | Main Disconnect Switch | 2 | Main DS ; Square D; ; ; 600V, 60A, fused | Halton | In Service | Morrison Heights PS | WWPS | Site | Process Electrical | Process Electrical |  | MCC | [5 empty] | 2010 | 25 | 2040 | HR-MORI-046 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Primary Power | MCC | 1 |  | 352_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
529 |  |  | 201659 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 43 | Manual Transfer Switch | 2 | MTS ; Square D; ; ; 600V, 60A | Halton | In Service | Morrison Heights PS | WWPS | Site | Process Electrical | Process Electrical |  | MCC | [5 empty] | 2010 | 25 | 2040 | HR-MORI-047 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Primary Power | Transfer Switch | 1 |  | 353_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
530 |  |  | 201659 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 43 | Power Meter | 2 | Power Meter ; elster; ; ; 600V | Halton | In Service | Morrison Heights PS | WWPS | Site | Process Electrical | Process Electrical |  | MCC | [5 empty] | 2010 | 25 | 2040 | HR-MORI-047 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Primary Power | MCC | 1 |  | 354_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
531 |  |  | 201659 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 646 | Dry Well Lights | 1 | Dry Well Lights ; elster; ; ; Fluorescent | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Process Electrical | Process Electrical |  | Lighting | [5 empty] | 1973 | 25 | 2025 | HR-MORI-056 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Building | Electrical - Lighting | 1 |  | 355_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
532 |  |  | 201659 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 646 | Control Panel | 3 | Control Panel ; elster; ; ; 600V | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Process Electrical | Process Electrical |  | Panel, Breaker | [5 empty] | 1973 | 25 | 2025 | HR-MORI-057 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 356_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
533 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Wet well Light | 1 | Wet well Light; ; ; ; rated for class 1, div 1 | Halton | In Service | Raymar Pl PS | WWPS | Wetwell | Building Electrical | Process Electrical |  | Lighting | [5 empty] | 1985 | 25 | 2021 | HR-RAYM-026 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 357_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
534 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 45 | Enclosure Light | 1 | Enclosure Light; ; ; ; fluorescent | Halton | In Service | Raymar Pl PS | WWPS | Site | Building Electrical | Process Electrical |  | Lighting | [5 empty] | 1985 | 25 | 2025 | HR-RAYM-026 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Building | Electrical - Lighting | 1 |  | 358_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
535 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Outdoor Enclosure | 1 | Outdoor Enclosure; ; ; ; | Halton | In Service | Raymar Pl PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 1985 | 25 | 2025 | HR-RAYM-057 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Primary Power | MCC | 1 |  | 359_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
536 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 45 | Power Meter | 2 | Power Meter; Sensus; ; ; | Halton | In Service | Raymar Pl PS | WWPS | Site | Process Electrical | Process Electrical |  | MCC | [5 empty] | 2006 | 25 | 2036 | HR-RAYM-059 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Primary Power | MCC | 1 |  | 360_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
537 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 45 | Pump #1 VFD and Breaker | 2 | Pump #1 VFD and Breaker; A-B; PowerFlex 40; ; 240V, size 1 | Halton | In Service | Raymar Pl PS | WWPS | Site | Process Electrical | Process Electrical |  | VFD | [5 empty] | 2006 | 25 | 2036 | HR-RAYM-063 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 361_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
538 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 12 | Pump #2 VFD and Breaker | 2 | Pump #2 VFD and Breaker; A-B; PowerFlex 40; ; 240V, size 1 | Halton | In Service | Raymar Pl PS | WWPS | Site | Process Electrical | Process Electrical |  | VFD | [5 empty] | 2006 | 25 | 2036 | HR-RAYM-063 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 362_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
539 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 45 | Control Panel with Main DS and MTS | 3 | Control Panel with Main DS and MTS; ; ; ; 240V, 60A | Halton | In Service | Raymar Pl PS | WWPS | Site | Process Electrical | Process Electrical |  | Panel, Breaker | [5 empty] | 1985 | 25 | 2025 | HR-RAYM-077 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 363_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
540 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 45 | Gen Connect Recept | 2 | Gen Connect Recept; ; AR648; ; 240V, 60A | Halton | In Service | Raymar Pl PS | WWPS | Site | Process Electrical | Process Electrical |  | Generator | [5 empty] | 1985 | 25 | 2025 | HR-RAYM-130 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 1.5966e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Primary Power | Standby Generator | 1 |  | 364_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
576 |  |  | 201612 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Dry Wall Sump Pump | 1 | Installation year was assumed to be 1975 | Halton |  | Chancery Lane PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Misc. Building Services | [5 empty] | 1975 | 30 |  | HR-CNRY-132 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 1.5961e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Building | Plumbing - Sanitary Waste | 1 |  | 293_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
577 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Dry Wall Portable Heater | 1 | Installation year assumed to be 1975 | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Unit Heater | [5 empty] | 1975 | 30 |  | HR-CNRY-018 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 1.5961e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Building | HVAC - Heat Generating Systems | 1 |  | 294_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
578 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  | Dry Wall Portable Dehumidifier | 1 | Manufacturer: Garrison, installation year assumed to be 1975 | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Dehumidifier | [5 empty] | 1975 | 30 |  | HR-CNRY-009 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 1.5961e+18 | Maira Rafiq | 1.6004e+18 |  |  |  |  | Building | HVAC - Cooling Generating Systems | 1 |  | 295_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
579 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Dry Wall Portable Heater | 1 | Installation year assumed to be 1980 | Halton |  | Chartwell Rd. PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Unit Heater | [5 empty] | 1983 | 30 |  | HR-CTWL-007 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 1.5961e+18 | Maira Rafiq | 1.5986e+18 |  |  |  |  | Building | HVAC - Heat Generating Systems | 1 |  | 296_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
580 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Dry Well Dehumidifier | 1 | Installation year assumed to be 1980 | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Dehumidifier | [5 empty] | 1983 | 30 |  | HR-CTWL-008 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 1.5961e+18 | Maira Rafiq | 1.6006e+18 |  |  |  |  | Building | HVAC - Heat Generating Systems | 1 |  | 297_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
581 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Dry Wall Sump Pump | 1 | Installation year was assumed to be 1980 | Halton |  | Chartwell Rd. PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Misc. Building Services | [5 empty] | 1983 | 30 |  | HR-CTWL-019 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 1.5961e+18 | Maira Rafiq | 1.5986e+18 |  |  |  |  | Building | Plumbing - Sanitary Waste | 1 |  | 299_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
583 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 15 | Dry Wall Sump Pump | 1 |  | Halton |  | Cumnock PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Misc. Building Services | [5 empty] | 1974 | 30 |  | HR-CMNK-021 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 1.5961e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Building | Plumbing - Sanitary Waste | 1 |  | 301_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
584 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Dry Wall Portable Heater | 1 | Installation year assumed to be 1975 | Halton | In Service | Cumnock PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Unit Heater | [5 empty] | 1974 | 30 |  | HR-CMNK-007 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 1.5961e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Building | HVAC - Heat Generating Systems | 1 |  | 302_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
585 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Dry Wall Portable Dehumidifier | 1 | Installation year assumed to be 1975 | Halton | In Service | Cumnock PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Dehumidifier | [5 empty] | 1974 | 30 |  | HR-CMNK-008 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 1.5961e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Building | HVAC - Cooling Generating Systems | 1 |  | 303_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
586 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  | Wet Well Ventilation Pipe | 1 | one 2 inches diameter steel pipe vent | Halton | In Service | Cumnock PS | WWPS | Wet Well | Building Mechanical | Building Services |  | Misc. Building Services | [5 empty] | 1974 | 30 |  | HR-CMNK-034 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 1.5961e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 304_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
587 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 642 | Wet Well Ventilation Pipe | 1 | one 4 inches diameter gooseneck pipe vent | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Building Mechanical | Building Services |  | Misc. Building Services | [5 empty] | 1977 | 30 |  | HR-ENIS-001 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 1.5961e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 305_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
588 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 15 | Dry Wall Sump Pump | 1 | Installation year was assumed to be 1985 | Halton |  | First Street PS | WWPS | Dry Well | Building Mechanical | Building Services | [7 empty] | 1986 | 30 |  | HR-FRST-009 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 1.5961e+18 | [8 empty] | 1 |  | 306_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
589 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 643 | Dry Wall Portable Heater | 1 | Installation year assumed to be 1985 | Halton |  | First Street PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Unit Heater | [5 empty] | 1986 | 30 |  | HR-FRST-003 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 1.5961e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Building | HVAC - Heat Generating Systems | 1 |  | 307_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
590 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 643 | Dry Well Dehumidifier | 1 | Manufacturer: Simplicity, installation year assumed to be 1985 | Halton |  | First Street PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Dehumidifier | [5 empty] | 1986 | 30 |  | HR-FRST-004 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 1.5961e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Building | HVAC - Distribution Systems | 1 |  | 308_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
592 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 645 | Wet Well Ventilation Pipe | 1 | one 4 inches diameter gooseneck steel pipe vent | Halton | In Service | Garlock Gdns PS | WWPS | Wet Well | Building Mechanical | Building Services |  | Misc. Building Services | [5 empty] | 1977 | 30 |  | HR-GGDN-001 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 1.5961e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 310_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
593 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  | Dry Wall Portable Heater | 1 |  | Halton |  | Morrison Heights PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Unit Heater | [5 empty] | 1973 | 30 |  | HR-MORI-007 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 1.5961e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Building | HVAC - Heat Generating Systems | 1 |  | 311_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
594 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 646 | Dry Well Dehumidifier | 1 |  | Halton |  | Morrison Heights PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Dehumidifier | [5 empty] | 1973 | 30 |  | HR-MORI-008 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 1.5961e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Building | HVAC - Cooling Generating Systems | 1 |  | 312_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
595 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Wet Well Ventilation Pipe | 1 | one 4 inches diameter steel pipe vent with insect screen | Halton | In Service | Raymar Pl PS | WWPS | Wet Well | Building Mechanical | Building Services |  | Misc. Building Services | [5 empty] | 1985 | 30 |  | HR-RAYM-056 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 1.5961e+18 | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Wet Well | 1 |  | 313_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
611 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 25 | Yard Hydrant | 1 |  | Halton | In Service | Chancery Lane PS | WWPS | Site | Site Works | Site Works |  | Misc. Site Works | [5 empty] | 1975 | 20 | 2035 | HR-CNRY-034 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Joseph De Paolo | 1.595e+18 | Maira Rafiq | 1.5983e+18 |  |  |  |  | Site Works | Yard Piping | 1 |  | 281_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
612 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 27 | Yard Hydrant | 1 |  | Halton | In Service | Chartwell Rd. PS | WWPS | Site | Site Works | Site Works |  | Misc. Site Works | [5 empty] | 1983 | 20 | 2035 | HR-CTWL-025 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Joseph De Paolo | 1.595e+18 | Maira Rafiq | 1.5983e+18 |  |  |  |  | Site Works | Yard Piping | 1 |  | 282_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
613 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 30 | Yard Hydrant | 1 |  | Halton | In Service | Cumnock PS | WWPS | Site | Site Works | Site Works |  | Misc. Site Works | [5 empty] | 1974 | 20 | 2035 | HR-CMNK-158 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Joseph De Paolo | 1.595e+18 | Maira Rafiq | 1.5983e+18 |  |  |  |  | Site Works | Yard Piping | 1 |  | 283_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
614 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 33 | Yard Hydrant | 1 |  | Halton | In Service | Ennisclaire Drive PS | WWPS | Site | Site Works | Site Works |  | Misc. Site Works | [5 empty] | 1977 | 20 | 2035 | HR-ENIS-026 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Joseph De Paolo | 1.595e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Site Works | Yard Piping | 1 |  | 284_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
615 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 37 | Yard Hydrant | 1 |  | Halton | In Service | First Street PS | WWPS | Site | Site Works | Site Works |  | Misc. Site Works | [5 empty] | 1968 | 20 | 2035 | HR-FRST-095 |  | 2 |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Joseph De Paolo | 1.595e+18 | Maira Rafiq | 1.5983e+18 |  |  |  |  | Site Works | Yard Piping | 1 |  | 285_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
616 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 40 | Yard Hydrant (New Asset) | 1 |  | Halton |  | Garlock Gdns PS | WWPS | Site | Site Works | Site Works |  | Misc. Site Works | [5 empty] | 1977 | 20 | 2035 |  |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | CAMR061927 | 1.5983e+18 | Maira Rafiq | 1.5983e+18 |  |  |  |  | Site Works | Yard Piping | 1 |  | 286_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
622 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 43 | Yard Hydrant | 1 |  | Halton |  | Morrison Heights PS | WWPS | Site | Site Works | Site Works |  | Misc. Site Works | [5 empty] | 1973 | 20 | 2036 | HR-MORI-029 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | CAMR061927 | 1.5983e+18 | Maira Rafiq | 1.5983e+18 |  |  |  |  | Site Works | Yard Piping | 1 |  | 292_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
623 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 45 | Yard Hydrant (New Asset) | 1 |  | Halton |  | Raymar Pl PS | WWPS | Site | Site Works | Site Works |  | Misc. Site Works | [5 empty] | 1985 | 20 | 2035 |  |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [10 empty] | CAMR061927 | 1.5983e+18 | Maira Rafiq | 1.5983e+18 |  |  |  |  | Site Works | Yard Piping | 1 |  | 293_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
632 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 6 | Dry Well |  | Chartwell Rd. PS Dry Well | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1983 | [10 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.598e+18 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
633 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 6 | Wet Well |  | Chartwell Rd. PS Wet Well | Halton | In Service | Chartwell Rd. PS | WWPS | Wet Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1983 |  |  | HR-CTWL-024 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.5986e+18 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
638 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 5 | Dry Well |  |  | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1975 |  |  | HR-CNRY-004 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.6004e+18 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
639 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 5 | Wet Well |  |  | Halton | In Service | Chancery Lane PS | WWPS | Process Structural | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1975 |  |  | HR-CNRY-033 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.5983e+18 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
640 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 7 | Dry Well |  | Cumnock PS Dry Well | Halton | In Service | Cumnock PS | WWPS | Dry Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1974 |  | 0 | HR-CMNK-033 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.6007e+18 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
641 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 7 | Wet Well |  | Cumnock PS Wet Well | Halton | In Service | Cumnock PS | WWPS | Wet Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1974 |  |  | HR-CMNK-032 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.5983e+18 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
642 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 8 | Wet Well |  | Ennisclaire Drive PS Wet Well | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1977 |  |  | HR-ENIS-002 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.5983e+18 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
643 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 9 | Dry Well |  | First Street PS Dry Well | Halton | In Service | First Street PS | WWPS | Dry Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1986 |  |  | HR-FRST-065 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.5983e+18 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
644 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 9 | Wet Well |  | First Street PS Wet Well | Halton | In Service | First Street PS | WWPS | Wet Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1986 |  |  | HR-FRST-094 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.5983e+18 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
645 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 10 | Wet Well |  | Garlock Gdns PS Wet Well | Halton | In Service | Garlock Gdns PS | WWPS | Wet Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1977 |  |  | HR-GGDN-088 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.5983e+18 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
646 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 11 | Dry Well |  | Morrison Heights PS Dry Well | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1973 |  |  | HR-MORI-098 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.5983e+18 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
647 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 11 | Wet Well |  | Morrison Heights PS Wet Well | Halton | In Service | Morrison Heights PS | WWPS | Wet Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1973 |  |  | HR-MORI-124 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.5983e+18 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
648 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 12 | Wet Well |  | Raymar Pl PS Wet Well | Halton | In Service | Raymar Pl PS | WWPS | Wet Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1985 |  |  | HR-RAYM-054 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.5983e+18 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
651 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 33 | concrete pavers | 1 |  | Halton | In Service | Ennisclaire Drive PS | WWPS | Site | Site Works | Site Works |  | Misc. Site Works | [5 empty] | 1977 | 20 |  | HR-ENIS-026 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [10 empty] | CAMR061927 | 1.5983e+18 | Maira Rafiq | 1.6007e+18 |  |  |  |  | Site Works | Sidewalk | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
661 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Cathodic Protection | 2 | Cathodic Protection for Underground Tank | Halton | In Service | Chancery Lane PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2010 | 25 |  | HR-CNRY-037 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.6004e+18 |  |  |  |  | Primary Power | MCC | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
663 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 151 | Pump 2 Piping | 3 | 150mm diameter, approx. 5m ductile iron pipe | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS | [5 empty] | 1983 | 60 | 0 | HR-CTWL-033 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.6006e+18 |  |  |  |  | Pumping | Pump Assembly |  |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
665 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Discharge Piping | 3 | 150mm diameter, approx. 5m ductile iron pipe | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS | [5 empty] | 1983 | 60 | 0 | HR-CTWL-014 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.6006e+18 |  |  |  |  | Pumping | Discharge Header |  |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
666 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 165 | Pump 2 Piping | 3 | 100mm diameter, approx. 5m ductile pipe | Halton | In Service | Cumnock PS | Cumnock PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS | [5 empty] | 1974 | 60 | 0 | HR-CMNK-027 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.6007e+18 |  |  |  |  | Pumping | Pump Assembly | 2 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
667 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Cathodic Protection | 2 | Cathodic Protection for Underground Tank | Halton | In Service | Cumnock PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2010 | 25 |  | HR-CNRY-037 |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.6007e+18 |  |  |  |  | Primary Power | MCC | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
669 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 40 | Discharge Header | 3 | 100mm diameter, approx. 5m ductile pipe | Halton | In Service | Garlock Gdns PS | Garlock Gdns PS | Dry Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS | [5 empty] | 1977 | 60 | 0 |  |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Wet Well |  |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
670 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  | Dry Well Concrete Foundation | 2 |  | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Building Structural | Building and Process Structural |  | Misc. Structural | [5 empty] | 1973 | 60 | 2035 |  |  | 3 |  | 3 |  |  |  | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.6008e+18 |  |  |  |  | Building | Substructure | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
671 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Discharge Header | 3 | 100mm diameter, approx. 8.6 m ductile iron pipe | Halton | In Service | Raymar Pl PS | Raymar Pl PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS | [5 empty] | 1985 | 60 | 0 | HR-RAYM-040 |  | 4 |  | 4 |  |  |  | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 1.6008e+18 |  |  |  |  | Pumping | Discharge Header | 2 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE

## P_Sheet1
AssetID | CoF | CustomClientCategory | InstallYear | AvgESL | VisualCondition | PoF
5 |  | Asset Hierarchy
6 |  | Asset Hierarchy
7 |  | Asset Hierarchy
8 |  | Asset Hierarchy
9 |  | Asset Hierarchy | 1977
10 |  | Asset Hierarchy
11 |  | Asset Hierarchy
12 |  | Asset Hierarchy
24 | 2 | Building and Process Structural | 1975 | 60 | 3 | 3
25 |  | Asset Hierarchy
26 | 2 | Building and Process Structural | 1983 | 60 | 3 | 3
27 |  | Asset Hierarchy
28 | 2 | Building and Process Structural | 1983 | 60 | 3 | 3
29 | 2 | Building and Process Structural | 1974 | 60 | 3 | 3
30 |  | Asset Hierarchy
31 | 2 | Building and Process Structural | 1974 | 60 | 3 | 3
33 |  | Asset Hierarchy
34 | 2 | Building and Process Structural | 1977 | 60 | 3 | 3
35 |  | Asset Hierarchy
36 | 2 | Building and Process Structural | 1986 | 60 | 3 | 3
37 |  | Asset Hierarchy | 1986
38 | 2 | Building and Process Structural | 1986 | 60 | 3 | 3
40 |  | Asset Hierarchy
41 | 2 | Building and Process Structural | 1977 | 60 | 3 | 3
42 | 2 | Building and Process Structural | 1973 | 60 | 3 | 3
43 |  | Asset Hierarchy
44 | 2 | Building and Process Structural | 1973 | 60 | 3 | 3
45 |  | Asset Hierarchy
46 | 2 | Building and Process Structural | 1985 | 60 | 3 | 3
53 | 2 | Process Mechanical Equipment | 1977 | 30 | 3 | 3
54 | 2 | Process Mechanical Equipment | 1977 | 30 | 4 | 4
55 | 2 | Process Mechanical Equipment | 1977 | 30 | 4 | 4
56 | 2 | Process Electrical | 1977 | 25 | 3 | 3
57 | 2 | Process Mechanical Equipment | 1977 | 30 | 4 | 4
58 | 2 | Process Mechanical Equipment | 1977 | 30 | 4 | 4
59 | 2 | Process Mechanical Equipment | 1977 | 30 | 4 | 4
60 | 4 | Process Piping | 1977 | 60 | 3 | 3
61 | 1 | Building Services | 1985 | 30 | 3 | 3
62 | 2 | Process Mechanical Equipment | 1985 | 30 | 3 | 3
63 | 2 | Process Mechanical Equipment | 1985 | 30 | 4 | 4
64 | 2 | Process Mechanical Equipment | 1985 | 30 | 4 | 4
65 | 2 | Process Mechanical Equipment | 1985 | 30 | 3 | 3
66 | 2 | Process Mechanical Equipment | 1985 | 30 | 4 | 4
67 | 2 | Process Mechanical Equipment | 1985 | 30 | 4 | 4
68 | 4 | Process Piping | 1985 | 60 | 3 | 3
69 | 1 | Building Services | 1973 | 30 | 4 | 4
70 | 2 | Process Instrumentation | 2008 | 15 | 2 | 2
71 | 1 | Building Services | 1973 | 30 | 3 | 3
72 | 2 | Process Mechanical Equipment | 1973 | 30 | 4 | 4
73 | 2 | Process Mechanical Equipment | 1973 | 30 | 4 | 4
74 | 2 | Process Electrical | 1973 | 25 | 3 | 3
75 | 2 | Process Mechanical Equipment | 1973 | 30 | 4 | 4
76 | 2 | Process Mechanical Equipment | 1973 | 30 | 4 | 4
78 | 2 | Process Mechanical Equipment | 1973 | 30 | 4 | 4
79 | 2 | Process Mechanical Equipment | 1973 | 30 | 4 | 4
80 | 2 | Process Electrical | 1973 | 25 | 3 | 3
81 | 2 | Process Mechanical Equipment | 1973 | 30 | 4 | 4
82 | 2 | Process Mechanical Equipment | 1973 | 30 | 3 | 3
83 | 5 | Process Piping | 1973 | 60 | 3 | 3
129 | 1 | Building Services | 1975 | 30 | 4 | 4
130 | 2 | Process Instrumentation | 2009 | 15 | 3 | 3
131 | 1 | Building Services | 1975 | 30 | 4 | 4
132 | 2 | Process Mechanical Equipment | 1975 | 30 | 3 | 3
133 | 2 | Process Mechanical Equipment | 1975 | 30 | 3 | 3
134 | 2 | Process Electrical | 1975 | 25 | 3 | 3
135 | 2 | Process Mechanical Equipment | 1975 | 30 | 3 | 3
136 | 2 | Process Mechanical Equipment | 1975 | 30 | 3 | 3
137 | 2 | Process Mechanical Equipment | 1975 | 30 | 3 | 3
138 | 2 | Process Mechanical Equipment | 1975 | 30 | 3 | 3
139 | 2 | Process Electrical | 1975 | 25 | 3 | 3
140 | 2 | Process Mechanical Equipment | 1975 | 30 | 3 | 3
141 | 2 | Process Mechanical Equipment | 1975 | 30 | 3 | 3
142 | 4 | Process Piping | 1975 | 60 | 3 | 3
143 | 1 | Building Services | 1983 | 30 | 4 | 4
144 | 2 | Process Instrumentation | 2009 | 15 | 2 | 2
145 | 1 | Building Services | 1983 | 30 | 4 | 4
146 | 2 | Process Mechanical Equipment | 1983 | 30 | 4 | 4
147 | 2 | Process Mechanical Equipment | 1983 | 30 | 4 | 4
148 | 2 | Process Mechanical Equipment | 1983 | 30 | 3 | 3
149 | 2 | Process Mechanical Equipment | 1983 | 30 | 4 | 4
150 | 2 | Process Mechanical Equipment | 1983 | 30 | 4 | 4
151 | 2 | Process Mechanical Equipment | 1983 | 30 | 4 | 4
152 | 2 | Process Mechanical Equipment | 1983 | 30 | 4 | 4
153 | 2 | Process Mechanical Equipment | 1983 | 30 | 3 | 3
154 | 2 | Process Mechanical Equipment | 1983 | 30 | 4 | 4
155 | 2 | Process Mechanical Equipment | 1983 | 30 | 4 | 4
156 | 4 | Process Piping | 1983 | 60 | 2 | 2
157 | 1 | Building Services | 1974 | 30 | 4 | 4
158 | 2 | Process Instrumentation | 2009 | 15 | 3 | 3
159 | 1 | Building Services | 1974 | 30 | 3 | 3
160 | 2 | Process Mechanical Equipment | 1974 | 30 | 3 | 3
161 | 2 | Process Mechanical Equipment | 1974 | 30 | 4 | 4
162 | 2 | Process Electrical | 1974 | 25 | 3 | 3
163 | 2 | Process Mechanical Equipment | 1974 | 30 | 4 | 4
164 | 2 | Process Mechanical Equipment | 1974 | 30 | 4 | 4
165 | 2 | Process Mechanical Equipment | 1974 | 30 | 3 | 3
166 | 2 | Process Mechanical Equipment | 1974 | 30 | 4 | 4
167 | 2 | Process Electrical | 1974 | 25 | 3 | 3
168 | 2 | Process Mechanical Equipment | 1974 | 30 | 4 | 4
169 | 2 | Process Mechanical Equipment | 1974 | 30 | 4 | 4
170 | 4 | Process Piping | 1974 | 60 | 3 | 3
172 | 2 | Process Instrumentation | 2019 | 15 | 3 | 3
174 | 2 | Process Mechanical Equipment | 1977 | 30 | 3 | 3
175 | 2 | Process Mechanical Equipment | 1977 | 30 | 4 | 4
177 | 2 | Process Mechanical Equipment | 1977 | 30 | 4 | 4
178 | 3 | Process Piping | 1977 | 60 | 3 | 3
179 | 1 | Building Services | 1986 | 30 | 3 | 3
180 | 2 | Process Instrumentation | 2009 | 15 | 3 | 3
181 | 1 | Building Services | 1986 | 30 | 3 | 3
182 | 2 | Process Mechanical Equipment | 1986 | 30 | 3 | 3
183 | 2 | Process Mechanical Equipment | 1986 | 30 | 3 | 3
184 | 2 | Process Electrical | 1986 | 25 | 3 | 3
185 | 2 | Process Mechanical Equipment | 1986 | 30 | 3 | 3
186 | 2 | Process Mechanical Equipment | 1986 | 30 | 5 | 5
187 | 2 | Process Mechanical Equipment | 1986 | 30 | 3 | 3
188 | 2 | Process Mechanical Equipment | 1986 | 30 | 3 | 3
189 | 2 | Process Electrical | 1986 | 25 | 3 | 3
190 | 2 | Process Mechanical Equipment | 1986 | 30 | 3 | 3
191 | 2 | Process Mechanical Equipment | 1986 | 30 | 3 | 3
192 | 4 | Process Piping | 1986 | 60 | 3 | 3
237 | 3 | Process Piping | 1975 | 60 | 3 | 3
238 | 3 | Process Piping | 1975 | 60 | 3 | 3
240 | 3 | Process Piping | 1975 | 60 | 3 | 3
241 | 3 | Process Piping | 1975 | 60 | 3 | 3
242 | 3 | Process Piping | 1983 | 60 | 2 | 2
243 | 3 | Process Piping | 1983 | 60 | 3 | 3
244 | 2 | Process Mechanical Equipment | 1983 | 30 | 3 | 3
247 | 3 | Process Piping | 1974 | 60 | 2 | 2
248 | 3 | Process Piping | 1974 | 60 | 3 | 3
249 | 2 | Process Mechanical Equipment | 1974 | 30 | 2 | 2
250 | 3 | Process Piping | 1974 | 60 | 2 | 2
251 | 3 | Process Piping | 1977 | 60 | 3 | 3
252 | 3 | Process Piping | 1977 | 60 | 4 | 4
253 | 3 | Process Piping | 1977 | 60 | 4 | 4
254 | 3 | Process Piping | 1986 | 60 | 2 | 2
255 | 3 | Process Piping | 1986 | 60 | 3 | 3
256 | 3 | Process Piping | 1986 | 60 | 2 | 2
257 | 3 | Process Piping | 1986 | 60 | 2 | 2
258 | 3 | Process Piping | 1986 | 60 | 2 | 2
259 | 3 | Process Piping | 1977 | 60 | 3 | 3
260 | 3 | Process Piping | 1977 | 60 | 4 | 4
261 | 3 | Process Piping | 1977 | 60 | 4 | 4
262 | 3 | Process Piping | 1973 | 60 | 3 | 3
263 | 3 | Process Piping | 1973 | 60 | 3 | 3
264 | 3 | Process Piping | 1973 | 60 | 3 | 3
265 | 3 | Process Piping | 1973 | 60 | 3 | 3
266 | 3 | Process Piping | 1985 | 60 | 3 | 3
267 | 3 | Process Piping | 1985 | 60 | 4 | 4
268 | 3 | Process Piping | 1985 | 60 | 4 | 4
301 | 2 | Building and Process Structural | 1975 | 60 | 3 | 3
302 | 1 | Building and Process Structural | 1975 | 60 | 3 | 3
303 | 2 | Building and Process Structural | 1975 | 60 | 3 | 3
304 | 1 | Building and Process Structural | 1975 | 60 | 3 | 3
305 | 1 | Building and Process Structural | 1975 | 60 | 3 | 3
306 | 2 | Building and Process Structural | 1975 | 60 | 2 | 2
307 | 2 | Building and Process Structural | 1975 | 60 | 3 | 3
308 | 2 | Building and Process Structural | 1975 | 60 | 3 | 3
309 | 2 | Building and Process Structural | 1975 | 60 | 3 | 3
317 | 2 | Building and Process Structural | 1983 | 60 | 3 | 3
318 | 1 | Building and Process Structural | 1983 | 60 | 3 | 3
319 | 2 | Building and Process Structural | 1983 | 60 | 3 | 3
320 | 1 | Building and Process Structural | 1983 | 60 | 3 | 3
321 | 2 | Building and Process Structural | 1983 | 60 | 3 | 3
322 | 2 | Building and Process Structural | 1983 | 60 | 3 | 3
323 | 2 | Building and Process Structural | 1983 | 60 | 3 | 3
324 | 1 | Building and Process Structural | 1983 | 60 | 3 | 3
325 | 2 | Building and Process Structural | 1974 | 60 | 2 | 2
326 | 2 | Building and Process Structural | 1974 | 60 | 3 | 3
327 | 1 | Building and Process Structural | 1974 | 60 | 2 | 2
328 | 1 | Building and Process Structural | 1974 | 60 | 3 | 3
329 | 2 | Building and Process Structural | 1974 | 60 | 3 | 3
330 | 2 | Building and Process Structural | 1974 | 60 | 3 | 3
331 | 1 | Building and Process Structural | 1974 | 60 | 3 | 3
332 | 2 | Building and Process Structural | 1974 | 60 | 3 | 3
333 | 1 | Building and Process Structural | 1977 | 60 | 2 | 2
334 | 2 | Building and Process Structural | 1977 | 60 | 3 | 3
335 | 2 | Building and Process Structural | 1977 | 60 | 3 | 3
336 | 2 | Building and Process Structural | 1977 | 60 | 3 | 3
337 | 2 | Building and Process Structural | 1977 | 60 | 4 | 4
338 | 2 | Building and Process Structural | 1986 | 60 | 3 | 3
339 | 2 | Building and Process Structural | 1986 | 60 | 3 | 3
340 | 1 | Building and Process Structural | 1986 | 60 | 3 | 3
341 | 2 | Building and Process Structural | 1986 | 60 | 4 | 4
342 | 1 | Building and Process Structural | 1986 | 60 | 3 | 3
343 | 2 | Building and Process Structural | 1986 | 60 | 3 | 3
344 | 1 | Building and Process Structural | 1986 | 60 | 3 | 3
345 | 2 | Building and Process Structural | 1986 | 60 | 4 | 4
346 | 1 | Building and Process Structural | 1977 | 60 | 2 | 2
347 | 2 | Building and Process Structural | 1977 | 60 | 3 | 3
348 | 2 | Building and Process Structural | 1977 | 60 | 4 | 4
349 | 2 | Building and Process Structural | 1977 | 60 | 3 | 3
350 | 1 | Building and Process Structural | 1973 | 60 | 3 | 3
351 | 2 | Building and Process Structural | 1973 | 60 | 3 | 3
352 | 2 | Building and Process Structural | 1973 | 60 | 3 | 3
353 | 1 | Building and Process Structural | 1973 | 60 | 3 | 3
354 | 1 | Building and Process Structural | 1973 | 60 | 3 | 3
355 | 2 | Building and Process Structural | 1973 | 60 | 3 | 3
356 | 2 | Building and Process Structural | 1973 | 60 | 3 | 3
357 | 1 | Building and Process Structural | 1985 | 60 | 3 | 3
358 | 1 | Building and Process Structural | 1985 | 60 | 3 | 3
359 | 1 | Building and Process Structural | 1985 | 60 | 3 | 3
360 | 2 | Building and Process Structural | 1985 | 60 | 3 | 3
361 | 2 | Building and Process Structural | 1985 | 60 | 3 | 3
362 | 2 | Building and Process Structural | 1985 | 60 | 3 | 3
363 | 2 | Building and Process Structural | 1985 | 60 | 4 | 4
382 | 2 | Building and Process Structural | 1986 | 60 | 3 | 3
383 | 2 | Building and Process Structural | 1974 | 60 | 3 | 3
384 | 2 | Building and Process Structural | 1983 | 60 | 3 | 3
385 | 2 | Building and Process Structural | 1975 | 60 | 3 | 3
387 |  | Building and Process Structural | 1977 | 60 | 2 | 2
392 | 2 | Process Mechanical Equipment | 1977 | 30 | 5 | 5
393 | 2 | Process Mechanical Equipment | 1977 | 30 | 4 | 4
394 | 2 | Process Mechanical Equipment | 1977 | 30 | 5 | 5
395 | 2 | Process Mechanical Equipment | 1977 | 30 | 5 | 5
396 | 2 | Process Mechanical Equipment | 1977 | 30 | 3 | 3
397 | 2 | Process Mechanical Equipment | 1977 | 30 | 4 | 4
399 | 2 | Process Mechanical Equipment | 1977 | 30 | 4 | 4
400 | 2 | Process Mechanical Equipment | 1977 | 30 | 4 | 4
401 | 2 | Process Mechanical Equipment | 1977 | 30 | 3 | 3
402 | 2 | Process Mechanical Equipment | 1977 | 30 | 4 | 4
403 | 2 | Process Mechanical Equipment | 1977 | 30 | 5 | 5
404 | 2 | Process Mechanical Equipment | 1977 | 30 | 3 | 3
405 | 2 | Process Mechanical Equipment | 1985 | 30 | 4 | 4
406 | 2 | Process Mechanical Equipment | 1985 | 30 | 4 | 4
422 | 1 | Process Instrumentation | 2009 | 15 | 3 | 3
423 | 2 | Process Instrumentation | 2009 | 15 | 2 | 2
424 | 2 | Process Instrumentation | 2009 | 15 | 2 | 2
429 | 2 | Process Instrumentation | 2019 | 15 | 2 | 2
430 | 1 | Process Instrumentation | 2019 | 15 | 2 | 2
431 | 1 | Process Instrumentation | 2016 | 15 | 2 | 2
432 | 2 | Process Instrumentation | 2009 | 15 | 2 | 2
433 | 1 | Process Instrumentation | 2016 | 15 | 3 | 3
434 | 2 | Process Instrumentation | 2009 | 15 | 2 | 2
435 | 1 | Process Instrumentation | 2009 | 15 | 3 | 3
436 | 2 | Process Instrumentation | 2009 | 15 | 2 | 2
437 | 2 | Process Instrumentation | 2009 | 15 | 2 | 2
438 | 1 | Process Instrumentation | 2016 | 15 | 2 | 2
439 | 2 | Process Instrumentation | 2019 | 15 | 2 | 2
440 | 2 | Process Instrumentation | 2009 | 15 | 2 | 2
441 | 1 | Process Instrumentation | 2016 | 15 | 2 | 2
442 | 2 | Process Instrumentation | 2009 | 15 | 2 | 2
443 | 2 | Process Instrumentation | 2008 | 15 | 2 | 2
444 | 2 | Process Instrumentation | 2016 | 15 | 2 | 2
445 | 2 | Process Instrumentation | 2009 | 15 | 2 | 2
446 | 2 | Process Instrumentation | 2009 | 15 | 2 | 2
447 | 1 | Process Instrumentation | 2016 | 15 | 2 | 2
448 | 2 | Process Instrumentation | 2009 | 15 | 2 | 2
485 | 2 | Process Electrical | 2010 | 25 | 2 | 2
486 | 2 | Process Electrical | 2010 | 25 | 2 | 2
487 | 2 | Process Electrical | 2010 | 25 | 2 | 2
488 | 2 | Process Electrical | 2010 | 25 | 2 | 2
489 | 1 | Process Electrical | 1975 | 25 | 2 | 2
490 | 2 | Process Electrical | 2010 | 25 | 2 | 2
491 | 3 | Process Electrical | 1975 | 25 | 3 | 3
492 | 2 | Process Electrical | 1965 | 25 | 2 | 2
493 | 2 | Process Electrical | 2010 | 25 | 3 | 3
494 | 2 | Process Electrical | 2010 | 25 | 2 | 2
495 | 2 | Process Electrical | 2010 | 25 | 3 | 3
496 | 1 | Building Services | 1965 | 30 | 2 | 2
497 | 3 | Process Electrical | 1965 | 25 | 3 | 3
498 | 2 | Process Electrical | 1965 | 25 | 2 | 2
499 | 2 | Process Electrical | 1993 | 25 | 3 | 3
500 | 2 | Process Electrical | 1993 | 25 | 3 | 3
501 | 2 | Process Electrical | 1993 | 25 | 2 | 2
502 | 2 | Process Electrical | 1993 | 25 | 3 | 3
503 | 1 | Process Electrical | 1974 | 25 | 3 | 3
504 | 3 | Process Electrical | 1974 | 25 | 3 | 3
505 | 2 | Process Electrical | 1972 | 25 | 3 | 3
506 | 3 | Process Electrical | 1972 | 25 | 2 | 2
507 | 2 | Process Electrical | 2007 | 25 | 2 | 2
508 | 2 | Process Electrical | 2007 | 25 | 2 | 2
509 | 2 | Process Electrical | 2007 | 25 | 2 | 2
510 | 2 | Process Electrical | 2007 | 25 | 3 | 3
511 | 1 | Process Electrical | 2007 | 25 | 4 | 4
512 | 2 | Process Electrical | 2010 | 25 | 2 | 2
513 | 2 | Process Electrical | 2010 | 25 | 3 | 3
514 | 2 | Process Electrical | 2010 | 25 | 2 | 2
515 | 2 | Process Electrical | 2010 | 25 | 3 | 3
516 | 3 | Process Electrical | 1983 | 25 | 3 | 3
517 | 2 | Process Electrical | 2010 | 25 | 2 | 2
518 | 1 | Process Electrical | 2000 | 25 | 2 | 2
519 | 1 | Process Electrical | 1977 | 25 | 3 | 3
520 | 1 | Process Electrical | 1977 | 25 | 3 | 3
521 | 2 | Process Electrical | 2003 | 25 | 2 | 2
522 | 3 | Process Electrical | 1977 | 25 | 3 | 3
523 | 2 | Process Electrical | 1977 | 25 | 3 | 3
524 | 2 | Process Electrical | 2003 | 25 | 2 | 2
525 | 2 | Process Electrical | 2003 | 25 | 2 | 2
526 | 2 | Process Electrical | 2010 | 25 | 2 | 2
527 | 2 | Process Electrical | 2010 | 25 | 2 | 2
528 | 2 | Process Electrical | 2010 | 25 | 3 | 3
529 | 2 | Process Electrical | 2010 | 25 | 3 | 3
530 | 2 | Process Electrical | 2010 | 25 | 2 | 2
531 | 1 | Process Electrical | 1973 | 25 | 3 | 3
532 | 3 | Process Electrical | 1973 | 25 | 3 | 3
533 | 1 | Process Electrical | 1985 | 25 | 5 | 3
534 | 1 | Process Electrical | 1985 | 25 | 3 | 3
535 | 1 | Process Electrical | 1985 | 25 | 3 | 3
536 | 2 | Process Electrical | 2006 | 25 | 2 | 2
537 | 2 | Process Electrical | 2006 | 25 | 2 | 2
538 | 2 | Process Electrical | 2006 | 25 | 2 | 2
539 | 3 | Process Electrical | 1985 | 25 | 2 | 2
540 | 2 | Process Electrical | 1985 | 25 | 2 | 2
576 | 1 | Building Services | 1975 | 30 | 3 | 3
577 | 1 | Building Services | 1975 | 30 | 2 | 2
578 | 1 | Building Services | 1975 | 30 | 2 | 2
579 | 1 | Building Services | 1983 | 30 | 2 | 2
580 | 1 | Building Services | 1983 | 30 | 2 | 2
581 | 1 | Building Services | 1983 | 30 | 4 | 4
583 | 1 | Building Services | 1974 | 30 | 3 | 3
584 | 1 | Building Services | 1974 | 30 | 3 | 3
585 | 1 | Building Services | 1974 | 30 | 2 | 2
586 | 1 | Building Services | 1974 | 30 | 2 | 2
587 | 1 | Building Services | 1977 | 30 | 3 | 3
588 | 1 | Building Services | 1986 | 30 | 3 | 3
589 | 1 | Building Services | 1986 | 30 | 2 | 2
590 | 1 | Building Services | 1986 | 30 | 2 | 2
592 | 1 | Building Services | 1977 | 30 | 3 | 3
593 | 1 | Building Services | 1973 | 30 | 2 | 2
594 | 1 | Building Services | 1973 | 30 | 2 | 2
595 | 1 | Building Services | 1985 | 30 | 2 | 2
611 | 1 | Site Works | 1975 | 20 | 2 | 2
612 | 1 | Site Works | 1983 | 20 | 2 | 2
613 | 1 | Site Works | 1974 | 20 | 2 | 2
614 | 1 | Site Works | 1977 | 20 | 2 | 2
615 | 1 | Site Works | 1968 | 20 | 2 | 2
616 | 1 | Site Works | 1977 | 20 | 4 | 4
622 | 1 | Site Works | 1973 | 20 | 3 | 3
623 | 1 | Site Works | 1985 | 20 | 4 | 4
632 |  | Asset Hierarchy | 1983
633 |  | Asset Hierarchy | 1983
638 |  | Asset Hierarchy | 1975
639 |  | Asset Hierarchy | 1975
640 |  | Asset Hierarchy | 1974
641 |  | Asset Hierarchy | 1974
642 |  | Asset Hierarchy | 1977
643 |  | Asset Hierarchy | 1986
644 |  | Asset Hierarchy | 1986
645 |  | Asset Hierarchy | 1977
646 |  | Asset Hierarchy | 1973
647 |  | Asset Hierarchy | 1973
648 |  | Asset Hierarchy | 1985
651 | 1 | Site Works | 1977 | 20 | 3 | 3
661 | 2 | Process Electrical | 2010 | 25 | 3 | 3
663 | 3 | Process Piping | 1983 | 60 | 3 | 3
665 | 3 | Process Piping | 1983 | 60 | 3 | 3
666 | 3 | Process Piping | 1974 | 60 | 3 | 3
667 | 2 | Process Electrical | 2010 | 25 | 3 | 3
669 | 3 | Process Piping | 1977 | 60 | 3 | 3
670 | 2 | Building and Process Structural | 1973 | 60 | 3 | 3
671 | 3 | Process Piping | 1985 | 60 | 4 | 4

## P_Comment
ParentID | Comment Type | Comment
24 | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed.
26 | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was noted throughout.
28 | Condition Comment | The asset was observed to be in fair condition. Exposed corroded reinforcement was observed.
29 | Condition Comment | The asset was observed to be in fair condition. Moderate corrosion was noted throughout.
31 | Condition Comment | The asset was observed to be in fair condition. Efflorescence deposits/leak at joint was noted. Concrete delamination/spalling at joint was observed.
34 | Condition Comment | The asset was observed to be in fair condition. Exposed corroded reinforcement, rust spots and concrete parging spalling were noted at joints.
36 | Condition Comment | The asset was observed to be in fair condition. Corrosion was noted throughout.
38 | Condition Comment | The asset was observed to be in fair condition.
41 | Condition Comment | The asset was observed to be in fair condition. Rust spots was observed noted.
42 | Condition Comment | The asset was observed to be in fair condition. Corrosion was observed was noted at the base.
44 | Condition Comment | The asset was observed to be in fair condition. Exposed corroded reinforcement and concrete spalling noted was observed.
46 | Condition Comment | The asset was observed to be in fair condition. Exposed corroded reinforcement and concrete spalling was noted at the pipe penetration.
53 | Condition Comment | The asset was observed to be in fair condition. The pump was near the end of its expected life.
54 | Condition Comment | The asset was observed to be in poor condition. Heavy corrosion was observed on the valve.
55 | Condition Comment | The asset was observed to be in poor condition. Heavy corrosion was observed on the valve.
56 | Condition Comment | The asset was assumed to be in fair condition.
57 | Condition Comment | The asset was observed to be in poor condition. The pump was near the end of its expected service life.
58 | Condition Comment | The asset was observed to be in poor condition. Severe corrosion was observed on the surface of the valve.
59 | Condition Comment | The asset was observed to be in poor condition. Heavy corrosion was observed on the valve.
60 | Condition Comment | The asset was observed to be in fair condition. The pipe was at half of its expected service life.
61 | Condition Comment | The asset was observed to be in fair condition. Surface staining on exhaust fan pipe was observed.
62 | Condition Comment | The asset was observed to be in fair condition. The pump was near the end of its expected service life.
63 | Condition Comment | The asset was observed to be in poor condition. Heavy corrosion was observed on the surface of the valve.
64 | Condition Comment | The asset was observed to be in poor condition. Heavy corrosion was observed on the surface of the valve.
65 | Condition Comment | The asset was observed to be in fair condition. The pump was near the end of its expected service life.
66 | Condition Comment | The asset was observed to be in poor condition. Heavy corrosion was observed on the surface of the valve.
67 | Condition Comment | The asset was observed to be in poor condition. Heavy corrosion was observed on the surface of the valve.
68 | Condition Comment | The asset was assumed to be in fair condition.
69 | Condition Comment | The asset was observed to be in poor condition. Moderate corrosion was observed and deterioration was observed on the surface of the pump. The pump was beyond its expected service life.
70 | Condition Comment | The asset was observed to be in good condition.
71 | Condition Comment | The asset was observed to be in fair condition. Paint peeling was observed.
72 | Condition Comment | The asset was observed to be in poor condition. Corrosion was observed and deterioration was observed on the surface of the pump. The pump was beyond its expected service life.
73 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the surface of the valve. The valve was beyond its expected service life.
74 | Condition Comment | The asset was observed to be in fair condition. Minor paint wear was observed.
75 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the surface of the valve. The valve was beyond its expected service life.
76 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the surface of the valve. The valve was beyond its expected service life.
78 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the surface of the pump. The pump was beyond its expected service life.
79 | Condition Comment | The asset was observed to be in poor condition. Deterioration and corrosion were observed on the surface of the valve. The valve was beyond its expected service life was observed.
80 | Condition Comment | The asset was observed to be in fair condition. Minor paint wear was observed.
81 | Condition Comment | The asset was observed to be in poor condition. Corrosion was observed on the surface of the valve. The valve was beyond its expected service life.
82 | Condition Comment | The asset was observed to be in fair condition. Minor deterioration was observed on the surface of the valve. The valve was beyond its expected service life was observed.
83 | Condition Comment | The asset was assumed to be in fair condition.
129 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the surface of the pump. The pump was beyond the end of its expected service life.
130 | Condition Comment | The asset was observed to be in fair condition. Dust and corrosion were observed.
131 | Condition Comment | The asset was observed to be in poor condition. The exhaust fan was missing and as per section 7.2.9 of moecc's design guidelines for sewage works, mechanical ventilation is required for below ground surface dry well were observed.
132 | Condition Comment | The asset was observed to be in fair condition. Deterioration was observed on the surface of the pump and it is beyond the end of its expected service life.
133 | Condition Comment | The asset was observed to be in fair condition. Corrosion and deterioration were observed on the surface of the valve. The valve was beyond its expected service life.
134 | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed on casing.
135 | Condition Comment | The asset was observed to be in fair condition. Corrosion and deterioration were observed on the surface of the valve. The valve was beyond its expected service life.
136 | Condition Comment | The asset was observed to be in fair condition. Corrosion and deterioration were observed on the surface of the valve. The valve was beyond its expected service life.
137 | Condition Comment | The asset was observed to be in fair condition. Deterioration was observed on the surface of the pump and it is beyond the end of its expected service life was observed.
138 | Condition Comment | The asset was observed to be in fair condition. Corrosion and deterioration were observed on the surface of the valve. The valve was beyond its expected service life.
139 | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed on casing.
140 | Condition Comment | The asset was observed to be in fair condition. Corrosion and deterioration were observed on the surface of the valve. The valve was beyond its expected service life.
141 | Condition Comment | The asset was observed to be in fair condition. Corrosion and deterioration were observed on the surface of the valve. The valve was beyond its expected service life.
142 | Condition Comment | The asset was assumed to be in fair condition and the pipe is at half of its expected service life.
143 | Condition Comment | The asset was observed to be in poor condition. Severe corrosion and deterioration were observed on the surface of the pump. The pump was near the end of its expected service life.
144 | Condition Comment | The asset was observed to be in good condition.
145 | Condition Comment | The asset was observed to be in poor condition. As per section 7.2.9 of moecc's design guidelines for sewage works, mechanical ventilation is required for below ground surface dry well was observed.
146 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the surface of the pump. The pump was near the end of its expected service life.
147 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the surface of the valve. The valve is near the end of its expected service life.
148 | Condition Comment | The asset was observed to be in fair condition. Minor surface corrosion was observed.
149 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the valve. The valve was near the end of its expected service life.
150 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the valve. The valve was near the end of its expected service life.
151 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the surface of the pump. The pump was near the end of its expected service life.
152 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the valve. The valve was near the end of its expected service life.
153 | Condition Comment | The asset was observed to be in fair condition. Minor surface corrosion and paint wear were observed.
154 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the valve. The valve was near the end of its expected service life.
155 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the valve. The valve was near the end of its expected service life.
156 | Condition Comment | The asset was observed to be in good condition.
157 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the surface of the pump. The pump was near the end of its expected service life.
158 | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed on nuts.
159 | Condition Comment | The asset was observed to be in fair condition. Surface corrosion was observed.
160 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the surface of the pump. The pump was near the end of its expected service life.
161 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the valve. The valve was near the end of its expected service life.
162 | Condition Comment | The asset was observed to be in fair condition. Paint wear was observed.
163 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the valve. The valve was near the end of its expected service life.
164 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the valve. The valve was near the end of its expected service life.
165 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the surface of the pump. The pump was near the end of its expected service life.
166 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the surface of the valve. The valve was near the end of its expected service life.
167 | Condition Comment | The asset was observed to be in fair condition. Paint wear was observed.
168 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the valve. The valve was near the end of its expected service life.
169 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the valve. The valve was near the end of its expected service life.
170 | Condition Comment | The asset was assumed to be in fair condition. The pipe was at half of its expected service life were observed.
172 | Condition Comment | The asset was observed to be in very good condition.
174 | Condition Comment | The asset was observed to be in fair condition. The pump was beyond its expected service life.
175 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the valve. The valve was near the end of its expected service life.
177 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the valve. The valve was near the end of its expected service life.
178 | Condition Comment | The asset was assumed to be in fair condition. The pipe was at half of its expected service life were observed.
179 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the surface of the pump. The pump was near the end of its expected service life.
180 | Condition Comment | The asset was observed to be in fair condition. Nuts were not secured properly.
181 | Condition Comment | The asset was observed to be in fair condition. Paint peeling was observed.
182 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the surface of the pump. The pump was near the end of its expected service life.
183 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the valve. The valve was near the end of its expected service life.
184 | Condition Comment | The asset was observed to be in fair condition. Paint wear was observed.
185 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the valve. The valve was near the end of its expected service life.
186 | Condition Comment | The asset was observed to be in very poor condition. Severe corrosion and deterioration were observed on the valve. The valve was near the end of its expected service life.
187 | Condition Comment | The asset was observed to be in fair condition. Deterioration was observed on the surface of the pump. The pump was near the end of its expected service life was observed.
188 | Condition Comment | The asset was observed to be in fair condition. Deterioration were observed on the valve. The valve was near the end of its expected service life.
189 | Condition Comment | The asset was observed to be in fair condition. Paint wear was observed.
190 | Condition Comment | The asset was observed to be in fair condition. Corrosion and deterioration were observed on the valve. The valve was near the end of its expected service life.
191 | Condition Comment | The asset was observed to be in fair condition. Minor deterioration was observed on the surface of the valve. The valve was near the end of its expected service life.
192 | Condition Comment | The asset was assumed to be in fair condition.
237 | Condition Comment | The asset was assumed to be in fair condition. The pipe is at half of its expected service life.
238 | Condition Comment | The asset was assumed to be in fair condition. The pipe is at half of its expected service life.
240 | Condition Comment | The asset was assumed to be in fair condition. The pipe is at half of its expected service life.
241 | Condition Comment | The asset was assumed to be in fair condition. The pipe is at half of its expected service life.
242 | Condition Comment | The asset was observed to be in good condition.
243 | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed.
244 | Condition Comment | The asset was observed to be in fair condition. Corrosion was observed.
247 | Condition Comment | The asset was observed to be in good condition. The pipe was at half of its expected service life.
248 | Condition Comment | The asset was observed to be in good condition. The pipe was at half of its expected service life.
249 | Condition Comment | The asset was observed to be in good condition.
250 | Condition Comment | The asset was observed to be in good condition.
251 | Condition Comment | The asset was assumed to be fair and the pipe was at half of its expected service life.
252 | Condition Comment | The asset was observed to be in poor condition. Heavy corrosion was observed on the surface of the pipe.
253 | Condition Comment | The asset was observed to be in poor condition. Heavy corrosion was observed on the surface of the pipe.
254 | Condition Comment | The asset was observed to be in good condition.
255 | Condition Comment | The asset was assumed to be in fair condition.
256 | Condition Comment | The asset was observed to be in good condition.
257 | Condition Comment | The asset was observed to be in good condition.
258 | Condition Comment | The asset was observed to be in good condition.
259 | Condition Comment | The asset was observed to be in fair condition. The pipe was at half of its expected service life.
260 | Condition Comment | The asset was observed to be in poor condition. Heavy corrosion was observed on the pipe.
261 | Condition Comment | The asset was observed to be in poor condition. Heavy corrosion was observed on the pipe.
262 | Condition Comment | The asset was assumed to be in fair condition. The pipe passed half of its expected service life.
263 | Condition Comment | The asset was observed to be in fair condition. Minor deterioration was observed on the pipe and it passed half of its expected service life.
264 | Condition Comment | The asset was observed to be in fair condition. Minor deterioration was observed on the pipe and it passed half of its expected service life.
265 | Condition Comment | The asset was observed to be in fair condition. Minor deterioration was observed on the pipe and it passed half of its expected service life.
266 | Condition Comment | The asset was assumed to be in fair condition.
267 | Condition Comment | The asset was observed to be in poor condition. Heavy corrosion and deterioration were observed.
268 | Condition Comment | The asset was observed to be in poor condition. Heavy corrosion and deterioration were observed was observed.
301 | Condition Comment | The asset was observed to be in fair condition. Rust spots was observed noted.
302 | Condition Comment | The asset was observed to be in fair condition. Minor corrosion and paint wear were noted.
303 | Condition Comment | The asset was observed to be in fair condition. Minor paint wear was observed.
304 | Condition Comment | The asset was observed to be in fair condition. Peeling paint on exterior was observed.
305 | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed on the underside.
306 | Condition Comment | The asset was observed to be in good condition.
307 | Condition Comment | The asset was observed to be in fair condition. Corrosion was observed noted.
308 | Condition Comment | The asset was observed to be in fair condition. Corrosion was observed noted.
309 | Condition Comment | The asset was observed to be in fair condition. To be inspected yearly and as per occupational health and safety act, r.s.o. 1990, c. o.1 the davit socket base is to be inspected every year.
317 | Condition Comment | The asset was observed to be in fair condition. Minor corrosion and paint wear were noted.
318 | Condition Comment | The asset was observed to be in fair condition. Paint wear was observed.
319 | Condition Comment | The asset was observed to be in fair condition. To be inspected yearly and as per occupational health and safety act, r.s.o. 1990, c. o.1 the davit socket base is to be inspected every year.
320 | Condition Comment | The asset was observed to be in fair condition. Surface corrosion noted on underside was observed.
321 | Condition Comment | The asset was observed to be in fair condition. To be inspected yearly and as per occupational health and safety act, r.s.o. 1990, c. o.1 the davit socket base is to be inspected every year.
322 | Condition Comment | The asset was observed to be in fair condition. Bent was observed ladder rung.
323 | Condition Comment | The asset was observed to be in fair condition. Corrosion was observed noted.
324 | Condition Comment | The asset was observed to be in fair condition. Weathered paint was observed on exterior and minor corrosion was noted inside.
325 | Condition Comment | The asset was observed to be in good condition.
326 | Condition Comment | The asset was observed to be in fair condition. Discoloration of the checker plate was noted.
327 | Condition Comment | The asset was observed to be in good condition.
328 | Condition Comment | The asset was observed to be in fair condition. Weathered paint was observed.
329 | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed.
330 | Condition Comment | The asset was observed to be in fair condition based on its age.
331 | Condition Comment | The asset was observed to be in fair condition. Peeling paint on exterior and corrosion were observed.
332 | Condition Comment | The asset was observed to be in fair condition. To be inspected yearly and as per occupational health and safety act, r.s.o. 1990, c. o.1 the davit socket base is to be inspected every year.
333 | Condition Comment | The asset was observed to be in good condition.
334 | Condition Comment | The asset was observed to be in fair condition. Staining/corrosion noted was observed.
335 | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed.
336 | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed.
337 | Condition Comment | The asset was observed to be in fair condition. To be inspected yearly and as per occupational health and safety act, r.s.o. 1990, c. o.1 the davit socket base is to be inspected every year.
338 | Condition Comment | The asset was observed to be in fair condition.
339 | Condition Comment | The asset was observed to be in fair condition. Fixed portion of platform grating was noted to be bent.
340 | Condition Comment | The asset was observed to be in fair condition.
341 | Condition Comment | The asset was observed to be in fair condition. To be inspected yearly and as per occupational health and safety act, r.s.o. 1990, c. o.1 the davit socket base is to be inspected every year.
342 | Condition Comment | The asset was observed to be in fair condition. Corrosion and paint wear were noted.
343 | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed.
344 | Condition Comment | The asset was observed to be in fair condition. Flaking/missing on exterior was observed.
345 | Condition Comment | The asset was observed to be in fair condition. To be inspected yearly and as per occupational health and safety act, r.s.o. 1990, c. o.1 the davit socket base is to be inspected every year.
346 | Condition Comment | The asset was observed to be in good condition.
347 | Condition Comment | The asset was observed to be in fair condition. Pitting was observed.
348 | Condition Comment | The asset was observed to be in fair condition. To be inspected yearly and as per occupational health and safety act, r.s.o. 1990, c. o.1 the davit socket base is to be inspected every year.
349 | Condition Comment | The asset was observed to be in fair condition. Calcium buildup and pitting was noted
350 | Condition Comment | The asset was observed to be in fair condition. Paint wear was observed.
351 | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed.
352 | Condition Comment | The asset was observed to be in fair condition.
353 | Condition Comment | The asset was observed to be in fair condition. Weathered paint was observed and missing paint on exterior.
354 | Condition Comment | The asset was observed to be in fair condition.
355 | Condition Comment | The asset was observed to be in fair condition.
356 | Condition Comment | The asset was observed to be in fair condition. Anchors were corroded was observed.
357 | Condition Comment | The asset was observed to be in fair condition. Minor corrosion and staining were noted.
358 | Condition Comment | The asset was observed to be in fair condition. Missing safety grating was noted. The pump hatch 1 was missing grating. under Ontario regulation 213/91 this presents a fall hazard when the hatches are left open.
359 | Condition Comment | The asset was observed to be in fair condition. Missing safety grating was noted. The pump hatch 1 was missing grating. under Ontario regulation 213/91 this presents a fall hazard when the hatches are left open.
360 | Condition Comment | The asset was observed to be in fair condition. Calcium buildup and corrosion were observed.
361 | Condition Comment | The asset was observed to be in fair condition. Calcium buildup and corrosion were observed.
362 | Condition Comment | The asset was observed to be in fair condition. Gratings now clipped down. Corrosion was observed noted.
363 | Condition Comment | The asset was observed to be in fair condition. To be inspected yearly and as per occupational health and safety act, r.s.o. 1990, c. o.1 the davit socket base is to be inspected every year.
382 | Condition Comment | The asset was assumed to be in fair condition as it was not visible.
383 | Condition Comment | The asset was assumed to be in fair condition as it was not visible.
384 | Condition Comment | The asset was assumed to be in fair condition as it was not visible.
385 | Condition Comment | The asset was assumed to be in fair condition as it was not visible.
387 | Condition Comment | The asset was observed to be in good condition.
392 | Condition Comment | The asset was observed to be in very poor condition. Severe corrosion was observed on the surface of the valve. The valve was beyond its expected service life.
393 | Condition Comment | The asset was observed to be in poor condition. The pump was beyond its expected service life.
394 | Condition Comment | The asset was observed to be in very poor condition. Severe corrosion was observed on the surface of the valve. The valve was beyond its expected service life.
395 | Condition Comment | The asset was observed to be in very poor condition. Severe corrosion was observed on the surface of the valve. The valve was beyond its expected service life.
396 | Condition Comment | The asset was observed to be in fair condition. Minor deterioration was observed on the bar screen.
397 | Condition Comment | The asset was observed to be in poor condition. The pump was beyond its expected service life.
399 | Condition Comment | The asset was observed to be in poor condition. The pump was beyond its expected service life.
400 | Condition Comment | The asset was observed to be in very poor condition. Severe corrosion was observed on the surface of the valve. The valve was beyond its expected service life.
401 | Condition Comment | The asset was assumed to be in fair condition.
402 | Condition Comment | The asset was observed to be in poor condition. Heavy corrosion was observed on the surface of the valve. The valve was beyond its expected service life was observed.
403 | Condition Comment | The asset was observed to be in very poor condition. Severe corrosion was observed on the surface of the valve. The valve was beyond its expected service life.
404 | Condition Comment | The asset was observed to be in fair condition. Debris was clogging at the bar screen, which in terms start clogging the inlet pipe.
405 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the surface of the valve. The valve was near the end of its expected service life.
406 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the surface of the valve.
422 | Condition Comment | The asset was observed to be in fair condition. The asset was obsolete.
423 | Condition Comment | The asset was observed to be in good condition.
424 | Condition Comment | The asset was observed to be in good condition. Dust was observed.
429 | Condition Comment | The asset was observed to be in good condition.
430 | Condition Comment | The asset was observed to be in good condition.
431 | Condition Comment | The asset was observed to be in good condition.
432 | Condition Comment | The asset was observed to be in good condition.
433 | Condition Comment | The asset was observed to be in very good condition.
434 | Condition Comment | The asset was observed to be in good condition.
435 | Condition Comment | The asset was observed to be in fair condition. The asset was obsolete.
436 | Condition Comment | The asset was observed to be in good condition.
437 | Condition Comment | The asset was observed to be in good condition.
438 | Condition Comment | The asset was observed to be in good condition.
439 | Condition Comment | The asset was observed to be in good condition.
440 | Condition Comment | The asset was observed to be in good condition.
441 | Condition Comment | The asset was observed to be in good condition.
442 | Condition Comment | The asset was observed to be in good condition.
443 | Condition Comment | The asset was observed to be in good condition.
444 | Condition Comment | The asset was observed to be in good condition.
445 | Condition Comment | The asset was observed to be in good condition.
446 | Condition Comment | The asset was observed to be in good condition. Bolts were not secured properly.
447 | Condition Comment | The asset was observed to be in good condition.
448 | Condition Comment | The asset was observed to be in good condition.
485 | Condition Comment | The asset was observed to be in good condition.
486 | Condition Comment | The asset was observed to be in good condition.
487 | Condition Comment | The asset was observed to be in good condition.
488 | Condition Comment | The asset was observed to be in good condition.
489 | Condition Comment | The asset was observed to be in good condition. Replace with led fixtures rated for class 1, div 2.
490 | Condition Comment | The asset was observed to be in fair condition. Inside the panel is not getting drained properly.
491 | Condition Comment | The asset was observed to be in fair condition. Replace with nema 4x panel.
492 | Condition Comment | The asset was observed to be in good condition.
493 | Condition Comment | The asset was observed to be in fair condition. Missing was observed arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the panel which may require examination, adjustment, servicing.
494 | Condition Comment | The asset was observed to be in good condition.
495 | Condition Comment | The asset was observed to be in fair condition. Missing was observed arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the panel which may require examination, adjustment, servicing.
496 | Condition Comment | The asset was observed to be in good condition. Replace with led in next upgrade.
497 | Condition Comment | The asset was observed to be in fair condition. Missing was observed arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the panel which may require examination, adjustment, servicing.
498 | Condition Comment | The asset was observed to be in good condition.
499 | Condition Comment | The asset was observed to be in fair condition. Bottom of interior has corroded and replace with nema 3r enclosure in next upgrade.
500 | Condition Comment | The asset was observed to be in fair condition. Missing was observed arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the panel which may require examination, adjustment, servicing.
501 | Condition Comment | The asset was observed to be in good condition.
502 | Condition Comment | The asset was observed to be in fair condition. Missing was observed arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the panel which may require examination, adjustment, servicing.
503 | Condition Comment | The asset was observed to be in fair condition. Replace with led fixture in next upgrade. to be rated for class 1, div 2.
504 | Condition Comment | The asset was observed to be in fair condition. Missing was observed arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the panel which may require examination, adjustment, servicing.
505 | Condition Comment | The asset was observed to be in fair condition. Top surface and doors were corroded and to be replaced with nema 3r enclosure.
506 | Condition Comment | The asset was observed to be in fair condition. Missing was observed arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the panel which may require examination, adjustment, servicing.
507 | Condition Comment | The asset was observed to be in good condition.
508 | Condition Comment | The asset was observed to be in good condition.
509 | Condition Comment | The asset was observed to be in good condition.
510 | Condition Comment | The asset was observed to be in fair condition. Missing was observed arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the panel which may require examination, adjustment, servicing.
511 | Condition Comment | The asset was observed to be in poor condition. Severely corroded was observed.
512 | Condition Comment | The asset was observed to be in good condition.
513 | Condition Comment | The asset was observed to be in fair condition. Misplaced and outdated arc flash label was noted. Shock and arc flash hazard as no arc flash label were installed. as per (Ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the vfd breaker which may require examination, adjustment, servicing.
514 | Condition Comment | The asset was observed to be in good condition.
515 | Condition Comment | The asset was observed to be in fair condition. Misplaced and outdated arc flash label was noted. Shock and arc flash hazard as no arc flash label were installed. as per (Ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the vfd breaker which may require examination, adjustment, servicing.
516 | Condition Comment | The asset was observed to be in fair condition. Misplaced and outdated arc flash label was noted. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the vfd breaker which may require examination, adjustment, servicing.
517 | Condition Comment | The asset was observed to be in good condition.
518 | Condition Comment | The asset was observed to be in good condition. Replace with LED in next upgrade.
519 | Condition Comment | The asset was observed to be in good condition. Replace with LED in next upgrade.
520 | Condition Comment | The asset was observed to be in good condition. Replace with LED in next upgrade.
521 | Condition Comment | The asset was observed to be in good condition.
522 | Condition Comment | The asset was observed to be in fair condition. To have separate main DS, MTS, and CP. Outdated arc flash label was noted. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the vfd breaker which may require examination, adjustment, servicing.
523 | Condition Comment | The asset was observed to be in fair condition.
524 | Condition Comment | The asset was observed to be in good condition.
525 | Condition Comment | The asset was observed to be in good condition.
526 | Condition Comment | The asset was observed to be in good condition.
527 | Condition Comment | The asset was observed to be in good condition.
528 | Condition Comment | The asset was observed to be in fair condition. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the vfd breaker which may require examination, adjustment, servicing.
529 | Condition Comment | The asset was observed to be in fair condition. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the vfd breaker which may require examination, adjustment, servicing.
530 | Condition Comment | The asset was observed to be in good condition.
531 | Condition Comment | The asset was observed to be in fair condition. One of the lights doesn’t work and to be replaced with LED.
532 | Condition Comment | The asset was observed to be in fair condition. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the vfd breaker which may require examination, adjustment, servicing.
533 | Condition Comment | The asset was observed to be in very poor condition as it was not working.
534 | Condition Comment | The asset was observed to be in fair condition. To be replaced with LED
535 | Condition Comment | The asset was observed to be in fair condition. To be replaced with nema 3r enclosure.
536 | Condition Comment | The asset was observed to be in good condition.
537 | Condition Comment | The asset was observed to be in good condition.
538 | Condition Comment | The asset was observed to be in good condition.
539 | Condition Comment | The asset was observed to be in good condition. Replace with separate main ds, mts and cp and shock and arc flash hazard as the existing arc flash label are outdated. As per (workplace electrical safety (csa z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents.
540 | Condition Comment | The asset was observed to be in good condition.
576 | Condition Comment | The asset was observed to be in fair condition. Surface corrosion was observed.
577 | Condition Comment | The asset was observed to be in good condition.
578 | Condition Comment | The asset was observed to be in good condition.
579 | Condition Comment | The asset was observed to be in good condition.
580 | Condition Comment | The asset was observed to be in good condition.
581 | Condition Comment | The asset was observed to be in poor condition. Severe corrosion was observed.
583 | Condition Comment | The asset was observed to be in fair condition. Surface corrosion was observed.
584 | Condition Comment | The asset was observed to be in fair condition. Surface corrosion was observed.
585 | Condition Comment | The asset was observed to be in good condition.
586 | Condition Comment | The asset was observed to be in good condition.
587 | Condition Comment | The asset was observed to be in fair condition. Miscellaneous surface staining was observed.
588 | Condition Comment | The asset was assumed to be in fair condition.
589 | Condition Comment | The asset was observed to be in good condition.
590 | Condition Comment | The asset was observed to be in good condition.
592 | Condition Comment | The asset was observed to be in fair condition. Paint peeling was observed.
593 | Condition Comment | The asset was observed to be in good condition.
594 | Condition Comment | The asset was observed to be in good condition.
595 | Condition Comment | The asset was observed to be in good condition.
611 | Condition Comment | The asset was observed to be in good condition.
612 | Condition Comment | The asset was observed to be in good condition.
613 | Condition Comment | The asset was observed to be in good condition.
614 | Condition Comment | The asset was observed to be in good condition.
615 | Condition Comment | The asset was observed to be in good condition.
616 | Condition Comment | The asset was observed to be in poor condition. In accordance with section 19.8.3 of the region's water and wastewater design manual (January 2012), a yard hydrant complete with a backflow preventer with a 37.5mm water service line shall be provided for flushing and cleaning purposes. it is recommended to have it installed.
622 | Condition Comment | The asset was observed to be in fair condition. Minor surface rust and defects was observed.
623 | Condition Comment | The asset was observed to be in poor condition. In accordance with section 19.8.3 of the region's water and wastewater design manual (January 2012), a yard hydrant complete with a backflow preventer with a 37.5mm water service line shall be provided for flushing and cleaning purposes. it is recommended to have it installed.
651 | Condition Comment | The asset was observed to be in fair condition. fair and overgrown vegetation were observed.
661 | Condition Comment | The cathodic protection was assumed to be in good condition. The installation of the cathodic protection system was assumed to coincide with the installation of the above grade panel.
663 | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed.
665 | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed.
666 | Condition Comment | The asset was observed to be in fair condition. Corrosion was observed.
667 | Condition Comment | The cathodic protection was assumed to be in good condition. The installation of the cathodic protection system was assumed to coincide with the installation of the above grade panel.
669 | Condition Comment | The asset was assumed to be in fair condition.
670 | Condition Comment | The asset was assumed to be in fair condition based on its age.
671 | Condition Comment | The asset was observed to be in poor condition. Heavy corrosion and deterioration was observed.

## P_replacement
ParentID | WorkYear | Recurring | WorkFrequency | ParentID |  | 56 | 2026 | True | 25
24 | 2035 | True | 60 | 24 | 0 | 255 | 2046 | True | 60
26 | 2043 | True | 60 | 26 | 0 | 401 | 2026 | True | 30
28 | 2043 | True | 60 | 28 | 0 | 593 | 2026 | True | 30
29 | 2034 | True | 60 | 29 | 0
31 | 2034 | True | 60 | 31 | 0
34 | 2037 | True | 60 | 34 | 0
36 | 2046 | True | 60 | 36 | 0
38 | 2046 | True | 60 | 38 | 0
41 | 2037 | True | 60 | 41 | 0
42 | 2033 | True | 60 | 42 | 0
44 | 2033 | True | 60 | 44 | 0
46 | 2045 | True | 60 | 46 | 0
53 | 2026 | True | 30 | 53 | 0
54 | 2026 | True | 30 | 54 | 0
55 | 2026 | True | 30 | 55 | 0
57 | 2026 | True | 30 | 57 | 0
58 | 2026 | True | 30 | 58 | 0
59 | 2026 | True | 30 | 59 | 0
60 | 2037 | True | 60 | 60 | 0
61 | 2026 | True | 30 | 61 | 0
62 | 2026 | True | 30 | 62 | 0
63 | 2026 | True | 30 | 63 | 0
64 | 2026 | True | 30 | 64 | 0
65 | 2026 | True | 30 | 65 | 0
66 | 2026 | True | 30 | 66 | 0
67 | 2026 | True | 30 | 67 | 0
68 | 2045 | True | 60 | 68 | 0
69 | 2026 | True | 30 | 69 | 0
70 | 2029 | True | 15 | 70 | 0
71 | 2026 | True | 30 | 71 | 0
72 | 2026 | True | 30 | 72 | 0
73 | 2026 | True | 30 | 73 | 0
74 | 2026 | True | 25 | 74 | 0
75 | 2026 | True | 30 | 75 | 0
76 | 2026 | True | 30 | 76 | 0
78 | 2026 | True | 30 | 78 | 0
79 | 2026 | True | 30 | 79 | 0
80 | 2026 | True | 25 | 80 | 0
81 | 2026 | True | 30 | 81 | 0
82 | 2026 | True | 30 | 82 | 0
83 | 2033 | True | 60 | 83 | 0
129 | 2026 | True | 30 | 129 | 0
130 | 2030 | True | 15 | 130 | 0
131 | 2026 | True | 30 | 131 | 0
132 | 2026 | True | 30 | 132 | 0
133 | 2026 | True | 30 | 133 | 0
134 | 2026 | True | 25 | 134 | 0
135 | 2026 | True | 30 | 135 | 0
136 | 2026 | True | 30 | 136 | 0
137 | 2026 | True | 30 | 137 | 0
138 | 2026 | True | 30 | 138 | 0
139 | 2026 | True | 25 | 139 | 0
140 | 2026 | True | 30 | 140 | 0
141 | 2026 | True | 30 | 141 | 0
142 | 2035 | True | 60 | 142 | 0
143 | 2026 | True | 30 | 143 | 0
144 | 2030 | True | 15 | 144 | 0
145 | 2026 | True | 30 | 145 | 0
146 | 2026 | True | 30 | 146 | 0
147 | 2026 | True | 30 | 147 | 0
148 | 2026 | True | 30 | 148 | 0
149 | 2026 | True | 30 | 149 | 0
150 | 2026 | True | 30 | 150 | 0
151 | 2026 | True | 30 | 151 | 0
152 | 2026 | True | 30 | 152 | 0
153 | 2026 | True | 30 | 153 | 0
154 | 2026 | True | 30 | 154 | 0
155 | 2026 | True | 30 | 155 | 0
156 | 2043 | True | 60 | 156 | 0
157 | 2026 | True | 30 | 157 | 0
158 | 2030 | True | 15 | 158 | 0
159 | 2026 | True | 30 | 159 | 0
160 | 2026 | True | 30 | 160 | 0
161 | 2026 | True | 30 | 161 | 0
162 | 2026 | True | 25 | 162 | 0
163 | 2026 | True | 30 | 163 | 0
164 | 2026 | True | 30 | 164 | 0
165 | 2026 | True | 30 | 165 | 0
166 | 2026 | True | 30 | 166 | 0
167 | 2026 | True | 25 | 167 | 0
168 | 2026 | True | 30 | 168 | 0
169 | 2026 | True | 30 | 169 | 0
170 | 2034 | True | 60 | 170 | 0
172 | 2034 | True | 15 | 172 | 0
174 | 2026 | True | 30 | 174 | 0
175 | 2026 | True | 30 | 175 | 0
177 | 2026 | True | 30 | 177 | 0
178 | 2037 | True | 60 | 178 | 0
179 | 2026 | True | 30 | 179 | 0
180 | 2030 | True | 15 | 180 | 0
181 | 2026 | True | 30 | 181 | 0
182 | 2026 | True | 30 | 182 | 0
183 | 2026 | True | 30 | 183 | 0
184 | 2026 | True | 25 | 184 | 0
185 | 2026 | True | 30 | 185 | 0
186 | 2022 | True | 30 | 186 | 0
187 | 2026 | True | 30 | 187 | 0
188 | 2026 | True | 30 | 188 | 0
189 | 2026 | True | 25 | 189 | 0
190 | 2026 | True | 30 | 190 | 0
191 | 2026 | True | 30 | 191 | 0
192 | 2046 | True | 60 | 192 | 0
237 | 2035 | True | 60 | 237 | 0
238 | 2035 | True | 60 | 238 | 0
240 | 2035 | True | 60 | 240 | 0
241 | 2035 | True | 60 | 241 | 0
242 | 2043 | True | 60 | 242 | 0
243 | 2043 | True | 60 | 243 | 0
244 | 2026 | True | 30 | 244 | 0
247 | 2034 | True | 60 | 247 | 0
248 | 2034 | True | 60 | 248 | 0
249 | 2026 | True | 30 | 249 | 0
250 | 2034 | True | 60 | 250 | 0
251 | 2037 | True | 60 | 251 | 0
252 | 2037 | True | 60 | 252 | 0
253 | 2037 | True | 60 | 253 | 0
254 | 2046 | True | 60 | 254 | 0
256 | 2046 | True | 60 | 256 | 0
257 | 2046 | True | 60 | 257 | 0
258 | 2046 | True | 60 | 258 | 0
259 | 2037 | True | 60 | 259 | 0
260 | 2037 | True | 60 | 260 | 0
261 | 2037 | True | 60 | 261 | 0
262 | 2033 | True | 60 | 262 | 0
263 | 2033 | True | 60 | 263 | 0
264 | 2033 | True | 60 | 264 | 0
265 | 2033 | True | 60 | 265 | 0
266 | 2045 | True | 60 | 266 | 0
267 | 2045 | True | 60 | 267 | 0
268 | 2045 | True | 60 | 268 | 0
301 | 2035 | True | 60 | 301 | 0
302 | 2035 | True | 60 | 302 | 0
303 | 2035 | True | 60 | 303 | 0
304 | 2035 | True | 60 | 304 | 0
305 | 2035 | True | 60 | 305 | 0
306 | 2035 | True | 60 | 306 | 0
307 | 2035 | True | 60 | 307 | 0
308 | 2035 | True | 60 | 308 | 0
309 | 2035 | True | 60 | 309 | 0
317 | 2043 | True | 60 | 317 | 0
318 | 2043 | True | 60 | 318 | 0
319 | 2043 | True | 60 | 319 | 0
320 | 2043 | True | 60 | 320 | 0
321 | 2043 | True | 60 | 321 | 0
322 | 2043 | True | 60 | 322 | 0
323 | 2043 | True | 60 | 323 | 0
324 | 2043 | True | 60 | 324 | 0
325 | 2034 | True | 60 | 325 | 0
326 | 2034 | True | 60 | 326 | 0
327 | 2034 | True | 60 | 327 | 0
328 | 2034 | True | 60 | 328 | 0
329 | 2034 | True | 60 | 329 | 0
330 | 2034 | True | 60 | 330 | 0
331 | 2034 | True | 60 | 331 | 0
332 | 2034 | True | 60 | 332 | 0
333 | 2037 | True | 60 | 333 | 0
334 | 2037 | True | 60 | 334 | 0
335 | 2037 | True | 60 | 335 | 0
336 | 2037 | True | 60 | 336 | 0
337 | 2037 | True | 60 | 337 | 0
338 | 2046 | True | 60 | 338 | 0
339 | 2046 | True | 60 | 339 | 0
340 | 2046 | True | 60 | 340 | 0
341 | 2046 | True | 60 | 341 | 0
342 | 2046 | True | 60 | 342 | 0
343 | 2046 | True | 60 | 343 | 0
344 | 2046 | True | 60 | 344 | 0
345 | 2046 | True | 60 | 345 | 0
346 | 2037 | True | 60 | 346 | 0
347 | 2037 | True | 60 | 347 | 0
348 | 2037 | True | 60 | 348 | 0
349 | 2037 | True | 60 | 349 | 0
350 | 2033 | True | 60 | 350 | 0
351 | 2033 | True | 60 | 351 | 0
352 | 2033 | True | 60 | 352 | 0
353 | 2033 | True | 60 | 353 | 0
354 | 2033 | True | 60 | 354 | 0
355 | 2033 | True | 60 | 355 | 0
356 | 2033 | True | 60 | 356 | 0
357 | 2045 | True | 60 | 357 | 0
358 | 2045 | True | 60 | 358 | 0
359 | 2045 | True | 60 | 359 | 0
360 | 2045 | True | 60 | 360 | 0
361 | 2045 | True | 60 | 361 | 0
362 | 2045 | True | 60 | 362 | 0
363 | 2045 | True | 60 | 363 | 0
382 | 2046 | True | 60 | 382 | 0
383 | 2034 | True | 60 | 383 | 0
384 | 2043 | True | 60 | 384 | 0
385 | 2035 | True | 60 | 385 | 0
387 | 2037 | True | 60 | 387 | 0
392 | 2022 | True | 30 | 392 | 0
393 | 2026 | True | 30 | 393 | 0
394 | 2022 | True | 30 | 394 | 0
395 | 2022 | True | 30 | 395 | 0
396 | 2026 | True | 30 | 396 | 0
397 | 2026 | True | 30 | 397 | 0
399 | 2026 | True | 30 | 399 | 0
400 | 2026 | True | 30 | 400 | 0
402 | 2026 | True | 30 | 402 | 0
403 | 2022 | True | 30 | 403 | 0
404 | 2026 | True | 30 | 404 | 0
405 | 2026 | True | 30 | 405 | 0
406 | 2026 | True | 30 | 406 | 0
422 | 2030 | True | 15 | 422 | 0
423 | 2030 | True | 15 | 423 | 0
424 | 2030 | True | 15 | 424 | 0
429 | 2034 | True | 15 | 429 | 0
430 | 2034 | True | 15 | 430 | 0
431 | 2031 | True | 15 | 431 | 0
432 | 2030 | True | 15 | 432 | 0
433 | 2031 | True | 15 | 433 | 0
434 | 2030 | True | 15 | 434 | 0
435 | 2030 | True | 15 | 435 | 0
436 | 2030 | True | 15 | 436 | 0
437 | 2030 | True | 15 | 437 | 0
438 | 2031 | True | 15 | 438 | 0
439 | 2034 | True | 15 | 439 | 0
440 | 2030 | True | 15 | 440 | 0
441 | 2031 | True | 15 | 441 | 0
442 | 2030 | True | 15 | 442 | 0
443 | 2029 | True | 15 | 443 | 0
444 | 2031 | True | 15 | 444 | 0
445 | 2030 | True | 15 | 445 | 0
446 | 2030 | True | 15 | 446 | 0
447 | 2031 | True | 15 | 447 | 0
448 | 2030 | True | 15 | 448 | 0
485 | 2035 | True | 25 | 485 | 0
486 | 2035 | True | 25 | 486 | 0
487 | 2035 | True | 25 | 487 | 0
488 | 2035 | True | 25 | 488 | 0
489 | 2026 | True | 25 | 489 | 0
490 | 2035 | True | 25 | 490 | 0
491 | 2022 | True | 25 | 491 | 0
492 | 2026 | True | 25 | 492 | 0
493 | 2035 | True | 25 | 493 | 0
494 | 2035 | True | 25 | 494 | 0
495 | 2035 | True | 25 | 495 | 0
496 | 2026 | True | 30 | 496 | 0
497 | 2022 | True | 25 | 497 | 0
498 | 2026 | True | 25 | 498 | 0
499 | 2026 | True | 25 | 499 | 0
500 | 2026 | True | 25 | 500 | 0
501 | 2026 | True | 25 | 501 | 0
502 | 2026 | True | 25 | 502 | 0
503 | 2026 | True | 25 | 503 | 0
504 | 2022 | True | 25 | 504 | 0
505 | 2026 | True | 25 | 505 | 0
506 | 2026 | True | 25 | 506 | 0
507 | 2032 | True | 25 | 507 | 0
508 | 2032 | True | 25 | 508 | 0
509 | 2032 | True | 25 | 509 | 0
510 | 2032 | True | 25 | 510 | 0
511 | 2032 | True | 25 | 511 | 0
512 | 2035 | True | 25 | 512 | 0
513 | 2035 | True | 25 | 513 | 0
514 | 2035 | True | 25 | 514 | 0
515 | 2035 | True | 25 | 515 | 0
516 | 2022 | True | 25 | 516 | 0
517 | 2035 | True | 25 | 517 | 0
518 | 2031 | True | 25 | 518 | 0
519 | 2026 | True | 25 | 519 | 0
520 | 2026 | True | 25 | 520 | 0
521 | 2028 | True | 25 | 521 | 0
522 | 2022 | True | 25 | 522 | 0
523 | 2026 | True | 25 | 523 | 0
524 | 2028 | True | 25 | 524 | 0
525 | 2028 | True | 25 | 525 | 0
526 | 2035 | True | 25 | 526 | 0
527 | 2035 | True | 25 | 527 | 0
528 | 2035 | True | 25 | 528 | 0
529 | 2035 | True | 25 | 529 | 0
530 | 2035 | True | 25 | 530 | 0
531 | 2026 | True | 25 | 531 | 0
532 | 2022 | True | 25 | 532 | 0
533 | 2026 | True | 25 | 533 | 0
534 | 2026 | True | 25 | 534 | 0
535 | 2026 | True | 25 | 535 | 0
536 | 2031 | True | 25 | 536 | 0
537 | 2031 | True | 25 | 537 | 0
538 | 2031 | True | 25 | 538 | 0
539 | 2026 | True | 25 | 539 | 0
540 | 2026 | True | 25 | 540 | 0
576 | 2026 | True | 30 | 576 | 0
577 | 2026 | True | 30 | 577 | 0
578 | 2026 | True | 30 | 578 | 0
579 | 2026 | True | 30 | 579 | 0
580 | 2026 | True | 30 | 580 | 0
581 | 2026 | True | 30 | 581 | 0
583 | 2026 | True | 30 | 583 | 0
584 | 2026 | True | 30 | 584 | 0
585 | 2026 | True | 30 | 585 | 0
586 | 2026 | True | 30 | 586 | 0
587 | 2026 | True | 30 | 587 | 0
588 | 2026 | True | 30 | 588 | 0
589 | 2026 | True | 30 | 589 | 0
590 | 2026 | True | 30 | 590 | 0
592 | 2026 | True | 30 | 592 | 0
594 | 2026 | True | 30 | 594 | 0
595 | 2026 | True | 30 | 595 | 0
611 | 2026 | True | 20 | 611 | 0
612 | 2026 | True | 20 | 612 | 0
613 | 2026 | True | 20 | 613 | 0
614 | 2026 | True | 20 | 614 | 0
615 | 2026 | True | 20 | 615 | 0
616 | 2026 | True | 20 | 616 | 0
622 | 2026 | True | 20 | 622 | 0
623 | 2026 | True | 20 | 623 | 0
651 | 2026 | True | 20 | 651 | 0
661 | 2035 | True | 25 | 661 | 0
663 | 2043 | True | 60 | 663 | 0
665 | 2043 | True | 60 | 665 | 0
666 | 2034 | True | 60 | 666 | 0
667 | 2035 | True | 25 | 667 | 0
669 | 2037 | True | 60 | 669 | 0
670 | 2033 | True | 60 | 670 | 0
671 | 2045 | True | 60 | 671 | 0

## comment
ParentID | AssetName | Comment Type | Comment
24 | Dry Well Structure | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed.
26 | Dry Well Structure | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was noted throughout.
28 | Wet Well Concrete Structure | Condition Comment | The asset was observed to be in fair condition. Exposed corroded reinforcement was observed.
29 | Dry Well Structure | Condition Comment | The asset was observed to be in fair condition. Moderate corrosion was noted throughout.
31 | Wet Well Concrete Structure | Condition Comment | The asset was observed to be in fair condition. Efflorescence deposits/leak at joint was noted. Concrete delamination/spalling at joint was observed.
34 | Wet Well Concrete Structure | Condition Comment | The asset was observed to be in fair condition. Exposed corroded reinforcement, rust spots and concrete parging spalling were noted at joints.
36 | Dry Well | Condition Comment | The asset was observed to be in fair condition. Corrosion was noted throughout.
38 | Wet Well Concrete Structure | Condition Comment | The asset was observed to be in fair condition.
41 | Wet Well Concrete Structure | Condition Comment | The asset was observed to be in fair condition. Rust spots was observed noted.
42 | Dry Well Structure | Condition Comment | The asset was observed to be in fair condition. Corrosion was observed was noted at the base.
44 | Wet Well Concrete Structure | Condition Comment | The asset was observed to be in fair condition. Exposed corroded reinforcement and concrete spalling noted was observed.
46 | Wet Well Concrete Structure | Condition Comment | The asset was observed to be in fair condition. Exposed corroded reinforcement and concrete spalling was noted at the pipe penetration.
53 | Sewage Lift Pump #1 | Condition Comment | The asset was observed to be in fair condition. The pump was near the end of its expected life.
54 | Sewage Lift Pump #1 Check Valve | Condition Comment | The asset was observed to be in poor condition. Heavy corrosion was observed on the valve.
55 | Sewage Lift Pump #1 Discharge Valve | Condition Comment | The asset was observed to be in poor condition. Heavy corrosion was observed on the valve.
56 | Variable Frequency Drive Pump # 1 | Condition Comment | The asset was assumed to be in fair condition.
57 | Sewage Lift Pump #2 | Condition Comment | The asset was observed to be in poor condition. The pump was near the end of its expected service life.
58 | Sewage Lift Pump #2 Check Valve | Condition Comment | The asset was observed to be in poor condition. Severe corrosion was observed on the surface of the valve.
59 | Sewage Lift Pump #2 Discharge Valve | Condition Comment | The asset was observed to be in poor condition. Heavy corrosion was observed on the valve.
60 | Forcemain | Condition Comment | The asset was observed to be in fair condition. The pipe was at half of its expected service life.
61 | Wet Well Exhaust Fan | Condition Comment | The asset was observed to be in fair condition. Surface staining on exhaust fan pipe was observed.
62 | Sewage Lift Pump #1 | Condition Comment | The asset was observed to be in fair condition. The pump was near the end of its expected service life.
63 | Sewage Lift Pump #1 Check Valve | Condition Comment | The asset was observed to be in poor condition. Heavy corrosion was observed on the surface of the valve.
64 | Sewage Lift Pump #1 Discharge Valve | Condition Comment | The asset was observed to be in poor condition. Heavy corrosion was observed on the surface of the valve.
65 | Sewage Lift Pump #2 | Condition Comment | The asset was observed to be in fair condition. The pump was near the end of its expected service life.
66 | Sewage Lift Pump #1 Check Valve | Condition Comment | The asset was observed to be in poor condition. Heavy corrosion was observed on the surface of the valve.
67 | Sewage Lift Pump #1 Discharge Valve | Condition Comment | The asset was observed to be in poor condition. Heavy corrosion was observed on the surface of the valve.
68 | Forcemain | Condition Comment | The asset was assumed to be in fair condition.
69 | Dry Well Sump Pump | Condition Comment | The asset was observed to be in poor condition. Moderate corrosion was observed and deterioration was observed on the surface of the pump. The pump was beyond its expected service life.
70 | TRANSMITTER LEVEL WET WELL #1 | Condition Comment | The asset was observed to be in good condition.
71 | Dry Wall Exhaust Fan | Condition Comment | The asset was observed to be in fair condition. Paint peeling was observed.
72 | Sewage Lift Pump #1 | Condition Comment | The asset was observed to be in poor condition. Corrosion was observed and deterioration was observed on the surface of the pump. The pump was beyond its expected service life.
73 | Sewage Lift Pump #1 Check Valve | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the surface of the valve. The valve was beyond its expected service life.
74 | Sewage Lift Pump #1 Motor Drive | Condition Comment | The asset was observed to be in fair condition. Minor paint wear was observed.
75 | Sewage Lift Pump #1 Inlet Valve | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the surface of the valve. The valve was beyond its expected service life.
76 | Sewage Lift Pump #1 Discharge Valve | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the surface of the valve. The valve was beyond its expected service life.
78 | Sewage Lift Pump #2 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the surface of the pump. The pump was beyond its expected service life.
79 | Sewage Lift Pump #2 Check Valve | Condition Comment | The asset was observed to be in poor condition. Deterioration and corrosion were observed on the surface of the valve. The valve was beyond its expected service life was observed.
80 | Sewage Lift Pump #2 Motor Drive | Condition Comment | The asset was observed to be in fair condition. Minor paint wear was observed.
81 | Sewage Lift Pump #2 Inlet Valve | Condition Comment | The asset was observed to be in poor condition. Corrosion was observed on the surface of the valve. The valve was beyond its expected service life.
82 | Sewage Lift Pump #2 Discharge Valve | Condition Comment | The asset was observed to be in fair condition. Minor deterioration was observed on the surface of the valve. The valve was beyond its expected service life was observed.
83 | Forcemain | Condition Comment | The asset was assumed to be in fair condition.
129 | PUMP #1 SUMP | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the surface of the pump. The pump was beyond the end of its expected service life.
130 | TRANSMITTER LEVEL WET WELL | Condition Comment | The asset was observed to be in fair condition. Dust and corrosion were observed.
131 | FAN EXHAUST #1 | Condition Comment | The asset was observed to be in poor condition. The exhaust fan was missing and as per section 7.2.9 of moecc's design guidelines for sewage works, mechanical ventilation is required for below ground surface dry well were observed.
132 | Sewage Lift Pump #1 | Condition Comment | The asset was observed to be in fair condition. Deterioration was observed on the surface of the pump and it is beyond the end of its expected service life.
133 | Sewage Lift Pump #1 Check Valve | Condition Comment | The asset was observed to be in fair condition. Corrosion and deterioration were observed on the surface of the valve. The valve was beyond its expected service life.
134 | MOTOR DRIVE SEWAGE LIFT PUMP #1 | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed on casing.
135 | Sewage Lift Pump #1 Inlet Valve | Condition Comment | The asset was observed to be in fair condition. Corrosion and deterioration were observed on the surface of the valve. The valve was beyond its expected service life.
136 | Sewage Lift Pump #1 Discharge Valve | Condition Comment | The asset was observed to be in fair condition. Corrosion and deterioration were observed on the surface of the valve. The valve was beyond its expected service life.
137 | Sewage Lift Pump #2 | Condition Comment | The asset was observed to be in fair condition. Deterioration was observed on the surface of the pump and it is beyond the end of its expected service life was observed.
138 | Sewage Lift Pump #2 Check Valve | Condition Comment | The asset was observed to be in fair condition. Corrosion and deterioration were observed on the surface of the valve. The valve was beyond its expected service life.
139 | MOTOR DRIVE SEWAGE LIFT PUMP #2 | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed on casing.
140 | Sewage Lift Pump #2 Inlet Valve | Condition Comment | The asset was observed to be in fair condition. Corrosion and deterioration were observed on the surface of the valve. The valve was beyond its expected service life.
141 | Sewage Lift Pump #1 Discharge Valve | Condition Comment | The asset was observed to be in fair condition. Corrosion and deterioration were observed on the surface of the valve. The valve was beyond its expected service life.
142 | Forcemain | Condition Comment | The asset was assumed to be in fair condition and the pipe is at half of its expected service life.
143 | PUMP #1 SUMP | Condition Comment | The asset was observed to be in poor condition. Severe corrosion and deterioration were observed on the surface of the pump. The pump was near the end of its expected service life.
144 | WET WELL LEVEL TRANSMITTER #1 | Condition Comment | The asset was observed to be in good condition.
145 | FAN EXHAUST #1 | Condition Comment | The asset was observed to be in poor condition. As per section 7.2.9 of moecc's design guidelines for sewage works, mechanical ventilation is required for below ground surface dry well was observed.
146 | Sewage Lift Pump #1 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the surface of the pump. The pump was near the end of its expected service life.
147 | Sewage Lift Pump #1 Check Valve | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the surface of the valve. The valve is near the end of its expected service life.
148 | Sewage Lift Pump #1 Motor Drive | Condition Comment | The asset was observed to be in fair condition. Minor surface corrosion was observed.
149 | Sewage Lift Pum #1 Inlet Valve | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the valve. The valve was near the end of its expected service life.
150 | Sewage Lift Pump #1 Discharge Valve | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the valve. The valve was near the end of its expected service life.
151 | Sewage Lift Pump #2 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the surface of the pump. The pump was near the end of its expected service life.
152 | Sewage Lift Pump #2 Check Valve | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the valve. The valve was near the end of its expected service life.
153 | Sewage Lift Pump #2 Motor Drive | Condition Comment | The asset was observed to be in fair condition. Minor surface corrosion and paint wear were observed.
154 | Sewage Lift Pump #2 Inlet Valve | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the valve. The valve was near the end of its expected service life.
155 | Sewage Lift Pump #2 Discharge Valve | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the valve. The valve was near the end of its expected service life.
156 | Forcemain | Condition Comment | The asset was observed to be in good condition.
157 | PUMP SUMP | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the surface of the pump. The pump was near the end of its expected service life.
158 | TRANSMITTER LEVEL WET WELL #1 | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed on nuts.
159 | Dry Well Exhaust Fan | Condition Comment | The asset was observed to be in fair condition. Surface corrosion was observed.
160 | Sewage Lift Pump #1 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the surface of the pump. The pump was near the end of its expected service life.
161 | Sewage Lift Pump #1 Check Valve | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the valve. The valve was near the end of its expected service life.
162 | Sewage Lift Pump #1 Motor Drive | Condition Comment | The asset was observed to be in fair condition. Paint wear was observed.
163 | Sewage Lift Pump #1 Inlet Valve | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the valve. The valve was near the end of its expected service life.
164 | Sewage Lift Pump #1 Discharge Valve | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the valve. The valve was near the end of its expected service life.
165 | Sewage Lift Pump #2 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the surface of the pump. The pump was near the end of its expected service life.
166 | Sewage Lift Pump #2 Check Valve | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the surface of the valve. The valve was near the end of its expected service life.
167 | Sewage Lift Pump #2 Motor Drive | Condition Comment | The asset was observed to be in fair condition. Paint wear was observed.
168 | Sewage Lift Pump #2 Inlet Valve | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the valve. The valve was near the end of its expected service life.
169 | Sewage Lift Pump #2 Discharge Valve | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the valve. The valve was near the end of its expected service life.
170 | Forcemain | Condition Comment | The asset was assumed to be in fair condition. The pipe was at half of its expected service life were observed.
172 | TRANSMITTER LEVEL WET WELL | Condition Comment | The asset was observed to be in very good condition.
174 | Sewage Lift Pump #1 | Condition Comment | The asset was observed to be in fair condition. The pump was beyond its expected service life.
175 | Sewage Lift Pump #1 Check Valve | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the valve. The valve was near the end of its expected service life.
177 | Sewage Lift Pump #1 Knife Gate Valve | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the valve. The valve was near the end of its expected service life.
178 | Forcemain | Condition Comment | The asset was assumed to be in fair condition. The pipe was at half of its expected service life were observed.
179 | Sump Pump #1 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the surface of the pump. The pump was near the end of its expected service life.
180 | TRANSMITTER LEVEL WET WELL #1 | Condition Comment | The asset was observed to be in fair condition. Nuts were not secured properly.
181 | Dry Well Exhaust Fan | Condition Comment | The asset was observed to be in fair condition. Paint peeling was observed.
182 | Sewage Lift Pump #1 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the surface of the pump. The pump was near the end of its expected service life.
183 | Sewage Lift Pump #1 Check Valve | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the valve. The valve was near the end of its expected service life.
184 | Sewage Lift Pump #2 Motor Drive | Condition Comment | The asset was observed to be in fair condition. Paint wear was observed.
185 | Sewage Lift Pump #1 Inlet Valve | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the valve. The valve was near the end of its expected service life.
186 | Sewage Lift Pump #1 Discharge Valve | Condition Comment | The asset was observed to be in very poor condition. Severe corrosion and deterioration were observed on the valve. The valve was near the end of its expected service life.
187 | Sewage Lift Pump #2 | Condition Comment | The asset was observed to be in fair condition. Deterioration was observed on the surface of the pump. The pump was near the end of its expected service life was observed.
188 | Sewage Lift Pump #2 Check Valve | Condition Comment | The asset was observed to be in fair condition. Deterioration were observed on the valve. The valve was near the end of its expected service life.
189 | Sewage Lift Pump #2 Motor Drive | Condition Comment | The asset was observed to be in fair condition. Paint wear was observed.
190 | Sewage Lift Pump #2 Inlet Valve | Condition Comment | The asset was observed to be in fair condition. Corrosion and deterioration were observed on the valve. The valve was near the end of its expected service life.
191 | Sewage Lift Pump #2 Disccharge Valve | Condition Comment | The asset was observed to be in fair condition. Minor deterioration was observed on the surface of the valve. The valve was near the end of its expected service life.
192 | Forcemain | Condition Comment | The asset was assumed to be in fair condition.
237 | Overflow Piping | Condition Comment | The asset was assumed to be in fair condition. The pipe is at half of its expected service life.
238 | Discharge Header | Condition Comment | The asset was assumed to be in fair condition. The pipe is at half of its expected service life.
240 | Pump 1 Piping | Condition Comment | The asset was assumed to be in fair condition. The pipe is at half of its expected service life.
241 | Pump 2 Piping | Condition Comment | The asset was assumed to be in fair condition. The pipe is at half of its expected service life.
242 | Overflow Piping | Condition Comment | The asset was observed to be in good condition.
243 | Pump 1 Piping | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed.
244 | Bar Screen | Condition Comment | The asset was observed to be in fair condition. Corrosion was observed.
247 | Overflow Piping | Condition Comment | The asset was observed to be in good condition. The pipe was at half of its expected service life.
248 | Pump 1 Piping | Condition Comment | The asset was observed to be in good condition. The pipe was at half of its expected service life.
249 | Bar Screen | Condition Comment | The asset was observed to be in good condition.
250 | Discharge Header | Condition Comment | The asset was observed to be in good condition.
251 | Overflow Piping | Condition Comment | The asset was assumed to be fair and the pipe was at half of its expected service life.
252 | Pump 1 Piping | Condition Comment | The asset was observed to be in poor condition. Heavy corrosion was observed on the surface of the pipe.
253 | Pump 2 Piping | Condition Comment | The asset was observed to be in poor condition. Heavy corrosion was observed on the surface of the pipe.
254 | Overflow Piping | Condition Comment | The asset was observed to be in good condition.
255 | Emergency Pumping Riser | Condition Comment | The asset was assumed to be in fair condition.
256 | Pump 1 Piping | Condition Comment | The asset was observed to be in good condition.
257 | Pump 2 Piping | Condition Comment | The asset was observed to be in good condition.
258 | Discharge Header | Condition Comment | The asset was observed to be in good condition.
259 | Overflow Piping | Condition Comment | The asset was observed to be in fair condition. The pipe was at half of its expected service life.
260 | Pump 1 Discharge Piping | Condition Comment | The asset was observed to be in poor condition. Heavy corrosion was observed on the pipe.
261 | Pump 2 Discharge Piping | Condition Comment | The asset was observed to be in poor condition. Heavy corrosion was observed on the pipe.
262 | Overflow Piping | Condition Comment | The asset was assumed to be in fair condition. The pipe passed half of its expected service life.
263 | Pump 1 Piping | Condition Comment | The asset was observed to be in fair condition. Minor deterioration was observed on the pipe and it passed half of its expected service life.
264 | Pump 2 Piping | Condition Comment | The asset was observed to be in fair condition. Minor deterioration was observed on the pipe and it passed half of its expected service life.
265 | Discharge Piping | Condition Comment | The asset was observed to be in fair condition. Minor deterioration was observed on the pipe and it passed half of its expected service life.
266 | Overflow Piping | Condition Comment | The asset was assumed to be in fair condition.
267 | Pump 1 Discharge Piping | Condition Comment | The asset was observed to be in poor condition. Heavy corrosion and deterioration were observed.
268 | Pump 2 Discharge Piping | Condition Comment | The asset was observed to be in poor condition. Heavy corrosion and deterioration were observed was observed.
301 | Wet Well Concrete Structure | Condition Comment | The asset was observed to be in fair condition. Rust spots was observed noted.
302 | Dry Well Access Hatch | Condition Comment | The asset was observed to be in fair condition. Minor corrosion and paint wear were noted.
303 | Dry Well Access Ladder | Condition Comment | The asset was observed to be in fair condition. Minor paint wear was observed.
304 | Protective Paint | Condition Comment | The asset was observed to be in fair condition. Peeling paint on exterior was observed.
305 | Manhole Frame and Cover | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed on the underside.
306 | Wet Well Access Ladder | Condition Comment | The asset was observed to be in good condition.
307 | Wet Well Aluminum Platform | Condition Comment | The asset was observed to be in fair condition. Corrosion was observed noted.
308 | Wet Well Aluminum Guardrail | Condition Comment | The asset was observed to be in fair condition. Corrosion was observed noted.
309 | Davit Socket Base | Condition Comment | The asset was observed to be in fair condition. To be inspected yearly and as per occupational health and safety act, r.s.o. 1990, c. o.1 the davit socket base is to be inspected every year.
317 | Dry Well Access Ladder | Condition Comment | The asset was observed to be in fair condition. Minor corrosion and paint wear were noted.
318 | Dry Well Access Hatch | Condition Comment | The asset was observed to be in fair condition. Paint wear was observed.
319 | Dry Well Davit Socket Base | Condition Comment | The asset was observed to be in fair condition. To be inspected yearly and as per occupational health and safety act, r.s.o. 1990, c. o.1 the davit socket base is to be inspected every year.
320 | Wet Well Access Hatch | Condition Comment | The asset was observed to be in fair condition. Surface corrosion noted on underside was observed.
321 | Wet Well Davit Socket Base | Condition Comment | The asset was observed to be in fair condition. To be inspected yearly and as per occupational health and safety act, r.s.o. 1990, c. o.1 the davit socket base is to be inspected every year.
322 | Wet Well Access Ladder | Condition Comment | The asset was observed to be in fair condition. Bent was observed ladder rung.
323 | Checker Plate Platform | Condition Comment | The asset was observed to be in fair condition. Corrosion was observed noted.
324 | Dry Well Protective Paint | Condition Comment | The asset was observed to be in fair condition. Weathered paint was observed on exterior and minor corrosion was noted inside.
325 | Wet Well Access Ladder | Condition Comment | The asset was observed to be in good condition.
326 | Wet Well Checker Plate Platform | Condition Comment | The asset was observed to be in fair condition. Discoloration of the checker plate was noted.
327 | Manhole Frame and Cover | Condition Comment | The asset was observed to be in good condition.
328 | Dry Well Access Hatch | Condition Comment | The asset was observed to be in fair condition. Weathered paint was observed.
329 | Dry Well Access Ladder | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed.
330 | Dry Aluminum Grating | Condition Comment | The asset was observed to be in fair condition based on its age.
331 | Protective Paint | Condition Comment | The asset was observed to be in fair condition. Peeling paint on exterior and corrosion were observed.
332 | Davit Socket Base | Condition Comment | The asset was observed to be in fair condition. To be inspected yearly and as per occupational health and safety act, r.s.o. 1990, c. o.1 the davit socket base is to be inspected every year.
333 | Wet Well Access Hatch | Condition Comment | The asset was observed to be in good condition.
334 | Wet Well Access Ladder | Condition Comment | The asset was observed to be in fair condition. Staining/corrosion noted was observed.
335 | Wet Well Aluminum Platform | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed.
336 | Wet Well Aluminum Guardrail | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed.
337 | Davit Socket Base | Condition Comment | The asset was observed to be in fair condition. To be inspected yearly and as per occupational health and safety act, r.s.o. 1990, c. o.1 the davit socket base is to be inspected every year.
338 | Wet Well Access Ladder | Condition Comment | The asset was observed to be in fair condition.
339 | Wet Well Aluminum Platform | Condition Comment | The asset was observed to be in fair condition. Fixed portion of platform grating was noted to be bent.
340 | Manhole Frame and Cover | Condition Comment | The asset was observed to be in fair condition.
341 | Davit Socket Base | Condition Comment | The asset was observed to be in fair condition. To be inspected yearly and as per occupational health and safety act, r.s.o. 1990, c. o.1 the davit socket base is to be inspected every year.
342 | Dry Well Access Hatch | Condition Comment | The asset was observed to be in fair condition. Corrosion and paint wear were noted.
343 | Dry Well Access Ladder | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed.
344 | Protective Paint | Condition Comment | The asset was observed to be in fair condition. Flaking/missing on exterior was observed.
345 | Dry Well Davit Socket Base | Condition Comment | The asset was observed to be in fair condition. To be inspected yearly and as per occupational health and safety act, r.s.o. 1990, c. o.1 the davit socket base is to be inspected every year.
346 | Wet Well Access Hatch | Condition Comment | The asset was observed to be in good condition.
347 | Wet Well Access Ladder | Condition Comment | The asset was observed to be in fair condition. Pitting was observed.
348 | Wet Well Davit Socket Base | Condition Comment | The asset was observed to be in fair condition. To be inspected yearly and as per occupational health and safety act, r.s.o. 1990, c. o.1 the davit socket base is to be inspected every year.
349 | Wet Well Aluminum Platform | Condition Comment | The asset was observed to be in fair condition. Calcium buildup and pitting was noted
350 | Dry Well Access Hatch | Condition Comment | The asset was observed to be in fair condition. Paint wear was observed.
351 | Dry Well Access Ladder | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed.
352 | Dry Well Davit Socket Base | Condition Comment | The asset was observed to be in fair condition.
353 | Protective Paint | Condition Comment | The asset was observed to be in fair condition. Weathered paint was observed and missing paint on exterior.
354 | Manhole Frame and Cover | Condition Comment | The asset was observed to be in fair condition.
355 | Wet Well Access Ladder | Condition Comment | The asset was observed to be in fair condition.
356 | Wet Well Davit Socket Base | Condition Comment | The asset was observed to be in fair condition. Anchors were corroded was observed.
357 | Wet Well Access Hatch | Condition Comment | The asset was observed to be in fair condition. Minor corrosion and staining were noted.
358 | Pump Hatch 1 | Condition Comment | The asset was observed to be in fair condition. Missing safety grating was noted. The pump hatch 1 was missing grating. under Ontario regulation 213/91 this presents a fall hazard when the hatches are left open.
359 | Pump Hatch 2 | Condition Comment | The asset was observed to be in fair condition. Missing safety grating was noted. The pump hatch 1 was missing grating. under Ontario regulation 213/91 this presents a fall hazard when the hatches are left open.
360 | Wet Well Access Ladder | Condition Comment | The asset was observed to be in fair condition. Calcium buildup and corrosion were observed.
361 | We Well Access Ladder | Condition Comment | The asset was observed to be in fair condition. Calcium buildup and corrosion were observed.
362 | Wet Well Aluminum Platform | Condition Comment | The asset was observed to be in fair condition. Gratings now clipped down. Corrosion was observed noted.
363 | Wet Well Davit Socket Base | Condition Comment | The asset was observed to be in fair condition. To be inspected yearly and as per occupational health and safety act, r.s.o. 1990, c. o.1 the davit socket base is to be inspected every year.
382 | Dry Well Concrete Foundation | Condition Comment | The asset was assumed to be in fair condition as it was not visible.
383 | Dry Well Concrete Foundation | Condition Comment | The asset was assumed to be in fair condition as it was not visible.
384 | Dry Well Concrete Foundation | Condition Comment | The asset was assumed to be in fair condition as it was not visible.
385 | Dry Well Concrete Foundation | Condition Comment | The asset was assumed to be in fair condition as it was not visible.
387 | Grab Bar | Condition Comment | The asset was observed to be in good condition.
392 | VALVE KNIFE GATE SEWAGE LIFT PUMP #2 | Condition Comment | The asset was observed to be in very poor condition. Severe corrosion was observed on the surface of the valve. The valve was beyond its expected service life.
393 | PUMP #2 SEWAGE LIFT | Condition Comment | The asset was observed to be in poor condition. The pump was beyond its expected service life.
394 | VALVE CHECK SEWAGE LIFT PUMP #2 | Condition Comment | The asset was observed to be in very poor condition. Severe corrosion was observed on the surface of the valve. The valve was beyond its expected service life.
395 | VALVE KNIFE GATE SEWAGE LIFT PUMP #2 | Condition Comment | The asset was observed to be in very poor condition. Severe corrosion was observed on the surface of the valve. The valve was beyond its expected service life.
396 | Bar Screen | Condition Comment | The asset was observed to be in fair condition. Minor deterioration was observed on the bar screen.
397 | PUMP #2 SEWAGE LIFT | Condition Comment | The asset was observed to be in poor condition. The pump was beyond its expected service life.
399 | Sewage Lift Pump #2 | Condition Comment | The asset was observed to be in poor condition. The pump was beyond its expected service life.
400 | VALVE CHECK SEWAGE LIFT PUMP #2 | Condition Comment | The asset was observed to be in very poor condition. Severe corrosion was observed on the surface of the valve. The valve was beyond its expected service life.
401 | VALVE KNIFE GATE SEWAGE LIFT PUMP #1 | Condition Comment | The asset was assumed to be in fair condition.
402 | Sewage Lift Pump #2 Check Valve | Condition Comment | The asset was observed to be in poor condition. Heavy corrosion was observed on the surface of the valve. The valve was beyond its expected service life was observed.
403 | Sewage Lift Pump #2 Knife Gate Valve | Condition Comment | The asset was observed to be in very poor condition. Severe corrosion was observed on the surface of the valve. The valve was beyond its expected service life.
404 | Bar Screen | Condition Comment | The asset was observed to be in fair condition. Debris was clogging at the bar screen, which in terms start clogging the inlet pipe.
405 | VALVE DISCHARGE #3 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the surface of the valve. The valve was near the end of its expected service life.
406 | Discharge Valve #3 | Condition Comment | The asset was observed to be in poor condition. Corrosion and deterioration were observed on the surface of the valve.
422 | Remote Signal Telephone Transmitter | Condition Comment | The asset was observed to be in fair condition. The asset was obsolete.
423 | Wet Well Floats | Condition Comment | The asset was observed to be in good condition.
424 | Sump Float | Condition Comment | The asset was observed to be in good condition. Dust was observed.
429 | Wet Well Float | Condition Comment | The asset was observed to be in good condition.
430 | Sump Float | Condition Comment | The asset was observed to be in good condition.
431 | Remote Signals Telephone Transmitter | Condition Comment | The asset was observed to be in good condition.
432 | Sump Float | Condition Comment | The asset was observed to be in good condition.
433 | Remote Signals Telephone Transmitter | Condition Comment | The asset was observed to be in very good condition.
434 | Wet Well Floats | Condition Comment | The asset was observed to be in good condition.
435 | Remote Signals Telephone Transmitter | Condition Comment | The asset was observed to be in fair condition. The asset was obsolete.
436 | Wet Well Floats | Condition Comment | The asset was observed to be in good condition.
437 | Sump Float | Condition Comment | The asset was observed to be in good condition.
438 | Remote Signals Telephone Transmitter | Condition Comment | The asset was observed to be in good condition.
439 | Wet Well Float | Condition Comment | The asset was observed to be in good condition.
440 | Wet Well Level Transmitter | Condition Comment | The asset was observed to be in good condition.
441 | Remote Signals Telephone Transmitter | Condition Comment | The asset was observed to be in good condition.
442 | Wet Well Floats | Condition Comment | The asset was observed to be in good condition.
443 | Sump Float | Condition Comment | The asset was observed to be in good condition.
444 | Remote Signals Telephone Transmitter | Condition Comment | The asset was observed to be in good condition.
445 | Wet Well Float | Condition Comment | The asset was observed to be in good condition.
446 | Wet Well Level Transmitter | Condition Comment | The asset was observed to be in good condition. Bolts were not secured properly.
447 | Remote Signals Telephone Transmitter | Condition Comment | The asset was observed to be in good condition.
448 | Wet Well Floats | Condition Comment | The asset was observed to be in good condition.
485 | Main Disconnect Switch | Condition Comment | The asset was observed to be in good condition.
486 | Power Meter | Condition Comment | The asset was observed to be in good condition.
487 | Manual Transfer Switch | Condition Comment | The asset was observed to be in good condition.
488 | Generator Connection Receptacle | Condition Comment | The asset was observed to be in good condition.
489 | Dry Well Lights | Condition Comment | The asset was observed to be in good condition. Replace with led fixtures rated for class 1, div 2.
490 | Outdoor Enclosure | Condition Comment | The asset was observed to be in fair condition. Inside the panel is not getting drained properly.
491 | Pump Control Panel | Condition Comment | The asset was observed to be in fair condition. Replace with nema 4x panel.
492 | Outdoor Electrical Enclosure | Condition Comment | The asset was observed to be in good condition.
493 | Main Disconnect Switch | Condition Comment | The asset was observed to be in fair condition. Missing was observed arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the panel which may require examination, adjustment, servicing.
494 | Power Meter | Condition Comment | The asset was observed to be in good condition.
495 | Manual Transfer Switch | Condition Comment | The asset was observed to be in fair condition. Missing was observed arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the panel which may require examination, adjustment, servicing.
496 | Dry Well Lighting | Condition Comment | The asset was observed to be in good condition. Replace with led in next upgrade.
497 | Control Panel | Condition Comment | The asset was observed to be in fair condition. Missing was observed arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the panel which may require examination, adjustment, servicing.
498 | Generator Connection Receptacle | Condition Comment | The asset was observed to be in good condition.
499 | Outdoor Enclosure | Condition Comment | The asset was observed to be in fair condition. Bottom of interior has corroded and replace with nema 3r enclosure in next upgrade.
500 | Main Disconnect Switch | Condition Comment | The asset was observed to be in fair condition. Missing was observed arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the panel which may require examination, adjustment, servicing.
501 | Power Meter | Condition Comment | The asset was observed to be in good condition.
502 | Manual Transfer Switch | Condition Comment | The asset was observed to be in fair condition. Missing was observed arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the panel which may require examination, adjustment, servicing.
503 | Drywell Lighting | Condition Comment | The asset was observed to be in fair condition. Replace with led fixture in next upgrade. to be rated for class 1, div 2.
504 | Control Panel | Condition Comment | The asset was observed to be in fair condition. Missing was observed arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the panel which may require examination, adjustment, servicing.
505 | outdoor enclosure | Condition Comment | The asset was observed to be in fair condition. Top surface and doors were corroded and to be replaced with nema 3r enclosure.
506 | Control Panel with Main DS | Condition Comment | The asset was observed to be in fair condition. Missing was observed arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the panel which may require examination, adjustment, servicing.
507 | Pump #1 VFD with Breaker | Condition Comment | The asset was observed to be in good condition.
508 | Pump #2 VFD with Breaker | Condition Comment | The asset was observed to be in good condition.
509 | Generator Connection Receptacle | Condition Comment | The asset was observed to be in good condition.
510 | Manual Transfer Switch | Condition Comment | The asset was observed to be in fair condition. Missing was observed arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the panel which may require examination, adjustment, servicing.
511 | Wet Well Light | Condition Comment | The asset was observed to be in poor condition. Severely corroded was observed.
512 | Outdoor Enclosure | Condition Comment | The asset was observed to be in good condition.
513 | Main Fused Disconnect Switch | Condition Comment | The asset was observed to be in fair condition. Misplaced and outdated arc flash label was noted. Shock and arc flash hazard as no arc flash label were installed. as per (Ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the vfd breaker which may require examination, adjustment, servicing.
514 | Power Meter | Condition Comment | The asset was observed to be in good condition.
515 | Manual Transfer Switch | Condition Comment | The asset was observed to be in fair condition. Misplaced and outdated arc flash label was noted. Shock and arc flash hazard as no arc flash label were installed. as per (Ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the vfd breaker which may require examination, adjustment, servicing.
516 | Control Panel | Condition Comment | The asset was observed to be in fair condition. Misplaced and outdated arc flash label was noted. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the vfd breaker which may require examination, adjustment, servicing.
517 | Generator Connection Receptacle | Condition Comment | The asset was observed to be in good condition.
518 | Dry Well Lights | Condition Comment | The asset was observed to be in good condition. Replace with LED in next upgrade.
519 | Wet Well Light | Condition Comment | The asset was observed to be in good condition. Replace with LED in next upgrade.
520 | Enclosure Light | Condition Comment | The asset was observed to be in good condition. Replace with LED in next upgrade.
521 | Power Meter | Condition Comment | The asset was observed to be in good condition.
522 | Control Panel with Main DS and MTS | Condition Comment | The asset was observed to be in fair condition. To have separate main DS, MTS, and CP. Outdated arc flash label was noted. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the vfd breaker which may require examination, adjustment, servicing.
523 | Generator Connect Recept. | Condition Comment | The asset was observed to be in fair condition.
524 | Pump #1 VFD with Breaker | Condition Comment | The asset was observed to be in good condition.
525 | Pump #2 VFD with Breaker | Condition Comment | The asset was observed to be in good condition.
526 | Outdoor Enclosure | Condition Comment | The asset was observed to be in good condition.
527 | Generator Connect Recept. | Condition Comment | The asset was observed to be in good condition.
528 | Main Disconnect Switch | Condition Comment | The asset was observed to be in fair condition. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the vfd breaker which may require examination, adjustment, servicing.
529 | Manual Transfer Switch | Condition Comment | The asset was observed to be in fair condition. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the vfd breaker which may require examination, adjustment, servicing.
530 | Power Meter | Condition Comment | The asset was observed to be in good condition.
531 | Dry Well Lights | Condition Comment | The asset was observed to be in fair condition. One of the lights doesn’t work and to be replaced with LED.
532 | Control Panel | Condition Comment | The asset was observed to be in fair condition. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario electrical safety code (oesc)) section2-306.1 & 2-306.2 arc flash label is required for the vfd breaker which may require examination, adjustment, servicing.
533 | Wet well Light | Condition Comment | The asset was observed to be in very poor condition as it was not working.
534 | Enclosure Light | Condition Comment | The asset was observed to be in fair condition. To be replaced with LED
535 | Outdoor Enclosure | Condition Comment | The asset was observed to be in fair condition. To be replaced with nema 3r enclosure.
536 | Power Meter | Condition Comment | The asset was observed to be in good condition.
537 | Pump #1 VFD and Breaker | Condition Comment | The asset was observed to be in good condition.
538 | Pump #2 VFD and Breaker | Condition Comment | The asset was observed to be in good condition.
539 | Control Panel with Main DS and MTS | Condition Comment | The asset was observed to be in good condition. Replace with separate main ds, mts and cp and shock and arc flash hazard as the existing arc flash label are outdated. As per (workplace electrical safety (csa z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents.
540 | Gen Connect Recept | Condition Comment | The asset was observed to be in good condition.
576 | Dry Wall Sump Pump | Condition Comment | The asset was observed to be in fair condition. Surface corrosion was observed.
577 | Dry Wall Portable Heater | Condition Comment | The asset was observed to be in good condition.
578 | Dry Wall Portable Dehumidifier | Condition Comment | The asset was observed to be in good condition.
579 | Dry Wall Portable Heater | Condition Comment | The asset was observed to be in good condition.
580 | Dry Well Dehumidifier | Condition Comment | The asset was observed to be in good condition.
581 | Dry Wall Sump Pump | Condition Comment | The asset was observed to be in poor condition. Severe corrosion was observed.
583 | Dry Wall Sump Pump | Condition Comment | The asset was observed to be in fair condition. Surface corrosion was observed.
584 | Dry Wall Portable Heater | Condition Comment | The asset was observed to be in fair condition. Surface corrosion was observed.
585 | Dry Wall Portable Dehumidifier | Condition Comment | The asset was observed to be in good condition.
586 | Wet Well Ventilation Pipe | Condition Comment | The asset was observed to be in good condition.
587 | Wet Well Ventilation Pipe | Condition Comment | The asset was observed to be in fair condition. Miscellaneous surface staining was observed.
588 | Dry Wall Sump Pump | Condition Comment | The asset was assumed to be in fair condition.
589 | Dry Wall Portable Heater | Condition Comment | The asset was observed to be in good condition.
590 | Dry Well Dehumidifier | Condition Comment | The asset was observed to be in good condition.
592 | Wet Well Ventilation Pipe | Condition Comment | The asset was observed to be in fair condition. Paint peeling was observed.
593 | Dry Wall Portable Heater | Condition Comment | The asset was observed to be in good condition.
594 | Dry Well Dehumidifier | Condition Comment | The asset was observed to be in good condition.
595 | Wet Well Ventilation Pipe | Condition Comment | The asset was observed to be in good condition.
611 | Yard Hydrant | Condition Comment | The asset was observed to be in good condition.
612 | Yard Hydrant | Condition Comment | The asset was observed to be in good condition.
613 | Yard Hydrant | Condition Comment | The asset was observed to be in good condition.
614 | Yard Hydrant | Condition Comment | The asset was observed to be in good condition.
615 | Yard Hydrant | Condition Comment | The asset was observed to be in good condition.
616 | Yard Hydrant (New Asset) | Condition Comment | The asset was observed to be in poor condition. In accordance with section 19.8.3 of the region's water and wastewater design manual (January 2012), a yard hydrant complete with a backflow preventer with a 37.5mm water service line shall be provided for flushing and cleaning purposes. it is recommended to have it installed.
622 | Yard Hydrant | Condition Comment | The asset was observed to be in fair condition. Minor surface rust and defects was observed.
623 | Yard Hydrant (New Asset) | Condition Comment | The asset was observed to be in poor condition. In accordance with section 19.8.3 of the region's water and wastewater design manual (January 2012), a yard hydrant complete with a backflow preventer with a 37.5mm water service line shall be provided for flushing and cleaning purposes. it is recommended to have it installed.
651 | concrete pavers | Condition Comment | The asset was observed to be in fair condition. fair and overgrown vegetation were observed.
661 | Cathodic Protection | Condition Comment | The cathodic protection was assumed to be in good condition. The installation of the cathodic protection system was assumed to coincide with the installation of the above grade panel.
663 | Pump 2 Piping | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed.
665 | Discharge Piping | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed.
666 | Pump 2 Piping | Condition Comment | The asset was observed to be in fair condition. Corrosion was observed.
667 | Cathodic Protection | Condition Comment | The cathodic protection was assumed to be in good condition. The installation of the cathodic protection system was assumed to coincide with the installation of the above grade panel.
669 | Discharge Header | Condition Comment | The asset was assumed to be in fair condition.
670 | Dry Well Concrete Foundation | Condition Comment | The asset was assumed to be in fair condition based on its age.
671 | Discharge Header | Condition Comment | The asset was observed to be in poor condition. Heavy corrosion and deterioration was observed.

## rehab
| 0 | 1 | 2 | 3 | 4
0 | ParentID | AssetName | RehabComment | Rehabyear | RehabUnitMaterialCost
1 | 28 | Wet Well Concrete Structure | Structural repairs to address asset defects. | 2026 | 0
2 | 31 | Wet Well Concrete Structure | Structural repairs to address asset defects. | 2026 | 0
3 | 34 | Wet Well Concrete Structure | Structural repairs to address asset defects. | 2026 | 0
4 | 38 | Wet Well Concrete Structure | Structural repairs to address asset defects. | 2026 | 0
5 | 41 | Wet Well Concrete Structure | Structural repairs to address asset defects. | 2026 | 0
6 | 44 | Wet Well Concrete Structure | Structural repairs to address asset defects. | 2026 | 0
7 | 46 | Wet Well Concrete Structure | Structural repairs to address asset defects. | 2026 | 0
8 | 301 | Wet Well Concrete Structure | Structural repairs to address asset defects. | 2026 | 0
9 | 382 | Dry Well Concrete Foundation | Structural repairs to address asset defects. | 2026 | 0
10 | 383 | Dry Well Concrete Foundation | Structural repairs to address asset defects. | 2026 | 0
11 | 384 | Dry Well Concrete Foundation | Structural repairs to address asset defects. | 2026 | 0
12 | 385 | Dry Well Concrete Foundation | Structural repairs to address asset defects. | 2026 | 0
13 | 670 | Dry Well Concrete Foundation | Structural repairs to address asset defects. | 2026 | 0