## Final
AssetID | ClientAssetID0 | ClientAssetID1 | ClientAssetID2 | UniformatL0 | UniformatL1 | UniformatL2 | UniformatL3 | UniformatL4 | UniformatL5 | MasterFormatX | MasterFormatX2 | FlagAsProcess | FlagAsSubProcess | FlagAsAssembly | FlagAsParent | ParentID | AssetName | CoF | AssetDescription | Owner | Status | SiteName | FacilityName | LocationName | AssetCategory | CustomClientCategory | AssetType | CustomClientAssetType | Manufacturer | Model | SerialNumber | InspectionType | AssessmentYear | InstallYear | AvgESL | ReplaceYear | PhotoName | DrawingName | VisualCondition | PerformanceCondition | PoF | RedundancyFactor | CostID | MaterialUnitCost | Quantity | UnitOfQuantity | CostYear | CostSource | MarkupEquipment | MarkupLabour | MarkupAncillary | MarkupRemoval | MarkupEngineering | MarkupAdministration | MarkupContractor | MarkupContingency | TotalReplacementMarkup | LastEditor | LastEditTime | PlannerReviewer | PlannerReviewTime | DisciplineReview | DisciplineReviewTime | PMReview | PMReviewTime | TempProcess | TempSubProcess | TempSubProcessInstance | SizeCapacity | DBNotes | CountCapex | CountOpex | CountComments | CountDrawings | PreventDeletion | PreventEdit | TempComments1 | TempComments2 | TempComments3 | TempRehabComment | TempRehabYear | TempRehabCost
5 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE |  | Chancery Lane PS |  |  | Halton |  | Chancery Lane PS | WWPS |  | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-14 11:26 | [8 empty] | 1 |  | 5_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
6 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE |  | Chartwell Rd. PS |  |  | Halton |  | Chartwell Rd. PS | WWPS |  | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 2020-07-10 11:19 | [8 empty] | 1 |  | 6_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
7 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE |  | Cumnock PS |  |  | Halton |  | Cumnock PS | WWPS |  | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 2020-07-10 11:19 | [8 empty] | 1 |  | 7_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
8 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE |  | Ennisclaire Drive PS |  |  | Halton |  | Ennisclaire Drive PS | WWPS |  | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-28 16:16 | [8 empty] | 1 |  | 8_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
9 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE |  | First Street PS |  |  | Halton |  | First Street PS | WWPS |  | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1977 |  |  | HR-FRST-006 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 17:48 | [8 empty] | 1 |  | 9_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
10 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE |  | Garlock Gdns PS |  |  | Halton |  | Garlock Gdns PS | WWPS |  | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 2020-07-10 11:19 | [8 empty] | 1 |  | 10_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
11 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE |  | Morrison Heights PS |  |  | Halton |  | Morrison Heights PS | WWPS |  | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 2020-07-10 11:19 | [8 empty] | 1 |  | 11_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
12 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE |  | Raymar Pl PS |  |  | Halton |  | Raymar Pl PS | WWPS |  | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 2020-07-10 11:19 | [8 empty] | 1 |  | 12_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
24 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Dry Well Structure | 2 | Chancery Lane PS Dry Well | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Tank, Steel | [5 empty] | 1975 |  |  | HR-CNRY-004 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:20 | Maira Rafiq | 2020-09-18 10:44 |  |  |  |  | Building | Substructure | 1 |  | 24_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Minor corrosion noted | Good
25 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 5 | Site |  | Chancery Lane PS Site | Halton |  | Chancery Lane PS | WWPS | Site | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 2020-07-10 11:17 | [8 empty] | 1 |  | 25_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
26 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Dry Well Structure | 2 | Chartwell Rd. PS Dry Well | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Building Structural | Building and Process Structural |  | Tank, Steel | [5 empty] | 1983 |  |  | HR-CTWL-073 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:29 | Maira Rafiq | 2020-09-18 13:53 |  |  |  |  | Building | Substructure | 1 |  | 26_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Minor corrosion noted throughout | Good
27 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 6 | Site |  | Chartwell Rd. PS Site | Halton |  | Chartwell Rd. PS | WWPS | Site | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 2020-07-10 11:17 | [8 empty] | 1 |  | 27_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
28 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 633 | Wet Well Concrete Structure | 2 | Chartwell Rd. PS Wet Well | Halton | In Service | Chartwell Rd. PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Tank, Concrete | [5 empty] | 1983 |  |  | HR-CTWL-024 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:29 | Maira Rafiq | 2020-08-28 17:12 |  |  |  |  | Pumping | Wet Well | 1 |  | 28_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Exposed corroded reinforcement | Fair
29 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Dry Well Structure | 2 | Cumnock PS Dry Well | Halton | In Service | Cumnock PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Tank, Steel | [5 empty] | 1974 |  |  | HR-CMNK-122 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:38 | Maira Rafiq | 2020-09-20 22:11 |  |  |  |  | Building | Substructure | 1 |  | 29_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Moderate corrosion noted throughout | Fair
30 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 7 | Site |  | Cumnock PS Site | Halton |  | Cumnock PS | WWPS | Site | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 2020-07-10 11:17 | [8 empty] | 1 |  | 30_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
31 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 641 | Wet Well Concrete Structure | 2 | Cumnock PS Wet Well | Halton | In Service | Cumnock PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Tank, Concrete | [5 empty] | 1974 |  |  | HR-CMNK-138 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:39 | Maira Rafiq | 2020-09-20 22:03 |  |  |  |  | Pumping | Wet Well | 1 |  | 31_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Efflorescence deposits/leak at joint. Concrete delamination/spalling at joint | Fair
33 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 8 | Site |  | Ennisclaire Drive PS Site | Halton |  | Ennisclaire Drive PS | WWPS | Site | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 2020-07-10 11:17 | [8 empty] | 1 |  | 33_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
34 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 642 | Wet Well Concrete Structure | 2 | Ennisclaire Drive PS Wet Well | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Tank, Concrete | [5 empty] | 1977 |  |  | HR-ENIS-002 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:54 | Maira Rafiq | 2020-09-21 16:55 |  |  |  |  | Pumping | Wet Well | 1 |  | 34_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Exposed corroded reinforcement, rust spots and concrete parging spalling was noted at joints | Fair
35 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 9 |  |  | First Street PS | Halton |  | First Street PS | WWPS |  | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 2020-07-10 11:16 | [8 empty] | 1 |  | 35_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
36 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 9 | Dry Well | 2 | First Street PS Dry Well | Halton | In Service | First Street PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Tank, Steel | [5 empty] | 1986 |  |  | HR-FRST-065 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:14 | Maira Rafiq | 2020-09-21 17:30 |  |  |  |  | Building | Substructure | 1 |  | 36_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Corrosion noted throughout | Fair
37 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 9 | Site |  | First Street PS Site | Halton |  | First Street PS | WWPS | Site | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1986 | [10 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 2020-07-10 11:16 | Maira Rafiq | 2020-09-21 23:19 | [6 empty] | 1 |  | 37_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
38 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 9 | Wet Well Concrete Structure | 2 | First Street PS Wet Well | Halton | In Service | First Street PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Tank, Concrete | [5 empty] | 1986 |  |  | HR-FRST-094 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:15 | Maira Rafiq | 2020-09-21 19:12 |  |  |  |  | Pumping | Wet Well | 1 |  | 38_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair
40 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 10 | Site |  | Garlock Gdns PS Site | Halton |  | Garlock Gdns PS | WWPS | Site | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 2020-07-10 11:16 | [8 empty] | 1 |  | 40_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
41 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 10 | Wet Well Concrete Structure | 2 | Garlock Gdns PS Wet Well | Halton | In Service | Garlock Gdns PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Tank, Concrete | [5 empty] | 1977 |  |  | HR-GGDN-088 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:24 | Maira Rafiq | 2020-09-22 10:46 |  |  |  |  | Pumping | Wet Well | 1 |  | 41_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Rust spots noted | Fair
42 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 11 | Dry Well Structure | 2 | Morrison Heights PS Dry Well | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Tank, Steel | [5 empty] | 1973 |  | 2033 | HR-MORI-098 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:29 | Maira Rafiq | 2020-09-22 11:23 |  |  |  |  | Building | Substructure | 1 |  | 42_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Corrosion was noted at the base | Fair
43 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 11 | Site |  | Morrison Heights PS Site | Halton |  | Morrison Heights PS | WWPS | Site | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 2020-07-10 11:15 | [8 empty] | 1 |  | 43_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
44 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 11 | Wet Well Concrete Structure | 2 | Morrison Heights PS Wet Well | Halton | In Service | Morrison Heights PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Tank, Concrete | [5 empty] | 1973 |  | 2033 | HR-MORI-124 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:29 | Maira Rafiq | 2020-09-22 11:24 |  |  |  |  | Pumping | Wet Well | 1 |  | 44_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Exposed corroded reinforcement and concrete spalling noted | Fair
45 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 12 | Site |  | Raymar Pl PS Site | Halton |  | Raymar Pl PS | WWPS | Site | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 2020-07-10 11:15 | [8 empty] | 1 |  | 45_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
46 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Wet Well Concrete Structure | 2 | Raymar Pl PS Wet Well | Halton | In Service | Raymar Pl PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Tank, Concrete | [5 empty] | 1985 |  |  | HR-RAYM-054 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:32 | Maira Rafiq | 2020-09-22 12:45 |  |  |  |  | Pumping | Wet Well | 1 |  | 46_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Exposed corroded reinforcement and concrete spalling was noted at the pipe penetration | Fair
53 |  |  | 201575 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 645 | Sewage Lift Pump #1 | 2 | Sewage Lift Pump #1;Flygt;CP3085.183;;8 L/s at 8m TDH 3 hp | Halton | In Service | Garlock Gdns PS | Garlock Gdns PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | FLYGT | C3085-183-4438 | 3085-183-0710219 |  | 2020 | 1977 |  |  | HR-GGDN-015 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 17:00 | Maira Rafiq | 2020-09-22 10:50 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 53_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | The pump was near the end of its expected life.
54 |  |  | 201576 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 53 | Sewage Lift Pump #1 Check Valve | 2 | Check Valve #1;;;;100 mm dia | Halton | In Service | Garlock Gdns PS | Garlock Gdns PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Valve | VALMATIC | SWING FLEX | N/A |  | 2020 | 1977 |  |  | HR-GGDN-006 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 17:00 | Maira Rafiq | 2020-09-22 10:51 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 54_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Heavy corrosion was observed on the valve.
55 |  |  | 211093 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 53 | Sewage Lift Pump #1 Discharge Valve | 2 | Knife Gate Valve #1;;;;100 mm dia | Halton | In Service | Garlock Gdns PS | Garlock Gdns PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Valve | STAFSJO | NW100 | N/A |  | 2020 | 1977 |  |  | HR-GGDN-005 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 17:01 | Maira Rafiq | 2020-09-22 10:52 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 55_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Heavy corrosion was observed on the valve.
56 |  |  | 219156 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 41 | Variable Frequency Drive Pump # 1 | 2 | 26.1 AMPS | Halton |  | Garlock Gdns PS | Garlock Gdns PS | Wet Well | Process Electrical | Process Electrical |  | VFD | ALLEN BRADLEY | POWERFLEX-40 | BB024NOW6350010 |  | 2020 | 1977 | [10 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-22 11:17 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 56_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
57 |  |  | 201577 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 645 | Sewage Lift Pump #2 | 2 | Sewage Lift Pump #1;Flygt;CP3085.183;;8 L/s at 8m TDH 3 hp | Halton | Not In Service | Garlock Gdns PS | Garlock Gdns PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | FLYGT | 3085-183-4438 | 3085-183-0710220 |  | 2020 | 1977 |  |  | HR-GGDN-016 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 17:02 | Maira Rafiq | 2020-09-22 10:52 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 57_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | The pump was near the end of its expected service life
58 |  |  | 201578 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 57 | Sewage Lift Pump #2 Check Valve | 2 | Check Valve #2;;;;100 mm dia | Halton | In Service | Garlock Gdns PS | Garlock Gdns PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Valve | VALMATIC | SWING FLEX | N/A |  | 2020 | 1977 |  |  | HR-GGDN-010 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 17:03 | Maira Rafiq | 2020-09-22 10:52 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 58_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Severe corrosion was observed on the surface of the valve
59 |  |  | 211094 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 57 | Sewage Lift Pump #2 Discharge Valve | 2 | Knife Gate Valve #1;;;;100 mm dia | Halton | In Service | Garlock Gdns PS | Garlock Gdns PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Valve | STAFSJO | NW100 | N/A |  | 2020 | 1977 |  |  | HR-GGDN-012 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 17:05 | Maira Rafiq | 2020-09-22 10:53 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 59_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Heavy corrosion was observed on the valve
60 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 40 | Forcemain | 4 | 100mm diameter, approx. 237m ductile forcemain | Halton | In Service | Garlock Gdns PS | Garlock Gdns PS | Site | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 2020 | 1977 | [10 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 17:06 | Maira Rafiq | 2020-09-22 10:53 |  |  |  |  | Pumping | Discharge Header |  |  | 60_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | The pipe was at half of its expected service life.
61 |  |  | 201546 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 648 | Wet Well Exhaust Fan | 1 | 115 VOLTS/PHASE 1, capacity: 325 cfm | Halton |  | Raymar Pl PS | Raymar Pl PS | Wet Well | Building Mechanical | Building Services |  | Fan | N/A | N/A | N/A |  | 2020 | 1985 |  |  | HR-RAYM-001 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:39 | Maira Rafiq | 2020-09-22 13:22 |  |  |  |  | Pumping | HVAC - Distribution Systems |  |  | 61_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Surface staining on exhaust fan pipe | fair
62 |  |  | 201547 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 648 | Sewage Lift Pump #1 | 2 | Sewage Lift Pump #1;Flygt;CP3101;;6.6 L/s at 11.4 m TDH 5 HP | Halton | In Service | Raymar Pl PS | Raymar Pl PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | FLYGT | 3101 MT | 10534 |  | 2020 | 1985 |  |  | HR-RAYM-025 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 14:17 | Maira Rafiq | 2020-09-22 13:07 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 62_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | The pump was near the end of its expected service life.
63 |  |  | 211079 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 62 | Sewage Lift Pump #1 Check Valve | 2 | Check Valve #1;Flygt;;;100 mm dia | Halton | In Service | Raymar Pl PS | Raymar Pl PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Valve | HILLEN DE LELIE | BALL CHECK | N/A |  | 2020 | 1985 |  |  | HR-RAYM-009 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 14:23 | Maira Rafiq | 2020-09-22 13:08 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 63_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Heavy corrosion was observed on the surface of the valve
64 |  |  | 211080 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 62 | Sewage Lift Pump #1 Discharge Valve | 2 | Gate Valve #1;;;;100 mm dia | Halton | In Service | Raymar Pl PS | Raymar Pl PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Valve | JENKINS | GATE VALVE | N/A |  | 2020 | 1985 |  |  | HR-RAYM-010 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 14:29 | Maira Rafiq | 2020-09-22 13:08 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 64_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Heavy corrosion was observed on the surface of the valve
65 |  |  | 201548 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 648 | Sewage Lift Pump #2 | 2 | Sewage Lift Pump #2;Flygt;CP3101;;6.6 L/s at 11.4 m TDH 5 HP | Halton | In Service | Raymar Pl PS | Raymar Pl PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | FLYGT | C3102-180 | 355048-433 |  | 2020 | 1985 |  |  | HR-RAYM-012 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 14:34 | Maira Rafiq | 2020-09-22 13:09 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 65_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | The pump was near the end of its expected service life.
66 |  |  | 211081 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 65 | Sewage Lift Pump #1 Check Valve | 2 | Check Valve #1;Flygt;;;100 mm dia | Halton | In Service | Raymar Pl PS | Raymar Pl PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Valve | HILLEN DE LELIE | BALL CHECK | N/A |  | 2020 | 1985 |  |  | HR-RAYM-007 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 14:47 | Maira Rafiq | 2020-09-22 13:10 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 66_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Heavy corrosion was observed on the surface of the valve.
67 |  |  | 211082 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 65 | Sewage Lift Pump #1 Discharge Valve | 2 | Gate Valve #2;;;;100 mm dia | Halton | In Service | Raymar Pl PS | Raymar Pl PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Valve | JENKINS | GATE VALVE | N/A |  | 2020 | 1985 |  |  | HR-RAYM-006 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 14:49 | Maira Rafiq | 2020-09-22 13:11 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 67_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Heavy corrosion was observed on the surface of the valve
68 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 45 | Forcemain | 4 | 100mm diameter, approx. 165m PVC SDR 35 pipe | Halton | In Service | Raymar Pl PS | Raymar Pl PS | Site | Process Mechanical | Process Piping |  | Piping, PVC |  |  |  |  | 2020 | 1985 | [10 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 14:54 | Maira Rafiq | 2020-09-22 13:13 |  |  |  |  | Pumping | Discharge Header |  |  | 68_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | assumed to be good
69 |  |  | 201661 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 646 | Dry Well Sump Pump | 1 | 1/4" | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Pump, Centrifugal | N/A | SE-CIA-SFS | N/A |  | 2020 | 1973 |  |  | HR-MORI-024 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:38 | Maira Rafiq | 2020-09-22 12:34 |  |  |  |  | Pumping | Pump Assembly |  |  | 69_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the pump. The pump was beyond its expected service life. | Moderate surface corrosion
70 |  |  | 201662 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 647 | TRANSMITTER LEVEL WET WELL #1 | 2 | 72" Wet Well Level Transmitter; Siemens Milltronics; Multiranger 100; ; ; | Halton | In Service | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Instrumentation | Process Instrumentation |  | Transmitter | MILLTRONICS | MULTIRANGER 100 | 012105122XB |  | 2020 | 2008 |  | 2030 | HR-MORI-009 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 18:11 | Maira Rafiq | 2020-08-24 09:31 |  |  |  |  | Pumping | Wet Well |  |  | 70_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | good
71 |  |  | 201653 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 646 | Dry Wall Exhaust Fan | 1 |  | Halton |  | Morrison Heights PS | Morrison Heights PS | Dry Well | Building Mechanical | Building Services |  | Fan | FASCO | D112 | 7108-0195 |  | 2020 | 1973 |  |  | HR-MORI-115 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:38 | Maira Rafiq | 2020-09-22 12:35 |  |  |  |  | Pumping | HVAC - Distribution Systems |  |  | 71_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | paint peeling | fair
72 |  |  | 201654 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 646 | Sewage Lift Pump #1 | 2 | Sewage Lift Pump #1;Clow Pumps;N4310;;12 L/s 7.5 hp | Halton | In Service | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | CLOW | N 4310 | 918126 |  | 2020 | 1973 |  |  | HR-MORI-020 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 10:26 | Maira Rafiq | 2020-09-22 12:09 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 72_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the pump. The pump was beyond its expected service life.
73 |  |  | 217113 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 72 | Sewage Lift Pump #1 Check Valve | 2 | Check Valve #1;Swing-Flex;Model 504A;;100 mm dia | Halton | In Service | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | EDDY IOWA | N/A | N/A |  | 2020 | 1973 |  |  | HR-MORI-019 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 10:20 | Maira Rafiq | 2020-09-22 12:04 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 73_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the valve. The valve was beyond its expected service life
74 |  |  | 201656 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 72 | Sewage Lift Pump #1 Motor Drive | 2 | 7.5 HP | Halton |  | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Electrical | Process Electrical |  | Motor | U.S. MOTORS | TYPE 1 | 9204320-901 |  | 2020 | 1973 |  |  | HR-MORI-012 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-22 12:26 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 74_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | minor paint wear
75 |  |  | 211145 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 72 | Sewage Lift Pump #1 Inlet Valve | 2 | Inlet Knife Gate Valve #1;Trueline;;;100 mm dia | Halton | In Service | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | IOWA | N/A | N/A |  | 2020 | 1973 |  |  | HR-MORI-022 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 10:16 | Maira Rafiq | 2020-09-22 12:05 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 75_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the valve. The valve was beyond its expected service life.
76 |  |  | 211146 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 72 | Sewage Lift Pump #1 Discharge Valve | 2 | Discharge Knife Gate Valve #1;Trueline;;;100 mm dia | Halton | In Service | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | IOWA | N/A | N/A |  | 2020 | 1973 |  |  | HR-MORI-018 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 11:17 | Maira Rafiq | 2020-09-22 12:06 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 76_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the valve. The valve was beyond its expected service life.
78 |  |  | 201657 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 646 | Sewage Lift Pump #2 | 2 | Sewage Lift Pump #2;Clow Pumps;N4310;;12 L/s 7.5 hp | Halton | In Service | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | CLOW | N 4310 | 918126 |  | 2020 | 1973 |  |  | HR-MORI-012 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 10:26 | Maira Rafiq | 2020-09-22 12:09 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 78_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the pump. The pump was beyond its expected service life.
79 |  |  | 201658 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 78 | Sewage Lift Pump #2 Check Valve | 2 | Check Valve #2;Swing-Flex;Model 504A;;100 mm dia | Halton | In Service | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | EDDY IOWA | N/A | N/A |  | 2020 | 1973 |  |  | HR-MORI-014 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 11:12 | Maira Rafiq | 2020-09-22 12:10 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 79_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Deterioration and corrosion was observed on the surface of the valve. The valve was beyond its expected service life
80 |  |  | 201659 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 78 | Sewage Lift Pump #2 Motor Drive | 2 | 7.5 HP | Halton |  | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Electrical | Process Electrical |  | Motor | U.S. ELECTRIC MOTORS | N/A | 9204320-901 |  | 2020 | 1973 |  |  | HR-MORI-020 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-22 12:26 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 80_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | minor paint wear
81 |  |  | 211147 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 78 | Sewage Lift Pump #2 Inlet Valve | 2 | Inlet Knife Gate Valve #1;Trueline;;;100 mm dia | Halton | In Service | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | IOWA | N/A | N/A |  | 2020 | 1973 |  |  | HR-MORI-011 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 11:15 | Maira Rafiq | 2020-09-22 12:10 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 81_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion was observed on the surface of the valve. The valve was beyond its expected service life.
82 |  |  | 211148 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 78 | Sewage Lift Pump #2 Discharge Valve | 2 | Discharge Knife Gate Valve #1;Trueline;;;100 mm dia | Halton | In Service | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | IOWA | N/A | N/A |  | 2020 | 1973 |  |  | HR-MORI-015 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 11:18 | Maira Rafiq | 2020-09-22 12:12 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 82_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Minor deterioration was observed on the surface of the valve. The valve was beyond its expected service life.
83 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 43 | Forcemain | 5 | 150mm diameter, approx. 254m PVC series 125 pipe | Halton | In Service | Morrison Heights PS | Morrison Heights PS | Site | Process Mechanical | Process Piping |  | Piping, PVC |  |  |  |  | 2020 | 1973 | [10 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 11:41 | Maira Rafiq | 2020-09-22 12:12 |  |  |  |  | Pumping | Discharge Header |  |  | 83_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | assumed to be fair | The pipe passed half of its expected service life.
129 |  |  | 201612 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 24 | PUMP #1 SUMP | 1 | Sump Pump;;;; | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Building Mechanical | Building Services |  | Pump | HYDROMATIC |  |  |  | 2020 | 1975 |  |  | HR-CNRY-010 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 09:06 | Maira Rafiq | 2020-09-18 11:55 |  |  |  |  | Pumping | Pump Assembly |  |  | 129_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration were observed on the surface of the pump. The pump is beyond the end of its expected service life
130 |  |  | 211126 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 638 | TRANSMITTER LEVEL WET WELL | 2 | 94.5" Wet Well Level Transmitter; Siemens Milltronics; MultiRanger 200; ; ; | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Instrumentation | Process Instrumentation |  | Transmitter | MILLTRONICS | MULTIRANGER PLUS | 082191 012-19 |  | 2020 | 2009 |  | 2030 | HR-CNRY-008 |  |  |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 15:12 | Maira Rafiq | 2020-08-24 08:39 |  |  |  |  | Pumping | Wet Well |  |  | 130_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Dust | Corrosion
131 |  |  | 201605 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 638 | FAN EXHAUST #1 | 1 | 115 VOLTS/PHASE 1 | Halton | Missing | Chancery Lane PS | Chancery Lane PS | Dry Well | Building Mechanical | Building Services |  | Fan | N/A | N/A | N/A |  | 2020 | 1975 | [10 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:23 | Maira Rafiq | 2020-09-18 11:53 |  |  |  |  | Building | HVAC - Distribution Systems |  |  | 131_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | The exhaust fan was missing | As per Section 7.2.9 of MOECC's Design Guidelines for Sewage Works, mechanical ventilation is required for below ground surface dry well.
132 |  |  | 201606 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 638 | Sewage Lift Pump #1 | 2 | Sewage Lift Pump #1;Smith & Loveless;4B2A;;16.7 L/s at 11.6 m TDH 5HP | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Pump | SMITH AND LOVELESS | 4B2A | 9750232 |  | 2020 | 1975 |  |  | HR-CNRY-012 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 09:09 | Maira Rafiq | 2020-09-18 12:36 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 132_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | Deterioration was observed on the surface of the pump and it is beyond the end of its expected service life.
133 |  |  | 201607 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 132 | Sewage Lift Pump #1 Check Valve | 2 | Check Valve #1;Smith & Loveless;;150 mm dia | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | SMITH AND LOVELESS |  |  |  | 2020 | 1975 |  |  | HR-CNRY-014 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 09:24 | Maira Rafiq | 2020-09-18 12:52 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 133_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | Corrasion and deterioration was observed on the surface of the valve. The valve is beyond its expected service life.
134 |  |  | 201608 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 638 | MOTOR DRIVE SEWAGE LIFT PUMP #1 | 2 | 5 HP/1160 RPM | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Electrical | Process Electrical |  | Motor | ROBBIN & MYERS | S & L - N-BPM1 | CF50232 |  | 2020 | 1975 |  |  | HR-CNRY-116 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-18 11:28 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 134_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | minor corrosion on casing
135 |  |  | 211127 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 132 | Sewage Lift Pump #1 Inlet Valve | 2 | Inlet Gate Valve No.1;Smith & Loveless;;;150 mm dia | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | STOCKHAM | N/A | N/A |  | 2020 | 1975 |  |  | HR-CNRY-011 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 09:33 | Maira Rafiq | 2020-09-18 12:52 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 135_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | Corrosion and deterioration was observed on the surface of the valve. The valve is beyond its expected service life.
136 |  |  | 211128 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 132 | Sewage Lift Pump #1 Discharge Valve | 2 | Discharge Gate Valve No.1;Smith & Loveless;;;150 mm dia | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | STOCKHAM | N/A | N/A |  | 2020 | 1975 |  |  | HR-CNRY-015 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 09:36 | Maira Rafiq | 2020-09-18 12:52 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 136_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | Corrosion and deterioration was observed on the surface of the valve. The valve is beyond its expected service life.
137 |  |  | 201609 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 638 | Sewage Lift Pump #2 | 2 | Sewage Lift Pump #2;Smith & Loveless;4B2A;;16.7 L/s at 11.6 m TDH 5HP | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | SMITH AND LOVELESS | 4B2A | 9750232 |  | 2020 | 1975 |  |  | HR-CNRY-022 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 09:39 | Maira Rafiq | 2020-09-18 12:52 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 137_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | Deterioration was observed on the surface of the pump and it is beyond the end of its expected service life.
138 |  |  | 201610 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 137 | Sewage Lift Pump #2 Check Valve | 2 | Check Valve #2;Smith & Loveless;;150 mm dia | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | SMITH AND LOVELESS | N/A | N/A |  | 2020 | 1975 |  |  | HR-CNRY-021 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 09:45 | Maira Rafiq | 2020-09-18 12:52 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 138_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | Corrasion and deterioration was observed on the surface of the valve. The valve is beyond its expected service life.
139 |  |  | 201611 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 24 | MOTOR DRIVE SEWAGE LIFT PUMP #2 | 2 | 5 HP/1160 RPM | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Electrical | Process Electrical |  | Motor | ROBBIN & MYERS | S&L- N-BPMII | CB50231 |  | 2020 | 1975 |  |  | HR-CNRY-116 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-18 11:29 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 139_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | minor corrosion on casing
140 |  |  | 211129 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 137 | Sewage Lift Pump #2 Inlet Valve | 2 | Inlet Gate Valve No.2;Smith & Loveless;;;150 mm dia | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | STOCKHAM | N/A | N/A |  | 2020 | 1975 |  |  | HR-CNRY-020 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 09:51 | Maira Rafiq | 2020-09-18 12:53 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 140_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | Corrosion and deterioration was observed on the surface of the valve. The valve is beyond its expected service life.
141 |  |  | 211130 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 137 | Sewage Lift Pump #1 Discharge Valve | 2 | Discharge Gate Valve No.2;Smith & Loveless;;;150 mm dia | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | STOCKHAM | N/A | N/A |  | 2020 | 1975 |  |  | HR-CNRY-023 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 09:55 | Maira Rafiq | 2020-09-18 12:53 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 141_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | Corrosion and deterioration was observed on the surface of the valve. The valve is beyond its expected service life.
142 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 25 | Forcemain | 4 | 150mm diameter, approx. 350 m ductile Iron forcemain piping | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Site | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 2020 | 1975 | [10 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 09:57 | Maira Rafiq | 2020-09-18 12:42 |  |  |  |  | Pumping | Discharge Header |  |  | 142_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | assumed to be in good condition | The pipe is at half of its expected service life.
143 |  |  | 201557 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 26 | PUMP #1 SUMP | 1 | Sump Pump;;;; | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Building Mechanical | Building Services |  | Pump, Centrifugal | SMITH AND LOVELESS | N/A | N/A |  | 2020 | 1983 |  |  | HR-CTWL-019 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 10:41 | Maira Rafiq | 2020-09-20 10:57 |  |  |  |  | Pumping | Pump Assembly |  |  | 143_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Severe corrosion and deterioration were observed on the surface of the pump. The pump was near the end of its expected service life.
144 |  |  | 201558 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 633 | WET WELL LEVEL TRANSMITTER #1 | 2 | 80" Wet Well Level Transmitter; Siemens Milltronics; Multiranger Plus; ; ; | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation |  | Transmitter | MILLTRONICS | MULTIRANGER PLUS | 061489 186-07 |  | 2020 | 2009 |  | 2025 | HR-CTWL-005 |  |  |  | 1 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 16:13 | Maira Rafiq | 2020-09-20 10:52 |  |  |  |  | Pumping | Wet Well |  |  | 144_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | good
145 |  |  | 201550 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 632 | FAN EXHAUST #1 | 1 | 115 VOLTS/PHASE 1 | Halton | Missing | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Building Mechanical | Building Services |  | Fan |  |  |  |  | 2020 | 1983 |  | 2021 | [8 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:25 | Maira Rafiq | 2020-09-20 10:46 |  |  |  |  | Building | HVAC - Distribution Systems |  |  | 145_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | As per Section 7.2.9 of MOECC's Design Guidelines for Sewage Works, mechanical ventilation is required for below ground surface dry well.
146 |  |  | 201551 | 0 | [7 empty] | FALSE | FALSE | FALSE | TRUE | 632 | Sewage Lift Pump #1 | 2 | Sewage Lift Pump #1;Smith & Loveless;4B2;;;16.5 L/s at 10.1 m TDH 5 HP | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | SMITH AND LOVELESS | 4B2 | 6537098 |  | 2020 | 1983 |  |  | HR-CTWL-017 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 10:54 | Maira Rafiq | 2020-09-20 11:01 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 146_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the pump. The pump was near the end of its expected service life.
147 |  |  | 201552 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 146 | Sewage Lift Pump #1 Check Valve | 2 | Discharge Check Valve #1;Smith and Loveless;;;150 mm dia | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | SMITH AND LOVELESS |  |  |  | 2020 | 1983 |  |  | HR-CTWL-016 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 11:00 | Maira Rafiq | 2020-09-20 11:02 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 147_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the valve. The valve is near the end of its expected service life.
148 |  |  | 201553 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 146 | Sewage Lift Pump #1 Motor Drive | 2 | 5 HP/1160 RPM | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Motor | ROBIN MYERS |  | ABM3U7098 |  | 2020 | 1983 |  |  | HR-CTWL-017 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-20 11:05 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 148_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Minor surface corrosion
149 |  |  | 211083 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 26 | Sewage Lift Pum #1 Inlet Valve | 2 | Inlet Gate Valve #1;Clow;;;150 mm dia | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | EDDY IOWA | N/A | N/A |  | 2020 | 1983 |  | 0 | HR-CTWL-018 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 11:05 | Maira Rafiq | 2020-09-20 11:02 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 149_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the valve. The valve was near the end of its expected service life.
150 |  |  | 211084 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 146 | Sewage Lift Pump #1 Discharge Valve | 2 | Discharge Gate Valve #1;Clow;;;150 mm dia | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | CLOW | N/A | N/A |  | 2020 | 1983 |  |  | HR-CTWL-015 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 11:05 | Maira Rafiq | 2020-09-20 11:03 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 150_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the valve. The valve was near the end of its expected service life.
151 |  |  | 201554 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 632 | Sewage Lift Pump #2 | 2 | Sewage Lift Pump #2;Smith & Loveless;4B2;;;16.5 L/s at 10.1 m TDH 5 HP | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | SMITH AND LOVELESS | 4B2 | 6537097 |  | 2020 | 1983 |  |  | HR-CTWL-010 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 11:16 | Maira Rafiq | 2020-09-20 11:04 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 151_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the pump. The pump was near the end of its expected service life.
152 |  |  | 201555 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 151 | Sewage Lift Pump #2 Check Valve | 2 | Discharge Check Valve #2;Smith and Loveless;;;150 mm dia | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | SMITH AND LOVELESS | N/A | N/A |  | 2020 | 1983 |  |  | HR-CTWL-012 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 11:22 | Maira Rafiq | 2020-09-20 11:04 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 152_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the valve. The valve is near the end of its expected service life.
153 |  |  | 201556 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 151 | Sewage Lift Pump #2 Motor Drive | 2 | 5 HP/1160 RPM | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Motor | ROBIN MYERS |  | ABM3U7097 |  | 2020 | 1983 |  |  | HR-CTWL-027 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-20 11:06 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 153_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Minor surface corrosion and paint wear
154 |  |  | 211085 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 151 | Sewage Lift Pump #2 Inlet Valve | 2 | Inlet Gate Valve #2;Clow;;;150 mm dia | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | EDDY IOWA | N/A | N/A |  | 2020 | 1983 |  |  | HR-CTWL-009 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 11:32 | Maira Rafiq | 2020-09-20 11:06 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 154_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the valve. The valve was near the end of its expected service life.
155 |  |  | 211086 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 151 | Sewage Lift Pump #2 Discharge Valve | 2 | Discharge Gate Valve #2;Clow;;;150 mm dia | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | CLOW | N/A | N/A |  | 2020 | 1983 |  |  | HR-CTWL-013 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 11:37 | Maira Rafiq | 2020-09-20 11:07 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 155_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the valve. The valve was near the end of its expected service life.
156 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 27 | Forcemain | 4 | 200mm diameter, approx. 40m ductile iron forcemain | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Site | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 2020 | 1983 | [10 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 13:21 | Maira Rafiq | 2020-09-20 11:07 |  |  |  |  | Pumping | Discharge Header |  |  | 156_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Good
157 |  |  | 201649 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 29 | PUMP SUMP | 1 | Sump Pump;;;; | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Building Mechanical | Building Services |  | Pump, Centrifugal | N/A | N/A | N/A |  | 2020 | 1974 |  |  | HR-CMNK-021 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 13:58 | Maira Rafiq | 2020-09-21 15:27 |  |  |  |  | Pumping | Pump Assembly |  |  | 157_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the pump. The pump is beyond its expected service life.
158 |  |  | 201651 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 641 | TRANSMITTER LEVEL WET WELL #1 | 2 | 76.25" Wet Well Level Transmitter; Siemens Milltronics; Multiranger Plus; ; ; | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Process Instrumentation | Process Instrumentation |  | Transmitter | MILLTRONICS | MULTIRANGER PLUS | 05-25-94 118-6D |  | 2020 | 2009 |  | 2030 | HR-CMNK-005 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 17:01 | Maira Rafiq | 2020-08-24 08:57 |  |  |  |  | Pumping | Wet Well |  |  | 158_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Minor corrosion on nuts
159 |  |  | 201640 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 640 | Dry Well Exhaust Fan | 1 | 115 VOLTS, installation year assumed to be 1974 | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Building Mechanical | Building Services |  | Fan | N/A | N/A | N/A |  | 2020 | 1974 |  |  | HR-CMNK-121 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:31 | Maira Rafiq | 2020-09-21 15:23 |  |  |  |  | Building | HVAC - Distribution Systems |  |  | 159_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Surface corrosion
160 |  |  | 201641 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 640 | Sewage Lift Pump #1 | 2 | Sewage Lift Pump #1;Clow;N4310;;6.3 L/s 3 hp | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | CLOW | N4310 | 918126 |  | 2020 | 1974 |  |  | HR-CMNK-013 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 14:06 | Maira Rafiq | 2020-09-21 15:31 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 160_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | Corrosion and deterioration was observed on the surface of the pump. The pump was beyond its expected service life.
161 |  |  | 201642 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 160 | Sewage Lift Pump #1 Check Valve | 2 | Check Valve #1;Crow;;;100 mm dia | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | IOWA | N/A | N/A |  | 2020 | 1974 |  |  | HR-CMNK-014 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 14:12 | Maira Rafiq | 2020-09-21 15:32 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 161_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Moderate corrosion and deterioration was observed on the surface of the valve. The valve was beyond its expected service life.
162 |  |  | 201643 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 29 | Sewage Lift Pump #1 Motor Drive | 2 | 7.9HP | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Process Electrical | Process Electrical |  | Motor | U.S. MOTORS | AV-9 | R2071304 |  | 2020 | 1974 |  |  | HR-CMNK-013 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-21 15:14 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 162_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | paint wear
163 |  |  | 211141 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 160 | Sewage Lift Pump #1 Inlet Valve | 2 | Inlet Gate Valve #1;Crow;;;100 mm dia | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | IOWA | N/A | N/A |  | 2020 | 1974 |  |  | HR-CMNK-011 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 14:13 | Maira Rafiq | 2020-09-21 15:32 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 163_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the valve.
164 |  |  | 211142 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 160 | Sewage Lift Pump #1 Discharge Valve | 2 | Discharge Gate Valve #1;Crow;;;100 mm dia | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | IOWA | N/A | N/A |  | 2020 | 1974 |  |  | HR-CMNK-015 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 14:13 | Maira Rafiq | 2020-09-21 15:33 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 164_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the valve.
165 |  |  | 201645 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 640 | Sewage Lift Pump #2 | 2 | Sewage Lift Pump #2;Clow;N4310;;6.3 L/s 3 hp | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | CLOW | N4310 | 918127 |  | 2020 | 1974 |  |  | HR-CMNK-019 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 14:15 | Maira Rafiq | 2020-09-21 15:34 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 165_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Corrosion and deterioration was observed on the surface of the pump. The pump was beyond its expected service life.
166 |  |  | 201646 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 165 | Sewage Lift Pump #2 Check Valve | 2 | Check Valve #1;Crow;;;100 mm dia | Halton | 20 | Cumnock PS | Cumnock PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | IOWA | N/A | N/A |  | 2020 | 1974 |  |  | HR-CMNK-018 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 14:18 | Maira Rafiq | 2020-09-21 15:34 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 166_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the pump. The pump was beyond its expected service life.
167 |  |  | 201647 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 29 | Sewage Lift Pump #2 Motor Drive | 2 | 7.5P | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Process Electrical | Process Electrical |  | Motor | U.S. MOTORS | AV-9 | R2071304 |  | 2020 | 1974 |  |  | HR-CMNK-019 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-21 15:15 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 167_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | paint wear
168 |  |  | 211143 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 165 | Sewage Lift Pump #2 Inlet Valve | 2 | Inlet Gate Valve #2;Crow;;;100 mm dia | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | IOWA | N/A | N/A |  | 2020 | 1974 |  |  | HR-CMNK-020 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 14:19 | Maira Rafiq | 2020-09-21 15:34 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 168_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the valve.
169 |  |  | 211144 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 165 | Sewage Lift Pump #2 Discharge Valve | 2 | Discharge Gate Valve #2;Crow;;;100 mm dia | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | IOWA (CLOW) | N/A | N/A |  | 2020 | 1974 |  |  | HR-CMNK-017 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 14:22 | Maira Rafiq | 2020-09-21 15:35 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 169_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the valve.
170 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 30 | Forcemain | 4 | 150mm diameter, approx. 79 m ductile iron pipe | Halton | In Service | Cumnock PS | Cumnock PS | Site | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 2020 | 1974 | [10 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 14:24 | Maira Rafiq | 2020-09-21 15:36 |  |  |  |  | Pumping | Discharge Header |  |  | 170_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | assumed to be good | The pipe was at half of its expected service life.
172 |  |  | 211126 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 642 | TRANSMITTER LEVEL WET WELL | 2 | 94.5" Wet Well Level Transmitter; Siemens Milltronics; Multiranger 200; ; ; | Halton | In Service | Ennisclaire Drive PS | WWPS | Site | Process Instrumentation | Process Instrumentation |  | Transmitter | MILLTRONICS | MULTIRANGER PLUS | 082191 012-19 |  | 2020 | 2019 |  | 2035 | HR-ENIS-030 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 17:40 | Maira Rafiq | 2020-08-24 09:02 |  |  |  |  | Pumping | Wet Well | 1 |  | 172_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | very good
174 |  |  | 201606 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 642 | Sewage Lift Pump #1 | 2 | Sewage Pump #1;Flygt;C3082MT;;7.8 L/s at 7.2 m TDH 2hp | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | SMITH AND LOVELESS | 4B2A | 9750232 |  | 2020 | 1977 |  |  | HR-ENIS-009 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:01 | Maira Rafiq | 2020-09-21 17:12 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 174_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | The pump was beyond its expected service life.
175 |  |  | 201607 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 174 | Sewage Lift Pump #1 Check Valve | 2 | Check Valve #1;;;;100 mm dia | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | SMITH AND LOVELESS |  |  |  | 2020 | 1977 |  |  | HR-ENIS-010 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 15:01 | Maira Rafiq | 2020-09-21 17:13 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 175_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Heavy corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
177 |  |  | 211127 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 174 | Sewage Lift Pump #1 Knife Gate Valve | 2 | Knife Gate Valve #1;;;;100 mm dia | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | STOCKHAM | N/A | N/A |  | 2020 | 1977 |  |  | HR-ENIS-012 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 15:10 | Maira Rafiq | 2020-09-21 17:13 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 177_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Heavy corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
178 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 33 | Forcemain | 3 | 100mm diameter, approx. 290m Ductile Iron forcemain | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Site | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 2020 | 1977 | [10 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 15:11 | Maira Rafiq | 2020-09-21 17:14 |  |  |  |  | Pumping | Discharge Header |  |  | 178_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | assumed to be fair | The pipe was at half of its expected service life
179 |  |  | 201543 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 643 | Sump Pump #1 | 1 | Sump Pump;;;; | Halton | In Service | First Street PS | First Street PS | Dry Well | Building Mechanical | Building Services |  | Pump, Submersible | HYDROMATIC | SV-25A |  |  | 2020 | 1986 |  |  | HR-FRST-009 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:16 | Maira Rafiq | 2020-09-21 23:41 |  |  |  |  | Building | Plumbing - Sanitary Waste |  |  | 179_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | Corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
180 |  |  | 201545 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 644 | TRANSMITTER LEVEL WET WELL #1 | 2 | 18.5" Wet Well Level Transmitter; Siemens Milltronics; Multiranger Plus; ; ; | Halton | In Service | First Street PS | First Street PS | Dry Well | Process Instrumentation | Process Instrumentation |  | Transmitter | MILLTRONICS | MULTIRANGER PLUS | 05-17-94 211GE |  | 2020 | 2009 |  | 2030 | HR-FRST-006 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 17:50 | Maira Rafiq | 2020-08-24 09:10 |  |  |  |  | Pumping | Wet Well |  |  | 180_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | nuts were not secured properly | good
181 |  |  | 201536 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 643 | Dry Well Exhaust Fan | 1 | 115 V./60 HZ., Installation year assumed to be 1985 | Halton |  | First Street PS | First Street PS | Dry Well | Building Mechanical | Building Services |  | Fan | DAYTON | 40 | N/A |  | 2020 | 1986 |  |  | HR-FRST-018 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:36 | Maira Rafiq | 2020-09-22 12:40 |  |  |  |  | Pumping | HVAC - Distribution Systems |  |  | 181_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Paint peeling | fair
182 |  |  | 201537 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 643 | Sewage Lift Pump #1 | 2 | Sewage Lift Pump #1;Clow;Model 4310;;15.8 L/s at 12.2 m TDH 7.5hp | Halton | In Service | First Street PS | First Street PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Pump | CLOW | 431O | 261755 |  | 2020 | 1986 |  |  | HR-FRST-016 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:23 | Maira Rafiq | 2020-09-21 23:28 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 182_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Deterioration was observed on the surface of the pump. The pump was near the end of its expected service life.
183 |  |  | 201538 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 182 | Sewage Lift Pump #1 Check Valve | 2 | Check Valve #1;Kennedy;;;100 mm dia | Halton | In Service | First Street PS | First Street PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | KENNEDY | FIG 106 | 11071 |  | 2020 | 1986 |  |  | HR-FRST-015 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:28 | Maira Rafiq | 2020-09-21 23:29 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 183_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Corrosion and deterioration was observed on the valve. The pump was near the end of its expected service life.
184 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 36 | Sewage Lift Pump #2 Motor Drive | 2 | 7.5 HP/1755 RPM | Halton |  | First Street PS | First Street PS | Dry Well | Process Electrical | Process Electrical |  | Motor | RELIANCE ELECTRIC | P | 1YAB31452A1 |  | 2020 | 1986 | [10 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-21 23:19 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 184_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | paint wear
185 |  |  | 211075 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 182 | Sewage Lift Pump #1 Inlet Valve | 2 | Inlet Gate Valve #1;Kennedy;;;100 mm dia | Halton | In Service | First Street PS | First Street PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | CLOW | EDDY IOWA | N/A |  | 2020 | 1986 |  |  | HR-FRST-014 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:28 | Maira Rafiq | 2020-09-21 23:29 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 185_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Corrosion and deterioration was observed on the valve. The pump was near the end of its expected service life.
186 |  |  | 211076 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 182 | Sewage Lift Pump #1 Discharge Valve | 2 | Discharge Gate Valve #1;Kennedy;;;100 mm dia | Halton | In Service | First Street PS | First Street PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | CLOW | EDDY IOWA | N/A |  | 2020 | 1986 |  |  | HR-FRST-017 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:29 | Maira Rafiq | 2020-09-21 23:30 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 186_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Very Poor | Severe corrosion and deterioration was observed on the valve. The pump was near the end of its expected service life.
187 |  |  | 201540 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 643 | Sewage Lift Pump #2 | 2 | Sewage Lift Pump #2;Clow;Model 4310;;15.8 L/s at 12.2 m TDH 7.5hp | Halton | In Service | First Street PS | First Street PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Pump | CLOW | 431O | 261755 |  | 2020 | 1986 |  |  | HR-FRST-010 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:32 | Maira Rafiq | 2020-09-21 23:32 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 187_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Deterioration was observed on the surface of the pump. The pump was near the end of its expected service life.
188 |  |  | 201541 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 187 | Sewage Lift Pump #2 Check Valve | 2 | Check Valve #1;;;;100 mm dia | Halton | In Service | First Street PS | First Street PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | KENNEDY | FIG 106 | 11071 |  | 2020 | 1986 |  |  | HR-FRST-011 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:34 | Maira Rafiq | 2020-09-21 23:33 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 188_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | expected service life.
189 |  |  | 201542 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 36 | Sewage Lift Pump #2 Motor Drive | 2 | 7.5 HP/1755 RPM | Halton | In Service | First Street PS | First Street PS | Dry Well | Process Electrical | Process Electrical |  | Motor | RELIANCE ELECTRIC | P | 1YAB31452A2UK |  | 2020 | 1986 |  |  | HR-FRST-023 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 14:32 | Maira Rafiq | 2020-09-21 23:19 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 189_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | paint wear
190 |  |  | 211077 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 187 | Sewage Lift Pump #2 Inlet Valve | 2 | Inlet Gate Valve #1;;;;100 mm dia | Halton | In Service | First Street PS | First Street PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | CLOW | EDDY IOWA | N/A |  | 2020 | 1986 |  |  | HR-FRST-030 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:38 | Maira Rafiq | 2020-09-21 23:33 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 190_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Corrosion and deterioration was observed on the valve. The pump was near the end of its expected service life.
191 |  |  | 211078 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 187 | Sewage Lift Pump #2 Disccharge Valve | 2 | Discharge Gate Valve #1;;;;100 mm dia | Halton | In Service | First Street PS | First Street PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | CLOW | EDDY IOWA | N/A |  | 2020 | 1986 |  |  | HR-FRST-012 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:38 | Maira Rafiq | 2020-09-21 23:34 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 191_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | Minor deterioration was observed on the surface of the valve. The valve was near the end of its expected service life.
192 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 37 | Forcemain | 4 | 150mm diameter, approx. 150 m PVC pipe | Halton | In Service | First Street PS | First Street PS | Site | Process Mechanical | Process Piping |  | Piping, PVC |  |  |  |  | 2020 | 1986 | [10 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:44 | Maira Rafiq | 2020-09-21 23:35 |  |  |  |  | Pumping | Discharge Header |  |  | 192_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | assumed to be good
237 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 25 | Overflow Piping | 3 | 250mm diameter, approx. 147 m concrete pipe | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Site | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1975 |  |  | HR-CNRY-043 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 10:04 | Maira Rafiq | 2020-09-18 13:02 |  |  |  |  | Pumping | Wet Well |  |  | 237_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | The pipe is at half of its expected service life.
238 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 638 | Discharge Header | 3 | 150mm diameter, approx. 5 m cast iron piping | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1975 |  |  | HR-CNRY-031 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 10:12 | Maira Rafiq | 2020-09-18 13:05 |  |  |  |  | Pumping | Discharge Header |  |  | 238_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | The pipe is at half of its expected service life.
240 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 132 | Pump 1 Piping | 3 | 150mm diameter, approx. 4.5m ductile piping | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1975 |  | 0 | HR-CNRY-116 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-18 13:09 |  |  |  |  | Pumping | Discharge Header | 1 |  | 240_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | The pipe is at half of its expected service life.
241 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 137 | Pump 2 Piping | 3 | 150mm diameter, approx. 4.5m ductile piping | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1975 |  | 0 | HR-CNRY-116 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-18 13:10 |  |  |  |  | Pumping | Discharge Header | 2 |  | 241_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | The pipe is at half of its expected service life.
242 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 27 | Overflow Piping | 3 | 250mm diameter, approx. 10.5 m (4.5 m PVC pipe, 6 m CMP pipe) | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Site | Process Mechanical | Process Piping |  | Piping, PVC |  |  |  |  | 0 | 1983 | [10 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 13:22 | [6 empty] | Pumping | Wet Well |  |  | 242_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Good
243 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 146 | Pump 1 Piping | 3 | 150mm diameter, approx. 5m ductile iron pipe | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1983 |  |  | HR-CTWL-033 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 13:25 | Maira Rafiq | 2020-09-20 13:45 |  |  |  |  | Pumping | Pump Assembly |  |  | 243_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Minor corrosion
244 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 633 | Bar Screen | 2 | Bar Screen;;;; | Halton |  | Chartwell Rd. PS | Chartwell Rd. PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Screen |  |  |  |  | 0 | 1983 |  |  | HR-CTWL-054 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 15:25 | Maira Rafiq | 2020-09-20 13:47 |  |  |  |  | Pumping | Wet Well |  |  | 244_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | corrosion
247 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 30 | Overflow Piping | 3 | 300mm diameter, approx. 2.5m CMP pipe | Halton | In Service | Cumnock PS | Cumnock PS | Site | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1974 |  |  | HR-CMNK-147 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 14:33 | Maira Rafiq | 2020-09-21 15:36 |  |  |  |  | Pumping | Wet Well |  |  | 247_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Good | The pipe was at half of its expected service life.
248 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 160 | Pump 1 Piping | 3 | 100mm diameter, approx. 5m ductile pipe | Halton | In Service | Cumnock PS | Cumnock PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1974 |  |  | HR-CMNK-010 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 14:33 | Maira Rafiq | 2020-09-21 15:41 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 248_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | The pipe was at half of its expected service life.
249 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 641 | Bar Screen | 2 | Bar Screen | Halton | In Service | Cumnock PS | Cumnock PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1974 |  |  | HR-CMNK-136 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 14:36 | Maira Rafiq | 2020-09-21 15:41 |  |  |  |  | Pumping | Wet Well |  |  | 249_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | good
250 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 640 | Discharge Header | 3 | 100mm diameter, approx. 5m, ductile iron stand pipe | Halton |  | Cumnock PS | Cumnock PS | Dry Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1974 |  | 0 | [8 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-21 15:41 |  |  |  |  | Pumping | Discharge Header |  |  | 250_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Good
251 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 33 | Overflow Piping | 3 | 200mm diameter, approx. 22m | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Site | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1977 | [10 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 15:13 | Maira Rafiq | 2020-09-21 17:15 |  |  |  |  | Pumping | Wet Well |  |  | 251_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Assumed to be fair | The pipe was at half of its expected service life
252 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 174 | Pump 1 Piping | 3 | 100mm diameter, approx. 5 m | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1977 |  |  | HR-ENIS-013 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 15:15 | Maira Rafiq | 2020-09-21 17:16 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 252_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Heavy corrosion was observed on the surface of the pipe
253 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 399 | Pump 2 Piping | 3 | 100mm diameter, approx. 5m | Halton |  | Ennisclaire Drive PS | WWPS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1977 |  | 0 | HR-ENIS-013 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-21 17:18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 253_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Heavy corrosion was observed on the surface of the pipe
254 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 38 | Overflow Piping | 3 | 250mm diameter, approx. 3.5 m connect to storm sewer | Halton | In Service | First Street PS | First Street PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1986 |  |  | HR-FRST-012 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:46 | Maira Rafiq | 2020-09-21 23:36 |  |  |  |  | Pumping | Suction |  |  | 254_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Good
255 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 35 | Emergency Pumping Riser | 3 | 100mm diameter, approx. 1.6m | Halton |  | First Street PS | First Street PS |  | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1986 | [10 empty] | 1 | ea. | 2020 | [18 empty] | Pumping | Discharge Header |  |  | 255_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
256 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 182 | Pump 1 Piping | 3 | 100mm diameter, approx. 5 m ductile iron pipe | Halton | In Service | First Street PS | First Street PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1986 |  |  | HR-FRST-013 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:48 | Maira Rafiq | 2020-09-21 23:38 |  |  |  |  | Pumping | Suction |  |  | 256_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Good
257 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 187 | Pump 2 Piping | 3 | 100mm diameter, approx. 3m ductile iron pipe | Halton | In Service | First Street PS | First Street PS |  | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1986 |  | 0 | [8 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-21 23:38 |  |  |  |  | Pumping | Pump Assembly |  |  | 257_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Good
258 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 643 | Discharge Header | 3 | 100mm diameter, approx. 7m ductile iron | Halton | In Service | First Street PS | First Street PS | Dry Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1986 |  | 0 | [8 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-21 23:38 |  |  |  |  | Pumping | Discharge Header |  |  | 258_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Good
259 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 40 | Overflow Piping | 3 | 300mm diameter, approx. 6m | Halton |  | Garlock Gdns PS | Garlock Gdns PS | Site | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1977 | [10 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 17:06 | [6 empty] | Pumping | Wet Well |  |  | 259_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | The pipe was at half of its expected service life.
260 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 53 | Pump 1 Discharge Piping | 3 | 100mm diameter, approx. 5m ductile pipe | Halton | In Service | Garlock Gdns PS | Garlock Gdns PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1977 |  |  | HR-GGDN-014 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 17:08 | Maira Rafiq | 2020-09-22 11:02 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 260_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Heavy corrosion was observed on the pipe
261 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 57 | Pump 2 Discharge Piping | 3 | 100mm diameter, approx. 5m ductile pipe | Halton | In Service | Garlock Gdns PS | Garlock Gdns PS | Dry Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1977 |  | 0 | [8 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-22 11:04 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 261_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Heavy corrosion was observed on the pipe
262 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 43 | Overflow Piping | 3 | 150mm diameter, approx. 9 m overflow piping | Halton | In Service | Morrison Heights PS | Morrison Heights PS | Site | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1973 |  |  | HR-MORI-123 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 11:43 | Maira Rafiq | 2020-09-22 12:14 |  |  |  |  | Pumping | Wet Well |  |  | 262_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | The pipe passed half of its expected service life.
263 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 72 | Pump 1 Piping | 3 | Ductile Iron, 100mm dia, 5 m length | Halton |  | Morrison Heights PS | Morrison Heights PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1973 |  |  | HR-MORI-115 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 11:46 | Maira Rafiq | 2020-09-22 12:17 |  |  |  |  | Pumping | Suction | 1 |  | 263_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Minor deterioration was observed on the pipe and it passed half of its expected service life.
264 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 78 | Pump 2 Piping | 3 | Ductile Iron, 100mm dia, 5 m length | Halton |  | Morrison Heights PS | Morrison Heights PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1973 |  | 0 | HR-MORI-115 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-22 12:18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 264_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Minor deterioration was observed on the pipe and it passed half of its expected service life.
265 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 646 | Discharge Piping | 3 | Ductile Iron, 100mm dia, 5 m length | Halton |  | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1973 |  | 0 | HR-MORI-115 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-22 12:19 |  |  |  |  | Pumping | Wet Well |  |  | 265_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Minor deterioration was observed on the pipe and it passed half of its expected service life.
266 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 648 | Overflow Piping | 3 | 100mm diameter, approx. 4.5m | Halton | In Service | Raymar Pl PS | Raymar Pl PS | Wetwell | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1985 | [10 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 14:55 | Maira Rafiq | 2020-09-22 13:15 |  |  |  |  | Pumping | Wet Well |  |  | 266_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | assumed to be good
267 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 62 | Pump 1 Discharge Piping | 3 | 100mm diameter, approx. 5m ductile pipe | Halton |  | Raymar Pl PS | Raymar Pl PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1985 |  | 0 | HR-RAYM-040 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-22 13:21 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 267_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Heavy corrosion and deterioration was observed
268 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 65 | Pump 2 Discharge Piping | 3 | 100mm diameter, approx. 8.6 m ductile iron pipe | Halton | In Service | Raymar Pl PS | Raymar Pl PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1985 |  |  | HR-RAYM-040 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 14:58 | Maira Rafiq | 2020-09-22 13:21 |  |  |  |  | Pumping | Wet Well | 2 |  | 268_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Heavy corrosion and deterioration was observed
301 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 639 | Wet Well Concrete Structure | 2 |  | Halton | In Service | Chancery Lane PS | WWPS | Process Structural | Process Structural | Building and Process Structural |  | Tank, Concrete | [5 empty] | 1975 |  |  | HR-CNRY-033 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:20 | Maira Rafiq | 2020-09-18 11:01 |  |  |  |  | Pumping | Wet Well | 1 |  | 302_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Rust spots noted | Fair
302 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Dry Well Access Hatch | 1 | Chancery Lane PS Dry Well | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1975 |  | 2035 | HR-CNRY-037 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:20 | Maira Rafiq | 2020-09-18 11:01 |  |  |  |  | Building | Substructure | 1 |  | 303_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | minor corrosion and paint wear
303 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Dry Well Access Ladder | 2 | Chancery Lane PS Dry Well | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1975 |  | 2035 | HR-CNRY-004 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:20 | Maira Rafiq | 2020-09-18 11:00 |  |  |  |  | Building | Substructure | 1 |  | 304_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | minor paint wear
304 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Protective Paint | 1 | Chancery Lane PS Dry Well | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Misc. Structural | [5 empty] | 1975 |  | 2035 | HR-CNRY-041 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:20 | Maira Rafiq | 2020-09-18 11:00 |  |  |  |  | Building | Interior Finishes | 1 |  | 305_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Peeling paint on exterior | Fair
305 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 639 | Manhole Frame and Cover | 1 |  | Halton | In Service | Chancery Lane PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Misc. Structural | [5 empty] | 1975 |  |  | HR-CNRY-035 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:21 | Maira Rafiq | 2020-09-18 11:00 |  |  |  |  | Pumping | Wet Well | 1 |  | 307_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | minor corrosion on the underside
306 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 639 | Wet Well Access Ladder | 2 |  | Halton | In Service | Chancery Lane PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1975 |  | 2035 | HR-CNRY-033 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:21 | Maira Rafiq | 2020-09-18 11:01 |  |  |  |  | Pumping | Wet Well | 1 |  | 308_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
307 |  |  |  | 0 |  |  |  |  | 0 |  |  | TRUE | FALSE | FALSE | FALSE | 639 | Wet Well Aluminum Platform | 2 |  | Halton | In Service | Chancery Lane PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1975 |  | 2035 | HR-CNRY-033 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:21 | Maira Rafiq | 2020-09-18 11:00 |  |  |  |  | Pumping | Wet Well | 1 |  | 309_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Corrosion noted | Fair
308 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 639 | Wet Well Aluminum Guardrail | 2 |  | Halton | In Service | Chancery Lane PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1975 |  | 2035 | HR-CNRY-033 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:21 | Maira Rafiq | 2020-09-18 11:00 |  |  |  |  | Pumping | Wet Well | 1 |  | 310_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Corrosion noted | Fair
309 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Davit Socket Base | 2 |  | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Misc. Structural | [5 empty] | 1975 |  | 2035 | HR-CNRY-037 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:21 | Maira Rafiq | 2020-09-18 11:00 |  |  |  |  | Building |  | 1 |  | 312_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | To be inspected yearly | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
317 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Dry Well Access Ladder | 2 | Chartwell Rd. PS Dry Well | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1983 |  | 2046 | HR-CTWL-024 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:29 | Maira Rafiq | 2020-09-18 14:03 |  |  |  |  | Building | Interior Construction | 1 |  | 320_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Minor corrosion and paint wear
318 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Dry Well Access Hatch | 1 | Chartwell Rd. PS Dry Well | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1983 |  | 2046 | HR-CTWL-023 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:29 | Maira Rafiq | 2020-09-18 14:06 |  |  |  |  | Building | Interior Construction | 1 |  | 321_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | paint wear
319 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Dry Well Davit Socket Base | 2 |  | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1983 |  | 2046 | HR-CTWL-023 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:29 | Maira Rafiq | 2020-09-20 10:17 |  |  |  |  | Building | Conveying (Elevators, Cranes) | 1 |  | 322_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | To be inspected every year | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
320 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 633 | Wet Well Access Hatch | 1 |  | Halton | In Service | Chartwell Rd. PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1983 |  | 2046 | HR-CTWL-025 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:30 | Maira Rafiq | 2020-09-20 10:17 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 323_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Surface corrosion noted on underside | Fair
321 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 633 | Wet Well Davit Socket Base | 2 |  | Halton | In Service | Chartwell Rd. PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1983 |  | 2046 | HR-CTWL-025 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:30 | Maira Rafiq | 2020-09-20 10:18 |  |  |  |  | Building |  | 1 |  | 324_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | To be inspected every year | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
322 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 633 | Wet Well Access Ladder | 2 |  | Halton | In Service | Chartwell Rd. PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1983 |  | 2046 | HR-CTWL-073 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:30 | Maira Rafiq | 2020-09-20 10:18 |  |  |  |  | Pumping | Wet Well | 1 |  | 325_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Bent ladder rung | Fair
323 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 633 | Checker Plate Platform | 2 |  | Halton | In Service | Chartwell Rd. PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1983 |  | 2036 | HR-CTWL-073 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:30 | Maira Rafiq | 2020-09-20 10:18 |  |  |  |  | Pumping | Wet Well | 1 |  | 326_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Corrosion noted | Fair
324 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Dry Well Protective Paint | 1 |  | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Misc. Structural | [5 empty] | 1983 |  | 2046 | HR-CTWL-024 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:31 | Maira Rafiq | 2020-09-20 10:20 |  |  |  |  | Building | Interior Finishes | 1 |  | 327_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Weathered paint on exterior and minor corrosion inside | Fair
325 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 31 | Wet Well Access Ladder | 2 | Cumnock PS Wet Well | Halton | In Service | Cumnock PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1974 |  | 2034 | HR-CMNK-156 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:39 | Maira Rafiq | 2020-09-21 13:57 |  |  |  |  | Pumping | Wet Well | 1 |  | 328_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
326 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 641 | Wet Well Checker Plate Platform | 2 | Cumnock PS Wet Well | Halton | In Service | Cumnock PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1974 |  | 2034 | HR-CMNK-157 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:39 | Maira Rafiq | 2020-09-21 13:58 |  |  |  |  | Pumping | Wet Well | 1 |  | 329_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | discoloration of the checker plate
327 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 641 | Manhole Frame and Cover | 1 | Cumnock PS Wet Well | Halton | In Service | Cumnock PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1974 |  | 2034 | HR-CMNK-095 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:39 | Maira Rafiq | 2020-09-20 22:13 |  |  |  |  | Pumping | Wet Well | 1 |  | 330_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
328 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Dry Well Access Hatch | 1 | Cumnock PS Dry Well | Halton | In Service | Cumnock PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1974 |  | 2034 | HR-CMNK-033 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:39 | Maira Rafiq | 2020-09-20 22:14 |  |  |  |  | Building | Substructure | 1 |  | 331_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | weathered paint
329 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Dry Well Access Ladder | 2 | Cumnock PS Dry Well | Halton | In Service | Cumnock PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1974 |  | 2034 | HR-CMNK-128 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:42 | Maira Rafiq | 2020-09-20 22:16 |  |  |  |  | Building | Substructure | 1 |  | 332_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Minor corrosion
330 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | TRUE | FALSE | FALSE | 640 | Dry Aluminum Grating | 2 | Cumnock PS Dry Well | Halton | In Service | Cumnock PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1974 |  | 2034 | HR-CMNK-126 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:43 | Maira Rafiq | 2020-09-20 22:18 |  |  |  |  | Building | Substructure | 1 |  | 333_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair based on age
331 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Protective Paint | 1 | Cumnock PS Dry Well | Halton | In Service | Cumnock PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Misc. Architectural | [5 empty] | 1974 |  | 2034 | HR-CMNK-126 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:47 | Maira Rafiq | 2020-09-20 22:21 |  |  |  |  | Building | Interior Finishes | 1 |  | 334_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Peeling paint on exterior and corrosion | Fair
332 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Davit Socket Base | 2 | Cumnock PS Dry Well | Halton | In Service | Cumnock PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Misc. Structural | [5 empty] | 1974 |  | 2034 | HR-CMNK-035 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:48 | Maira Rafiq | 2020-09-20 22:24 |  |  |  |  | Building |  | 1 |  | 335_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | To be inspected every year | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
333 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 642 | Wet Well Access Hatch | 1 | Ennisclaire Drive PS Wet Well | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1977 |  |  | HR-ENIS-001 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:55 | Maira Rafiq | 2020-09-21 16:57 |  |  |  |  | Pumping | Wet Well | 1 |  | 336_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
334 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 642 | Wet Well Access Ladder | 2 | Ennisclaire Drive PS Wet Well | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1977 |  | 2036 | HR-ENIS-002 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:55 | Maira Rafiq | 2020-09-21 16:57 |  |  |  |  | Pumping | Wet Well | 1 |  | 337_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Staining/corrosion noted | Fair
335 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 642 | Wet Well Aluminum Platform | 2 | Ennisclaire Drive PS Wet Well | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1977 |  |  | HR-ENIS-004 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:55 | Maira Rafiq | 2020-09-21 16:57 |  |  |  |  | Pumping | Wet Well | 1 |  | 338_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Minor corrosion
336 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 642 | Wet Well Aluminum Guardrail | 2 | Ennisclaire Drive PS Wet Well | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1977 |  | 2036 | HR-ENIS-002 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:55 | Maira Rafiq | 2020-09-21 16:59 |  |  |  |  | Pumping | Wet Well | 1 |  | 339_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | minor corrosion
337 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 642 | Davit Socket Base | 2 | Ennisclaire Drive PS Wet Well | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1977 |  |  | HR-ENIS-001 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:55 | Maira Rafiq | 2020-09-21 17:00 |  |  |  |  | Building |  | 1 |  | 340_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | To be inspected every year. As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year. | Fair
338 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 644 | Wet Well Access Ladder | 2 | First Street PS Wet Well | Halton | In Service | First Street PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1986 |  | 2046 | HR-FRST-094 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:15 | Maira Rafiq | 2020-09-21 19:13 |  |  |  |  | Pumping | Wet Well | 1 |  | 341_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair
339 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 644 | Wet Well Aluminum Platform | 2 | First Street PS Wet Well | Halton | In Service | First Street PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1986 |  | 2046 | HR-FRST-094 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:15 | Maira Rafiq | 2020-09-21 19:14 |  |  |  |  | Pumping | Wet Well | 1 |  | 342_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fixed portion of platform grating was noted to be bent | Fair
340 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 644 | Manhole Frame and Cover | 1 | First Street PS Wet Well | Halton | In Service | First Street PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1986 |  |  | HR-FRST-097 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:16 | Maira Rafiq | 2020-09-21 19:14 |  |  |  |  | Pumping | Wet Well | 1 |  | 343_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair
341 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 644 | Davit Socket Base | 2 | First Street PS Wet Well | Halton | In Service | First Street PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Misc. Structural | [5 empty] | 1986 |  | 2046 | HR-FRST-098 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:16 | Maira Rafiq | 2020-09-21 19:15 |  |  |  |  | Pumping | Wet Well | 1 |  | 344_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | To be inspected every year. As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year. | Fair
342 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 643 | Dry Well Access Hatch | 1 | First Street PS Dry Well | Halton | In Service | First Street PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1986 |  | 2046 | HR-FRST-029 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:16 | Maira Rafiq | 2020-09-21 19:19 |  |  |  |  | Building | Substructure | 1 |  | 345_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | corrosion and paint wear
343 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 643 | Dry Well Access Ladder | 2 | First Street PS Dry Well | Halton |  | First Street PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1986 |  | 2046 | HR-FRST-019 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:16 | Maira Rafiq | 2020-09-21 19:19 |  |  |  |  | Building | Substructure | 1 |  | 346_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Minor corrosion
344 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 643 | Protective Paint | 1 | First Street PS Dry Well | Halton | In Service | First Street PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Misc. Architectural | [5 empty] | 1986 |  |  | HR-FRST-019 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:16 | Maira Rafiq | 2020-09-21 19:20 |  |  |  |  | Building | Interior Finishes | 1 |  | 347_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Flaking/missing on exterior | Fair
345 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 643 | Dry Well Davit Socket Base | 2 | First Street PS Dry Well | Halton | In Service | First Street PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1986 |  | 2046 | HR-FRST-029 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:16 | Maira Rafiq | 2020-09-21 19:21 |  |  |  |  | Building |  | 1 |  | 348_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | To be inspected every year. As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
346 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 645 | Wet Well Access Hatch | 1 | Garlock Gdns PS Wet Well | Halton | In Service | Garlock Gdns PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1977 |  |  | HR-GGDN-023 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:24 | Maira Rafiq | 2020-09-22 10:47 |  |  |  |  | Pumping | Wet Well | 1 |  | 349_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Good
347 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 645 | Wet Well Access Ladder | 2 | Garlock Gdns PS Wet Well | Halton | In Service | Garlock Gdns PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1977 |  | 2040 | HR-GGDN-088 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:24 | Maira Rafiq | 2020-09-22 10:48 |  |  |  |  | Pumping | Wet Well | 1 |  | 350_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Pitting noted | Fair
348 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 645 | Wet Well Davit Socket Base | 2 | Garlock Gdns PS Wet Well | Halton | In Service | Garlock Gdns PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1977 |  |  | HR-GGDN-023 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:24 | Maira Rafiq | 2020-09-22 10:49 |  |  |  |  | Pumping | Wet Well | 1 |  | 351_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | To be inspected yearly. As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
349 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 645 | Wet Well Aluminum Platform | 2 | Garlock Gdns PS Wet Well | Halton | In Service | Garlock Gdns PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1977 |  | 2040 | HR-GGDN-088 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:24 | Maira Rafiq | 2020-09-22 10:49 |  |  |  |  | Pumping | Wet Well | 1 |  | 352_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Calcium buildup and pitting noted | fair
350 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 646 | Dry Well Access Hatch | 1 | Morrison Heights PS Dry Well | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1973 |  | 2033 | HR-MORI-096 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:29 | Maira Rafiq | 2020-09-22 11:25 |  |  |  |  | Building | Substructure | 1 |  | 353_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | paint wear
351 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 646 | Dry Well Access Ladder | 2 | Morrison Heights PS Dry Well | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1973 |  | 2033 | HR-MORI-097 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:29 | Maira Rafiq | 2020-09-22 11:27 |  |  |  |  | Building | Substructure | 1 |  | 354_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | minor corrosion
352 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 42 | Dry Well Davit Socket Base | 2 | Morrison Heights PS Dry Well | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1973 |  | 2033 | HR-MORI-096 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:29 | Maira Rafiq | 2020-09-22 11:27 |  |  |  |  | Building | Substructure | 1 |  | 355_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair
353 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 646 | Protective Paint | 1 | Morrison Heights PS Dry Well | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Misc. Architectural | [5 empty] | 1973 |  | 2033 | HR-MORI-097 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:29 | Maira Rafiq | 2020-09-22 11:28 |  |  |  |  | Building | Interior Finishes | 1 |  | 356_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Weathered paint and missing paint on exterior
354 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 647 | Manhole Frame and Cover | 1 | Morrison Heights PS Wet Well | Halton | In Service | Morrison Heights PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1973 |  | 2033 | HR-MORI-001 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:29 | Maira Rafiq | 2020-09-22 11:28 |  |  |  |  | Pumping | Wet Well | 1 |  | 357_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair
355 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 647 | Wet Well Access Ladder | 2 | Morrison Heights PS Wet Well | Halton | In Service | Morrison Heights PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1973 |  | 2033 | HR-MORI-001 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:30 | Maira Rafiq | 2020-09-22 11:28 |  |  |  |  | Pumping | Wet Well | 1 |  | 358_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair
356 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 647 | Wet Well Davit Socket Base | 2 | Morrison Heights PS Wet Well | Halton | In Service | Morrison Heights PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1973 |  | 2033 | HR-MORI-001 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:30 | Maira Rafiq | 2020-09-22 11:29 |  |  |  |  | Pumping | Wet Well | 1 |  | 359_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Anchors were corroded
357 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Wet Well Access Hatch | 1 | Raymar Pl PS Wet Well | Halton | In Service | Raymar Pl PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1985 |  |  | HR-RAYM-029 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:32 | Maira Rafiq | 2020-09-22 12:47 |  |  |  |  | Pumping | Wet Well | 1 |  | 360_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | minor corrosion and staining
358 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Pump Hatch 1 | 1 | Raymar Pl PS Wet Well | Halton | In Service | Raymar Pl PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1985 |  |  | HR-RAYM-029 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:32 | Maira Rafiq | 2020-09-22 12:52 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 361_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Missing safety grating. The Pump Hatch 1 was missing grating. Under Ontario Regulation 213/91 this presents a fall hazard when the hatches are left open.
359 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Pump Hatch 2 | 1 | Raymar Pl PS Wet Well | Halton |  | Raymar Pl PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1985 |  |  | HR-RAYM-029 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:32 | Maira Rafiq | 2020-09-22 12:52 |  |  |  |  | Pumping | Wet Well | 2 |  | 362_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Missing safety grating. The Pump Hatch 1 was missing grating. Under Ontario Regulation 213/91 this presents a fall hazard when the hatches are left open.
360 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Wet Well Access Ladder | 2 | Exterior to platform | Halton |  | Raymar Pl PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1985 |  |  | HR-RAYM-054 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:32 | Maira Rafiq | 2020-09-22 12:51 |  |  |  |  | Pumping | Wet Well | 1 |  | 363_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Calcium buildup and corrosion noted | Fair
361 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | We Well Access Ladder | 2 | Platform to base | Halton | In Service | Raymar Pl PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1985 |  |  | HR-RAYM-054 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:32 | Maira Rafiq | 2020-09-22 12:54 |  |  |  |  | Pumping | Wet Well | 1 |  | 364_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Calcium buildup and corrosion noted | Fair
362 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Wet Well Aluminum Platform | 2 | Raymar Pl PS Wet Well | Halton | In Service | Raymar Pl PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1985 |  |  | HR-RAYM-054 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:32 | Maira Rafiq | 2020-09-22 12:54 |  |  |  |  | Pumping | Wet Well | 1 |  | 365_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Gratings now clipped down | Corrosion noted | Fair
363 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Wet Well Davit Socket Base | 2 | Raymar Pl PS Wet Well | Halton |  | Raymar Pl PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1985 |  |  | HR-RAYM-029 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:32 | Maira Rafiq | 2020-09-22 12:56 |  |  |  |  | Pumping | Wet Well | 1 |  | 366_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | To be inspected every year. As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
382 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 643 | Dry Well Concrete Foundation | 2 | First Street PS Dry Well | Halton | In Service | First Street PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Tank, Concrete | [5 empty] | 1986 | [10 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-15 11:29 | Maira Rafiq | 2020-09-21 19:21 |  |  |  |  | Building | Superstructure | 1 |  | 385_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Not visible/inspected. Assumed to be good as no settlement was noted. | Good
383 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Dry Well Concrete Foundation | 2 | Cumnock PS Dry Well | Halton | In Service | Cumnock PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Misc. Structural | [5 empty] | 1974 | [10 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-15 12:58 | Maira Rafiq | 2020-09-20 22:20 |  |  |  |  | Building | Superstructure | 1 |  | 386_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Not visible/inspected. Assumed to be good as no settlement was noted.
384 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Dry Well Concrete Foundation | 2 | Chartwell Rd. PS Dry Well | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Misc. Structural | [5 empty] | 1983 |  | 2043 | [8 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-15 13:15 | Maira Rafiq | 2020-09-20 10:20 |  |  |  |  | Building | Substructure | 1 |  | 387_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Not visible/inspected. Assumed to be good as no settlement was noted.
385 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Dry Well Concrete Foundation | 2 | Chancery Lane PS Dry Well | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Building Structural | Building and Process Structural |  | Reinforced Concrete | [5 empty] | 1975 | [10 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-15 15:07 | Maira Rafiq | 2020-09-18 11:24 |  |  |  |  | Building | Substructure | 1 |  | 388_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Not visible/inspected. Assumed to be good as no settlement was noted
387 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 41 | Grab Bar |  | Garlock Gdns PS Wet Well | Halton | In Service | Garlock Gdns PS | WWPS | Wet Well | Building Structural | Building and Process Structural | [7 empty] | 1977 |  | 2036 | HR-GGDN-023 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:25 | [8 empty] | 1 |  | 390_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Good
392 |  |  | 211127 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 32 | VALVE KNIFE GATE SEWAGE LIFT PUMP #2 | 2 | Knife Gate Valve #2;;;;100 mm dia | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Dry Well |  | Process Mechanical Equipment |  | Valve | [5 empty] | 1977 |  |  | HR-ENIS-013 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 15:09 | [8 empty] | 1 |  | 279_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Very Poor | Severe corrosion was observed on the surface of the valve. The valve was beyond its expected service life
393 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 32 | PUMP #2 SEWAGE LIFT | 2 | Sewage Pump #2;Flygt;C3082MT;;7.8 L/s at 7.2 m TDH 2hp | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Dry Well |  | Process Mechanical Equipment |  | Pump, Centrifugal | [5 empty] | 1977 |  |  | HR-ENIS-009 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 15:19 | [8 empty] | 1 |  | 280_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | The pump was beyond its expected service life.
394 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 32 | VALVE CHECK SEWAGE LIFT PUMP #2 | 2 | Check Valve #2;;;;100 mm dia | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Dry Well |  | Process Mechanical Equipment |  | Valve | [5 empty] | 1977 |  |  | HR-ENIS-014 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 15:19 | [8 empty] | 1 |  | 281_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Very Poor | Severe corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
395 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 32 | VALVE KNIFE GATE SEWAGE LIFT PUMP #2 | 2 | Knife Gate Valve #2;;;;100 mm dia | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Dry Well |  | Process Mechanical Equipment |  | Valve | [5 empty] | 1977 |  |  | HR-ENIS-013 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 15:20 | [8 empty] | 1 |  | 282_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Very Poor | Severe corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
396 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 32 | Bar Screen | 2 | Bar Screen;;;;6.5'X3.25' | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Dry Well |  | Process Mechanical Equipment |  | Valve | [5 empty] | 1977 |  |  | HR-ENIS-015 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 15:23 | [8 empty] | 1 |  | 283_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Minor deterioration was observed on the bar screen.
397 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 32 | PUMP #2 SEWAGE LIFT | 2 | Sewage Pump #2;Flygt;C3082MT;;7.8 L/s at 7.2 m TDH 2hp | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Dry Well |  | Process Mechanical Equipment |  | Pump, Centrifugal | [5 empty] | 1977 |  |  | HR-ENIS-009 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 15:26 | [8 empty] | 1 |  | 284_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | The pump was beyond its expected service life.
399 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 642 | Sewage Lift Pump #2 | 2 | Sewage Pump #1;Flygt;C3082MT;;7.8 L/s at 7.2 m TDH 2hp | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | pump | [5 empty] | 1977 |  |  | HR-ENIS-009 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:01 | Maira Rafiq | 2020-09-21 17:24 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 286_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | poor | The pump was beyond its expected service life
400 |  |  | 201607 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 32 | VALVE CHECK SEWAGE LIFT PUMP #2 | 2 | Check Valve #2;;;;100 mm dia | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Dry Well |  | Process Mechanical Equipment |  | Valve | [5 empty] | 1977 |  |  | HR-ENIS-014 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:03 | [8 empty] | 1 |  | 287_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Severe corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
401 |  |  | 211127 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 32 | VALVE KNIFE GATE SEWAGE LIFT PUMP #1 | 2 | Knife Gate Valve #1;;;;100 mm dia | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Dry Well |  | Process Mechanical Equipment |  | Valve | [5 empty] | 1977 |  |  | HR-ENIS-012 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:03 | [8 empty] | 1 |  | 288_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
402 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 399 | Sewage Lift Pump #2 Check Valve | 2 | Check Valve #1;;;;100 mm dia | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Valve | [5 empty] | 1977 |  |  | HR-ENIS-014 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:05 | Maira Rafiq | 2020-09-21 17:23 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 289_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Heavy corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
403 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 399 | Sewage Lift Pump #2 Knife Gate Valve | 2 | Knife Gate Valve #2;;;;100 mm dia | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Valve | [5 empty] | 1977 |  |  | HR-ENIS-013 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:07 | Maira Rafiq | 2020-09-21 17:23 |  |  |  |  | Pumping | Wet Well | 2 |  | 290_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Very Poor | Severe corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
404 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 645 | Bar Screen | 2 | Bar Screen;;;; | Halton | In Service | Garlock Gdns PS | Garlock Gdns PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Piping, DI/CPP/Steel/SS | [5 empty] | 1977 |  |  | HR-GGDN-013 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 17:09 | Maira Rafiq | 2020-09-22 11:10 |  |  |  |  | Pumping | Wet Well | 1 |  | 292_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Debris is clogging at the bar screen, which in terms start clogging the inlet pipe.
405 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 46 | VALVE DISCHARGE #3 | 2 | Gate Valve #3;;;;100 mm dia | Halton | In Service | Raymar Pl PS | Raymar Pl PS | Wet Well |  | Process Mechanical Equipment |  | Valve | [5 empty] | 1985 |  |  | HR-RAYM-017 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 14:51 | [8 empty] | 1 |  | 293_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the valve. The valve was near the end of its expected service life.
406 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Discharge Valve #3 | 2 | Gate Valve #3;;;;100 mm dia | Halton | In Service | Raymar Pl PS | WWPS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Valve | [5 empty] | 1985 |  |  | HR-RAYM-017 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 15:10 | Maira Rafiq | 2020-09-22 13:20 |  |  |  |  | Pumping | Discharge Header | 1 |  | 294_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the valve
422 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Remote Signal Telephone Transmitter | 1 | Remote Signal Telephone Transmitter; Pribusin; IUC-X9-TXC; ; ; | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation |  | Transmitter | [5 empty] | 2009 |  | 2009 | HR-CNRY-108 |  |  |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 16:03 | Maira Rafiq | 2020-08-24 08:45 |  |  |  |  | Communications | Telephone/IT | 1 |  | 288_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | obsolete
423 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 639 | Wet Well Floats | 2 | Wet Well Floats; ; ; ; ; | Halton | In Service | Chancery Lane PS | WWPS | Wet Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2009 |  | 2030 | HR-CNRY-064 |  |  |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 16:06 | Maira Rafiq | 2020-08-24 08:46 |  |  |  |  | Pumping | Wet Well | 1 |  | 289_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
424 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Sump Float | 2 | Sump Float; ; ; ; ; | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2009 |  |  | HR-CNRY-132 |  |  |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 16:09 | Maira Rafiq | 2020-08-24 08:47 |  |  |  |  | Building | Plumbing - Sanitary Waste | 1 |  | 290_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Dust | good
429 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 633 | Wet Well Float | 2 | Wet Well Float; ; ; ; ; | Halton | In Service | Chartwell Rd. PS | WWPS | Wet Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2019 |  | 2025 | HR-CTWL-065 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 16:32 | Maira Rafiq | 2020-09-20 10:52 |  |  |  |  | Pumping | Suction Header | 1 |  | 295_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
430 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Sump Float | 1 | Sump Float; ; ; ; ; | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2019 |  | 2025 | HR-CTWL-016 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 16:34 | Maira Rafiq | 2020-09-20 10:52 |  |  |  |  | Building | Plumbing - Sanitary Waste | 1 |  | 296_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
431 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Remote Signals Telephone Transmitter | 1 | Remote Signals Telephone Transmitter; Pribusin; IUC-X9-TXC; ; ; | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation |  | Transmitter | [5 empty] | 2016 |  | 2030 | HR-CTWL-128 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 16:47 | Maira Rafiq | 2020-08-21 16:16 |  |  |  |  | Communications | Telephone/IT | 1 |  | 297_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
432 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Sump Float | 2 | Sump Float; ; ; ; ; | Halton | In Service | Cumnock PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2009 |  | 2030 | HR-CMNK-023 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 17:05 | Maira Rafiq | 2020-08-24 08:57 |  |  |  |  | Building | Plumbing - Sanitary Waste | 1 |  | 298_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
433 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Remote Signals Telephone Transmitter | 1 | Remote Signals Telephone Transmitter; Pribusin; IUC-X9-TXC; ; ; | Halton | In Service | Cumnock PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation |  | Transmitter | [5 empty] | 2016 |  |  | HR-CMNK-079 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 17:07 | Maira Rafiq | 2020-08-24 08:58 |  |  |  |  | Communications | Telephone/IT | 1 |  | 299_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | very good
434 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 641 | Wet Well Floats | 2 | Wet Well Floats; ; ; ; ; | Halton | In Service | Cumnock PS | WWPS | Wet Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2009 |  | 2030 | HR-CMNK-152 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 17:11 | Maira Rafiq | 2020-08-24 08:59 |  |  |  |  | Pumping | Wet Well | 1 |  | 300_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
435 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 33 | Remote Signals Telephone Transmitter | 1 | Remote Signals Telephone Transmitter; Pribusin; IUC-X9-TXC; ; ; | Halton | In Service | Ennisclaire Drive PS | WWPS | Site | Process Instrumentation | Process Instrumentation |  | Transmitter | [5 empty] | 2009 |  | 2030 | HR-ENIS-038 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 17:45 | Maira Rafiq | 2020-08-24 09:03 |  |  |  |  | Communications | Telephone/IT | 1 |  | 301_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | obsolete
436 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 642 | Wet Well Floats | 2 | Wet Well Floats; ; ; ; ; | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2009 |  | 2030 | HR-ENIS-081 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 17:47 | Maira Rafiq | 2020-08-24 09:03 |  |  |  |  | Pumping | Wet Well | 1 |  | 302_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
437 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 643 | Sump Float | 2 | Sump Float; ; ; ; ; | Halton | In Service | First Street PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2009 |  | 2030 | HR-FRST-024 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 17:52 | Maira Rafiq | 2020-08-24 09:10 |  |  |  |  | Building | Plumbing - Sanitary Waste | 1 |  | 303_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
438 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 643 | Remote Signals Telephone Transmitter | 1 | Remote Signals Telephone Transmitter; Pribusin; IUC-X9-TXC; ; ; | Halton | In Service | First Street PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation |  | Transmitter | [5 empty] | 2016 |  | 2030 | HR-FRST-153 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 17:55 | Maira Rafiq | 2020-08-24 09:11 |  |  |  |  | Communications | Telephone/IT | 1 |  | 304_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
439 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 644 | Wet Well Float | 2 | Wet Well Float; ; ; ; ; | Halton | In Service | First Street PS | WWPS | Wet Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2019 |  | 2030 | HR-FRST-088 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 17:58 | Maira Rafiq | 2020-08-24 09:11 |  |  |  |  | Pumping | Wet Well | 1 |  | 305_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Good
440 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 645 | Wet Well Level Transmitter | 2 | Wet Well Level Transmitter; Siemens Milltronics; Multiranger 100; ; ; | Halton | In Service | Garlock Gdns PS | WWPS | Site | Process Instrumentation | Process Instrumentation |  | Transmitter | [5 empty] | 2009 |  | 2030 | HR-GGDN-039 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 18:03 | Maira Rafiq | 2020-08-24 09:15 |  |  |  |  | Pumping | Wet Well | 1 |  | 306_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
441 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 40 | Remote Signals Telephone Transmitter | 1 | Remote Signals Telephone Transmitter; Pribusin; IUC-X9-TXC; ; ; | Halton | In Service | Garlock Gdns PS | WWPS | Site | Process Instrumentation | Process Instrumentation |  | Transmitter | [5 empty] | 2016 |  | 2030 | HR-GGDN-076 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 18:06 | Maira Rafiq | 2020-08-24 09:15 |  |  |  |  | Communications | Telephone/IT | 1 |  | 307_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
442 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 645 | Wet Well Floats | 2 | Wet Well Floats; ; ; ; ; | Halton | In Service | Garlock Gdns PS | WWPS | Wet Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2009 |  | 2030 | HR-GGDN-004 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 18:08 | Maira Rafiq | 2020-08-24 09:16 |  |  |  |  | Pumping | Wet Well | 1 |  | 308_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
443 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 646 | Sump Float | 2 | Sump Float; ; ; ; ; | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2008 |  | 2030 | HR-MORI-027 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 18:13 | Maira Rafiq | 2020-08-24 09:32 |  |  |  |  | Building | Plumbing - Sanitary Waste | 1 |  | 309_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
444 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 43 | Remote Signals Telephone Transmitter | 2 | Remote Signals Telephone Transmitter; Pribusin; IUC-X9-TXC; ; ; | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation |  | Transmitter | [5 empty] | 2016 |  | 2030 | HR-MORI-031 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 18:15 | Maira Rafiq | 2020-08-24 09:32 |  |  |  |  | Communications | Telephone/IT | 1 |  | 310_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
445 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 647 | Wet Well Float | 2 | Wet Well Float; ; ; ; ; | Halton | In Service | Morrison Heights PS | WWPS | Wet Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2009 |  | 2030 | HR-MORI-124 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 18:18 | Maira Rafiq | 2020-08-24 09:31 |  |  |  |  | Pumping | Wet Well | 1 |  | 311_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
446 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Wet Well Level Transmitter | 2 | Wet Well Level Transmitter; Siemens Milltronics; Multiranger Plus; ; ; | Halton | In Service | Raymar Pl PS | WWPS | Site | Process Instrumentation | Process Instrumentation |  | Transmitter | [5 empty] | 2009 |  | 2030 | HR-RAYM-080 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 18:22 | Maira Rafiq | 2020-08-24 09:35 |  |  |  |  | Pumping | Wet Well | 1 |  | 312_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | bolts were not secured properly
447 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 45 | Remote Signals Telephone Transmitter | 1 | Remote Signals Telephone Transmitter; Pribusin; IUC-X9-TXC; ; ; | Halton | In Service | Raymar Pl PS | WWPS | Site | Process Instrumentation | Process Instrumentation |  | Transmitter | [5 empty] | 2016 |  | 2030 | HR-RAYM-132 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 18:24 | Maira Rafiq | 2020-08-24 09:35 |  |  |  |  | Communications | Telephone/IT | 1 |  | 313_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
448 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Wet Well Floats | 2 | Wet Well Floats; ; ; ; ; | Halton | In Service | Raymar Pl PS | WWPS | Wet Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2009 |  | 2030 | HR-RAYM-011 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 18:32 | Maira Rafiq | 2020-08-24 09:36 |  |  |  |  | Pumping | Wet Well | 1 |  | 314_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
485 |  |  | 201611 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 25 | Main Disconnect Switch | 2 | Main Disconnect Switch; Square D; ; ;600V, 60A, fused | Halton | In Service | Chancery Lane PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2010 |  | 2040 | HR-CNRY-076 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-27 16:37 | Maira Rafiq | 2020-09-18 11:38 |  |  |  |  | Primary Power | MCC | 1 |  | 307_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
486 |  |  | 201611 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 25 | Power Meter | 2 | Power Meter; ; ; ; | Halton | In Service | Chancery Lane PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2010 |  | 2040 | HR-CNRY-080 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-27 16:37 | Maira Rafiq | 2020-09-18 11:38 |  |  |  |  | Primary Power | MCC | 1 |  | 309_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
487 |  |  | 201611 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 25 | Manual Transfer Switch | 2 | Manual Transfer Switch; Square D; ; ;600V, 60A | Halton | In Service | Chancery Lane PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2010 |  | 2040 | HR-CNRY-081 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-27 16:43 | Maira Rafiq | 2020-09-18 11:38 |  |  |  |  | Primary Power | Transfer Switch | 1 |  | 310_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
488 |  |  | 201611 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 25 | Generator Connection Receptacle | 2 | Generator Connection Receptacle; ; ; ;600V | Halton | In Service | Chancery Lane PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2010 |  | 2040 | HR-CNRY-072 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-27 16:45 | Maira Rafiq | 2020-09-18 11:39 |  |  |  |  | Primary Power | Standby Generator | 1 |  | 311_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
489 |  |  | 201611 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Dry Well Lights | 1 | Dry Well Lights; ; ; ;2 Fluorescent | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Process Electrical | Process Electrical |  | Lighting | [5 empty] | 1975 |  | 2025 | HR-CNRY-086 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-27 16:49 | Maira Rafiq | 2020-09-18 11:39 |  |  |  |  | Building | Electrical - Lighting | 1 |  | 312_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | replace with LED fixtures rated for class 1, div 2
490 |  |  | 201611 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 25 | Outdoor Enclosure | 2 | Outdoor Enclosure; ; ; ; | Halton | In Service | Chancery Lane PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2010 |  | 2040 | HR-CNRY-071 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-27 16:52 | Maira Rafiq | 2020-09-18 11:40 |  |  |  |  | Primary Power | MCC | 1 |  | 314_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | inside the panel is not getting drained properly
491 |  |  | 201611 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Pump Control Panel | 3 | Pump Control Panel; S&L; ; ; | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Process Electrical | Process Electrical |  | Panel, Breaker | [5 empty] | 1975 |  | 2025 | IMG_20200629_140353 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-27 16:56 | Maira Rafiq | 2020-09-18 11:40 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 315_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | replace with NEMA 4X panel
492 |  |  | 201556 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 27 | Outdoor Electrical Enclosure | 2 | Outdoor Electrical Enclosure; ; ; ; | Halton | In Service | Chartwell Rd. PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 1965 |  | 2025 | HR-CTWL-023 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-28 09:17 | Maira Rafiq | 2020-08-28 17:26 |  |  |  |  | Primary Power | MCC | 1 |  | 316_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
493 |  |  | 201556 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 27 | Main Disconnect Switch | 2 | Main Disconnect Switch; Square D; ; ;600V, 60A, fused | Halton | In Service | Chartwell Rd. PS | WWPS | Site | Process Electrical | Process Electrical |  | MCC | [5 empty] | 2010 |  | 2040 | HR-CTWL-079 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-28 09:42 | Maira Rafiq | 2020-09-20 10:28 |  |  |  |  | Primary Power | MCC | 1 |  | 317_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | missing arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servicin
494 |  |  | 201556 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 27 | Power Meter | 2 | Power Meter; Elster; ; ; | Halton | In Service | Chartwell Rd. PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2010 |  | 2040 | HR-CTWL-084 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-28 09:30 | Maira Rafiq | 2020-08-28 17:24 |  |  |  |  | Primary Power | MCC | 1 |  | 318_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
495 |  |  | 201556 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 27 | Manual Transfer Switch | 2 | Manual Transfer Switch; Square D; ; ; 600V, 60A | Halton | In Service | Chartwell Rd. PS | WWPS | Site | Process Electrical | Process Electrical |  | Panel, Breaker | [5 empty] | 2010 |  | 2040 | HR-CTWL-085 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-28 09:47 | Maira Rafiq | 2020-09-20 10:29 |  |  |  |  | Primary Power | Transfer Switch | 1 |  | 319_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | missing arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the receptacle which may require examination, adjustment, ser
496 |  |  | 201556 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Dry Well Lighting | 1 | Dry Well Lighting; ; ; ; 2 fluorescent lights | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Building Electrical | Building Services |  | Lighting | [5 empty] | 1965 |  | 2025 | HR-CTWL-085 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-28 09:40 | Maira Rafiq | 2020-08-28 17:25 |  |  |  |  | Building | Electrical - Lighting | 1 |  | 320_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | replace with LED in next upgrade
497 |  |  | 201556 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Control Panel | 3 | Control Panel; S&L; ; ; | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Process Electrical | Process Electrical |  | Panel, Breaker | [5 empty] | 1965 |  | 2025 | HR-CTWL-002 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-05 12:38 | Maira Rafiq | 2020-09-20 10:30 |  |  |  |  | Primary Power | MCC | 1 |  | 321_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | misplaced arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servic | Pump #1 breaker to be sized and replaced according to OESC-2018
498 |  |  | 201556 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Generator Connection Receptacle | 2 | Generator Connection Receptacle; ; ; ; 600V, 60A | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Process Electrical | Process Electrical |  | Generator | [5 empty] | 1965 |  | 2025 | HR-CTWL-002 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-28 09:52 | Maira Rafiq | 2020-08-28 17:25 |  |  |  |  | Primary Power | Standby Generator | 1 |  | 322_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
499 |  |  | 201647 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 30 | Outdoor Enclosure | 2 | Outdoor Enclosure | Halton | In Service | Cumnock PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 1993 |  | 2030 | HR-CMNK-036 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-28 15:33 | Maira Rafiq | 2020-09-21 15:17 |  |  |  |  | Primary Power | MCC | 1 |  | 323_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | bottom of interior has corroded | replace with NEMA 3R enclosure in next upgrade
500 |  |  | 201647 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 7 | Main Disconnect Switch | 2 | Main Disconnect Switch; Square D; ; ;600V, 60A | Halton | In Service | Cumnock PS | WWPS | Site | Process Electrical | Process Electrical |  | MCC | [5 empty] | 1993 |  | 2035 | HR-CMNK-038 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-28 15:57 | Maira Rafiq | 2020-09-21 15:21 |  |  |  |  | Primary Power | MCC | 1 |  | 324_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | missing arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servicin
501 |  |  | 201647 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 7 | Power Meter | 2 | Power Meter; elster; ; ; | Halton | In Service | Cumnock PS | WWPS | Site | Process Electrical | Process Electrical |  | MCC | [5 empty] | 1993 |  | 2035 | HR-CMNK-041 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-28 15:36 | Maira Rafiq | 2020-09-21 15:18 |  |  |  |  | Primary Power | MCC | 1 |  | 325_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
502 |  |  | 201647 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 7 | Manual Transfer Switch | 2 | Manual Transfer Switch; square D; ; ;600V, 60A | Halton | In Service | Cumnock PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 1993 |  | 2035 | HR-CMNK-042 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-28 15:58 | Maira Rafiq | 2020-09-21 15:22 |  |  |  |  | Primary Power | Transfer Switch | 1 |  | 326_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | missing arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servicin
503 |  |  | 201647 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Drywell Lighting | 1 | Drywell Lighting; ; ; ;2 fluorescent fixtures | Halton | In Service | Cumnock PS | WWPS | Dry Well | Process Electrical | Process Electrical |  | Lighting | [5 empty] | 1974 |  | 2025 | HR-CMNK-051 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-28 16:01 | Maira Rafiq | 2020-09-21 15:20 |  |  |  |  | Building | Electrical - Lighting | 1 |  | 327_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | fair | replace with LED fixture in next upgrade. To be rated for class 1, div 2
504 |  |  | 201647 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Control Panel | 3 | Control Panel; S&L; ; ; | Halton | In Service | Cumnock PS | WWPS | Dry Well | Process Electrical | Process Electrical |  | Panel, Breaker | [5 empty] | 1974 |  | 2025 | HR-CMNK-0003 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-28 16:09 | Maira Rafiq | 2020-09-21 15:22 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 328_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | bottom of interior was corroded | missing arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servicin
505 |  |  | 201608 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 33 | outdoor enclosure | 2 | outdoor enclosure | Halton | In Service | Ennisclaire Drive PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 1972 |  | 2025 | HR-ENIS-028 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 13:54 | Maira Rafiq | 2020-09-21 17:05 |  |  |  |  | Primary Power | MCC | 1 |  | 329_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | top surface and doors were corroded | to be replaced with NEMA 3R enclosure
506 |  |  | 201608 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 33 | Control Panel with Main DS | 3 | Control Panel with Main DS; | Halton | In Service | Ennisclaire Drive PS | WWPS | Site | Process Electrical | Process Electrical |  | Panel, Breaker | [5 empty] | 1972 |  | 2025 | HR-ENIS-029 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 14:23 | Maira Rafiq | 2020-09-21 17:06 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 330_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | outdated arc flash label. Shock and arc flash hazard as the existing arc flash label are outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreove
507 |  |  | 201608 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 33 | Pump #1 VFD with Breaker | 2 | Pump #1 VFD with Breaker; PowerFlex 40; Series A; ; ; Size 1, 7.5HP | Halton | In Service | Ennisclaire Drive PS | WWPS | Site | Process Electrical | Process Electrical |  | VFD | [5 empty] | 2007 |  | 2037 | HR-ENIS-053 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 14:03 | Maira Rafiq | 2020-09-21 17:07 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 331_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
508 |  |  | 201608 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 33 | Pump #2 VFD with Breaker | 2 | Pump #2 VFD with Breaker; PowerFlex 40; Series A; ; ; Size 1, 7.5HP | Halton | In Service | Ennisclaire Drive PS | WWPS | Site | Process Electrical | Process Electrical |  | VFD | [5 empty] | 2007 |  | 2037 | HR-ENIS-047 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 14:05 | Maira Rafiq | 2020-09-21 17:07 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 332_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
509 |  |  | 201608 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 33 | Generator Connection Receptacle | 2 | Generator Connection Receptacle; ; ; ; ; 240V, 60A | Halton | In Service | Ennisclaire Drive PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2007 |  | 2037 | HR-ENIS-060 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 14:08 | Maira Rafiq | 2020-09-21 17:08 |  |  |  |  | Primary Power | Standby Generator | 1 |  | 333_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
510 |  |  | 201608 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 33 | Manual Transfer Switch | 2 | Manual Transfer Switch; Moeller; ; ; ; 600V, 63A | Halton | In Service | Ennisclaire Drive PS | WWPS | Site | Process Electrical | Process Electrical |  | MCC | [5 empty] | 2007 |  | 2037 | HR-ENIS-061 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 14:17 | Maira Rafiq | 2020-09-21 17:09 |  |  |  |  | Primary Power | Transfer Switch | 1 |  | 334_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the switch which may require examination, adjustment, servicing, or maintenance while
511 |  |  | 201608 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 642 | Wet Well Light | 1 | Wet Well Light; ; ; ; ; class 1, div 1 rated | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Process Electrical | Process Electrical |  | Lighting | [5 empty] | 2007 |  | 2025 | HR-ENIS-061 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 14:21 | Maira Rafiq | 2020-09-21 17:09 |  |  |  |  | Building | Electrical - Lighting | 1 |  | 335_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | poor | severely corroded
512 |  |  | 201542 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 37 | Outdoor Enclosure | 2 | Outdoor Enclosure | Halton | In Service | First Street PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2010 |  | 2040 | HR-FRST-099 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 14:32 | Maira Rafiq | 2020-09-21 23:20 |  |  |  |  | Primary Power | MCC | 1 |  | 336_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
513 |  |  | 201542 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 37 | Main Fused Disconnect Switch | 2 | Main Fused Disconnect Switch; Square D; ; ; 600V, 60A | Halton | In Service | First Street PS | WWPS | Site | Process Electrical | Process Electrical |  | MCC | [5 empty] | 2010 |  | 2040 | HR-FRST-100 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 14:37 | Maira Rafiq | 2020-09-21 23:21 |  |  |  |  | Primary Power | MCC | 1 |  | 337_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | misplaced and outdated arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the VFD breaker which may require examination,
514 |  |  | 201542 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 37 | Power Meter | 2 | Power Meter; Elster; ; ; | Halton | In Service | First Street PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2010 |  | 2040 | HR-FRST-107 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 14:32 | Maira Rafiq | 2020-09-21 23:22 |  |  |  |  | Primary Power | MCC | 1 |  | 338_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
515 |  |  | 201542 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 37 | Manual Transfer Switch | 2 | Manual Transfer Switch; Square D; ; ;600V, 60A | Halton | In Service | First Street PS | WWPS | Site | Process Electrical | Process Electrical |  | MCC | [5 empty] | 2010 |  | 2040 | HR-FRST-109 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 14:39 | Maira Rafiq | 2020-09-21 23:23 |  |  |  |  | Primary Power | Transfer Switch | 1 |  | 339_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | misplaced and outdated arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the VFD breaker which may require examination,
516 |  |  | 201542 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 643 | Control Panel | 3 | Control Panel; Clow; AER-O-FLO; ;600V | Halton | In Service | First Street PS | WWPS | Dry Well | Process Electrical | Process Electrical |  | Panel, Breaker | [5 empty] | 1983 |  | 2025 | HR-FRST-001 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 14:46 | Maira Rafiq | 2020-09-21 23:24 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 340_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | misplaced and outdated arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the VFD breaker which may require examination,
517 |  |  | 201542 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 37 | Generator Connection Receptacle | 2 | Generator Connection Receptacle; ; ; ;600V, 60A | Halton | In Service | First Street PS | WWPS | Site | Process Electrical | Process Electrical |  | Generator | [5 empty] | 2010 |  | 2040 | HR-FRST-122 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 14:48 | Maira Rafiq | 2020-09-21 23:25 |  |  |  |  | Primary Power | Standby Generator | 1 |  | 341_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
518 |  |  | 201542 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 643 | Dry Well Lights | 1 | Dry Well Lights; ; ; rated for class 1, div 2 | Halton | In Service | First Street PS | WWPS | Site | Process Electrical | Process Electrical |  | Lighting | [5 empty] | 2000 |  | 2030 | HR-FRST-126 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 14:51 | Maira Rafiq | 2020-09-21 23:25 |  |  |  |  | Building | Electrical - Lighting | 1 |  | 342_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | replace with LED in next upgrade
519 |  |  | 219156 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 645 | Wet Well Light | 1 | Wet Well Light; ; ; ; florescent, class 1, div 1 rated | Halton | In Service | Garlock Gdns PS | WWPS | Wet Well | Process Electrical | Process Electrical |  | Lighting | [5 empty] | 1977 |  | 2025 | HR-GGDN-022 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 14:59 | Maira Rafiq | 2020-09-22 11:17 |  |  |  |  | Building | Electrical - Lighting | 1 |  | 343_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | to be replaced with LED
520 |  |  | 219156 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 40 | Enclosure Light | 1 | Enclosure Light; ; ; ; florescent | Halton | In Service | Garlock Gdns PS | WWPS | Site | Process Electrical | Process Electrical |  | Lighting | [5 empty] | 1977 |  | 2025 | HR-GGDN-028 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 15:08 | Maira Rafiq | 2020-09-22 11:18 |  |  |  |  | Building | Electrical - Lighting | 1 |  | 344_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | to be replaced with LED
521 |  |  | 219156 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 40 | Power Meter | 2 | Power Meter; ; ; ; | Halton | In Service | Garlock Gdns PS | WWPS | Site | Process Electrical | Process Electrical |  | MCC | [5 empty] | 2003 |  | 2033 | HR-GGDN-027 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 15:09 | Maira Rafiq | 2020-09-22 11:18 |  |  |  |  | Primary Power | MCC | 1 |  | 345_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
522 |  |  | 219156 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 40 | Control Panel with Main DS and MTS | 3 | Control Panel with Main DS; ; ; ; 240V, 30A | Halton | In Service | Garlock Gdns PS | WWPS | Site | Process Electrical | Process Electrical |  | Panel, Breaker | [5 empty] | 1977 |  | 2025 | HR-GGDN-037 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 15:14 | Maira Rafiq | 2020-09-22 11:20 |  |  |  |  | Primary Power | MCC | 1 |  | 346_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | to have separate Main DS, MTS, and CP | outdated arc flash label. Shock and arc flash hazard as the existing arc flash label are outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreove
523 |  |  | 219156 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 40 | Generator Connect Recept. | 2 | Generator Connect Recept.; ; ; ; 240V, 30A | Halton | In Service | Garlock Gdns PS | WWPS | Site | Process Electrical | Process Electrical |  | Generator | [5 empty] | 1977 |  | 2025 | HR-GGDN-056 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 15:16 | Maira Rafiq | 2020-09-22 11:20 |  |  |  |  | Primary Power | Standby Generator | 1 |  | 347_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | fair
524 |  |  | 219156 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 41 | Pump #1 VFD with Breaker | 2 | Pump #1 VFD with Breaker; PowerFlex 40; Series A; ; 240V, 30A, size 1 | Halton | In Service | Garlock Gdns PS | WWPS | Site | Process Electrical | Process Electrical |  | VFD | [5 empty] | 2003 |  | 2033 | HR-GGDN-057 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 15:20 | Maira Rafiq | 2020-09-22 11:21 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 348_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
525 |  |  | 219156 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 40 | Pump #2 VFD with Breaker | 2 | Pump #2 VFD with Breaker; PowerFlex 40; Series A; ; 240V, 30A, size 1 | Halton | In Service | Garlock Gdns PS | WWPS | Site | Process Electrical | Process Electrical |  | VFD | [5 empty] | 2003 |  | 2033 | HR-GGDN-057 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 15:21 | Maira Rafiq | 2020-09-22 11:22 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 349_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
526 |  |  | 201659 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 43 | Outdoor Enclosure | 2 | Outdoor Enclosure | Halton | In Service | Morrison Heights PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2010 |  | 2040 | HR-MORI-040 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 15:47 | Maira Rafiq | 2020-09-22 12:27 |  |  |  |  | Primary Power | MCC | 1 |  | 350_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
527 |  |  | 201659 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 43 | Generator Connect Recept. | 2 | Generator Connect Recept. ; ; ; ; 600V, 60A | Halton | In Service | Morrison Heights PS | WWPS | Site | Process Electrical | Process Electrical |  | Generator | [5 empty] | 2010 |  | 2040 | HR-MORI-041 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 15:47 | Maira Rafiq | 2020-09-22 12:27 |  |  |  |  | Primary Power | Standby Generator | 1 |  | 351_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
528 |  |  | 201659 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 43 | Main Disconnect Switch | 2 | Main DS ; Square D; ; ; 600V, 60A, fused | Halton | In Service | Morrison Heights PS | WWPS | Site | Process Electrical | Process Electrical |  | MCC | [5 empty] | 2010 |  | 2040 | HR-MORI-046 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 15:47 | Maira Rafiq | 2020-09-22 12:29 |  |  |  |  | Primary Power | MCC | 1 |  | 352_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the control panel which may require examination, adjustment, servicing, or maintenance
529 |  |  | 201659 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 43 | Manual Transfer Switch | 2 | MTS ; Square D; ; ; 600V, 60A | Halton | In Service | Morrison Heights PS | WWPS | Site | Process Electrical | Process Electrical |  | MCC | [5 empty] | 2010 |  | 2040 | HR-MORI-047 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 15:48 | Maira Rafiq | 2020-09-22 12:31 |  |  |  |  | Primary Power | Transfer Switch | 1 |  | 353_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the control panel which may require examination, adjustment, servicing, or maintenance
530 |  |  | 201659 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 43 | Power Meter | 2 | Power Meter ; elster; ; ; 600V | Halton | In Service | Morrison Heights PS | WWPS | Site | Process Electrical | Process Electrical |  | MCC | [5 empty] | 2010 |  | 2040 | HR-MORI-047 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 15:49 | Maira Rafiq | 2020-09-22 12:31 |  |  |  |  | Primary Power | MCC | 1 |  | 354_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
531 |  |  | 201659 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 646 | Dry Well Lights | 1 | Dry Well Lights ; elster; ; ; Fluorescent | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Process Electrical | Process Electrical |  | Lighting | [5 empty] | 1973 |  | 2025 | HR-MORI-056 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 15:55 | Maira Rafiq | 2020-09-22 12:31 |  |  |  |  | Building | Electrical - Lighting | 1 |  | 355_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | one of the lights doesn’t work | to be replaced with LED
532 |  |  | 201659 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 646 | Control Panel | 3 | Control Panel ; elster; ; ; 600V | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Process Electrical | Process Electrical |  | Panel, Breaker | [5 empty] | 1973 |  | 2025 | HR-MORI-057 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 16:06 | Maira Rafiq | 2020-09-22 12:32 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 356_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servicing, or maintenance while e
533 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Wet well Light | 1 | Wet well Light; ; ; ; rated for class 1, div 1 | Halton | In Service | Raymar Pl PS | WWPS | Wetwell | Building Electrical | Process Electrical |  | Lighting | [5 empty] | 1985 |  | 2021 | HR-RAYM-026 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 16:19 | Maira Rafiq | 2020-09-22 12:57 |  |  |  |  | Pumping | Wet Well | 1 |  | 357_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | it doesn't work
534 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 45 | Enclosure Light | 1 | Enclosure Light; ; ; ; fluorescent | Halton | In Service | Raymar Pl PS | WWPS | Site | Building Electrical | Process Electrical |  | Lighting | [5 empty] | 1985 |  | 2025 | HR-RAYM-026 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 16:20 | Maira Rafiq | 2020-09-22 12:58 |  |  |  |  | Building | Electrical - Lighting | 1 |  | 358_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | to be replaced with LED
535 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Outdoor Enclosure | 1 | Outdoor Enclosure; ; ; ; | Halton | In Service | Raymar Pl PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 1985 |  | 2025 | HR-RAYM-057 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 16:23 | Maira Rafiq | 2020-09-22 12:58 |  |  |  |  | Primary Power | MCC | 1 |  | 359_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | to be replaced with NEMA 3R enclosure
536 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 45 | Power Meter | 2 | Power Meter; Sensus; ; ; | Halton | In Service | Raymar Pl PS | WWPS | Site | Process Electrical | Process Electrical |  | MCC | [5 empty] | 2006 |  | 2036 | HR-RAYM-059 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 16:28 | Maira Rafiq | 2020-09-22 12:58 |  |  |  |  | Primary Power | MCC | 1 |  | 360_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
537 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 45 | Pump #1 VFD and Breaker | 2 | Pump #1 VFD and Breaker; A-B; PowerFlex 40; ; 240V, size 1 | Halton | In Service | Raymar Pl PS | WWPS | Site | Process Electrical | Process Electrical |  | VFD | [5 empty] | 2006 |  | 2036 | HR-RAYM-063 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 16:38 | Maira Rafiq | 2020-09-22 12:59 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 361_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
538 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 12 | Pump #2 VFD and Breaker | 2 | Pump #2 VFD and Breaker; A-B; PowerFlex 40; ; 240V, size 1 | Halton | In Service | Raymar Pl PS | WWPS | Site | Process Electrical | Process Electrical |  | VFD | [5 empty] | 2006 |  | 2036 | HR-RAYM-063 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 16:38 | Maira Rafiq | 2020-09-22 12:59 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 362_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
539 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 45 | Control Panel with Main DS and MTS | 3 | Control Panel with Main DS and MTS; ; ; ; 240V, 60A | Halton | In Service | Raymar Pl PS | WWPS | Site | Process Electrical | Process Electrical |  | Panel, Breaker | [5 empty] | 1985 |  | 2025 | HR-RAYM-077 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 16:43 | Maira Rafiq | 2020-09-22 13:03 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 363_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | replace with separate main DS, MTS and CP | Shock and arc flash hazard as the existing arc flash label are outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreover, the studies and reports
540 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 45 | Gen Connect Recept | 2 | Gen Connect Recept; ; AR648; ; 240V, 60A | Halton | In Service | Raymar Pl PS | WWPS | Site | Process Electrical | Process Electrical |  | Generator | [5 empty] | 1985 |  | 2025 | HR-RAYM-130 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 16:49 | Maira Rafiq | 2020-09-22 13:02 |  |  |  |  | Primary Power | Standby Generator | 1 |  | 364_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
576 |  |  | 201612 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Dry Wall Sump Pump | 1 | Installation year was assumed to be 1975 | Halton |  | Chancery Lane PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Misc. Building Services | [5 empty] | 1975 |  |  | HR-CNRY-132 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:24 | Maira Rafiq | 2020-09-18 11:53 |  |  |  |  | Building | Plumbing - Sanitary Waste | 1 |  | 293_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Surface corrosion
577 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Dry Wall Portable Heater | 1 | Installation year assumed to be 1975 | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Unit Heater | [5 empty] | 1975 |  |  | HR-CNRY-018 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:22 | Maira Rafiq | 2020-09-18 11:47 |  |  |  |  | Building | HVAC - Heat Generating Systems | 1 |  | 294_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
578 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  | Dry Wall Portable Dehumidifier | 1 | Manufacturer: Garrison, installation year assumed to be 1975 | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Dehumidifier | [5 empty] | 1975 |  |  | HR-CNRY-009 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:22 | Maira Rafiq | 2020-09-18 11:47 |  |  |  |  | Building | HVAC - Cooling Generating Systems | 1 |  | 295_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
579 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Dry Wall Portable Heater | 1 | Installation year assumed to be 1980 | Halton |  | Chartwell Rd. PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Unit Heater | [5 empty] | 1983 |  |  | HR-CTWL-007 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:26 | Maira Rafiq | 2020-08-28 17:29 |  |  |  |  | Building | HVAC - Heat Generating Systems | 1 |  | 296_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
580 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Dry Well Dehumidifier | 1 | Installation year assumed to be 1980 | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Dehumidifier | [5 empty] | 1983 |  |  | HR-CTWL-008 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:26 | Maira Rafiq | 2020-09-20 10:50 |  |  |  |  | Building | HVAC - Heat Generating Systems | 1 |  | 297_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
581 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Dry Wall Sump Pump | 1 | Installation year was assumed to be 1980 | Halton |  | Chartwell Rd. PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Misc. Building Services | [5 empty] | 1983 |  |  | HR-CTWL-019 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:26 | Maira Rafiq | 2020-08-28 17:29 |  |  |  |  | Building | Plumbing - Sanitary Waste | 1 |  | 299_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Severe corrosion
583 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 15 | Dry Wall Sump Pump | 1 |  | Halton |  | Cumnock PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Misc. Building Services | [5 empty] | 1974 |  |  | HR-CMNK-021 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:30 | Maira Rafiq | 2020-09-21 15:24 |  |  |  |  | Building | Plumbing - Sanitary Waste | 1 |  | 301_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | surface corrosion
584 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Dry Wall Portable Heater | 1 | Installation year assumed to be 1975 | Halton | In Service | Cumnock PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Unit Heater | [5 empty] | 1974 |  |  | HR-CMNK-007 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:30 | Maira Rafiq | 2020-09-21 15:25 |  |  |  |  | Building | HVAC - Heat Generating Systems | 1 |  | 302_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Surface corrosion
585 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Dry Wall Portable Dehumidifier | 1 | Installation year assumed to be 1975 | Halton | In Service | Cumnock PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Dehumidifier | [5 empty] | 1974 |  |  | HR-CMNK-008 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:30 | Maira Rafiq | 2020-09-21 15:26 |  |  |  |  | Building | HVAC - Cooling Generating Systems | 1 |  | 303_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
586 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  | Wet Well Ventilation Pipe | 1 | one 2 inches diameter steel pipe vent | Halton | In Service | Cumnock PS | WWPS | Wet Well | Building Mechanical | Building Services |  | Misc. Building Services | [5 empty] | 1974 |  |  | HR-CMNK-034 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:29 | Maira Rafiq | 2020-09-21 15:26 |  |  |  |  | Pumping | Wet Well | 1 |  | 304_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
587 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 642 | Wet Well Ventilation Pipe | 1 | one 4 inches diameter gooseneck pipe vent | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Building Mechanical | Building Services |  | Misc. Building Services | [5 empty] | 1977 |  |  | HR-ENIS-001 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:33 | Maira Rafiq | 2020-09-21 17:27 |  |  |  |  | Pumping | Wet Well | 1 |  | 305_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | miscellaneous surface staining
588 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 15 | Dry Wall Sump Pump | 1 | Installation year was assumed to be 1985 | Halton |  | First Street PS | WWPS | Dry Well | Building Mechanical | Building Services | [7 empty] | 1986 |  |  | HR-FRST-009 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:35 | [8 empty] | 1 |  | 306_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
589 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 643 | Dry Wall Portable Heater | 1 | Installation year assumed to be 1985 | Halton |  | First Street PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Unit Heater | [5 empty] | 1986 |  |  | HR-FRST-003 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:35 | Maira Rafiq | 2020-09-21 23:40 |  |  |  |  | Building | HVAC - Heat Generating Systems | 1 |  | 307_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
590 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 643 | Dry Well Dehumidifier | 1 | Manufacturer: Simplicity, installation year assumed to be 1985 | Halton |  | First Street PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Dehumidifier | [5 empty] | 1986 |  |  | HR-FRST-004 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:35 | Maira Rafiq | 2020-09-21 23:40 |  |  |  |  | Building | HVAC - Distribution Systems | 1 |  | 308_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
592 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 645 | Wet Well Ventilation Pipe | 1 | one 4 inches diameter gooseneck steel pipe vent | Halton | In Service | Garlock Gdns PS | WWPS | Wet Well | Building Mechanical | Building Services |  | Misc. Building Services | [5 empty] | 1977 |  |  | HR-GGDN-001 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:37 | Maira Rafiq | 2020-09-22 11:12 |  |  |  |  | Pumping | Wet Well | 1 |  | 310_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | paint peeling | fair
593 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  | Dry Wall Portable Heater | 1 |  | Halton |  | Morrison Heights PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Unit Heater | [5 empty] | 1973 |  |  | HR-MORI-007 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:37 | Maira Rafiq | 2020-09-22 12:36 |  |  |  |  | Building | HVAC - Heat Generating Systems | 1 |  | 311_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
594 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 646 | Dry Well Dehumidifier | 1 |  | Halton |  | Morrison Heights PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Dehumidifier | [5 empty] | 1973 |  |  | HR-MORI-008 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:37 | Maira Rafiq | 2020-09-22 12:38 |  |  |  |  | Building | HVAC - Cooling Generating Systems | 1 |  | 312_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
595 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Wet Well Ventilation Pipe | 1 | one 4 inches diameter steel pipe vent with insect screen | Halton | In Service | Raymar Pl PS | WWPS | Wet Well | Building Mechanical | Building Services |  | Misc. Building Services | [5 empty] | 1985 |  |  | HR-RAYM-056 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:39 | Maira Rafiq | 2020-09-22 13:06 |  |  |  |  | Pumping | Wet Well | 1 |  | 313_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
611 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 25 | Yard Hydrant | 1 |  | Halton | In Service | Chancery Lane PS | WWPS | Site | Site Works | Site Works |  | Misc. Site Works | [5 empty] | 1975 |  | 2035 | HR-CNRY-034 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Joseph De Paolo | 2020-07-17 10:40 | Maira Rafiq | 2020-08-24 14:03 |  |  |  |  | Site Works | Yard Piping | 1 |  | 281_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Good
612 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 27 | Yard Hydrant | 1 |  | Halton | In Service | Chartwell Rd. PS | WWPS | Site | Site Works | Site Works |  | Misc. Site Works | [5 empty] | 1983 |  | 2035 | HR-CTWL-025 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Joseph De Paolo | 2020-07-17 10:40 | Maira Rafiq | 2020-08-24 16:29 |  |  |  |  | Site Works | Yard Piping | 1 |  | 282_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Good
613 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 30 | Yard Hydrant | 1 |  | Halton | In Service | Cumnock PS | WWPS | Site | Site Works | Site Works |  | Misc. Site Works | [5 empty] | 1974 |  | 2035 | HR-CMNK-158 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Joseph De Paolo | 2020-07-17 10:39 | Maira Rafiq | 2020-08-24 16:30 |  |  |  |  | Site Works | Yard Piping | 1 |  | 283_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Good
614 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 33 | Yard Hydrant | 1 |  | Halton | In Service | Ennisclaire Drive PS | WWPS | Site | Site Works | Site Works |  | Misc. Site Works | [5 empty] | 1977 |  | 2035 | HR-ENIS-026 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Joseph De Paolo | 2020-07-17 10:39 | Maira Rafiq | 2020-09-21 16:54 |  |  |  |  | Site Works | Yard Piping | 1 |  | 284_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Good
615 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 37 | Yard Hydrant | 1 |  | Halton | In Service | First Street PS | WWPS | Site | Site Works | Site Works |  | Misc. Site Works | [5 empty] | 1968 |  | 2035 | HR-FRST-095 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Joseph De Paolo | 2020-07-17 10:39 | Maira Rafiq | 2020-08-24 16:39 |  |  |  |  | Site Works | Yard Piping | 1 |  | 285_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Good
616 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 40 | Yard Hydrant (New Asset) | 1 |  | Halton |  | Garlock Gdns PS | WWPS | Site | Site Works | Site Works |  | Misc. Site Works | [5 empty] | 1977 |  | 2035 | [8 empty] | 1 | ea. | 2020 | [10 empty] | CAMR061927 | 2020-08-24 16:41 | Maira Rafiq | 2020-08-24 16:42 |  |  |  |  | Site Works | Yard Piping | 1 |  | 286_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | In accordance with Section 19.8.3 of the Region's Water and Wastewater Design Manual (January 2012), a yard hydrant complete with a backflow preventer with a 37.5mm water service line shall be provided for flushing and cleaning purposes. It is recommended
622 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 43 | Yard Hydrant | 1 |  | Halton |  | Morrison Heights PS | WWPS | Site | Site Works | Site Works |  | Misc. Site Works | [5 empty] | 1973 |  | 2036 | HR-MORI-029 | [7 empty] | 1 | ea. | 2020 | [10 empty] | CAMR061927 | 2020-08-24 16:44 | Maira Rafiq | 2020-08-24 16:44 |  |  |  |  | Site Works | Yard Piping | 1 |  | 292_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Minor surface rust and defects
623 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 45 | Yard Hydrant (New Asset) | 1 |  | Halton |  | Raymar Pl PS | WWPS | Site | Site Works | Site Works |  | Misc. Site Works | [5 empty] | 1985 |  | 2035 | [8 empty] | 1 | ea. | 2020 | [10 empty] | CAMR061927 | 2020-08-24 16:46 | Maira Rafiq | 2020-08-24 16:46 |  |  |  |  | Site Works | Yard Piping | 1 |  | 293_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | In accordance with Section 19.8.3 of the Region's Water and Wastewater Design Manual (January 2012), a yard hydrant complete with a backflow preventer with a 37.5mm water service line shall be provided for flushing and cleaning purposes. It is recommended
632 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 6 | Dry Well |  | Chartwell Rd. PS Dry Well | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1983 | [10 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-21 16:04 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
633 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 6 | Wet Well |  | Chartwell Rd. PS Wet Well | Halton | In Service | Chartwell Rd. PS | WWPS | Wet Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1983 |  |  | HR-CTWL-024 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-28 17:20 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
638 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 5 | Dry Well |  |  | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1975 |  |  | HR-CNRY-004 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-18 10:59 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
639 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 5 | Wet Well |  |  | Halton | In Service | Chancery Lane PS | WWPS | Process Structural | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1975 |  |  | HR-CNRY-033 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-24 08:38 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
640 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 7 | Dry Well |  | Cumnock PS Dry Well | Halton | In Service | Cumnock PS | WWPS | Dry Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1974 |  | 0 | HR-CMNK-033 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-21 15:40 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
641 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 7 | Wet Well |  | Cumnock PS Wet Well | Halton | In Service | Cumnock PS | WWPS | Wet Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1974 |  |  | HR-CMNK-032 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-24 08:54 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
642 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 8 | Wet Well |  | Ennisclaire Drive PS Wet Well | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1977 |  |  | HR-ENIS-002 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-24 09:01 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
643 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 9 | Dry Well |  | First Street PS Dry Well | Halton | In Service | First Street PS | WWPS | Dry Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1986 |  |  | HR-FRST-065 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-24 09:05 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
644 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 9 | Wet Well |  | First Street PS Wet Well | Halton | In Service | First Street PS | WWPS | Wet Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1986 |  |  | HR-FRST-094 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-24 09:07 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
645 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 10 | Wet Well |  | Garlock Gdns PS Wet Well | Halton | In Service | Garlock Gdns PS | WWPS | Wet Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1977 |  |  | HR-GGDN-088 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-24 09:14 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
646 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 11 | Dry Well |  | Morrison Heights PS Dry Well | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1973 |  |  | HR-MORI-098 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-24 09:16 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
647 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 11 | Wet Well |  | Morrison Heights PS Wet Well | Halton | In Service | Morrison Heights PS | WWPS | Wet Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1973 |  |  | HR-MORI-124 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-24 09:17 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
648 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 12 | Wet Well |  | Raymar Pl PS Wet Well | Halton | In Service | Raymar Pl PS | WWPS | Wet Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1985 |  |  | HR-RAYM-054 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-24 09:33 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
651 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 33 | concrete pavers | 1 |  | Halton | In Service | Ennisclaire Drive PS | WWPS | Site | Site Works | Site Works |  | Misc. Site Works | [5 empty] | 1977 |  |  | HR-ENIS-026 | [7 empty] | 1 | ea. | 2020 | [10 empty] | CAMR061927 | 2020-08-24 16:38 | Maira Rafiq | 2020-09-21 16:53 |  |  |  |  | Site Works | Sidewalk | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Overgrown vegetation
661 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Cathodic Protection | 2 | Cathodic Protection for Underground Tank | Halton | In Service | Chancery Lane PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2010 |  |  | HR-CNRY-037 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-18 13:21 |  |  |  |  | Primary Power | MCC | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE | The Cathodic Protection was assumed to be in good condition. The installation of the cathodic protection system was assumed to coincide with the installation of the above grade panel.
663 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 151 | Pump 2 Piping | 3 | 150mm diameter, approx. 5m ductile iron pipe | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS | [5 empty] | 1983 |  | 0 | HR-CTWL-033 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-20 13:46 |  |  |  |  | Pumping | Pump Assembly |  |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Minor corrosion
665 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Discharge Piping | 3 | 150mm diameter, approx. 5m ductile iron pipe | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS | [5 empty] | 1983 |  | 0 | HR-CTWL-014 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-20 13:46 |  |  |  |  | Pumping | Discharge Header |  |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Minor corrosion
666 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 165 | Pump 2 Piping | 3 | 100mm diameter, approx. 5m ductile pipe | Halton | In Service | Cumnock PS | Cumnock PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS | [5 empty] | 1974 |  | 0 | HR-CMNK-027 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-21 15:41 |  |  |  |  | Pumping | Pump Assembly | 2 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Corrosion
667 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Cathodic Protection | 2 | Cathodic Protection for Underground Tank | Halton | In Service | Cumnock PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2010 |  |  | HR-CNRY-037 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-21 15:44 |  |  |  |  | Primary Power | MCC | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE | The Cathodic Protection was assumed to be in good condition. The installation of the cathodic protection system was assumed to coincide with the installation of the above grade panel.
669 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 40 | Discharge Header | 3 | 100mm diameter, approx. 5m ductile pipe | Halton | In Service | Garlock Gdns PS | Garlock Gdns PS | Dry Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS | [5 empty] | 1977 |  | 0 | [8 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-22 11:09 |  |  |  |  | Pumping | Wet Well |  |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE | Not observed
670 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  | Dry Well Concrete Foundation | 2 |  | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Building Structural | Building and Process Structural |  | Misc. Structural | [5 empty] | 1973 |  | 2035 |  |  |  |  | 3 |  |  |  | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-22 11:45 |  |  |  |  | Building | Substructure | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE | The asset was assumed to be in fair condition based on its age.
671 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Discharge Header | 3 | 100mm diameter, approx. 8.6 m ductile iron pipe | Halton | In Service | Raymar Pl PS | Raymar Pl PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS | [5 empty] | 1985 |  | 0 | HR-RAYM-040 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-22 13:21 |  |  |  |  | Pumping | Discharge Header | 2 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Heavy corrosion and deterioration was observed

## r_tblAsset
AssetID | ClientAssetID0 | ClientAssetID1 | ClientAssetID2 | UniformatL0 | UniformatL1 | UniformatL2 | UniformatL3 | UniformatL4 | UniformatL5 | MasterFormatX | MasterFormatX2 | FlagAsProcess | FlagAsSubProcess | FlagAsAssembly | FlagAsParent | ParentID | AssetName | CoF | AssetDescription | Owner | Status | SiteName | FacilityName | LocationName | AssetCategory | CustomClientCategory | AssetType | CustomClientAssetType | Manufacturer | Model | SerialNumber | InspectionType | AssessmentYear | InstallYear | AvgESL | ReplaceYear | PhotoName | DrawingName | VisualCondition | PerformanceCondition | PoF | RedundancyFactor | CostID | MaterialUnitCost | Quantity | UnitOfQuantity | CostYear | CostSource | MarkupEquipment | MarkupLabour | MarkupAncillary | MarkupRemoval | MarkupEngineering | MarkupAdministration | MarkupContractor | MarkupContingency | TotalReplacementMarkup | LastEditor | LastEditTime | PlannerReviewer | PlannerReviewTime | DisciplineReview | DisciplineReviewTime | PMReview | PMReviewTime | TempProcess | TempSubProcess | TempSubProcessInstance | SizeCapacity | DBNotes | CountCapex | CountOpex | CountComments | CountDrawings | PreventDeletion | PreventEdit | TempComments1 | TempComments2 | TempComments3 | TempRehabComment | TempRehabYear | TempRehabCost
5 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE |  | Chancery Lane PS |  |  | Halton |  | Chancery Lane PS | WWPS |  | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-14 11:26 | [8 empty] | 1 |  | 5_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
6 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE |  | Chartwell Rd. PS |  |  | Halton |  | Chartwell Rd. PS | WWPS |  | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 2020-07-10 11:19 | [8 empty] | 1 |  | 6_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
7 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE |  | Cumnock PS |  |  | Halton |  | Cumnock PS | WWPS |  | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 2020-07-10 11:19 | [8 empty] | 1 |  | 7_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
8 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE |  | Ennisclaire Drive PS |  |  | Halton |  | Ennisclaire Drive PS | WWPS |  | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-28 16:16 | [8 empty] | 1 |  | 8_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
9 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE |  | First Street PS |  |  | Halton |  | First Street PS | WWPS |  | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1977 |  |  | HR-FRST-006 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 17:48 | [8 empty] | 1 |  | 9_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
10 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE |  | Garlock Gdns PS |  |  | Halton |  | Garlock Gdns PS | WWPS |  | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 2020-07-10 11:19 | [8 empty] | 1 |  | 10_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
11 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE |  | Morrison Heights PS |  |  | Halton |  | Morrison Heights PS | WWPS |  | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 2020-07-10 11:19 | [8 empty] | 1 |  | 11_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
12 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE |  | Raymar Pl PS |  |  | Halton |  | Raymar Pl PS | WWPS |  | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 2020-07-10 11:19 | [8 empty] | 1 |  | 12_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
24 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Dry Well Structure | 2 | Chancery Lane PS Dry Well | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Tank, Steel | [5 empty] | 1975 |  |  | HR-CNRY-004 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:20 | Maira Rafiq | 2020-09-18 10:44 |  |  |  |  | Building | Substructure | 1 |  | 24_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Minor corrosion noted | Good
25 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 5 | Site |  | Chancery Lane PS Site | Halton |  | Chancery Lane PS | WWPS | Site | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 2020-07-10 11:17 | [8 empty] | 1 |  | 25_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
26 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Dry Well Structure | 2 | Chartwell Rd. PS Dry Well | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Building Structural | Building and Process Structural |  | Tank, Steel | [5 empty] | 1983 |  |  | HR-CTWL-073 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:29 | Maira Rafiq | 2020-09-18 13:53 |  |  |  |  | Building | Substructure | 1 |  | 26_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Minor corrosion noted throughout | Good
27 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 6 | Site |  | Chartwell Rd. PS Site | Halton |  | Chartwell Rd. PS | WWPS | Site | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 2020-07-10 11:17 | [8 empty] | 1 |  | 27_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
28 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 633 | Wet Well Concrete Structure | 2 | Chartwell Rd. PS Wet Well | Halton | In Service | Chartwell Rd. PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Tank, Concrete | [5 empty] | 1983 |  |  | HR-CTWL-024 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:29 | Maira Rafiq | 2020-08-28 17:12 |  |  |  |  | Pumping | Wet Well | 1 |  | 28_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Exposed corroded reinforcement | Fair
29 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Dry Well Structure | 2 | Cumnock PS Dry Well | Halton | In Service | Cumnock PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Tank, Steel | [5 empty] | 1974 |  |  | HR-CMNK-122 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:38 | Maira Rafiq | 2020-09-20 22:11 |  |  |  |  | Building | Substructure | 1 |  | 29_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Moderate corrosion noted throughout | Fair
30 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 7 | Site |  | Cumnock PS Site | Halton |  | Cumnock PS | WWPS | Site | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 2020-07-10 11:17 | [8 empty] | 1 |  | 30_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
31 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 641 | Wet Well Concrete Structure | 2 | Cumnock PS Wet Well | Halton | In Service | Cumnock PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Tank, Concrete | [5 empty] | 1974 |  |  | HR-CMNK-138 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:39 | Maira Rafiq | 2020-09-20 22:03 |  |  |  |  | Pumping | Wet Well | 1 |  | 31_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Efflorescence deposits/leak at joint. Concrete delamination/spalling at joint | Fair
33 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 8 | Site |  | Ennisclaire Drive PS Site | Halton |  | Ennisclaire Drive PS | WWPS | Site | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 2020-07-10 11:17 | [8 empty] | 1 |  | 33_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
34 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 642 | Wet Well Concrete Structure | 2 | Ennisclaire Drive PS Wet Well | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Tank, Concrete | [5 empty] | 1977 |  |  | HR-ENIS-002 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:54 | Maira Rafiq | 2020-09-21 16:55 |  |  |  |  | Pumping | Wet Well | 1 |  | 34_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Exposed corroded reinforcement, rust spots and concrete parging spalling was noted at joints | Fair
35 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 9 |  |  | First Street PS | Halton |  | First Street PS | WWPS |  | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 2020-07-10 11:16 | [8 empty] | 1 |  | 35_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
36 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 9 | Dry Well | 2 | First Street PS Dry Well | Halton | In Service | First Street PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Tank, Steel | [5 empty] | 1986 |  |  | HR-FRST-065 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:14 | Maira Rafiq | 2020-09-21 17:30 |  |  |  |  | Building | Substructure | 1 |  | 36_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Corrosion noted throughout | Fair
37 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 9 | Site |  | First Street PS Site | Halton |  | First Street PS | WWPS | Site | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1986 | [10 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 2020-07-10 11:16 | Maira Rafiq | 2020-09-21 23:19 | [6 empty] | 1 |  | 37_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
38 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 9 | Wet Well Concrete Structure | 2 | First Street PS Wet Well | Halton | In Service | First Street PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Tank, Concrete | [5 empty] | 1986 |  |  | HR-FRST-094 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:15 | Maira Rafiq | 2020-09-21 19:12 |  |  |  |  | Pumping | Wet Well | 1 |  | 38_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair
40 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 10 | Site |  | Garlock Gdns PS Site | Halton |  | Garlock Gdns PS | WWPS | Site | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 2020-07-10 11:16 | [8 empty] | 1 |  | 40_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
41 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 10 | Wet Well Concrete Structure | 2 | Garlock Gdns PS Wet Well | Halton | In Service | Garlock Gdns PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Tank, Concrete | [5 empty] | 1977 |  |  | HR-GGDN-088 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:24 | Maira Rafiq | 2020-09-22 10:46 |  |  |  |  | Pumping | Wet Well | 1 |  | 41_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Rust spots noted | Fair
42 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 11 | Dry Well Structure | 2 | Morrison Heights PS Dry Well | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Tank, Steel | [5 empty] | 1973 |  | 2033 | HR-MORI-098 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:29 | Maira Rafiq | 2020-09-22 11:23 |  |  |  |  | Building | Substructure | 1 |  | 42_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Corrosion was noted at the base | Fair
43 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 11 | Site |  | Morrison Heights PS Site | Halton |  | Morrison Heights PS | WWPS | Site | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 2020-07-10 11:15 | [8 empty] | 1 |  | 43_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
44 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 11 | Wet Well Concrete Structure | 2 | Morrison Heights PS Wet Well | Halton | In Service | Morrison Heights PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Tank, Concrete | [5 empty] | 1973 |  | 2033 | HR-MORI-124 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:29 | Maira Rafiq | 2020-09-22 11:24 |  |  |  |  | Pumping | Wet Well | 1 |  | 44_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Exposed corroded reinforcement and concrete spalling noted | Fair
45 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 12 | Site |  | Raymar Pl PS Site | Halton |  | Raymar Pl PS | WWPS | Site | Asset Hierarchy | Asset Hierarchy | [18 empty] | 1 | ea. | 2020 | [10 empty] | George Illaszewicz | 2020-07-10 11:15 | [8 empty] | 1 |  | 45_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
46 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Wet Well Concrete Structure | 2 | Raymar Pl PS Wet Well | Halton | In Service | Raymar Pl PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Tank, Concrete | [5 empty] | 1985 |  |  | HR-RAYM-054 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:32 | Maira Rafiq | 2020-09-22 12:45 |  |  |  |  | Pumping | Wet Well | 1 |  | 46_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Exposed corroded reinforcement and concrete spalling was noted at the pipe penetration | Fair
53 |  |  | 201575 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 645 | Sewage Lift Pump #1 | 2 | Sewage Lift Pump #1;Flygt;CP3085.183;;8 L/s at 8m TDH 3 hp | Halton | In Service | Garlock Gdns PS | Garlock Gdns PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | FLYGT | C3085-183-4438 | 3085-183-0710219 |  | 2020 | 1977 |  |  | HR-GGDN-015 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 17:00 | Maira Rafiq | 2020-09-22 10:50 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 53_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | The pump was near the end of its expected life.
54 |  |  | 201576 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 53 | Sewage Lift Pump #1 Check Valve | 2 | Check Valve #1;;;;100 mm dia | Halton | In Service | Garlock Gdns PS | Garlock Gdns PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Valve | VALMATIC | SWING FLEX | N/A |  | 2020 | 1977 |  |  | HR-GGDN-006 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 17:00 | Maira Rafiq | 2020-09-22 10:51 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 54_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Heavy corrosion was observed on the valve.
55 |  |  | 211093 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 53 | Sewage Lift Pump #1 Discharge Valve | 2 | Knife Gate Valve #1;;;;100 mm dia | Halton | In Service | Garlock Gdns PS | Garlock Gdns PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Valve | STAFSJO | NW100 | N/A |  | 2020 | 1977 |  |  | HR-GGDN-005 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 17:01 | Maira Rafiq | 2020-09-22 10:52 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 55_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Heavy corrosion was observed on the valve.
56 |  |  | 219156 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 41 | Variable Frequency Drive Pump # 1 | 2 | 26.1 AMPS | Halton |  | Garlock Gdns PS | Garlock Gdns PS | Wet Well | Process Electrical | Process Electrical |  | VFD | ALLEN BRADLEY | POWERFLEX-40 | BB024NOW6350010 |  | 2020 | 1977 | [10 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-22 11:17 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 56_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
57 |  |  | 201577 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 645 | Sewage Lift Pump #2 | 2 | Sewage Lift Pump #1;Flygt;CP3085.183;;8 L/s at 8m TDH 3 hp | Halton | Not In Service | Garlock Gdns PS | Garlock Gdns PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | FLYGT | 3085-183-4438 | 3085-183-0710220 |  | 2020 | 1977 |  |  | HR-GGDN-016 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 17:02 | Maira Rafiq | 2020-09-22 10:52 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 57_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | The pump was near the end of its expected service life
58 |  |  | 201578 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 57 | Sewage Lift Pump #2 Check Valve | 2 | Check Valve #2;;;;100 mm dia | Halton | In Service | Garlock Gdns PS | Garlock Gdns PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Valve | VALMATIC | SWING FLEX | N/A |  | 2020 | 1977 |  |  | HR-GGDN-010 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 17:03 | Maira Rafiq | 2020-09-22 10:52 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 58_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Severe corrosion was observed on the surface of the valve
59 |  |  | 211094 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 57 | Sewage Lift Pump #2 Discharge Valve | 2 | Knife Gate Valve #1;;;;100 mm dia | Halton | In Service | Garlock Gdns PS | Garlock Gdns PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Valve | STAFSJO | NW100 | N/A |  | 2020 | 1977 |  |  | HR-GGDN-012 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 17:05 | Maira Rafiq | 2020-09-22 10:53 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 59_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Heavy corrosion was observed on the valve
60 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 40 | Forcemain | 4 | 100mm diameter, approx. 237m ductile forcemain | Halton | In Service | Garlock Gdns PS | Garlock Gdns PS | Site | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 2020 | 1977 | [10 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 17:06 | Maira Rafiq | 2020-09-22 10:53 |  |  |  |  | Pumping | Discharge Header |  |  | 60_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | The pipe was at half of its expected service life.
61 |  |  | 201546 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 648 | Wet Well Exhaust Fan | 1 | 115 VOLTS/PHASE 1, capacity: 325 cfm | Halton |  | Raymar Pl PS | Raymar Pl PS | Wet Well | Building Mechanical | Building Services |  | Fan | N/A | N/A | N/A |  | 2020 | 1985 |  |  | HR-RAYM-001 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:39 | Maira Rafiq | 2020-09-22 13:22 |  |  |  |  | Pumping | HVAC - Distribution Systems |  |  | 61_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Surface staining on exhaust fan pipe | fair
62 |  |  | 201547 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 648 | Sewage Lift Pump #1 | 2 | Sewage Lift Pump #1;Flygt;CP3101;;6.6 L/s at 11.4 m TDH 5 HP | Halton | In Service | Raymar Pl PS | Raymar Pl PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | FLYGT | 3101 MT | 10534 |  | 2020 | 1985 |  |  | HR-RAYM-025 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 14:17 | Maira Rafiq | 2020-09-22 13:07 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 62_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | The pump was near the end of its expected service life.
63 |  |  | 211079 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 62 | Sewage Lift Pump #1 Check Valve | 2 | Check Valve #1;Flygt;;;100 mm dia | Halton | In Service | Raymar Pl PS | Raymar Pl PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Valve | HILLEN DE LELIE | BALL CHECK | N/A |  | 2020 | 1985 |  |  | HR-RAYM-009 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 14:23 | Maira Rafiq | 2020-09-22 13:08 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 63_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Heavy corrosion was observed on the surface of the valve
64 |  |  | 211080 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 62 | Sewage Lift Pump #1 Discharge Valve | 2 | Gate Valve #1;;;;100 mm dia | Halton | In Service | Raymar Pl PS | Raymar Pl PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Valve | JENKINS | GATE VALVE | N/A |  | 2020 | 1985 |  |  | HR-RAYM-010 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 14:29 | Maira Rafiq | 2020-09-22 13:08 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 64_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Heavy corrosion was observed on the surface of the valve
65 |  |  | 201548 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 648 | Sewage Lift Pump #2 | 2 | Sewage Lift Pump #2;Flygt;CP3101;;6.6 L/s at 11.4 m TDH 5 HP | Halton | In Service | Raymar Pl PS | Raymar Pl PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | FLYGT | C3102-180 | 355048-433 |  | 2020 | 1985 |  |  | HR-RAYM-012 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 14:34 | Maira Rafiq | 2020-09-22 13:09 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 65_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | The pump was near the end of its expected service life.
66 |  |  | 211081 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 65 | Sewage Lift Pump #1 Check Valve | 2 | Check Valve #1;Flygt;;;100 mm dia | Halton | In Service | Raymar Pl PS | Raymar Pl PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Valve | HILLEN DE LELIE | BALL CHECK | N/A |  | 2020 | 1985 |  |  | HR-RAYM-007 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 14:47 | Maira Rafiq | 2020-09-22 13:10 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 66_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Heavy corrosion was observed on the surface of the valve.
67 |  |  | 211082 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 65 | Sewage Lift Pump #1 Discharge Valve | 2 | Gate Valve #2;;;;100 mm dia | Halton | In Service | Raymar Pl PS | Raymar Pl PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Valve | JENKINS | GATE VALVE | N/A |  | 2020 | 1985 |  |  | HR-RAYM-006 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 14:49 | Maira Rafiq | 2020-09-22 13:11 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 67_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Heavy corrosion was observed on the surface of the valve
68 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 45 | Forcemain | 4 | 100mm diameter, approx. 165m PVC SDR 35 pipe | Halton | In Service | Raymar Pl PS | Raymar Pl PS | Site | Process Mechanical | Process Piping |  | Piping, PVC |  |  |  |  | 2020 | 1985 | [10 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 14:54 | Maira Rafiq | 2020-09-22 13:13 |  |  |  |  | Pumping | Discharge Header |  |  | 68_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | assumed to be good
69 |  |  | 201661 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 646 | Dry Well Sump Pump | 1 | 1/4" | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Pump, Centrifugal | N/A | SE-CIA-SFS | N/A |  | 2020 | 1973 |  |  | HR-MORI-024 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:38 | Maira Rafiq | 2020-09-22 12:34 |  |  |  |  | Pumping | Pump Assembly |  |  | 69_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the pump. The pump was beyond its expected service life. | Moderate surface corrosion
70 |  |  | 201662 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 647 | TRANSMITTER LEVEL WET WELL #1 | 2 | 72" Wet Well Level Transmitter; Siemens Milltronics; Multiranger 100; ; ; | Halton | In Service | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Instrumentation | Process Instrumentation |  | Transmitter | MILLTRONICS | MULTIRANGER 100 | 012105122XB |  | 2020 | 2008 |  | 2030 | HR-MORI-009 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 18:11 | Maira Rafiq | 2020-08-24 09:31 |  |  |  |  | Pumping | Wet Well |  |  | 70_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | good
71 |  |  | 201653 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 646 | Dry Wall Exhaust Fan | 1 |  | Halton |  | Morrison Heights PS | Morrison Heights PS | Dry Well | Building Mechanical | Building Services |  | Fan | FASCO | D112 | 7108-0195 |  | 2020 | 1973 |  |  | HR-MORI-115 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:38 | Maira Rafiq | 2020-09-22 12:35 |  |  |  |  | Pumping | HVAC - Distribution Systems |  |  | 71_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | paint peeling | fair
72 |  |  | 201654 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 646 | Sewage Lift Pump #1 | 2 | Sewage Lift Pump #1;Clow Pumps;N4310;;12 L/s 7.5 hp | Halton | In Service | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | CLOW | N 4310 | 918126 |  | 2020 | 1973 |  |  | HR-MORI-020 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 10:26 | Maira Rafiq | 2020-09-22 12:09 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 72_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the pump. The pump was beyond its expected service life.
73 |  |  | 217113 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 72 | Sewage Lift Pump #1 Check Valve | 2 | Check Valve #1;Swing-Flex;Model 504A;;100 mm dia | Halton | In Service | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | EDDY IOWA | N/A | N/A |  | 2020 | 1973 |  |  | HR-MORI-019 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 10:20 | Maira Rafiq | 2020-09-22 12:04 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 73_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the valve. The valve was beyond its expected service life
74 |  |  | 201656 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 72 | Sewage Lift Pump #1 Motor Drive | 2 | 7.5 HP | Halton |  | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Electrical | Process Electrical |  | Motor | U.S. MOTORS | TYPE 1 | 9204320-901 |  | 2020 | 1973 |  |  | HR-MORI-012 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-22 12:26 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 74_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | minor paint wear
75 |  |  | 211145 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 72 | Sewage Lift Pump #1 Inlet Valve | 2 | Inlet Knife Gate Valve #1;Trueline;;;100 mm dia | Halton | In Service | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | IOWA | N/A | N/A |  | 2020 | 1973 |  |  | HR-MORI-022 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 10:16 | Maira Rafiq | 2020-09-22 12:05 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 75_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the valve. The valve was beyond its expected service life.
76 |  |  | 211146 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 72 | Sewage Lift Pump #1 Discharge Valve | 2 | Discharge Knife Gate Valve #1;Trueline;;;100 mm dia | Halton | In Service | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | IOWA | N/A | N/A |  | 2020 | 1973 |  |  | HR-MORI-018 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 11:17 | Maira Rafiq | 2020-09-22 12:06 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 76_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the valve. The valve was beyond its expected service life.
78 |  |  | 201657 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 646 | Sewage Lift Pump #2 | 2 | Sewage Lift Pump #2;Clow Pumps;N4310;;12 L/s 7.5 hp | Halton | In Service | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | CLOW | N 4310 | 918126 |  | 2020 | 1973 |  |  | HR-MORI-012 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 10:26 | Maira Rafiq | 2020-09-22 12:09 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 78_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the pump. The pump was beyond its expected service life.
79 |  |  | 201658 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 78 | Sewage Lift Pump #2 Check Valve | 2 | Check Valve #2;Swing-Flex;Model 504A;;100 mm dia | Halton | In Service | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | EDDY IOWA | N/A | N/A |  | 2020 | 1973 |  |  | HR-MORI-014 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 11:12 | Maira Rafiq | 2020-09-22 12:10 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 79_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Deterioration and corrosion was observed on the surface of the valve. The valve was beyond its expected service life
80 |  |  | 201659 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 78 | Sewage Lift Pump #2 Motor Drive | 2 | 7.5 HP | Halton |  | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Electrical | Process Electrical |  | Motor | U.S. ELECTRIC MOTORS | N/A | 9204320-901 |  | 2020 | 1973 |  |  | HR-MORI-020 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-22 12:26 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 80_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | minor paint wear
81 |  |  | 211147 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 78 | Sewage Lift Pump #2 Inlet Valve | 2 | Inlet Knife Gate Valve #1;Trueline;;;100 mm dia | Halton | In Service | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | IOWA | N/A | N/A |  | 2020 | 1973 |  |  | HR-MORI-011 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 11:15 | Maira Rafiq | 2020-09-22 12:10 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 81_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion was observed on the surface of the valve. The valve was beyond its expected service life.
82 |  |  | 211148 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 78 | Sewage Lift Pump #2 Discharge Valve | 2 | Discharge Knife Gate Valve #1;Trueline;;;100 mm dia | Halton | In Service | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | IOWA | N/A | N/A |  | 2020 | 1973 |  |  | HR-MORI-015 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 11:18 | Maira Rafiq | 2020-09-22 12:12 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 82_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Minor deterioration was observed on the surface of the valve. The valve was beyond its expected service life.
83 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 43 | Forcemain | 5 | 150mm diameter, approx. 254m PVC series 125 pipe | Halton | In Service | Morrison Heights PS | Morrison Heights PS | Site | Process Mechanical | Process Piping |  | Piping, PVC |  |  |  |  | 2020 | 1973 | [10 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 11:41 | Maira Rafiq | 2020-09-22 12:12 |  |  |  |  | Pumping | Discharge Header |  |  | 83_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | assumed to be fair | The pipe passed half of its expected service life.
129 |  |  | 201612 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 24 | PUMP #1 SUMP | 1 | Sump Pump;;;; | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Building Mechanical | Building Services |  | Pump | HYDROMATIC |  |  |  | 2020 | 1975 |  |  | HR-CNRY-010 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 09:06 | Maira Rafiq | 2020-09-18 11:55 |  |  |  |  | Pumping | Pump Assembly |  |  | 129_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration were observed on the surface of the pump. The pump is beyond the end of its expected service life
130 |  |  | 211126 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 638 | TRANSMITTER LEVEL WET WELL | 2 | 94.5" Wet Well Level Transmitter; Siemens Milltronics; MultiRanger 200; ; ; | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Instrumentation | Process Instrumentation |  | Transmitter | MILLTRONICS | MULTIRANGER PLUS | 082191 012-19 |  | 2020 | 2009 |  | 2030 | HR-CNRY-008 |  |  |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 15:12 | Maira Rafiq | 2020-08-24 08:39 |  |  |  |  | Pumping | Wet Well |  |  | 130_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Dust | Corrosion
131 |  |  | 201605 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 638 | FAN EXHAUST #1 | 1 | 115 VOLTS/PHASE 1 | Halton | Missing | Chancery Lane PS | Chancery Lane PS | Dry Well | Building Mechanical | Building Services |  | Fan | N/A | N/A | N/A |  | 2020 | 1975 | [10 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:23 | Maira Rafiq | 2020-09-18 11:53 |  |  |  |  | Building | HVAC - Distribution Systems |  |  | 131_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | The exhaust fan was missing | As per Section 7.2.9 of MOECC's Design Guidelines for Sewage Works, mechanical ventilation is required for below ground surface dry well.
132 |  |  | 201606 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 638 | Sewage Lift Pump #1 | 2 | Sewage Lift Pump #1;Smith & Loveless;4B2A;;16.7 L/s at 11.6 m TDH 5HP | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Pump | SMITH AND LOVELESS | 4B2A | 9750232 |  | 2020 | 1975 |  |  | HR-CNRY-012 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 09:09 | Maira Rafiq | 2020-09-18 12:36 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 132_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | Deterioration was observed on the surface of the pump and it is beyond the end of its expected service life.
133 |  |  | 201607 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 132 | Sewage Lift Pump #1 Check Valve | 2 | Check Valve #1;Smith & Loveless;;150 mm dia | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | SMITH AND LOVELESS |  |  |  | 2020 | 1975 |  |  | HR-CNRY-014 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 09:24 | Maira Rafiq | 2020-09-18 12:52 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 133_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | Corrasion and deterioration was observed on the surface of the valve. The valve is beyond its expected service life.
134 |  |  | 201608 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 638 | MOTOR DRIVE SEWAGE LIFT PUMP #1 | 2 | 5 HP/1160 RPM | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Electrical | Process Electrical |  | Motor | ROBBIN & MYERS | S & L - N-BPM1 | CF50232 |  | 2020 | 1975 |  |  | HR-CNRY-116 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-18 11:28 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 134_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | minor corrosion on casing
135 |  |  | 211127 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 132 | Sewage Lift Pump #1 Inlet Valve | 2 | Inlet Gate Valve No.1;Smith & Loveless;;;150 mm dia | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | STOCKHAM | N/A | N/A |  | 2020 | 1975 |  |  | HR-CNRY-011 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 09:33 | Maira Rafiq | 2020-09-18 12:52 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 135_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | Corrosion and deterioration was observed on the surface of the valve. The valve is beyond its expected service life.
136 |  |  | 211128 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 132 | Sewage Lift Pump #1 Discharge Valve | 2 | Discharge Gate Valve No.1;Smith & Loveless;;;150 mm dia | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | STOCKHAM | N/A | N/A |  | 2020 | 1975 |  |  | HR-CNRY-015 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 09:36 | Maira Rafiq | 2020-09-18 12:52 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 136_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | Corrosion and deterioration was observed on the surface of the valve. The valve is beyond its expected service life.
137 |  |  | 201609 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 638 | Sewage Lift Pump #2 | 2 | Sewage Lift Pump #2;Smith & Loveless;4B2A;;16.7 L/s at 11.6 m TDH 5HP | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | SMITH AND LOVELESS | 4B2A | 9750232 |  | 2020 | 1975 |  |  | HR-CNRY-022 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 09:39 | Maira Rafiq | 2020-09-18 12:52 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 137_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | Deterioration was observed on the surface of the pump and it is beyond the end of its expected service life.
138 |  |  | 201610 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 137 | Sewage Lift Pump #2 Check Valve | 2 | Check Valve #2;Smith & Loveless;;150 mm dia | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | SMITH AND LOVELESS | N/A | N/A |  | 2020 | 1975 |  |  | HR-CNRY-021 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 09:45 | Maira Rafiq | 2020-09-18 12:52 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 138_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | Corrasion and deterioration was observed on the surface of the valve. The valve is beyond its expected service life.
139 |  |  | 201611 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 24 | MOTOR DRIVE SEWAGE LIFT PUMP #2 | 2 | 5 HP/1160 RPM | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Electrical | Process Electrical |  | Motor | ROBBIN & MYERS | S&L- N-BPMII | CB50231 |  | 2020 | 1975 |  |  | HR-CNRY-116 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-18 11:29 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 139_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | minor corrosion on casing
140 |  |  | 211129 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 137 | Sewage Lift Pump #2 Inlet Valve | 2 | Inlet Gate Valve No.2;Smith & Loveless;;;150 mm dia | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | STOCKHAM | N/A | N/A |  | 2020 | 1975 |  |  | HR-CNRY-020 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 09:51 | Maira Rafiq | 2020-09-18 12:53 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 140_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | Corrosion and deterioration was observed on the surface of the valve. The valve is beyond its expected service life.
141 |  |  | 211130 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 137 | Sewage Lift Pump #1 Discharge Valve | 2 | Discharge Gate Valve No.2;Smith & Loveless;;;150 mm dia | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | STOCKHAM | N/A | N/A |  | 2020 | 1975 |  |  | HR-CNRY-023 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 09:55 | Maira Rafiq | 2020-09-18 12:53 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 141_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | Corrosion and deterioration was observed on the surface of the valve. The valve is beyond its expected service life.
142 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 25 | Forcemain | 4 | 150mm diameter, approx. 350 m ductile Iron forcemain piping | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Site | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 2020 | 1975 | [10 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 09:57 | Maira Rafiq | 2020-09-18 12:42 |  |  |  |  | Pumping | Discharge Header |  |  | 142_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | assumed to be in good condition | The pipe is at half of its expected service life.
143 |  |  | 201557 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 26 | PUMP #1 SUMP | 1 | Sump Pump;;;; | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Building Mechanical | Building Services |  | Pump, Centrifugal | SMITH AND LOVELESS | N/A | N/A |  | 2020 | 1983 |  |  | HR-CTWL-019 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 10:41 | Maira Rafiq | 2020-09-20 10:57 |  |  |  |  | Pumping | Pump Assembly |  |  | 143_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Severe corrosion and deterioration were observed on the surface of the pump. The pump was near the end of its expected service life.
144 |  |  | 201558 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 633 | WET WELL LEVEL TRANSMITTER #1 | 2 | 80" Wet Well Level Transmitter; Siemens Milltronics; Multiranger Plus; ; ; | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation |  | Transmitter | MILLTRONICS | MULTIRANGER PLUS | 061489 186-07 |  | 2020 | 2009 |  | 2025 | HR-CTWL-005 |  |  |  | 1 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 16:13 | Maira Rafiq | 2020-09-20 10:52 |  |  |  |  | Pumping | Wet Well |  |  | 144_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | good
145 |  |  | 201550 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 632 | FAN EXHAUST #1 | 1 | 115 VOLTS/PHASE 1 | Halton | Missing | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Building Mechanical | Building Services |  | Fan |  |  |  |  | 2020 | 1983 |  | 2021 | [8 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:25 | Maira Rafiq | 2020-09-20 10:46 |  |  |  |  | Building | HVAC - Distribution Systems |  |  | 145_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | As per Section 7.2.9 of MOECC's Design Guidelines for Sewage Works, mechanical ventilation is required for below ground surface dry well.
146 |  |  | 201551 | 0 | [7 empty] | FALSE | FALSE | FALSE | TRUE | 632 | Sewage Lift Pump #1 | 2 | Sewage Lift Pump #1;Smith & Loveless;4B2;;;16.5 L/s at 10.1 m TDH 5 HP | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | SMITH AND LOVELESS | 4B2 | 6537098 |  | 2020 | 1983 |  |  | HR-CTWL-017 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 10:54 | Maira Rafiq | 2020-09-20 11:01 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 146_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the pump. The pump was near the end of its expected service life.
147 |  |  | 201552 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 146 | Sewage Lift Pump #1 Check Valve | 2 | Discharge Check Valve #1;Smith and Loveless;;;150 mm dia | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | SMITH AND LOVELESS |  |  |  | 2020 | 1983 |  |  | HR-CTWL-016 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 11:00 | Maira Rafiq | 2020-09-20 11:02 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 147_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the valve. The valve is near the end of its expected service life.
148 |  |  | 201553 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 146 | Sewage Lift Pump #1 Motor Drive | 2 | 5 HP/1160 RPM | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Motor | ROBIN MYERS |  | ABM3U7098 |  | 2020 | 1983 |  |  | HR-CTWL-017 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-20 11:05 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 148_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Minor surface corrosion
149 |  |  | 211083 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 26 | Sewage Lift Pum #1 Inlet Valve | 2 | Inlet Gate Valve #1;Clow;;;150 mm dia | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | EDDY IOWA | N/A | N/A |  | 2020 | 1983 |  | 0 | HR-CTWL-018 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 11:05 | Maira Rafiq | 2020-09-20 11:02 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 149_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the valve. The valve was near the end of its expected service life.
150 |  |  | 211084 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 146 | Sewage Lift Pump #1 Discharge Valve | 2 | Discharge Gate Valve #1;Clow;;;150 mm dia | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | CLOW | N/A | N/A |  | 2020 | 1983 |  |  | HR-CTWL-015 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 11:05 | Maira Rafiq | 2020-09-20 11:03 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 150_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the valve. The valve was near the end of its expected service life.
151 |  |  | 201554 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 632 | Sewage Lift Pump #2 | 2 | Sewage Lift Pump #2;Smith & Loveless;4B2;;;16.5 L/s at 10.1 m TDH 5 HP | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | SMITH AND LOVELESS | 4B2 | 6537097 |  | 2020 | 1983 |  |  | HR-CTWL-010 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 11:16 | Maira Rafiq | 2020-09-20 11:04 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 151_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the pump. The pump was near the end of its expected service life.
152 |  |  | 201555 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 151 | Sewage Lift Pump #2 Check Valve | 2 | Discharge Check Valve #2;Smith and Loveless;;;150 mm dia | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | SMITH AND LOVELESS | N/A | N/A |  | 2020 | 1983 |  |  | HR-CTWL-012 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 11:22 | Maira Rafiq | 2020-09-20 11:04 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 152_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the valve. The valve is near the end of its expected service life.
153 |  |  | 201556 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 151 | Sewage Lift Pump #2 Motor Drive | 2 | 5 HP/1160 RPM | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Motor | ROBIN MYERS |  | ABM3U7097 |  | 2020 | 1983 |  |  | HR-CTWL-027 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-20 11:06 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 153_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Minor surface corrosion and paint wear
154 |  |  | 211085 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 151 | Sewage Lift Pump #2 Inlet Valve | 2 | Inlet Gate Valve #2;Clow;;;150 mm dia | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | EDDY IOWA | N/A | N/A |  | 2020 | 1983 |  |  | HR-CTWL-009 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 11:32 | Maira Rafiq | 2020-09-20 11:06 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 154_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the valve. The valve was near the end of its expected service life.
155 |  |  | 211086 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 151 | Sewage Lift Pump #2 Discharge Valve | 2 | Discharge Gate Valve #2;Clow;;;150 mm dia | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | CLOW | N/A | N/A |  | 2020 | 1983 |  |  | HR-CTWL-013 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 11:37 | Maira Rafiq | 2020-09-20 11:07 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 155_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the valve. The valve was near the end of its expected service life.
156 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 27 | Forcemain | 4 | 200mm diameter, approx. 40m ductile iron forcemain | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Site | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 2020 | 1983 | [10 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 13:21 | Maira Rafiq | 2020-09-20 11:07 |  |  |  |  | Pumping | Discharge Header |  |  | 156_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Good
157 |  |  | 201649 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 29 | PUMP SUMP | 1 | Sump Pump;;;; | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Building Mechanical | Building Services |  | Pump, Centrifugal | N/A | N/A | N/A |  | 2020 | 1974 |  |  | HR-CMNK-021 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 13:58 | Maira Rafiq | 2020-09-21 15:27 |  |  |  |  | Pumping | Pump Assembly |  |  | 157_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the pump. The pump is beyond its expected service life.
158 |  |  | 201651 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 641 | TRANSMITTER LEVEL WET WELL #1 | 2 | 76.25" Wet Well Level Transmitter; Siemens Milltronics; Multiranger Plus; ; ; | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Process Instrumentation | Process Instrumentation |  | Transmitter | MILLTRONICS | MULTIRANGER PLUS | 05-25-94 118-6D |  | 2020 | 2009 |  | 2030 | HR-CMNK-005 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 17:01 | Maira Rafiq | 2020-08-24 08:57 |  |  |  |  | Pumping | Wet Well |  |  | 158_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Minor corrosion on nuts
159 |  |  | 201640 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 640 | Dry Well Exhaust Fan | 1 | 115 VOLTS, installation year assumed to be 1974 | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Building Mechanical | Building Services |  | Fan | N/A | N/A | N/A |  | 2020 | 1974 |  |  | HR-CMNK-121 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:31 | Maira Rafiq | 2020-09-21 15:23 |  |  |  |  | Building | HVAC - Distribution Systems |  |  | 159_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Surface corrosion
160 |  |  | 201641 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 640 | Sewage Lift Pump #1 | 2 | Sewage Lift Pump #1;Clow;N4310;;6.3 L/s 3 hp | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | CLOW | N4310 | 918126 |  | 2020 | 1974 |  |  | HR-CMNK-013 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 14:06 | Maira Rafiq | 2020-09-21 15:31 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 160_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | Corrosion and deterioration was observed on the surface of the pump. The pump was beyond its expected service life.
161 |  |  | 201642 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 160 | Sewage Lift Pump #1 Check Valve | 2 | Check Valve #1;Crow;;;100 mm dia | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | IOWA | N/A | N/A |  | 2020 | 1974 |  |  | HR-CMNK-014 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 14:12 | Maira Rafiq | 2020-09-21 15:32 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 161_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Moderate corrosion and deterioration was observed on the surface of the valve. The valve was beyond its expected service life.
162 |  |  | 201643 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 29 | Sewage Lift Pump #1 Motor Drive | 2 | 7.9HP | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Process Electrical | Process Electrical |  | Motor | U.S. MOTORS | AV-9 | R2071304 |  | 2020 | 1974 |  |  | HR-CMNK-013 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-21 15:14 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 162_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | paint wear
163 |  |  | 211141 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 160 | Sewage Lift Pump #1 Inlet Valve | 2 | Inlet Gate Valve #1;Crow;;;100 mm dia | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | IOWA | N/A | N/A |  | 2020 | 1974 |  |  | HR-CMNK-011 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 14:13 | Maira Rafiq | 2020-09-21 15:32 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 163_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the valve.
164 |  |  | 211142 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 160 | Sewage Lift Pump #1 Discharge Valve | 2 | Discharge Gate Valve #1;Crow;;;100 mm dia | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | IOWA | N/A | N/A |  | 2020 | 1974 |  |  | HR-CMNK-015 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 14:13 | Maira Rafiq | 2020-09-21 15:33 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 164_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the valve.
165 |  |  | 201645 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 640 | Sewage Lift Pump #2 | 2 | Sewage Lift Pump #2;Clow;N4310;;6.3 L/s 3 hp | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | CLOW | N4310 | 918127 |  | 2020 | 1974 |  |  | HR-CMNK-019 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 14:15 | Maira Rafiq | 2020-09-21 15:34 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 165_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Corrosion and deterioration was observed on the surface of the pump. The pump was beyond its expected service life.
166 |  |  | 201646 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 165 | Sewage Lift Pump #2 Check Valve | 2 | Check Valve #1;Crow;;;100 mm dia | Halton | 20 | Cumnock PS | Cumnock PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | IOWA | N/A | N/A |  | 2020 | 1974 |  |  | HR-CMNK-018 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 14:18 | Maira Rafiq | 2020-09-21 15:34 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 166_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the pump. The pump was beyond its expected service life.
167 |  |  | 201647 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 29 | Sewage Lift Pump #2 Motor Drive | 2 | 7.5P | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Process Electrical | Process Electrical |  | Motor | U.S. MOTORS | AV-9 | R2071304 |  | 2020 | 1974 |  |  | HR-CMNK-019 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-21 15:15 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 167_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | paint wear
168 |  |  | 211143 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 165 | Sewage Lift Pump #2 Inlet Valve | 2 | Inlet Gate Valve #2;Crow;;;100 mm dia | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | IOWA | N/A | N/A |  | 2020 | 1974 |  |  | HR-CMNK-020 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 14:19 | Maira Rafiq | 2020-09-21 15:34 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 168_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the valve.
169 |  |  | 211144 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 165 | Sewage Lift Pump #2 Discharge Valve | 2 | Discharge Gate Valve #2;Crow;;;100 mm dia | Halton | In Service | Cumnock PS | Cumnock PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | IOWA (CLOW) | N/A | N/A |  | 2020 | 1974 |  |  | HR-CMNK-017 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 14:22 | Maira Rafiq | 2020-09-21 15:35 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 169_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the valve.
170 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 30 | Forcemain | 4 | 150mm diameter, approx. 79 m ductile iron pipe | Halton | In Service | Cumnock PS | Cumnock PS | Site | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 2020 | 1974 | [10 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 14:24 | Maira Rafiq | 2020-09-21 15:36 |  |  |  |  | Pumping | Discharge Header |  |  | 170_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | assumed to be good | The pipe was at half of its expected service life.
172 |  |  | 211126 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 642 | TRANSMITTER LEVEL WET WELL | 2 | 94.5" Wet Well Level Transmitter; Siemens Milltronics; Multiranger 200; ; ; | Halton | In Service | Ennisclaire Drive PS | WWPS | Site | Process Instrumentation | Process Instrumentation |  | Transmitter | MILLTRONICS | MULTIRANGER PLUS | 082191 012-19 |  | 2020 | 2019 |  | 2035 | HR-ENIS-030 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 17:40 | Maira Rafiq | 2020-08-24 09:02 |  |  |  |  | Pumping | Wet Well | 1 |  | 172_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | very good
174 |  |  | 201606 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 642 | Sewage Lift Pump #1 | 2 | Sewage Pump #1;Flygt;C3082MT;;7.8 L/s at 7.2 m TDH 2hp | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Pump, Centrifugal | SMITH AND LOVELESS | 4B2A | 9750232 |  | 2020 | 1977 |  |  | HR-ENIS-009 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:01 | Maira Rafiq | 2020-09-21 17:12 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 174_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | The pump was beyond its expected service life.
175 |  |  | 201607 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 174 | Sewage Lift Pump #1 Check Valve | 2 | Check Valve #1;;;;100 mm dia | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | SMITH AND LOVELESS |  |  |  | 2020 | 1977 |  |  | HR-ENIS-010 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 15:01 | Maira Rafiq | 2020-09-21 17:13 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 175_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Heavy corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
177 |  |  | 211127 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 174 | Sewage Lift Pump #1 Knife Gate Valve | 2 | Knife Gate Valve #1;;;;100 mm dia | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | STOCKHAM | N/A | N/A |  | 2020 | 1977 |  |  | HR-ENIS-012 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 15:10 | Maira Rafiq | 2020-09-21 17:13 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 177_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Heavy corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
178 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 33 | Forcemain | 3 | 100mm diameter, approx. 290m Ductile Iron forcemain | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Site | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 2020 | 1977 | [10 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 15:11 | Maira Rafiq | 2020-09-21 17:14 |  |  |  |  | Pumping | Discharge Header |  |  | 178_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | assumed to be fair | The pipe was at half of its expected service life
179 |  |  | 201543 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 643 | Sump Pump #1 | 1 | Sump Pump;;;; | Halton | In Service | First Street PS | First Street PS | Dry Well | Building Mechanical | Building Services |  | Pump, Submersible | HYDROMATIC | SV-25A |  |  | 2020 | 1986 |  |  | HR-FRST-009 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:16 | Maira Rafiq | 2020-09-21 23:41 |  |  |  |  | Building | Plumbing - Sanitary Waste |  |  | 179_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | Corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
180 |  |  | 201545 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 644 | TRANSMITTER LEVEL WET WELL #1 | 2 | 18.5" Wet Well Level Transmitter; Siemens Milltronics; Multiranger Plus; ; ; | Halton | In Service | First Street PS | First Street PS | Dry Well | Process Instrumentation | Process Instrumentation |  | Transmitter | MILLTRONICS | MULTIRANGER PLUS | 05-17-94 211GE |  | 2020 | 2009 |  | 2030 | HR-FRST-006 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 17:50 | Maira Rafiq | 2020-08-24 09:10 |  |  |  |  | Pumping | Wet Well |  |  | 180_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | nuts were not secured properly | good
181 |  |  | 201536 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 643 | Dry Well Exhaust Fan | 1 | 115 V./60 HZ., Installation year assumed to be 1985 | Halton |  | First Street PS | First Street PS | Dry Well | Building Mechanical | Building Services |  | Fan | DAYTON | 40 | N/A |  | 2020 | 1986 |  |  | HR-FRST-018 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:36 | Maira Rafiq | 2020-09-22 12:40 |  |  |  |  | Pumping | HVAC - Distribution Systems |  |  | 181_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Paint peeling | fair
182 |  |  | 201537 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 643 | Sewage Lift Pump #1 | 2 | Sewage Lift Pump #1;Clow;Model 4310;;15.8 L/s at 12.2 m TDH 7.5hp | Halton | In Service | First Street PS | First Street PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Pump | CLOW | 431O | 261755 |  | 2020 | 1986 |  |  | HR-FRST-016 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:23 | Maira Rafiq | 2020-09-21 23:28 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 182_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Deterioration was observed on the surface of the pump. The pump was near the end of its expected service life.
183 |  |  | 201538 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 182 | Sewage Lift Pump #1 Check Valve | 2 | Check Valve #1;Kennedy;;;100 mm dia | Halton | In Service | First Street PS | First Street PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | KENNEDY | FIG 106 | 11071 |  | 2020 | 1986 |  |  | HR-FRST-015 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:28 | Maira Rafiq | 2020-09-21 23:29 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 183_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Corrosion and deterioration was observed on the valve. The pump was near the end of its expected service life.
184 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 36 | Sewage Lift Pump #2 Motor Drive | 2 | 7.5 HP/1755 RPM | Halton |  | First Street PS | First Street PS | Dry Well | Process Electrical | Process Electrical |  | Motor | RELIANCE ELECTRIC | P | 1YAB31452A1 |  | 2020 | 1986 | [10 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-21 23:19 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 184_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | paint wear
185 |  |  | 211075 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 182 | Sewage Lift Pump #1 Inlet Valve | 2 | Inlet Gate Valve #1;Kennedy;;;100 mm dia | Halton | In Service | First Street PS | First Street PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | CLOW | EDDY IOWA | N/A |  | 2020 | 1986 |  |  | HR-FRST-014 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:28 | Maira Rafiq | 2020-09-21 23:29 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 185_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Corrosion and deterioration was observed on the valve. The pump was near the end of its expected service life.
186 |  |  | 211076 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 182 | Sewage Lift Pump #1 Discharge Valve | 2 | Discharge Gate Valve #1;Kennedy;;;100 mm dia | Halton | In Service | First Street PS | First Street PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | CLOW | EDDY IOWA | N/A |  | 2020 | 1986 |  |  | HR-FRST-017 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:29 | Maira Rafiq | 2020-09-21 23:30 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 186_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Very Poor | Severe corrosion and deterioration was observed on the valve. The pump was near the end of its expected service life.
187 |  |  | 201540 | 0 | [7 empty] | FALSE | FALSE | TRUE | TRUE | 643 | Sewage Lift Pump #2 | 2 | Sewage Lift Pump #2;Clow;Model 4310;;15.8 L/s at 12.2 m TDH 7.5hp | Halton | In Service | First Street PS | First Street PS | Dry Well | Process Mechanical |  |  | Pump | CLOW | 431O | 261755 |  | 2020 | 1986 |  |  | HR-FRST-010 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:32 | Maira Rafiq | 2020-09-21 23:32 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 187_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Deterioration was observed on the surface of the pump. The pump was near the end of its expected service life.
188 |  |  | 201541 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 187 | Sewage Lift Pump #2 Check Valve | 2 | Check Valve #1;;;;100 mm dia | Halton | In Service | First Street PS | First Street PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | KENNEDY | FIG 106 | 11071 |  | 2020 | 1986 |  |  | HR-FRST-011 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:34 | Maira Rafiq | 2020-09-21 23:33 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 188_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | expected service life.
189 |  |  | 201542 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 36 | Sewage Lift Pump #2 Motor Drive | 2 | 7.5 HP/1755 RPM | Halton | In Service | First Street PS | First Street PS | Dry Well | Process Electrical | Process Electrical |  | Motor | RELIANCE ELECTRIC | P | 1YAB31452A2UK |  | 2020 | 1986 |  |  | HR-FRST-023 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 14:32 | Maira Rafiq | 2020-09-21 23:19 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 189_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | paint wear
190 |  |  | 211077 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 187 | Sewage Lift Pump #2 Inlet Valve | 2 | Inlet Gate Valve #1;;;;100 mm dia | Halton | In Service | First Street PS | First Street PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | CLOW | EDDY IOWA | N/A |  | 2020 | 1986 |  |  | HR-FRST-030 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:38 | Maira Rafiq | 2020-09-21 23:33 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 190_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Corrosion and deterioration was observed on the valve. The pump was near the end of its expected service life.
191 |  |  | 211078 | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 187 | Sewage Lift Pump #2 Disccharge Valve | 2 | Discharge Gate Valve #1;;;;100 mm dia | Halton | In Service | First Street PS | First Street PS | Dry Well | Process Mechanical | Process Mechanical Equipment |  | Valve | CLOW | EDDY IOWA | N/A |  | 2020 | 1986 |  |  | HR-FRST-012 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:38 | Maira Rafiq | 2020-09-21 23:34 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 191_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | Minor deterioration was observed on the surface of the valve. The valve was near the end of its expected service life.
192 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 37 | Forcemain | 4 | 150mm diameter, approx. 150 m PVC pipe | Halton | In Service | First Street PS | First Street PS | Site | Process Mechanical | Process Piping |  | Piping, PVC |  |  |  |  | 2020 | 1986 | [10 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:44 | Maira Rafiq | 2020-09-21 23:35 |  |  |  |  | Pumping | Discharge Header |  |  | 192_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | assumed to be good
237 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 25 | Overflow Piping | 3 | 250mm diameter, approx. 147 m concrete pipe | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Site | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1975 |  |  | HR-CNRY-043 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 10:04 | Maira Rafiq | 2020-09-18 13:02 |  |  |  |  | Pumping | Wet Well |  |  | 237_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | The pipe is at half of its expected service life.
238 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 638 | Discharge Header | 3 | 150mm diameter, approx. 5 m cast iron piping | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1975 |  |  | HR-CNRY-031 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 10:12 | Maira Rafiq | 2020-09-18 13:05 |  |  |  |  | Pumping | Discharge Header |  |  | 238_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | The pipe is at half of its expected service life.
240 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 132 | Pump 1 Piping | 3 | 150mm diameter, approx. 4.5m ductile piping | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1975 |  | 0 | HR-CNRY-116 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-18 13:09 |  |  |  |  | Pumping | Discharge Header | 1 |  | 240_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | The pipe is at half of its expected service life.
241 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 137 | Pump 2 Piping | 3 | 150mm diameter, approx. 4.5m ductile piping | Halton | In Service | Chancery Lane PS | Chancery Lane PS | Dry Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1975 |  | 0 | HR-CNRY-116 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-18 13:10 |  |  |  |  | Pumping | Discharge Header | 2 |  | 241_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | The pipe is at half of its expected service life.
242 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 27 | Overflow Piping | 3 | 250mm diameter, approx. 10.5 m (4.5 m PVC pipe, 6 m CMP pipe) | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Site | Process Mechanical | Process Piping |  | Piping, PVC |  |  |  |  | 0 | 1983 | [10 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 13:22 | [6 empty] | Pumping | Wet Well |  |  | 242_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Good
243 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 146 | Pump 1 Piping | 3 | 150mm diameter, approx. 5m ductile iron pipe | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1983 |  |  | HR-CTWL-033 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 13:25 | Maira Rafiq | 2020-09-20 13:45 |  |  |  |  | Pumping | Pump Assembly |  |  | 243_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Minor corrosion
244 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 633 | Bar Screen | 2 | Bar Screen;;;; | Halton |  | Chartwell Rd. PS | Chartwell Rd. PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Screen |  |  |  |  | 0 | 1983 |  |  | HR-CTWL-054 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 15:25 | Maira Rafiq | 2020-09-20 13:47 |  |  |  |  | Pumping | Wet Well |  |  | 244_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | corrosion
247 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 30 | Overflow Piping | 3 | 300mm diameter, approx. 2.5m CMP pipe | Halton | In Service | Cumnock PS | Cumnock PS | Site | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1974 |  |  | HR-CMNK-147 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 14:33 | Maira Rafiq | 2020-09-21 15:36 |  |  |  |  | Pumping | Wet Well |  |  | 247_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Good | The pipe was at half of its expected service life.
248 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 160 | Pump 1 Piping | 3 | 100mm diameter, approx. 5m ductile pipe | Halton | In Service | Cumnock PS | Cumnock PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1974 |  |  | HR-CMNK-010 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 14:33 | Maira Rafiq | 2020-09-21 15:41 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 248_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | The pipe was at half of its expected service life.
249 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 641 | Bar Screen | 2 | Bar Screen | Halton | In Service | Cumnock PS | Cumnock PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1974 |  |  | HR-CMNK-136 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 14:36 | Maira Rafiq | 2020-09-21 15:41 |  |  |  |  | Pumping | Wet Well |  |  | 249_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | good
250 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 640 | Discharge Header | 3 | 100mm diameter, approx. 5m, ductile iron stand pipe | Halton |  | Cumnock PS | Cumnock PS | Dry Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1974 |  | 0 | [8 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-21 15:41 |  |  |  |  | Pumping | Discharge Header |  |  | 250_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Good
251 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 33 | Overflow Piping | 3 | 200mm diameter, approx. 22m | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Site | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1977 | [10 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 15:13 | Maira Rafiq | 2020-09-21 17:15 |  |  |  |  | Pumping | Wet Well |  |  | 251_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Assumed to be fair | The pipe was at half of its expected service life
252 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 174 | Pump 1 Piping | 3 | 100mm diameter, approx. 5 m | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1977 |  |  | HR-ENIS-013 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 15:15 | Maira Rafiq | 2020-09-21 17:16 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 252_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Heavy corrosion was observed on the surface of the pipe
253 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 399 | Pump 2 Piping | 3 | 100mm diameter, approx. 5m | Halton |  | Ennisclaire Drive PS | WWPS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1977 |  | 0 | HR-ENIS-013 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-21 17:18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 253_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Heavy corrosion was observed on the surface of the pipe
254 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 38 | Overflow Piping | 3 | 250mm diameter, approx. 3.5 m connect to storm sewer | Halton | In Service | First Street PS | First Street PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1986 |  |  | HR-FRST-012 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:46 | Maira Rafiq | 2020-09-21 23:36 |  |  |  |  | Pumping | Suction |  |  | 254_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Good
255 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 35 | Emergency Pumping Riser | 3 | 100mm diameter, approx. 1.6m | Halton |  | First Street PS | First Street PS |  | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1986 | [10 empty] | 1 | ea. | 2020 | [18 empty] | Pumping | Discharge Header |  |  | 255_primary | 0 | 0 | 0 | 0 | FALSE | FALSE
256 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 182 | Pump 1 Piping | 3 | 100mm diameter, approx. 5 m ductile iron pipe | Halton | In Service | First Street PS | First Street PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1986 |  |  | HR-FRST-013 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:48 | Maira Rafiq | 2020-09-21 23:38 |  |  |  |  | Pumping | Suction |  |  | 256_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Good
257 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 187 | Pump 2 Piping | 3 | 100mm diameter, approx. 3m ductile iron pipe | Halton | In Service | First Street PS | First Street PS |  | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1986 |  | 0 | [8 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-21 23:38 |  |  |  |  | Pumping | Pump Assembly |  |  | 257_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Good
258 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 643 | Discharge Header | 3 | 100mm diameter, approx. 7m ductile iron | Halton | In Service | First Street PS | First Street PS | Dry Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1986 |  | 0 | [8 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-21 23:38 |  |  |  |  | Pumping | Discharge Header |  |  | 258_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Good
259 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 40 | Overflow Piping | 3 | 300mm diameter, approx. 6m | Halton |  | Garlock Gdns PS | Garlock Gdns PS | Site | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1977 | [10 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 17:06 | [6 empty] | Pumping | Wet Well |  |  | 259_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | The pipe was at half of its expected service life.
260 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 53 | Pump 1 Discharge Piping | 3 | 100mm diameter, approx. 5m ductile pipe | Halton | In Service | Garlock Gdns PS | Garlock Gdns PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1977 |  |  | HR-GGDN-014 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 17:08 | Maira Rafiq | 2020-09-22 11:02 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 260_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Heavy corrosion was observed on the pipe
261 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 57 | Pump 2 Discharge Piping | 3 | 100mm diameter, approx. 5m ductile pipe | Halton | In Service | Garlock Gdns PS | Garlock Gdns PS | Dry Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1977 |  | 0 | [8 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-22 11:04 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 261_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Heavy corrosion was observed on the pipe
262 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 43 | Overflow Piping | 3 | 150mm diameter, approx. 9 m overflow piping | Halton | In Service | Morrison Heights PS | Morrison Heights PS | Site | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1973 |  |  | HR-MORI-123 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 11:43 | Maira Rafiq | 2020-09-22 12:14 |  |  |  |  | Pumping | Wet Well |  |  | 262_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | The pipe passed half of its expected service life.
263 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 72 | Pump 1 Piping | 3 | Ductile Iron, 100mm dia, 5 m length | Halton |  | Morrison Heights PS | Morrison Heights PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1973 |  |  | HR-MORI-115 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 11:46 | Maira Rafiq | 2020-09-22 12:17 |  |  |  |  | Pumping | Suction | 1 |  | 263_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Minor deterioration was observed on the pipe and it passed half of its expected service life.
264 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 78 | Pump 2 Piping | 3 | Ductile Iron, 100mm dia, 5 m length | Halton |  | Morrison Heights PS | Morrison Heights PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1973 |  | 0 | HR-MORI-115 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-22 12:18 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 264_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Minor deterioration was observed on the pipe and it passed half of its expected service life.
265 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 646 | Discharge Piping | 3 | Ductile Iron, 100mm dia, 5 m length | Halton |  | Morrison Heights PS | Morrison Heights PS | Dry Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1973 |  | 0 | HR-MORI-115 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-22 12:19 |  |  |  |  | Pumping | Wet Well |  |  | 265_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Minor deterioration was observed on the pipe and it passed half of its expected service life.
266 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 648 | Overflow Piping | 3 | 100mm diameter, approx. 4.5m | Halton | In Service | Raymar Pl PS | Raymar Pl PS | Wetwell | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1985 | [10 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 14:55 | Maira Rafiq | 2020-09-22 13:15 |  |  |  |  | Pumping | Wet Well |  |  | 266_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | assumed to be good
267 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 62 | Pump 1 Discharge Piping | 3 | 100mm diameter, approx. 5m ductile pipe | Halton |  | Raymar Pl PS | Raymar Pl PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1985 |  | 0 | HR-RAYM-040 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-22 13:21 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 267_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Heavy corrosion and deterioration was observed
268 |  |  |  | 0 | [7 empty] | FALSE | FALSE | FALSE | FALSE | 65 | Pump 2 Discharge Piping | 3 | 100mm diameter, approx. 8.6 m ductile iron pipe | Halton | In Service | Raymar Pl PS | Raymar Pl PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS |  |  |  |  | 0 | 1985 |  |  | HR-RAYM-040 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 14:58 | Maira Rafiq | 2020-09-22 13:21 |  |  |  |  | Pumping | Wet Well | 2 |  | 268_primary | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Heavy corrosion and deterioration was observed
301 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 639 | Wet Well Concrete Structure | 2 |  | Halton | In Service | Chancery Lane PS | WWPS | Process Structural | Process Structural | Building and Process Structural |  | Tank, Concrete | [5 empty] | 1975 |  |  | HR-CNRY-033 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:20 | Maira Rafiq | 2020-09-18 11:01 |  |  |  |  | Pumping | Wet Well | 1 |  | 302_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Rust spots noted | Fair
302 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Dry Well Access Hatch | 1 | Chancery Lane PS Dry Well | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1975 |  | 2035 | HR-CNRY-037 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:20 | Maira Rafiq | 2020-09-18 11:01 |  |  |  |  | Building | Substructure | 1 |  | 303_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | minor corrosion and paint wear
303 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Dry Well Access Ladder | 2 | Chancery Lane PS Dry Well | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1975 |  | 2035 | HR-CNRY-004 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:20 | Maira Rafiq | 2020-09-18 11:00 |  |  |  |  | Building | Substructure | 1 |  | 304_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | minor paint wear
304 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Protective Paint | 1 | Chancery Lane PS Dry Well | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Misc. Structural | [5 empty] | 1975 |  | 2035 | HR-CNRY-041 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:20 | Maira Rafiq | 2020-09-18 11:00 |  |  |  |  | Building | Interior Finishes | 1 |  | 305_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Peeling paint on exterior | Fair
305 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 639 | Manhole Frame and Cover | 1 |  | Halton | In Service | Chancery Lane PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Misc. Structural | [5 empty] | 1975 |  |  | HR-CNRY-035 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:21 | Maira Rafiq | 2020-09-18 11:00 |  |  |  |  | Pumping | Wet Well | 1 |  | 307_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | minor corrosion on the underside
306 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 639 | Wet Well Access Ladder | 2 |  | Halton | In Service | Chancery Lane PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1975 |  | 2035 | HR-CNRY-033 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:21 | Maira Rafiq | 2020-09-18 11:01 |  |  |  |  | Pumping | Wet Well | 1 |  | 308_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
307 |  |  |  | 0 |  |  |  |  | 0 |  |  | TRUE | FALSE | FALSE | FALSE | 639 | Wet Well Aluminum Platform | 2 |  | Halton | In Service | Chancery Lane PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1975 |  | 2035 | HR-CNRY-033 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:21 | Maira Rafiq | 2020-09-18 11:00 |  |  |  |  | Pumping | Wet Well | 1 |  | 309_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Corrosion noted | Fair
308 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 639 | Wet Well Aluminum Guardrail | 2 |  | Halton | In Service | Chancery Lane PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1975 |  | 2035 | HR-CNRY-033 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:21 | Maira Rafiq | 2020-09-18 11:00 |  |  |  |  | Pumping | Wet Well | 1 |  | 310_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Corrosion noted | Fair
309 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Davit Socket Base | 2 |  | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Misc. Structural | [5 empty] | 1975 |  | 2035 | HR-CNRY-037 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:21 | Maira Rafiq | 2020-09-18 11:00 |  |  |  |  | Building |  | 1 |  | 312_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | To be inspected yearly | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
317 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Dry Well Access Ladder | 2 | Chartwell Rd. PS Dry Well | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1983 |  | 2046 | HR-CTWL-024 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:29 | Maira Rafiq | 2020-09-18 14:03 |  |  |  |  | Building | Interior Construction | 1 |  | 320_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Minor corrosion and paint wear
318 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Dry Well Access Hatch | 1 | Chartwell Rd. PS Dry Well | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1983 |  | 2046 | HR-CTWL-023 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:29 | Maira Rafiq | 2020-09-18 14:06 |  |  |  |  | Building | Interior Construction | 1 |  | 321_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | paint wear
319 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Dry Well Davit Socket Base | 2 |  | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1983 |  | 2046 | HR-CTWL-023 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:29 | Maira Rafiq | 2020-09-20 10:17 |  |  |  |  | Building | Conveying (Elevators, Cranes) | 1 |  | 322_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | To be inspected every year | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
320 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 633 | Wet Well Access Hatch | 1 |  | Halton | In Service | Chartwell Rd. PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1983 |  | 2046 | HR-CTWL-025 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:30 | Maira Rafiq | 2020-09-20 10:17 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 323_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Surface corrosion noted on underside | Fair
321 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 633 | Wet Well Davit Socket Base | 2 |  | Halton | In Service | Chartwell Rd. PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1983 |  | 2046 | HR-CTWL-025 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:30 | Maira Rafiq | 2020-09-20 10:18 |  |  |  |  | Building |  | 1 |  | 324_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | To be inspected every year | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
322 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 633 | Wet Well Access Ladder | 2 |  | Halton | In Service | Chartwell Rd. PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1983 |  | 2046 | HR-CTWL-073 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:30 | Maira Rafiq | 2020-09-20 10:18 |  |  |  |  | Pumping | Wet Well | 1 |  | 325_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Bent ladder rung | Fair
323 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 633 | Checker Plate Platform | 2 |  | Halton | In Service | Chartwell Rd. PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1983 |  | 2036 | HR-CTWL-073 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:30 | Maira Rafiq | 2020-09-20 10:18 |  |  |  |  | Pumping | Wet Well | 1 |  | 326_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Corrosion noted | Fair
324 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Dry Well Protective Paint | 1 |  | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Misc. Structural | [5 empty] | 1983 |  | 2046 | HR-CTWL-024 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:31 | Maira Rafiq | 2020-09-20 10:20 |  |  |  |  | Building | Interior Finishes | 1 |  | 327_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Weathered paint on exterior and minor corrosion inside | Fair
325 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 31 | Wet Well Access Ladder | 2 | Cumnock PS Wet Well | Halton | In Service | Cumnock PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1974 |  | 2034 | HR-CMNK-156 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:39 | Maira Rafiq | 2020-09-21 13:57 |  |  |  |  | Pumping | Wet Well | 1 |  | 328_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
326 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 641 | Wet Well Checker Plate Platform | 2 | Cumnock PS Wet Well | Halton | In Service | Cumnock PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1974 |  | 2034 | HR-CMNK-157 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:39 | Maira Rafiq | 2020-09-21 13:58 |  |  |  |  | Pumping | Wet Well | 1 |  | 329_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | discoloration of the checker plate
327 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 641 | Manhole Frame and Cover | 1 | Cumnock PS Wet Well | Halton | In Service | Cumnock PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1974 |  | 2034 | HR-CMNK-095 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:39 | Maira Rafiq | 2020-09-20 22:13 |  |  |  |  | Pumping | Wet Well | 1 |  | 330_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
328 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Dry Well Access Hatch | 1 | Cumnock PS Dry Well | Halton | In Service | Cumnock PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1974 |  | 2034 | HR-CMNK-033 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:39 | Maira Rafiq | 2020-09-20 22:14 |  |  |  |  | Building | Substructure | 1 |  | 331_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | weathered paint
329 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Dry Well Access Ladder | 2 | Cumnock PS Dry Well | Halton | In Service | Cumnock PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1974 |  | 2034 | HR-CMNK-128 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:42 | Maira Rafiq | 2020-09-20 22:16 |  |  |  |  | Building | Substructure | 1 |  | 332_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Minor corrosion
330 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | TRUE | FALSE | FALSE | 640 | Dry Aluminum Grating | 2 | Cumnock PS Dry Well | Halton | In Service | Cumnock PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1974 |  | 2034 | HR-CMNK-126 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:43 | Maira Rafiq | 2020-09-20 22:18 |  |  |  |  | Building | Substructure | 1 |  | 333_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair based on age
331 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Protective Paint | 1 | Cumnock PS Dry Well | Halton | In Service | Cumnock PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Misc. Architectural | [5 empty] | 1974 |  | 2034 | HR-CMNK-126 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:47 | Maira Rafiq | 2020-09-20 22:21 |  |  |  |  | Building | Interior Finishes | 1 |  | 334_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Peeling paint on exterior and corrosion | Fair
332 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Davit Socket Base | 2 | Cumnock PS Dry Well | Halton | In Service | Cumnock PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Misc. Structural | [5 empty] | 1974 |  | 2034 | HR-CMNK-035 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:48 | Maira Rafiq | 2020-09-20 22:24 |  |  |  |  | Building |  | 1 |  | 335_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | To be inspected every year | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
333 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 642 | Wet Well Access Hatch | 1 | Ennisclaire Drive PS Wet Well | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1977 |  |  | HR-ENIS-001 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:55 | Maira Rafiq | 2020-09-21 16:57 |  |  |  |  | Pumping | Wet Well | 1 |  | 336_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
334 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 642 | Wet Well Access Ladder | 2 | Ennisclaire Drive PS Wet Well | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1977 |  | 2036 | HR-ENIS-002 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:55 | Maira Rafiq | 2020-09-21 16:57 |  |  |  |  | Pumping | Wet Well | 1 |  | 337_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Staining/corrosion noted | Fair
335 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 642 | Wet Well Aluminum Platform | 2 | Ennisclaire Drive PS Wet Well | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1977 |  |  | HR-ENIS-004 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:55 | Maira Rafiq | 2020-09-21 16:57 |  |  |  |  | Pumping | Wet Well | 1 |  | 338_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Minor corrosion
336 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 642 | Wet Well Aluminum Guardrail | 2 | Ennisclaire Drive PS Wet Well | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1977 |  | 2036 | HR-ENIS-002 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:55 | Maira Rafiq | 2020-09-21 16:59 |  |  |  |  | Pumping | Wet Well | 1 |  | 339_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | minor corrosion
337 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 642 | Davit Socket Base | 2 | Ennisclaire Drive PS Wet Well | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1977 |  |  | HR-ENIS-001 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 12:55 | Maira Rafiq | 2020-09-21 17:00 |  |  |  |  | Building |  | 1 |  | 340_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | To be inspected every year. As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year. | Fair
338 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 644 | Wet Well Access Ladder | 2 | First Street PS Wet Well | Halton | In Service | First Street PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1986 |  | 2046 | HR-FRST-094 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:15 | Maira Rafiq | 2020-09-21 19:13 |  |  |  |  | Pumping | Wet Well | 1 |  | 341_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair
339 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 644 | Wet Well Aluminum Platform | 2 | First Street PS Wet Well | Halton | In Service | First Street PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1986 |  | 2046 | HR-FRST-094 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:15 | Maira Rafiq | 2020-09-21 19:14 |  |  |  |  | Pumping | Wet Well | 1 |  | 342_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fixed portion of platform grating was noted to be bent | Fair
340 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 644 | Manhole Frame and Cover | 1 | First Street PS Wet Well | Halton | In Service | First Street PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1986 |  |  | HR-FRST-097 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:16 | Maira Rafiq | 2020-09-21 19:14 |  |  |  |  | Pumping | Wet Well | 1 |  | 343_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair
341 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 644 | Davit Socket Base | 2 | First Street PS Wet Well | Halton | In Service | First Street PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Misc. Structural | [5 empty] | 1986 |  | 2046 | HR-FRST-098 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:16 | Maira Rafiq | 2020-09-21 19:15 |  |  |  |  | Pumping | Wet Well | 1 |  | 344_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | To be inspected every year. As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year. | Fair
342 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 643 | Dry Well Access Hatch | 1 | First Street PS Dry Well | Halton | In Service | First Street PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1986 |  | 2046 | HR-FRST-029 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:16 | Maira Rafiq | 2020-09-21 19:19 |  |  |  |  | Building | Substructure | 1 |  | 345_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | corrosion and paint wear
343 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 643 | Dry Well Access Ladder | 2 | First Street PS Dry Well | Halton |  | First Street PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1986 |  | 2046 | HR-FRST-019 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:16 | Maira Rafiq | 2020-09-21 19:19 |  |  |  |  | Building | Substructure | 1 |  | 346_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Minor corrosion
344 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 643 | Protective Paint | 1 | First Street PS Dry Well | Halton | In Service | First Street PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Misc. Architectural | [5 empty] | 1986 |  |  | HR-FRST-019 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:16 | Maira Rafiq | 2020-09-21 19:20 |  |  |  |  | Building | Interior Finishes | 1 |  | 347_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Flaking/missing on exterior | Fair
345 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 643 | Dry Well Davit Socket Base | 2 | First Street PS Dry Well | Halton | In Service | First Street PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1986 |  | 2046 | HR-FRST-029 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:16 | Maira Rafiq | 2020-09-21 19:21 |  |  |  |  | Building |  | 1 |  | 348_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | To be inspected every year. As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
346 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 645 | Wet Well Access Hatch | 1 | Garlock Gdns PS Wet Well | Halton | In Service | Garlock Gdns PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1977 |  |  | HR-GGDN-023 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:24 | Maira Rafiq | 2020-09-22 10:47 |  |  |  |  | Pumping | Wet Well | 1 |  | 349_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Good
347 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 645 | Wet Well Access Ladder | 2 | Garlock Gdns PS Wet Well | Halton | In Service | Garlock Gdns PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1977 |  | 2040 | HR-GGDN-088 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:24 | Maira Rafiq | 2020-09-22 10:48 |  |  |  |  | Pumping | Wet Well | 1 |  | 350_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Pitting noted | Fair
348 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 645 | Wet Well Davit Socket Base | 2 | Garlock Gdns PS Wet Well | Halton | In Service | Garlock Gdns PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1977 |  |  | HR-GGDN-023 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:24 | Maira Rafiq | 2020-09-22 10:49 |  |  |  |  | Pumping | Wet Well | 1 |  | 351_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | To be inspected yearly. As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
349 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 645 | Wet Well Aluminum Platform | 2 | Garlock Gdns PS Wet Well | Halton | In Service | Garlock Gdns PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1977 |  | 2040 | HR-GGDN-088 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:24 | Maira Rafiq | 2020-09-22 10:49 |  |  |  |  | Pumping | Wet Well | 1 |  | 352_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Calcium buildup and pitting noted | fair
350 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 646 | Dry Well Access Hatch | 1 | Morrison Heights PS Dry Well | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1973 |  | 2033 | HR-MORI-096 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:29 | Maira Rafiq | 2020-09-22 11:25 |  |  |  |  | Building | Substructure | 1 |  | 353_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | paint wear
351 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 646 | Dry Well Access Ladder | 2 | Morrison Heights PS Dry Well | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1973 |  | 2033 | HR-MORI-097 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:29 | Maira Rafiq | 2020-09-22 11:27 |  |  |  |  | Building | Substructure | 1 |  | 354_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | minor corrosion
352 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 42 | Dry Well Davit Socket Base | 2 | Morrison Heights PS Dry Well | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1973 |  | 2033 | HR-MORI-096 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:29 | Maira Rafiq | 2020-09-22 11:27 |  |  |  |  | Building | Substructure | 1 |  | 355_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair
353 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 646 | Protective Paint | 1 | Morrison Heights PS Dry Well | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Misc. Architectural | [5 empty] | 1973 |  | 2033 | HR-MORI-097 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:29 | Maira Rafiq | 2020-09-22 11:28 |  |  |  |  | Building | Interior Finishes | 1 |  | 356_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Weathered paint and missing paint on exterior
354 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 647 | Manhole Frame and Cover | 1 | Morrison Heights PS Wet Well | Halton | In Service | Morrison Heights PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1973 |  | 2033 | HR-MORI-001 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:29 | Maira Rafiq | 2020-09-22 11:28 |  |  |  |  | Pumping | Wet Well | 1 |  | 357_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair
355 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 647 | Wet Well Access Ladder | 2 | Morrison Heights PS Wet Well | Halton | In Service | Morrison Heights PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1973 |  | 2033 | HR-MORI-001 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:30 | Maira Rafiq | 2020-09-22 11:28 |  |  |  |  | Pumping | Wet Well | 1 |  | 358_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair
356 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 647 | Wet Well Davit Socket Base | 2 | Morrison Heights PS Wet Well | Halton | In Service | Morrison Heights PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1973 |  | 2033 | HR-MORI-001 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:30 | Maira Rafiq | 2020-09-22 11:29 |  |  |  |  | Pumping | Wet Well | 1 |  | 359_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Anchors were corroded
357 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Wet Well Access Hatch | 1 | Raymar Pl PS Wet Well | Halton | In Service | Raymar Pl PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1985 |  |  | HR-RAYM-029 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:32 | Maira Rafiq | 2020-09-22 12:47 |  |  |  |  | Pumping | Wet Well | 1 |  | 360_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | minor corrosion and staining
358 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Pump Hatch 1 | 1 | Raymar Pl PS Wet Well | Halton | In Service | Raymar Pl PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1985 |  |  | HR-RAYM-029 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:32 | Maira Rafiq | 2020-09-22 12:52 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 361_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Missing safety grating. The Pump Hatch 1 was missing grating. Under Ontario Regulation 213/91 this presents a fall hazard when the hatches are left open.
359 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Pump Hatch 2 | 1 | Raymar Pl PS Wet Well | Halton |  | Raymar Pl PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1985 |  |  | HR-RAYM-029 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:32 | Maira Rafiq | 2020-09-22 12:52 |  |  |  |  | Pumping | Wet Well | 2 |  | 362_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Missing safety grating. The Pump Hatch 1 was missing grating. Under Ontario Regulation 213/91 this presents a fall hazard when the hatches are left open.
360 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Wet Well Access Ladder | 2 | Exterior to platform | Halton |  | Raymar Pl PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1985 |  |  | HR-RAYM-054 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:32 | Maira Rafiq | 2020-09-22 12:51 |  |  |  |  | Pumping | Wet Well | 1 |  | 363_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Calcium buildup and corrosion noted | Fair
361 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | We Well Access Ladder | 2 | Platform to base | Halton | In Service | Raymar Pl PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1985 |  |  | HR-RAYM-054 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:32 | Maira Rafiq | 2020-09-22 12:54 |  |  |  |  | Pumping | Wet Well | 1 |  | 364_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Calcium buildup and corrosion noted | Fair
362 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Wet Well Aluminum Platform | 2 | Raymar Pl PS Wet Well | Halton | In Service | Raymar Pl PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1985 |  |  | HR-RAYM-054 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:32 | Maira Rafiq | 2020-09-22 12:54 |  |  |  |  | Pumping | Wet Well | 1 |  | 365_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Gratings now clipped down | Corrosion noted | Fair
363 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Wet Well Davit Socket Base | 2 | Raymar Pl PS Wet Well | Halton |  | Raymar Pl PS | WWPS | Wet Well | Process Structural | Building and Process Structural |  | Metal Grating / Hatches / Handrails | [5 empty] | 1985 |  |  | HR-RAYM-029 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:32 | Maira Rafiq | 2020-09-22 12:56 |  |  |  |  | Pumping | Wet Well | 1 |  | 366_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | To be inspected every year. As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
382 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 643 | Dry Well Concrete Foundation | 2 | First Street PS Dry Well | Halton | In Service | First Street PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Tank, Concrete | [5 empty] | 1986 | [10 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-15 11:29 | Maira Rafiq | 2020-09-21 19:21 |  |  |  |  | Building | Superstructure | 1 |  | 385_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Not visible/inspected. Assumed to be good as no settlement was noted. | Good
383 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Dry Well Concrete Foundation | 2 | Cumnock PS Dry Well | Halton | In Service | Cumnock PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Misc. Structural | [5 empty] | 1974 | [10 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-15 12:58 | Maira Rafiq | 2020-09-20 22:20 |  |  |  |  | Building | Superstructure | 1 |  | 386_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Not visible/inspected. Assumed to be good as no settlement was noted.
384 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Dry Well Concrete Foundation | 2 | Chartwell Rd. PS Dry Well | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Process Structural | Building and Process Structural |  | Misc. Structural | [5 empty] | 1983 |  | 2043 | [8 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-15 13:15 | Maira Rafiq | 2020-09-20 10:20 |  |  |  |  | Building | Substructure | 1 |  | 387_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Not visible/inspected. Assumed to be good as no settlement was noted.
385 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Dry Well Concrete Foundation | 2 | Chancery Lane PS Dry Well | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Building Structural | Building and Process Structural |  | Reinforced Concrete | [5 empty] | 1975 | [10 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-15 15:07 | Maira Rafiq | 2020-09-18 11:24 |  |  |  |  | Building | Substructure | 1 |  | 388_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Not visible/inspected. Assumed to be good as no settlement was noted
387 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 41 | Grab Bar |  | Garlock Gdns PS Wet Well | Halton | In Service | Garlock Gdns PS | WWPS | Wet Well | [9 empty] | 1977 |  | 2036 | HR-GGDN-023 | [7 empty] | 1 | ea. | 2020 | [10 empty] | David Ip | 2020-07-16 13:25 | [8 empty] | 1 |  | 390_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Good
392 |  |  | 211127 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 32 | VALVE KNIFE GATE SEWAGE LIFT PUMP #2 | 2 | Knife Gate Valve #2;;;;100 mm dia | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Dry Well |  | Process Mechanical Equipment |  | Valve | [5 empty] | 1977 |  |  | HR-ENIS-013 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 15:09 | [8 empty] | 1 |  | 279_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Very Poor | Severe corrosion was observed on the surface of the valve. The valve was beyond its expected service life
393 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 32 | PUMP #2 SEWAGE LIFT | 2 | Sewage Pump #2;Flygt;C3082MT;;7.8 L/s at 7.2 m TDH 2hp | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Dry Well |  | Process Mechanical Equipment |  | Pump, Centrifugal | [5 empty] | 1977 |  |  | HR-ENIS-009 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 15:19 | [8 empty] | 1 |  | 280_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | The pump was beyond its expected service life.
394 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 32 | VALVE CHECK SEWAGE LIFT PUMP #2 | 2 | Check Valve #2;;;;100 mm dia | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Dry Well |  | Process Mechanical Equipment |  | Valve | [5 empty] | 1977 |  |  | HR-ENIS-014 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 15:19 | [8 empty] | 1 |  | 281_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Very Poor | Severe corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
395 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 32 | VALVE KNIFE GATE SEWAGE LIFT PUMP #2 | 2 | Knife Gate Valve #2;;;;100 mm dia | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Dry Well |  | Process Mechanical Equipment |  | Valve | [5 empty] | 1977 |  |  | HR-ENIS-013 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 15:20 | [8 empty] | 1 |  | 282_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Very Poor | Severe corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
396 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 32 | Bar Screen | 2 | Bar Screen;;;;6.5'X3.25' | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Dry Well |  | Process Mechanical Equipment |  | Valve | [5 empty] | 1977 |  |  | HR-ENIS-015 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 15:23 | [8 empty] | 1 |  | 283_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Minor deterioration was observed on the bar screen.
397 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 32 | PUMP #2 SEWAGE LIFT | 2 | Sewage Pump #2;Flygt;C3082MT;;7.8 L/s at 7.2 m TDH 2hp | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Dry Well |  | Process Mechanical Equipment |  | Pump, Centrifugal | [5 empty] | 1977 |  |  | HR-ENIS-009 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 15:26 | [8 empty] | 1 |  | 284_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | The pump was beyond its expected service life.
399 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 642 | Sewage Lift Pump #2 | 2 | Sewage Pump #1;Flygt;C3082MT;;7.8 L/s at 7.2 m TDH 2hp | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | pump | [5 empty] | 1977 |  |  | HR-ENIS-009 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:01 | Maira Rafiq | 2020-09-21 17:24 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 286_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | poor | The pump was beyond its expected service life
400 |  |  | 201607 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 32 | VALVE CHECK SEWAGE LIFT PUMP #2 | 2 | Check Valve #2;;;;100 mm dia | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Dry Well |  | Process Mechanical Equipment |  | Valve | [5 empty] | 1977 |  |  | HR-ENIS-014 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:03 | [8 empty] | 1 |  | 287_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Severe corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
401 |  |  | 211127 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 32 | VALVE KNIFE GATE SEWAGE LIFT PUMP #1 | 2 | Knife Gate Valve #1;;;;100 mm dia | Halton | In Service | Ennisclaire Drive PS | Ennisclaire Drive PS | Dry Well |  | Process Mechanical Equipment |  | Valve | [5 empty] | 1977 |  |  | HR-ENIS-012 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:03 | [8 empty] | 1 |  | 288_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
402 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 399 | Sewage Lift Pump #2 Check Valve | 2 | Check Valve #1;;;;100 mm dia | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Valve | [5 empty] | 1977 |  |  | HR-ENIS-014 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:05 | Maira Rafiq | 2020-09-21 17:23 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 289_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Heavy corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
403 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 399 | Sewage Lift Pump #2 Knife Gate Valve | 2 | Knife Gate Valve #2;;;;100 mm dia | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Valve | [5 empty] | 1977 |  |  | HR-ENIS-013 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 16:07 | Maira Rafiq | 2020-09-21 17:23 |  |  |  |  | Pumping | Wet Well | 2 |  | 290_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Very Poor | Severe corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
404 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 645 | Bar Screen | 2 | Bar Screen;;;; | Halton | In Service | Garlock Gdns PS | Garlock Gdns PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Piping, DI/CPP/Steel/SS | [5 empty] | 1977 |  |  | HR-GGDN-013 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-20 17:09 | Maira Rafiq | 2020-09-22 11:10 |  |  |  |  | Pumping | Wet Well | 1 |  | 292_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Debris is clogging at the bar screen, which in terms start clogging the inlet pipe.
405 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 46 | VALVE DISCHARGE #3 | 2 | Gate Valve #3;;;;100 mm dia | Halton | In Service | Raymar Pl PS | Raymar Pl PS | Wet Well |  | Process Mechanical Equipment |  | Valve | [5 empty] | 1985 |  |  | HR-RAYM-017 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 14:51 | [8 empty] | 1 |  | 293_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the valve. The valve was near the end of its expected service life.
406 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Discharge Valve #3 | 2 | Gate Valve #3;;;;100 mm dia | Halton | In Service | Raymar Pl PS | WWPS | Wet Well | Process Mechanical | Process Mechanical Equipment |  | Valve | [5 empty] | 1985 |  |  | HR-RAYM-017 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Adrian Li | 2020-07-21 15:10 | Maira Rafiq | 2020-09-22 13:20 |  |  |  |  | Pumping | Discharge Header | 1 |  | 294_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Corrosion and deterioration was observed on the surface of the valve
422 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Remote Signal Telephone Transmitter | 1 | Remote Signal Telephone Transmitter; Pribusin; IUC-X9-TXC; ; ; | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation |  | Transmitter | [5 empty] | 2009 |  | 2009 | HR-CNRY-108 |  |  |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 16:03 | Maira Rafiq | 2020-08-24 08:45 |  |  |  |  | Communications | Telephone/IT | 1 |  | 288_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | obsolete
423 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 639 | Wet Well Floats | 2 | Wet Well Floats; ; ; ; ; | Halton | In Service | Chancery Lane PS | WWPS | Wet Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2009 |  | 2030 | HR-CNRY-064 |  |  |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 16:06 | Maira Rafiq | 2020-08-24 08:46 |  |  |  |  | Pumping | Wet Well | 1 |  | 289_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
424 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Sump Float | 2 | Sump Float; ; ; ; ; | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2009 |  |  | HR-CNRY-132 |  |  |  | 2 |  |  |  | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 16:09 | Maira Rafiq | 2020-08-24 08:47 |  |  |  |  | Building | Plumbing - Sanitary Waste | 1 |  | 290_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Dust | good
429 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 633 | Wet Well Float | 2 | Wet Well Float; ; ; ; ; | Halton | In Service | Chartwell Rd. PS | WWPS | Wet Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2019 |  | 2025 | HR-CTWL-065 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 16:32 | Maira Rafiq | 2020-09-20 10:52 |  |  |  |  | Pumping | Suction Header | 1 |  | 295_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
430 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Sump Float | 1 | Sump Float; ; ; ; ; | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2019 |  | 2025 | HR-CTWL-016 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 16:34 | Maira Rafiq | 2020-09-20 10:52 |  |  |  |  | Building | Plumbing - Sanitary Waste | 1 |  | 296_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
431 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Remote Signals Telephone Transmitter | 1 | Remote Signals Telephone Transmitter; Pribusin; IUC-X9-TXC; ; ; | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation |  | Transmitter | [5 empty] | 2016 |  | 2030 | HR-CTWL-128 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 16:47 | Maira Rafiq | 2020-08-21 16:16 |  |  |  |  | Communications | Telephone/IT | 1 |  | 297_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
432 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Sump Float | 2 | Sump Float; ; ; ; ; | Halton | In Service | Cumnock PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2009 |  | 2030 | HR-CMNK-023 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 17:05 | Maira Rafiq | 2020-08-24 08:57 |  |  |  |  | Building | Plumbing - Sanitary Waste | 1 |  | 298_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
433 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Remote Signals Telephone Transmitter | 1 | Remote Signals Telephone Transmitter; Pribusin; IUC-X9-TXC; ; ; | Halton | In Service | Cumnock PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation |  | Transmitter | [5 empty] | 2016 |  |  | HR-CMNK-079 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 17:07 | Maira Rafiq | 2020-08-24 08:58 |  |  |  |  | Communications | Telephone/IT | 1 |  | 299_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | very good
434 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 641 | Wet Well Floats | 2 | Wet Well Floats; ; ; ; ; | Halton | In Service | Cumnock PS | WWPS | Wet Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2009 |  | 2030 | HR-CMNK-152 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 17:11 | Maira Rafiq | 2020-08-24 08:59 |  |  |  |  | Pumping | Wet Well | 1 |  | 300_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
435 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 33 | Remote Signals Telephone Transmitter | 1 | Remote Signals Telephone Transmitter; Pribusin; IUC-X9-TXC; ; ; | Halton | In Service | Ennisclaire Drive PS | WWPS | Site | Process Instrumentation | Process Instrumentation |  | Transmitter | [5 empty] | 2009 |  | 2030 | HR-ENIS-038 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 17:45 | Maira Rafiq | 2020-08-24 09:03 |  |  |  |  | Communications | Telephone/IT | 1 |  | 301_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | obsolete
436 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 642 | Wet Well Floats | 2 | Wet Well Floats; ; ; ; ; | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2009 |  | 2030 | HR-ENIS-081 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 17:47 | Maira Rafiq | 2020-08-24 09:03 |  |  |  |  | Pumping | Wet Well | 1 |  | 302_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
437 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 643 | Sump Float | 2 | Sump Float; ; ; ; ; | Halton | In Service | First Street PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2009 |  | 2030 | HR-FRST-024 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 17:52 | Maira Rafiq | 2020-08-24 09:10 |  |  |  |  | Building | Plumbing - Sanitary Waste | 1 |  | 303_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
438 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 643 | Remote Signals Telephone Transmitter | 1 | Remote Signals Telephone Transmitter; Pribusin; IUC-X9-TXC; ; ; | Halton | In Service | First Street PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation |  | Transmitter | [5 empty] | 2016 |  | 2030 | HR-FRST-153 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 17:55 | Maira Rafiq | 2020-08-24 09:11 |  |  |  |  | Communications | Telephone/IT | 1 |  | 304_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
439 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 644 | Wet Well Float | 2 | Wet Well Float; ; ; ; ; | Halton | In Service | First Street PS | WWPS | Wet Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2019 |  | 2030 | HR-FRST-088 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 17:58 | Maira Rafiq | 2020-08-24 09:11 |  |  |  |  | Pumping | Wet Well | 1 |  | 305_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Good
440 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 645 | Wet Well Level Transmitter | 2 | Wet Well Level Transmitter; Siemens Milltronics; Multiranger 100; ; ; | Halton | In Service | Garlock Gdns PS | WWPS | Site | Process Instrumentation | Process Instrumentation |  | Transmitter | [5 empty] | 2009 |  | 2030 | HR-GGDN-039 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 18:03 | Maira Rafiq | 2020-08-24 09:15 |  |  |  |  | Pumping | Wet Well | 1 |  | 306_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
441 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 40 | Remote Signals Telephone Transmitter | 1 | Remote Signals Telephone Transmitter; Pribusin; IUC-X9-TXC; ; ; | Halton | In Service | Garlock Gdns PS | WWPS | Site | Process Instrumentation | Process Instrumentation |  | Transmitter | [5 empty] | 2016 |  | 2030 | HR-GGDN-076 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 18:06 | Maira Rafiq | 2020-08-24 09:15 |  |  |  |  | Communications | Telephone/IT | 1 |  | 307_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
442 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 645 | Wet Well Floats | 2 | Wet Well Floats; ; ; ; ; | Halton | In Service | Garlock Gdns PS | WWPS | Wet Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2009 |  | 2030 | HR-GGDN-004 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 18:08 | Maira Rafiq | 2020-08-24 09:16 |  |  |  |  | Pumping | Wet Well | 1 |  | 308_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
443 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 646 | Sump Float | 2 | Sump Float; ; ; ; ; | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2008 |  | 2030 | HR-MORI-027 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 18:13 | Maira Rafiq | 2020-08-24 09:32 |  |  |  |  | Building | Plumbing - Sanitary Waste | 1 |  | 309_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
444 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 43 | Remote Signals Telephone Transmitter | 2 | Remote Signals Telephone Transmitter; Pribusin; IUC-X9-TXC; ; ; | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation |  | Transmitter | [5 empty] | 2016 |  | 2030 | HR-MORI-031 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 18:15 | Maira Rafiq | 2020-08-24 09:32 |  |  |  |  | Communications | Telephone/IT | 1 |  | 310_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
445 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 647 | Wet Well Float | 2 | Wet Well Float; ; ; ; ; | Halton | In Service | Morrison Heights PS | WWPS | Wet Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2009 |  | 2030 | HR-MORI-124 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 18:18 | Maira Rafiq | 2020-08-24 09:31 |  |  |  |  | Pumping | Wet Well | 1 |  | 311_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
446 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Wet Well Level Transmitter | 2 | Wet Well Level Transmitter; Siemens Milltronics; Multiranger Plus; ; ; | Halton | In Service | Raymar Pl PS | WWPS | Site | Process Instrumentation | Process Instrumentation |  | Transmitter | [5 empty] | 2009 |  | 2030 | HR-RAYM-080 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 18:22 | Maira Rafiq | 2020-08-24 09:35 |  |  |  |  | Pumping | Wet Well | 1 |  | 312_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | bolts were not secured properly
447 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 45 | Remote Signals Telephone Transmitter | 1 | Remote Signals Telephone Transmitter; Pribusin; IUC-X9-TXC; ; ; | Halton | In Service | Raymar Pl PS | WWPS | Site | Process Instrumentation | Process Instrumentation |  | Transmitter | [5 empty] | 2016 |  | 2030 | HR-RAYM-132 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 18:24 | Maira Rafiq | 2020-08-24 09:35 |  |  |  |  | Communications | Telephone/IT | 1 |  | 313_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
448 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Wet Well Floats | 2 | Wet Well Floats; ; ; ; ; | Halton | In Service | Raymar Pl PS | WWPS | Wet Well | Process Instrumentation | Process Instrumentation |  | Sensor | [5 empty] | 2009 |  | 2030 | HR-RAYM-011 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Alex Wang | 2020-08-04 18:32 | Maira Rafiq | 2020-08-24 09:36 |  |  |  |  | Pumping | Wet Well | 1 |  | 314_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
485 |  |  | 201611 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 25 | Main Disconnect Switch | 2 | Main Disconnect Switch; Square D; ; ;600V, 60A, fused | Halton | In Service | Chancery Lane PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2010 |  | 2040 | HR-CNRY-076 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-27 16:37 | Maira Rafiq | 2020-09-18 11:38 |  |  |  |  | Primary Power | MCC | 1 |  | 307_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
486 |  |  | 201611 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 25 | Power Meter | 2 | Power Meter; ; ; ; | Halton | In Service | Chancery Lane PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2010 |  | 2040 | HR-CNRY-080 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-27 16:37 | Maira Rafiq | 2020-09-18 11:38 |  |  |  |  | Primary Power | MCC | 1 |  | 309_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
487 |  |  | 201611 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 25 | Manual Transfer Switch | 2 | Manual Transfer Switch; Square D; ; ;600V, 60A | Halton | In Service | Chancery Lane PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2010 |  | 2040 | HR-CNRY-081 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-27 16:43 | Maira Rafiq | 2020-09-18 11:38 |  |  |  |  | Primary Power | Transfer Switch | 1 |  | 310_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
488 |  |  | 201611 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 25 | Generator Connection Receptacle | 2 | Generator Connection Receptacle; ; ; ;600V | Halton | In Service | Chancery Lane PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2010 |  | 2040 | HR-CNRY-072 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-27 16:45 | Maira Rafiq | 2020-09-18 11:39 |  |  |  |  | Primary Power | Standby Generator | 1 |  | 311_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
489 |  |  | 201611 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Dry Well Lights | 1 | Dry Well Lights; ; ; ;2 Fluorescent | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Process Electrical | Process Electrical |  | Lighting | [5 empty] | 1975 |  | 2025 | HR-CNRY-086 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-27 16:49 | Maira Rafiq | 2020-09-18 11:39 |  |  |  |  | Building | Electrical - Lighting | 1 |  | 312_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | replace with LED fixtures rated for class 1, div 2
490 |  |  | 201611 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 25 | Outdoor Enclosure | 2 | Outdoor Enclosure; ; ; ; | Halton | In Service | Chancery Lane PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2010 |  | 2040 | HR-CNRY-071 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-27 16:52 | Maira Rafiq | 2020-09-18 11:40 |  |  |  |  | Primary Power | MCC | 1 |  | 314_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | inside the panel is not getting drained properly
491 |  |  | 201611 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Pump Control Panel | 3 | Pump Control Panel; S&L; ; ; | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Process Electrical | Process Electrical |  | Panel, Breaker | [5 empty] | 1975 |  | 2025 | IMG_20200629_140353 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-27 16:56 | Maira Rafiq | 2020-09-18 11:40 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 315_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | replace with NEMA 4X panel
492 |  |  | 201556 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 27 | Outdoor Electrical Enclosure | 2 | Outdoor Electrical Enclosure; ; ; ; | Halton | In Service | Chartwell Rd. PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 1965 |  | 2025 | HR-CTWL-023 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-28 09:17 | Maira Rafiq | 2020-08-28 17:26 |  |  |  |  | Primary Power | MCC | 1 |  | 316_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
493 |  |  | 201556 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 27 | Main Disconnect Switch | 2 | Main Disconnect Switch; Square D; ; ;600V, 60A, fused | Halton | In Service | Chartwell Rd. PS | WWPS | Site | Process Electrical | Process Electrical |  | MCC | [5 empty] | 2010 |  | 2040 | HR-CTWL-079 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-28 09:42 | Maira Rafiq | 2020-09-20 10:28 |  |  |  |  | Primary Power | MCC | 1 |  | 317_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | missing arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servicin
494 |  |  | 201556 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 27 | Power Meter | 2 | Power Meter; Elster; ; ; | Halton | In Service | Chartwell Rd. PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2010 |  | 2040 | HR-CTWL-084 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-28 09:30 | Maira Rafiq | 2020-08-28 17:24 |  |  |  |  | Primary Power | MCC | 1 |  | 318_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
495 |  |  | 201556 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 27 | Manual Transfer Switch | 2 | Manual Transfer Switch; Square D; ; ; 600V, 60A | Halton | In Service | Chartwell Rd. PS | WWPS | Site | Process Electrical | Process Electrical |  | Panel, Breaker | [5 empty] | 2010 |  | 2040 | HR-CTWL-085 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-28 09:47 | Maira Rafiq | 2020-09-20 10:29 |  |  |  |  | Primary Power | Transfer Switch | 1 |  | 319_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | missing arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the receptacle which may require examination, adjustment, ser
496 |  |  | 201556 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Dry Well Lighting | 1 | Dry Well Lighting; ; ; ; 2 fluorescent lights | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Building Electrical | Building Services |  | Lighting | [5 empty] | 1965 |  | 2025 | HR-CTWL-085 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-28 09:40 | Maira Rafiq | 2020-08-28 17:25 |  |  |  |  | Building | Electrical - Lighting | 1 |  | 320_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | replace with LED in next upgrade
497 |  |  | 201556 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Control Panel | 3 | Control Panel; S&L; ; ; | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Process Electrical | Process Electrical |  | Panel, Breaker | [5 empty] | 1965 |  | 2025 | HR-CTWL-002 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-05 12:38 | Maira Rafiq | 2020-09-20 10:30 |  |  |  |  | Primary Power | MCC | 1 |  | 321_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | misplaced arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servic | Pump #1 breaker to be sized and replaced according to OESC-2018
498 |  |  | 201556 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Generator Connection Receptacle | 2 | Generator Connection Receptacle; ; ; ; 600V, 60A | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Process Electrical | Process Electrical |  | Generator | [5 empty] | 1965 |  | 2025 | HR-CTWL-002 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-28 09:52 | Maira Rafiq | 2020-08-28 17:25 |  |  |  |  | Primary Power | Standby Generator | 1 |  | 322_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
499 |  |  | 201647 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 30 | Outdoor Enclosure | 2 | Outdoor Enclosure | Halton | In Service | Cumnock PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 1993 |  | 2030 | HR-CMNK-036 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-28 15:33 | Maira Rafiq | 2020-09-21 15:17 |  |  |  |  | Primary Power | MCC | 1 |  | 323_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | bottom of interior has corroded | replace with NEMA 3R enclosure in next upgrade
500 |  |  | 201647 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 7 | Main Disconnect Switch | 2 | Main Disconnect Switch; Square D; ; ;600V, 60A | Halton | In Service | Cumnock PS | WWPS | Site | Process Electrical | Process Electrical |  | MCC | [5 empty] | 1993 |  | 2035 | HR-CMNK-038 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-28 15:57 | Maira Rafiq | 2020-09-21 15:21 |  |  |  |  | Primary Power | MCC | 1 |  | 324_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | missing arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servicin
501 |  |  | 201647 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 7 | Power Meter | 2 | Power Meter; elster; ; ; | Halton | In Service | Cumnock PS | WWPS | Site | Process Electrical | Process Electrical |  | MCC | [5 empty] | 1993 |  | 2035 | HR-CMNK-041 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-28 15:36 | Maira Rafiq | 2020-09-21 15:18 |  |  |  |  | Primary Power | MCC | 1 |  | 325_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
502 |  |  | 201647 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 7 | Manual Transfer Switch | 2 | Manual Transfer Switch; square D; ; ;600V, 60A | Halton | In Service | Cumnock PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 1993 |  | 2035 | HR-CMNK-042 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-28 15:58 | Maira Rafiq | 2020-09-21 15:22 |  |  |  |  | Primary Power | Transfer Switch | 1 |  | 326_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | missing arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servicin
503 |  |  | 201647 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Drywell Lighting | 1 | Drywell Lighting; ; ; ;2 fluorescent fixtures | Halton | In Service | Cumnock PS | WWPS | Dry Well | Process Electrical | Process Electrical |  | Lighting | [5 empty] | 1974 |  | 2025 | HR-CMNK-051 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-28 16:01 | Maira Rafiq | 2020-09-21 15:20 |  |  |  |  | Building | Electrical - Lighting | 1 |  | 327_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | fair | replace with LED fixture in next upgrade. To be rated for class 1, div 2
504 |  |  | 201647 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Control Panel | 3 | Control Panel; S&L; ; ; | Halton | In Service | Cumnock PS | WWPS | Dry Well | Process Electrical | Process Electrical |  | Panel, Breaker | [5 empty] | 1974 |  | 2025 | HR-CMNK-0003 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-07-28 16:09 | Maira Rafiq | 2020-09-21 15:22 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 328_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | bottom of interior was corroded | missing arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servicin
505 |  |  | 201608 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 33 | outdoor enclosure | 2 | outdoor enclosure | Halton | In Service | Ennisclaire Drive PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 1972 |  | 2025 | HR-ENIS-028 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 13:54 | Maira Rafiq | 2020-09-21 17:05 |  |  |  |  | Primary Power | MCC | 1 |  | 329_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | top surface and doors were corroded | to be replaced with NEMA 3R enclosure
506 |  |  | 201608 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 33 | Control Panel with Main DS | 3 | Control Panel with Main DS; | Halton | In Service | Ennisclaire Drive PS | WWPS | Site | Process Electrical | Process Electrical |  | Panel, Breaker | [5 empty] | 1972 |  | 2025 | HR-ENIS-029 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 14:23 | Maira Rafiq | 2020-09-21 17:06 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 330_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | outdated arc flash label. Shock and arc flash hazard as the existing arc flash label are outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreove
507 |  |  | 201608 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 33 | Pump #1 VFD with Breaker | 2 | Pump #1 VFD with Breaker; PowerFlex 40; Series A; ; ; Size 1, 7.5HP | Halton | In Service | Ennisclaire Drive PS | WWPS | Site | Process Electrical | Process Electrical |  | VFD | [5 empty] | 2007 |  | 2037 | HR-ENIS-053 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 14:03 | Maira Rafiq | 2020-09-21 17:07 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 331_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
508 |  |  | 201608 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 33 | Pump #2 VFD with Breaker | 2 | Pump #2 VFD with Breaker; PowerFlex 40; Series A; ; ; Size 1, 7.5HP | Halton | In Service | Ennisclaire Drive PS | WWPS | Site | Process Electrical | Process Electrical |  | VFD | [5 empty] | 2007 |  | 2037 | HR-ENIS-047 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 14:05 | Maira Rafiq | 2020-09-21 17:07 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 332_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
509 |  |  | 201608 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 33 | Generator Connection Receptacle | 2 | Generator Connection Receptacle; ; ; ; ; 240V, 60A | Halton | In Service | Ennisclaire Drive PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2007 |  | 2037 | HR-ENIS-060 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 14:08 | Maira Rafiq | 2020-09-21 17:08 |  |  |  |  | Primary Power | Standby Generator | 1 |  | 333_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
510 |  |  | 201608 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 33 | Manual Transfer Switch | 2 | Manual Transfer Switch; Moeller; ; ; ; 600V, 63A | Halton | In Service | Ennisclaire Drive PS | WWPS | Site | Process Electrical | Process Electrical |  | MCC | [5 empty] | 2007 |  | 2037 | HR-ENIS-061 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 14:17 | Maira Rafiq | 2020-09-21 17:09 |  |  |  |  | Primary Power | Transfer Switch | 1 |  | 334_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the switch which may require examination, adjustment, servicing, or maintenance while
511 |  |  | 201608 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 642 | Wet Well Light | 1 | Wet Well Light; ; ; ; ; class 1, div 1 rated | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Process Electrical | Process Electrical |  | Lighting | [5 empty] | 2007 |  | 2025 | HR-ENIS-061 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 14:21 | Maira Rafiq | 2020-09-21 17:09 |  |  |  |  | Building | Electrical - Lighting | 1 |  | 335_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | poor | severely corroded
512 |  |  | 201542 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 37 | Outdoor Enclosure | 2 | Outdoor Enclosure | Halton | In Service | First Street PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2010 |  | 2040 | HR-FRST-099 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 14:32 | Maira Rafiq | 2020-09-21 23:20 |  |  |  |  | Primary Power | MCC | 1 |  | 336_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
513 |  |  | 201542 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 37 | Main Fused Disconnect Switch | 2 | Main Fused Disconnect Switch; Square D; ; ; 600V, 60A | Halton | In Service | First Street PS | WWPS | Site | Process Electrical | Process Electrical |  | MCC | [5 empty] | 2010 |  | 2040 | HR-FRST-100 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 14:37 | Maira Rafiq | 2020-09-21 23:21 |  |  |  |  | Primary Power | MCC | 1 |  | 337_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | misplaced and outdated arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the VFD breaker which may require examination,
514 |  |  | 201542 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 37 | Power Meter | 2 | Power Meter; Elster; ; ; | Halton | In Service | First Street PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2010 |  | 2040 | HR-FRST-107 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 14:32 | Maira Rafiq | 2020-09-21 23:22 |  |  |  |  | Primary Power | MCC | 1 |  | 338_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
515 |  |  | 201542 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 37 | Manual Transfer Switch | 2 | Manual Transfer Switch; Square D; ; ;600V, 60A | Halton | In Service | First Street PS | WWPS | Site | Process Electrical | Process Electrical |  | MCC | [5 empty] | 2010 |  | 2040 | HR-FRST-109 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 14:39 | Maira Rafiq | 2020-09-21 23:23 |  |  |  |  | Primary Power | Transfer Switch | 1 |  | 339_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | misplaced and outdated arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the VFD breaker which may require examination,
516 |  |  | 201542 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 643 | Control Panel | 3 | Control Panel; Clow; AER-O-FLO; ;600V | Halton | In Service | First Street PS | WWPS | Dry Well | Process Electrical | Process Electrical |  | Panel, Breaker | [5 empty] | 1983 |  | 2025 | HR-FRST-001 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 14:46 | Maira Rafiq | 2020-09-21 23:24 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 340_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | misplaced and outdated arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the VFD breaker which may require examination,
517 |  |  | 201542 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 37 | Generator Connection Receptacle | 2 | Generator Connection Receptacle; ; ; ;600V, 60A | Halton | In Service | First Street PS | WWPS | Site | Process Electrical | Process Electrical |  | Generator | [5 empty] | 2010 |  | 2040 | HR-FRST-122 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 14:48 | Maira Rafiq | 2020-09-21 23:25 |  |  |  |  | Primary Power | Standby Generator | 1 |  | 341_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
518 |  |  | 201542 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 643 | Dry Well Lights | 1 | Dry Well Lights; ; ; rated for class 1, div 2 | Halton | In Service | First Street PS | WWPS | Site | Process Electrical | Process Electrical |  | Lighting | [5 empty] | 2000 |  | 2030 | HR-FRST-126 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 14:51 | Maira Rafiq | 2020-09-21 23:25 |  |  |  |  | Building | Electrical - Lighting | 1 |  | 342_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | replace with LED in next upgrade
519 |  |  | 219156 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 645 | Wet Well Light | 1 | Wet Well Light; ; ; ; florescent, class 1, div 1 rated | Halton | In Service | Garlock Gdns PS | WWPS | Wet Well | Process Electrical | Process Electrical |  | Lighting | [5 empty] | 1977 |  | 2025 | HR-GGDN-022 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 14:59 | Maira Rafiq | 2020-09-22 11:17 |  |  |  |  | Building | Electrical - Lighting | 1 |  | 343_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | to be replaced with LED
520 |  |  | 219156 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 40 | Enclosure Light | 1 | Enclosure Light; ; ; ; florescent | Halton | In Service | Garlock Gdns PS | WWPS | Site | Process Electrical | Process Electrical |  | Lighting | [5 empty] | 1977 |  | 2025 | HR-GGDN-028 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 15:08 | Maira Rafiq | 2020-09-22 11:18 |  |  |  |  | Building | Electrical - Lighting | 1 |  | 344_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | to be replaced with LED
521 |  |  | 219156 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 40 | Power Meter | 2 | Power Meter; ; ; ; | Halton | In Service | Garlock Gdns PS | WWPS | Site | Process Electrical | Process Electrical |  | MCC | [5 empty] | 2003 |  | 2033 | HR-GGDN-027 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 15:09 | Maira Rafiq | 2020-09-22 11:18 |  |  |  |  | Primary Power | MCC | 1 |  | 345_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
522 |  |  | 219156 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 40 | Control Panel with Main DS and MTS | 3 | Control Panel with Main DS; ; ; ; 240V, 30A | Halton | In Service | Garlock Gdns PS | WWPS | Site | Process Electrical | Process Electrical |  | Panel, Breaker | [5 empty] | 1977 |  | 2025 | HR-GGDN-037 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 15:14 | Maira Rafiq | 2020-09-22 11:20 |  |  |  |  | Primary Power | MCC | 1 |  | 346_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | to have separate Main DS, MTS, and CP | outdated arc flash label. Shock and arc flash hazard as the existing arc flash label are outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreove
523 |  |  | 219156 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 40 | Generator Connect Recept. | 2 | Generator Connect Recept.; ; ; ; 240V, 30A | Halton | In Service | Garlock Gdns PS | WWPS | Site | Process Electrical | Process Electrical |  | Generator | [5 empty] | 1977 |  | 2025 | HR-GGDN-056 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 15:16 | Maira Rafiq | 2020-09-22 11:20 |  |  |  |  | Primary Power | Standby Generator | 1 |  | 347_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | fair
524 |  |  | 219156 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 41 | Pump #1 VFD with Breaker | 2 | Pump #1 VFD with Breaker; PowerFlex 40; Series A; ; 240V, 30A, size 1 | Halton | In Service | Garlock Gdns PS | WWPS | Site | Process Electrical | Process Electrical |  | VFD | [5 empty] | 2003 |  | 2033 | HR-GGDN-057 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 15:20 | Maira Rafiq | 2020-09-22 11:21 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 348_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
525 |  |  | 219156 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 40 | Pump #2 VFD with Breaker | 2 | Pump #2 VFD with Breaker; PowerFlex 40; Series A; ; 240V, 30A, size 1 | Halton | In Service | Garlock Gdns PS | WWPS | Site | Process Electrical | Process Electrical |  | VFD | [5 empty] | 2003 |  | 2033 | HR-GGDN-057 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 15:21 | Maira Rafiq | 2020-09-22 11:22 |  |  |  |  | Pumping | Pump Assembly | 2 |  | 349_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
526 |  |  | 201659 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 43 | Outdoor Enclosure | 2 | Outdoor Enclosure | Halton | In Service | Morrison Heights PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2010 |  | 2040 | HR-MORI-040 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 15:47 | Maira Rafiq | 2020-09-22 12:27 |  |  |  |  | Primary Power | MCC | 1 |  | 350_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
527 |  |  | 201659 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 43 | Generator Connect Recept. | 2 | Generator Connect Recept. ; ; ; ; 600V, 60A | Halton | In Service | Morrison Heights PS | WWPS | Site | Process Electrical | Process Electrical |  | Generator | [5 empty] | 2010 |  | 2040 | HR-MORI-041 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 15:47 | Maira Rafiq | 2020-09-22 12:27 |  |  |  |  | Primary Power | Standby Generator | 1 |  | 351_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
528 |  |  | 201659 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 43 | Main Disconnect Switch | 2 | Main DS ; Square D; ; ; 600V, 60A, fused | Halton | In Service | Morrison Heights PS | WWPS | Site | Process Electrical | Process Electrical |  | MCC | [5 empty] | 2010 |  | 2040 | HR-MORI-046 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 15:47 | Maira Rafiq | 2020-09-22 12:29 |  |  |  |  | Primary Power | MCC | 1 |  | 352_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the control panel which may require examination, adjustment, servicing, or maintenance
529 |  |  | 201659 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 43 | Manual Transfer Switch | 2 | MTS ; Square D; ; ; 600V, 60A | Halton | In Service | Morrison Heights PS | WWPS | Site | Process Electrical | Process Electrical |  | MCC | [5 empty] | 2010 |  | 2040 | HR-MORI-047 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 15:48 | Maira Rafiq | 2020-09-22 12:31 |  |  |  |  | Primary Power | Transfer Switch | 1 |  | 353_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the control panel which may require examination, adjustment, servicing, or maintenance
530 |  |  | 201659 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 43 | Power Meter | 2 | Power Meter ; elster; ; ; 600V | Halton | In Service | Morrison Heights PS | WWPS | Site | Process Electrical | Process Electrical |  | MCC | [5 empty] | 2010 |  | 2040 | HR-MORI-047 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 15:49 | Maira Rafiq | 2020-09-22 12:31 |  |  |  |  | Primary Power | MCC | 1 |  | 354_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
531 |  |  | 201659 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 646 | Dry Well Lights | 1 | Dry Well Lights ; elster; ; ; Fluorescent | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Process Electrical | Process Electrical |  | Lighting | [5 empty] | 1973 |  | 2025 | HR-MORI-056 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 15:55 | Maira Rafiq | 2020-09-22 12:31 |  |  |  |  | Building | Electrical - Lighting | 1 |  | 355_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | one of the lights doesn’t work | to be replaced with LED
532 |  |  | 201659 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 646 | Control Panel | 3 | Control Panel ; elster; ; ; 600V | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Process Electrical | Process Electrical |  | Panel, Breaker | [5 empty] | 1973 |  | 2025 | HR-MORI-057 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 16:06 | Maira Rafiq | 2020-09-22 12:32 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 356_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servicing, or maintenance while e
533 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Wet well Light | 1 | Wet well Light; ; ; ; rated for class 1, div 1 | Halton | In Service | Raymar Pl PS | WWPS | Wetwell | Building Electrical | Process Electrical |  | Lighting | [5 empty] | 1985 |  | 2021 | HR-RAYM-026 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 16:19 | Maira Rafiq | 2020-09-22 12:57 |  |  |  |  | Pumping | Wet Well | 1 |  | 357_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | it doesn't work
534 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 45 | Enclosure Light | 1 | Enclosure Light; ; ; ; fluorescent | Halton | In Service | Raymar Pl PS | WWPS | Site | Building Electrical | Process Electrical |  | Lighting | [5 empty] | 1985 |  | 2025 | HR-RAYM-026 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 16:20 | Maira Rafiq | 2020-09-22 12:58 |  |  |  |  | Building | Electrical - Lighting | 1 |  | 358_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | to be replaced with LED
535 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Outdoor Enclosure | 1 | Outdoor Enclosure; ; ; ; | Halton | In Service | Raymar Pl PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 1985 |  | 2025 | HR-RAYM-057 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 16:23 | Maira Rafiq | 2020-09-22 12:58 |  |  |  |  | Primary Power | MCC | 1 |  | 359_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | fair | to be replaced with NEMA 3R enclosure
536 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 45 | Power Meter | 2 | Power Meter; Sensus; ; ; | Halton | In Service | Raymar Pl PS | WWPS | Site | Process Electrical | Process Electrical |  | MCC | [5 empty] | 2006 |  | 2036 | HR-RAYM-059 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 16:28 | Maira Rafiq | 2020-09-22 12:58 |  |  |  |  | Primary Power | MCC | 1 |  | 360_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
537 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 45 | Pump #1 VFD and Breaker | 2 | Pump #1 VFD and Breaker; A-B; PowerFlex 40; ; 240V, size 1 | Halton | In Service | Raymar Pl PS | WWPS | Site | Process Electrical | Process Electrical |  | VFD | [5 empty] | 2006 |  | 2036 | HR-RAYM-063 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 16:38 | Maira Rafiq | 2020-09-22 12:59 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 361_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
538 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 12 | Pump #2 VFD and Breaker | 2 | Pump #2 VFD and Breaker; A-B; PowerFlex 40; ; 240V, size 1 | Halton | In Service | Raymar Pl PS | WWPS | Site | Process Electrical | Process Electrical |  | VFD | [5 empty] | 2006 |  | 2036 | HR-RAYM-063 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 16:38 | Maira Rafiq | 2020-09-22 12:59 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 362_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
539 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 45 | Control Panel with Main DS and MTS | 3 | Control Panel with Main DS and MTS; ; ; ; 240V, 60A | Halton | In Service | Raymar Pl PS | WWPS | Site | Process Electrical | Process Electrical |  | Panel, Breaker | [5 empty] | 1985 |  | 2025 | HR-RAYM-077 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 16:43 | Maira Rafiq | 2020-09-22 13:03 |  |  |  |  | Pumping | Pump Assembly | 1 |  | 363_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good | replace with separate main DS, MTS and CP | Shock and arc flash hazard as the existing arc flash label are outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreover, the studies and reports
540 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 45 | Gen Connect Recept | 2 | Gen Connect Recept; ; AR648; ; 240V, 60A | Halton | In Service | Raymar Pl PS | WWPS | Site | Process Electrical | Process Electrical |  | Generator | [5 empty] | 1985 |  | 2025 | HR-RAYM-130 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Amin Norouzizadeh | 2020-08-04 16:49 | Maira Rafiq | 2020-09-22 13:02 |  |  |  |  | Primary Power | Standby Generator | 1 |  | 364_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
576 |  |  | 201612 | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Dry Wall Sump Pump | 1 | Installation year was assumed to be 1975 | Halton |  | Chancery Lane PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Misc. Building Services | [5 empty] | 1975 |  |  | HR-CNRY-132 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:24 | Maira Rafiq | 2020-09-18 11:53 |  |  |  |  | Building | Plumbing - Sanitary Waste | 1 |  | 293_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Surface corrosion
577 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Dry Wall Portable Heater | 1 | Installation year assumed to be 1975 | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Unit Heater | [5 empty] | 1975 |  |  | HR-CNRY-018 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:22 | Maira Rafiq | 2020-09-18 11:47 |  |  |  |  | Building | HVAC - Heat Generating Systems | 1 |  | 294_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
578 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  | Dry Wall Portable Dehumidifier | 1 | Manufacturer: Garrison, installation year assumed to be 1975 | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Dehumidifier | [5 empty] | 1975 |  |  | HR-CNRY-009 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:22 | Maira Rafiq | 2020-09-18 11:47 |  |  |  |  | Building | HVAC - Cooling Generating Systems | 1 |  | 295_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
579 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Dry Wall Portable Heater | 1 | Installation year assumed to be 1980 | Halton |  | Chartwell Rd. PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Unit Heater | [5 empty] | 1983 |  |  | HR-CTWL-007 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:26 | Maira Rafiq | 2020-08-28 17:29 |  |  |  |  | Building | HVAC - Heat Generating Systems | 1 |  | 296_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
580 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Dry Well Dehumidifier | 1 | Installation year assumed to be 1980 | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Dehumidifier | [5 empty] | 1983 |  |  | HR-CTWL-008 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:26 | Maira Rafiq | 2020-09-20 10:50 |  |  |  |  | Building | HVAC - Heat Generating Systems | 1 |  | 297_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
581 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Dry Wall Sump Pump | 1 | Installation year was assumed to be 1980 | Halton |  | Chartwell Rd. PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Misc. Building Services | [5 empty] | 1983 |  |  | HR-CTWL-019 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:26 | Maira Rafiq | 2020-08-28 17:29 |  |  |  |  | Building | Plumbing - Sanitary Waste | 1 |  | 299_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Severe corrosion
583 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 15 | Dry Wall Sump Pump | 1 |  | Halton |  | Cumnock PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Misc. Building Services | [5 empty] | 1974 |  |  | HR-CMNK-021 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:30 | Maira Rafiq | 2020-09-21 15:24 |  |  |  |  | Building | Plumbing - Sanitary Waste | 1 |  | 301_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | surface corrosion
584 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Dry Wall Portable Heater | 1 | Installation year assumed to be 1975 | Halton | In Service | Cumnock PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Unit Heater | [5 empty] | 1974 |  |  | HR-CMNK-007 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:30 | Maira Rafiq | 2020-09-21 15:25 |  |  |  |  | Building | HVAC - Heat Generating Systems | 1 |  | 302_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Surface corrosion
585 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 640 | Dry Wall Portable Dehumidifier | 1 | Installation year assumed to be 1975 | Halton | In Service | Cumnock PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Dehumidifier | [5 empty] | 1974 |  |  | HR-CMNK-008 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:30 | Maira Rafiq | 2020-09-21 15:26 |  |  |  |  | Building | HVAC - Cooling Generating Systems | 1 |  | 303_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
586 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  | Wet Well Ventilation Pipe | 1 | one 2 inches diameter steel pipe vent | Halton | In Service | Cumnock PS | WWPS | Wet Well | Building Mechanical | Building Services |  | Misc. Building Services | [5 empty] | 1974 |  |  | HR-CMNK-034 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:29 | Maira Rafiq | 2020-09-21 15:26 |  |  |  |  | Pumping | Wet Well | 1 |  | 304_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
587 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 642 | Wet Well Ventilation Pipe | 1 | one 4 inches diameter gooseneck pipe vent | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Building Mechanical | Building Services |  | Misc. Building Services | [5 empty] | 1977 |  |  | HR-ENIS-001 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:33 | Maira Rafiq | 2020-09-21 17:27 |  |  |  |  | Pumping | Wet Well | 1 |  | 305_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | miscellaneous surface staining
588 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 15 | Dry Wall Sump Pump | 1 | Installation year was assumed to be 1985 | Halton |  | First Street PS | WWPS | Dry Well | Building Mechanical | Building Services | [7 empty] | 1986 |  |  | HR-FRST-009 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:35 | [8 empty] | 1 |  | 306_merge | 0 | 0 | 0 | 0 | FALSE | FALSE
589 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 643 | Dry Wall Portable Heater | 1 | Installation year assumed to be 1985 | Halton |  | First Street PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Unit Heater | [5 empty] | 1986 |  |  | HR-FRST-003 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:35 | Maira Rafiq | 2020-09-21 23:40 |  |  |  |  | Building | HVAC - Heat Generating Systems | 1 |  | 307_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
590 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 643 | Dry Well Dehumidifier | 1 | Manufacturer: Simplicity, installation year assumed to be 1985 | Halton |  | First Street PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Dehumidifier | [5 empty] | 1986 |  |  | HR-FRST-004 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:35 | Maira Rafiq | 2020-09-21 23:40 |  |  |  |  | Building | HVAC - Distribution Systems | 1 |  | 308_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
592 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 645 | Wet Well Ventilation Pipe | 1 | one 4 inches diameter gooseneck steel pipe vent | Halton | In Service | Garlock Gdns PS | WWPS | Wet Well | Building Mechanical | Building Services |  | Misc. Building Services | [5 empty] | 1977 |  |  | HR-GGDN-001 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:37 | Maira Rafiq | 2020-09-22 11:12 |  |  |  |  | Pumping | Wet Well | 1 |  | 310_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | paint peeling | fair
593 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  | Dry Wall Portable Heater | 1 |  | Halton |  | Morrison Heights PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Unit Heater | [5 empty] | 1973 |  |  | HR-MORI-007 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:37 | Maira Rafiq | 2020-09-22 12:36 |  |  |  |  | Building | HVAC - Heat Generating Systems | 1 |  | 311_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
594 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 646 | Dry Well Dehumidifier | 1 |  | Halton |  | Morrison Heights PS | WWPS | Dry Well | Building Mechanical | Building Services |  | Dehumidifier | [5 empty] | 1973 |  |  | HR-MORI-008 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:37 | Maira Rafiq | 2020-09-22 12:38 |  |  |  |  | Building | HVAC - Cooling Generating Systems | 1 |  | 312_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
595 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Wet Well Ventilation Pipe | 1 | one 4 inches diameter steel pipe vent with insect screen | Halton | In Service | Raymar Pl PS | WWPS | Wet Well | Building Mechanical | Building Services |  | Misc. Building Services | [5 empty] | 1985 |  |  | HR-RAYM-056 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Raymond Mu | 2020-07-30 11:39 | Maira Rafiq | 2020-09-22 13:06 |  |  |  |  | Pumping | Wet Well | 1 |  | 313_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | good
611 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 25 | Yard Hydrant | 1 |  | Halton | In Service | Chancery Lane PS | WWPS | Site | Site Works | Site Works |  | Misc. Site Works | [5 empty] | 1975 |  | 2035 | HR-CNRY-034 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Joseph De Paolo | 2020-07-17 10:40 | Maira Rafiq | 2020-08-24 14:03 |  |  |  |  | Site Works | Yard Piping | 1 |  | 281_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Good
612 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 27 | Yard Hydrant | 1 |  | Halton | In Service | Chartwell Rd. PS | WWPS | Site | Site Works | Site Works |  | Misc. Site Works | [5 empty] | 1983 |  | 2035 | HR-CTWL-025 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Joseph De Paolo | 2020-07-17 10:40 | Maira Rafiq | 2020-08-24 16:29 |  |  |  |  | Site Works | Yard Piping | 1 |  | 282_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Good
613 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 30 | Yard Hydrant | 1 |  | Halton | In Service | Cumnock PS | WWPS | Site | Site Works | Site Works |  | Misc. Site Works | [5 empty] | 1974 |  | 2035 | HR-CMNK-158 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Joseph De Paolo | 2020-07-17 10:39 | Maira Rafiq | 2020-08-24 16:30 |  |  |  |  | Site Works | Yard Piping | 1 |  | 283_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Good
614 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 33 | Yard Hydrant | 1 |  | Halton | In Service | Ennisclaire Drive PS | WWPS | Site | Site Works | Site Works |  | Misc. Site Works | [5 empty] | 1977 |  | 2035 | HR-ENIS-026 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Joseph De Paolo | 2020-07-17 10:39 | Maira Rafiq | 2020-09-21 16:54 |  |  |  |  | Site Works | Yard Piping | 1 |  | 284_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Good
615 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 37 | Yard Hydrant | 1 |  | Halton | In Service | First Street PS | WWPS | Site | Site Works | Site Works |  | Misc. Site Works | [5 empty] | 1968 |  | 2035 | HR-FRST-095 | [7 empty] | 1 | ea. | 2020 | [10 empty] | Joseph De Paolo | 2020-07-17 10:39 | Maira Rafiq | 2020-08-24 16:39 |  |  |  |  | Site Works | Yard Piping | 1 |  | 285_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Good
616 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 40 | Yard Hydrant (New Asset) | 1 |  | Halton |  | Garlock Gdns PS | WWPS | Site | Site Works | Site Works |  | Misc. Site Works | [5 empty] | 1977 |  | 2035 | [8 empty] | 1 | ea. | 2020 | [10 empty] | CAMR061927 | 2020-08-24 16:41 | Maira Rafiq | 2020-08-24 16:42 |  |  |  |  | Site Works | Yard Piping | 1 |  | 286_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | In accordance with Section 19.8.3 of the Region's Water and Wastewater Design Manual (January 2012), a yard hydrant complete with a backflow preventer with a 37.5mm water service line shall be provided for flushing and cleaning purposes. It is recommended
622 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 43 | Yard Hydrant | 1 |  | Halton |  | Morrison Heights PS | WWPS | Site | Site Works | Site Works |  | Misc. Site Works | [5 empty] | 1973 |  | 2036 | HR-MORI-029 | [7 empty] | 1 | ea. | 2020 | [10 empty] | CAMR061927 | 2020-08-24 16:44 | Maira Rafiq | 2020-08-24 16:44 |  |  |  |  | Site Works | Yard Piping | 1 |  | 292_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Minor surface rust and defects
623 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 45 | Yard Hydrant (New Asset) | 1 |  | Halton |  | Raymar Pl PS | WWPS | Site | Site Works | Site Works |  | Misc. Site Works | [5 empty] | 1985 |  | 2035 | [8 empty] | 1 | ea. | 2020 | [10 empty] | CAMR061927 | 2020-08-24 16:46 | Maira Rafiq | 2020-08-24 16:46 |  |  |  |  | Site Works | Yard Piping | 1 |  | 293_merge | 0 | 0 | 0 | 0 | FALSE | FALSE | In accordance with Section 19.8.3 of the Region's Water and Wastewater Design Manual (January 2012), a yard hydrant complete with a backflow preventer with a 37.5mm water service line shall be provided for flushing and cleaning purposes. It is recommended
632 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 6 | Dry Well |  | Chartwell Rd. PS Dry Well | Halton | In Service | Chartwell Rd. PS | WWPS | Dry Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1983 | [10 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-21 16:04 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
633 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 6 | Wet Well |  | Chartwell Rd. PS Wet Well | Halton | In Service | Chartwell Rd. PS | WWPS | Wet Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1983 |  |  | HR-CTWL-024 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-28 17:20 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
638 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 5 | Dry Well |  |  | Halton | In Service | Chancery Lane PS | WWPS | Dry Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1975 |  |  | HR-CNRY-004 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-18 10:59 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
639 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 5 | Wet Well |  |  | Halton | In Service | Chancery Lane PS | WWPS | Process Structural | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1975 |  |  | HR-CNRY-033 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-24 08:38 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
640 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 7 | Dry Well |  | Cumnock PS Dry Well | Halton | In Service | Cumnock PS | WWPS | Dry Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1974 |  | 0 | HR-CMNK-033 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-21 15:40 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
641 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 7 | Wet Well |  | Cumnock PS Wet Well | Halton | In Service | Cumnock PS | WWPS | Wet Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1974 |  |  | HR-CMNK-032 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-24 08:54 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
642 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 8 | Wet Well |  | Ennisclaire Drive PS Wet Well | Halton | In Service | Ennisclaire Drive PS | WWPS | Wet Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1977 |  |  | HR-ENIS-002 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-24 09:01 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
643 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 9 | Dry Well |  | First Street PS Dry Well | Halton | In Service | First Street PS | WWPS | Dry Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1986 |  |  | HR-FRST-065 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-24 09:05 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
644 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 9 | Wet Well |  | First Street PS Wet Well | Halton | In Service | First Street PS | WWPS | Wet Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1986 |  |  | HR-FRST-094 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-24 09:07 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
645 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 10 | Wet Well |  | Garlock Gdns PS Wet Well | Halton | In Service | Garlock Gdns PS | WWPS | Wet Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1977 |  |  | HR-GGDN-088 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-24 09:14 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
646 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 11 | Dry Well |  | Morrison Heights PS Dry Well | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1973 |  |  | HR-MORI-098 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-24 09:16 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
647 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 11 | Wet Well |  | Morrison Heights PS Wet Well | Halton | In Service | Morrison Heights PS | WWPS | Wet Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1973 |  |  | HR-MORI-124 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-24 09:17 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
648 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE | 12 | Wet Well |  | Raymar Pl PS Wet Well | Halton | In Service | Raymar Pl PS | WWPS | Wet Well | Asset Hierarchy | Asset Hierarchy | [7 empty] | 1985 |  |  | HR-RAYM-054 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-24 09:33 | [6 empty] | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
651 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 33 | concrete pavers | 1 |  | Halton | In Service | Ennisclaire Drive PS | WWPS | Site | Site Works | Site Works |  | Misc. Site Works | [5 empty] | 1977 |  |  | HR-ENIS-026 | [7 empty] | 1 | ea. | 2020 | [10 empty] | CAMR061927 | 2020-08-24 16:38 | Maira Rafiq | 2020-09-21 16:53 |  |  |  |  | Site Works | Sidewalk | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Overgrown vegetation
661 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Cathodic Protection | 2 | Cathodic Protection for Underground Tank | Halton | In Service | Chancery Lane PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2010 |  |  | HR-CNRY-037 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-18 13:21 |  |  |  |  | Primary Power | MCC | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE | The Cathodic Protection was assumed to be in good condition. The installation of the cathodic protection system was assumed to coincide with the installation of the above grade panel.
663 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 151 | Pump 2 Piping | 3 | 150mm diameter, approx. 5m ductile iron pipe | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS | [5 empty] | 1983 |  | 0 | HR-CTWL-033 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-20 13:46 |  |  |  |  | Pumping | Pump Assembly |  |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Minor corrosion
665 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 632 | Discharge Piping | 3 | 150mm diameter, approx. 5m ductile iron pipe | Halton | In Service | Chartwell Rd. PS | Chartwell Rd. PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS | [5 empty] | 1983 |  | 0 | HR-CTWL-014 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-20 13:46 |  |  |  |  | Pumping | Discharge Header |  |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Minor corrosion
666 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 165 | Pump 2 Piping | 3 | 100mm diameter, approx. 5m ductile pipe | Halton | In Service | Cumnock PS | Cumnock PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS | [5 empty] | 1974 |  | 0 | HR-CMNK-027 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-21 15:41 |  |  |  |  | Pumping | Pump Assembly | 2 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE | Fair | Corrosion
667 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 638 | Cathodic Protection | 2 | Cathodic Protection for Underground Tank | Halton | In Service | Cumnock PS | WWPS | Site | Process Electrical | Process Electrical |  | Misc. Electrical | [5 empty] | 2010 |  |  | HR-CNRY-037 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-21 15:44 |  |  |  |  | Primary Power | MCC | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE | The Cathodic Protection was assumed to be in good condition. The installation of the cathodic protection system was assumed to coincide with the installation of the above grade panel.
669 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 40 | Discharge Header | 3 | 100mm diameter, approx. 5m ductile pipe | Halton | In Service | Garlock Gdns PS | Garlock Gdns PS | Dry Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS | [5 empty] | 1977 |  | 0 | [8 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-22 11:09 |  |  |  |  | Pumping | Wet Well |  |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE | Not observed
670 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  | Dry Well Concrete Foundation | 2 |  | Halton | In Service | Morrison Heights PS | WWPS | Dry Well | Building Structural | Building and Process Structural |  | Misc. Structural | [5 empty] | 1973 |  | 2035 |  |  |  |  | 3 |  |  |  | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-22 11:45 |  |  |  |  | Building | Substructure | 1 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE | The asset was assumed to be in fair condition based on its age.
671 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 648 | Discharge Header | 3 | 100mm diameter, approx. 8.6 m ductile iron pipe | Halton | In Service | Raymar Pl PS | Raymar Pl PS | Wet Well | Process Mechanical | Process Piping |  | Piping, DI/CPP/Steel/SS | [5 empty] | 1985 |  | 0 | HR-RAYM-040 | [7 empty] | 1 | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-09-22 13:21 |  |  |  |  | Pumping | Discharge Header | 2 |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE | Poor | Heavy corrosion and deterioration was observed

## p_comments
ParentID | Comment | ParentID | Comment1 | Comment2 | Comment3 | Comment4 | Comment5 | Comment6 | Comment7 | Comment8 | Comment9 | Comment10
7 |  | 1
8 |  | 2
15 | The asset was in fair condition. Typical corrosion was noted throughout | 3
17 | The asset was in fair condition. Leakage was noted at joints. Concrete spalling was also noted at concrete parging of joints | 4
19 | The asset was observed to be in fair condition. Concrete spalling and exposed corroded reinforcement was noted. | 5
20 | The asset was observed to be in fair condition. Corrosion was observed. | 6
23 | The asset was observed to be in fair condition. Concrete spalling on roof, rust spots and concrete spalling at pipe penetration was observed. | 7
24 | Minor corrosion noted | 8
24 | Good | 9
26 | Minor corrosion noted throughout | 10
26 | Good | 11
28 | Exposed corroded reinforcement | 12
28 | Fair | 13
29 | Moderate corrosion noted throughout | 14
29 | Fair | 15 | The asset was in fair condition. Typical corrosion was noted throughout
31 | Efflorescence deposits/leak at joint. Concrete delamination/spalling at joint | 16
31 | Fair | 17 | The asset was in fair condition. Leakage was noted at joints. Concrete spalling was also noted at concrete parging of joints
34 | Exposed corroded reinforcement, rust spots and concrete parging spalling was noted at joints | 18
34 | Fair | 19 | The asset was observed to be in fair condition. Concrete spalling and exposed corroded reinforcement was noted.
36 | Corrosion noted throughout | 20 | The asset was observed to be in fair condition. Corrosion was observed.
36 | Fair | 21
38 | fair | 22
41 | Rust spots noted | 23 | The asset was observed to be in fair condition. Concrete spalling on roof, rust spots and concrete spalling at pipe penetration was observed.
41 | Fair | 24 | Minor corrosion noted | Good
42 | Corrosion was noted at the base | 25
42 | Fair | 26 | Minor corrosion noted throughout | Good
44 | Exposed corroded reinforcement and concrete spalling noted | 27
44 | Fair | 28 | Exposed corroded reinforcement | Fair
46 | Exposed corroded reinforcement and concrete spalling was noted at the pipe penetration | 29 | Moderate corrosion noted throughout | Fair
46 | Fair | 30
49 | The asset was observed to be in good condition. Rust spots was observed. | 31 | Efflorescence deposits/leak at joint. Concrete delamination/spalling at joint | Fair
50 | The asset was observed to be in fair condition. Corrosion at the SCADA equipment mount was observed. | 32
52 | The asset was observed to be in fair condition. Rust spots were noted at several locations. | 33
53 | Fair | 34 | Exposed corroded reinforcement, rust spots and concrete parging spalling was noted at joints | Fair
53 | The pump was near the end of its expected life. | 35
54 | Poor | 36 | Corrosion noted throughout | Fair
54 | Heavy corrosion was observed on the valve. | 37
55 | Poor | 38 | fair
55 | Heavy corrosion was observed on the valve. | 39
57 | Poor | 40
57 | The pump was near the end of its expected service life | 41 | Rust spots noted | Fair
58 | Poor | 42 | Corrosion was noted at the base | Fair
58 | Severe corrosion was observed on the surface of the valve | 43
59 | Poor | 44 | Exposed corroded reinforcement and concrete spalling noted | Fair
59 | Heavy corrosion was observed on the valve | 45
60 | Fair | 46 | Exposed corroded reinforcement and concrete spalling was noted at the pipe penetration | Fair
60 | The pipe was at half of its expected service life. | 47
61 | Surface staining on exhaust fan pipe | 48
61 | fair | 49 | The asset was observed to be in good condition. Rust spots was observed.
62 | Fair | 50 | The asset was observed to be in fair condition. Corrosion at the SCADA equipment mount was observed.
62 | The pump was near the end of its expected service life. | 51
63 | Poor | 52 | The asset was observed to be in fair condition. Rust spots were noted at several locations.
63 | Heavy corrosion was observed on the surface of the valve | 53 | Fair | The pump was near the end of its expected life.
64 | Poor | 54 | Poor | Heavy corrosion was observed on the valve.
64 | Heavy corrosion was observed on the surface of the valve | 55 | Poor | Heavy corrosion was observed on the valve.
65 | Fair | 56
65 | The pump was near the end of its expected service life. | 57 | Poor | The pump was near the end of its expected service life
66 | Poor | 58 | Poor | Severe corrosion was observed on the surface of the valve
66 | Heavy corrosion was observed on the surface of the valve. | 59 | Poor | Heavy corrosion was observed on the valve
67 | Poor | 60 | Fair | The pipe was at half of its expected service life.
67 | Heavy corrosion was observed on the surface of the valve | 61 | Surface staining on exhaust fan pipe | fair
68 | assumed to be good | 62 | Fair | The pump was near the end of its expected service life.
69 | Poor | 63 | Poor | Heavy corrosion was observed on the surface of the valve
69 | Corrosion and deterioration was observed on the surface of the pump. The pump was beyond its expected service life. | 64 | Poor | Heavy corrosion was observed on the surface of the valve
69 | Moderate surface corrosion | 65 | Fair | The pump was near the end of its expected service life.
70 | good | 66 | Poor | Heavy corrosion was observed on the surface of the valve.
71 | paint peeling | 67 | Poor | Heavy corrosion was observed on the surface of the valve
71 | fair | 68 | assumed to be good
72 | Poor | 69 | Poor | Corrosion and deterioration was observed on the surface of the pump. The pump was beyond its expected service life. | Moderate surface corrosion
72 | Corrosion and deterioration was observed on the surface of the pump. The pump was beyond its expected service life. | 70 | good
73 | Poor | 71 | paint peeling | fair
73 | Corrosion and deterioration was observed on the surface of the valve. The valve was beyond its expected service life | 72 | Poor | Corrosion and deterioration was observed on the surface of the pump. The pump was beyond its expected service life.
74 | Fair | 73 | Poor | Corrosion and deterioration was observed on the surface of the valve. The valve was beyond its expected service life
74 | minor paint wear | 74 | Fair | minor paint wear
75 | Poor | 75 | Poor | Corrosion and deterioration was observed on the surface of the valve. The valve was beyond its expected service life.
75 | Corrosion and deterioration was observed on the surface of the valve. The valve was beyond its expected service life. | 76 | Poor | Corrosion and deterioration was observed on the surface of the valve. The valve was beyond its expected service life.
76 | Poor | 77
76 | Corrosion and deterioration was observed on the surface of the valve. The valve was beyond its expected service life. | 78 | Poor | Corrosion and deterioration was observed on the surface of the pump. The pump was beyond its expected service life.
78 | Poor | 79 | Poor | Deterioration and corrosion was observed on the surface of the valve. The valve was beyond its expected service life
78 | Corrosion and deterioration was observed on the surface of the pump. The pump was beyond its expected service life. | 80 | Fair | minor paint wear
79 | Poor | 81 | Poor | Corrosion was observed on the surface of the valve. The valve was beyond its expected service life.
79 | Deterioration and corrosion was observed on the surface of the valve. The valve was beyond its expected service life | 82 | Fair | Minor deterioration was observed on the surface of the valve. The valve was beyond its expected service life.
80 | Fair | 83 | assumed to be fair | The pipe passed half of its expected service life.
80 | minor paint wear | 84 | The asset was observed to be in fair condition. Minor corrosion om piping and at pump base was observed.
81 | Poor | 85 | The asset was observed to be in good condition. Nuts were not secured properly.
81 | Corrosion was observed on the surface of the valve. The valve was beyond its expected service life. | 86 | The asset was observed to be in good condition. Dust was observed.
82 | Fair | 87 | Exhaust Fan 1 was missing during the assessment. | As per Section 7.2.9 of MOECC's Design Guidelines for Sewage Works, mechanical ventilation is required for below ground surface dry well.
82 | Minor deterioration was observed on the surface of the valve. The valve was beyond its expected service life. | 88 | The asset was observed to be in fair condition. Surface corrosion and paint wear was observed. The pump was original to the facility and had surpassed its expected service life. Pump testing was not undertaken as part of this assessment. Based on the age
83 | assumed to be fair | 89 | The asset was observed to be in fair condition. Minor surface corrosion and paint wear was observed.
83 | The pipe passed half of its expected service life. | 90 | The asset was observed to be in fair condition. Surface corrosion and deterioration was observed. The motor was original to the facility and had surpassed its expected service life.
84 | The asset was observed to be in fair condition. Minor corrosion om piping and at pump base was observed. | 91 | The asset was observed to be in fair condition. Minor surface corrosion and paint wear on the handwheel was observed.
85 | The asset was observed to be in good condition. Nuts were not secured properly. | 92 | The asset was observed to be in fair condition. Minor surface corrosion and paint wear on the handwheel was observed.
86 | The asset was observed to be in good condition. Dust was observed. | 93 | The asset was observed to be in fair condition. Surface corrosion and paint wear was observed. The pump was original to the facility and had surpassed its expected service life. Pump testing was not undertaken as part of this assessment. Based on the age
87 | Exhaust Fan 1 was missing during the assessment. | 94 | The asset was observed to be in fair condition. Minor surface corrosion and paint wear was observed.
87 | As per Section 7.2.9 of MOECC's Design Guidelines for Sewage Works, mechanical ventilation is required for below ground surface dry well. | 95 | The asset was observed to be in fair condition. Surface corrosion and deterioration was observed. The motor was original to the facility and had surpassed its expected service life.
88 | The asset was observed to be in fair condition. Surface corrosion and paint wear was observed. The pump was original to the facility and had surpassed its expected service life. Pump testing was not undertaken as part of this assessment. Based on the age | 96 | The asset was observed to be in fair condition. Minor surface corrosion and paint wear on the handwheel was observed.
89 | The asset was observed to be in fair condition. Minor surface corrosion and paint wear was observed. | 97 | The asset was observed to be in fair condition. Minor surface corrosion and paint wear on the handwheel was observed.
90 | The asset was observed to be in fair condition. Surface corrosion and deterioration was observed. The motor was original to the facility and had surpassed its expected service life. | 98 | The Forcemain was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken.
91 | The asset was observed to be in fair condition. Minor surface corrosion and paint wear on the handwheel was observed. | 99 | The asset was in fair condition. Moderate corrosion was observed.
92 | The asset was observed to be in fair condition. Minor surface corrosion and paint wear on the handwheel was observed. | 100 | The asset was observed to be in good condition. Dust was observed.
93 | The asset was observed to be in fair condition. Surface corrosion and paint wear was observed. The pump was original to the facility and had surpassed its expected service life. Pump testing was not undertaken as part of this assessment. Based on the age | 101 | Exhaust Fan 1 was missing during the assessment. | As per Section 7.2.9 of MOECC's Design Guidelines for Sewage Works, mechanical ventilation is required for below ground surface dry well.
94 | The asset was observed to be in fair condition. Minor surface corrosion and paint wear was observed. | 102 | The asset was observed to be in fair condition. Surface corrosion and paint wear was observed. The pump was original to the facility and had surpassed its expected service life. Pump testing was not undertaken as part of this assessment. Based on the age
95 | The asset was observed to be in fair condition. Surface corrosion and deterioration was observed. The motor was original to the facility and had surpassed its expected service life. | 103 | The asset was observed to be in fair condition. Surface corrosion and paint wear was observed. One of the bolts on the valve was also missing. The valve was original to the facility and had surpassed its expected service life.
96 | The asset was observed to be in fair condition. Minor surface corrosion and paint wear on the handwheel was observed. | 104 | The asset was observed to be in fair condition. Surface corrosion and paint wear was observed. The motor was original to the facility and had surpassed its expected service life.
97 | The asset was observed to be in fair condition. Minor surface corrosion and paint wear on the handwheel was observed. | 105 | The asset was observed to be in fair condition. Surface corrosion and paint wear was observed. The valve was original to the facility and had surpassed its expected service life.
98 | The Forcemain was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken. | 106 | The asset was observed to be in fair condition. Surface corrosion and paint wear was observed. The valve was original to the facility and had surpassed its expected service life.
99 | The asset was in fair condition. Moderate corrosion was observed. | 107 | The asset was observed to be in fair condition. Surface corrosion and paint wear was observed. The pump was original to the facility and had surpassed its expected service life. Pump testing was not undertaken as part of this assessment. Based on the age
100 | The asset was observed to be in good condition. Dust was observed. | 108 | The asset was observed to be in fair condition. Surface corrosion and paint wear was observed. The valve was original to the facility and had surpassed its expected service life.
101 | Exhaust Fan 1 was missing during the assessment. | 109 | The asset was observed to be in fair condition. Surface corrosion and paint wear was observed. The motor was original to the facility and had surpassed its expected service life.
101 | As per Section 7.2.9 of MOECC's Design Guidelines for Sewage Works, mechanical ventilation is required for below ground surface dry well. | 110 | The asset was observed to be in fair condition. Surface corrosion and paint wear was observed. The valve was original to the facility and had surpassed its expected service life.
102 | The asset was observed to be in fair condition. Surface corrosion and paint wear was observed. The pump was original to the facility and had surpassed its expected service life. Pump testing was not undertaken as part of this assessment. Based on the age | 111 | The asset was observed to be in fair condition. Surface corrosion and paint wear was observed. The valve was original to the facility and had surpassed its expected service life.
103 | The asset was observed to be in fair condition. Surface corrosion and paint wear was observed. One of the bolts on the valve was also missing. The valve was original to the facility and had surpassed its expected service life. | 112 | The Forcemain was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken.
104 | The asset was observed to be in fair condition. Surface corrosion and paint wear was observed. The motor was original to the facility and had surpassed its expected service life. | 113 | The exhaust fan was in fair condition. Heavy corrosion on motor of the exhaust fan was observed.
105 | The asset was observed to be in fair condition. Surface corrosion and paint wear was observed. The valve was original to the facility and had surpassed its expected service life. | 114 | The asset was observed to be in fair condition. The pump was working but it was near the end of its expected service life. Pump testing was not undertaken as part of this assessment. Based on the age of the pumps, replacement is recommended in the next 10
106 | The asset was observed to be in fair condition. Surface corrosion and paint wear was observed. The valve was original to the facility and had surpassed its expected service life. | 115 | The asset was observed to be in poor condition. Heavy corrosion and deterioration was observed on the surface of the valve. The valve was near the end of its expected service life.
107 | The asset was observed to be in fair condition. Surface corrosion and paint wear was observed. The pump was original to the facility and had surpassed its expected service life. Pump testing was not undertaken as part of this assessment. Based on the age | 116 | The asset was observed to be in poor condition. Heavy corrosion and deterioration was observed on the surface of the valve. The valve was near the end of its expected service life.
108 | The asset was observed to be in fair condition. Surface corrosion and paint wear was observed. The valve was original to the facility and had surpassed its expected service life. | 117 | The asset was observed to be in fair condition. The pump was working but it was near the end of its expected service life. Pump testing was not undertaken as part of this assessment. . Based on the age of the pumps, replacement is recommended in the next
109 | The asset was observed to be in fair condition. Surface corrosion and paint wear was observed. The motor was original to the facility and had surpassed its expected service life. | 118 | The asset was observed to be in poor condition. Heavy corrosion and deterioration was observed on the surface of the valve. The valve was near the end of its expected service life.
110 | The asset was observed to be in fair condition. Surface corrosion and paint wear was observed. The valve was original to the facility and had surpassed its expected service life. | 119 | The asset was observed to be in poor condition. Heavy corrosion and deterioration was observed on the surface of the valve. The valve was near the end of its expected service life.
111 | The asset was observed to be in fair condition. Surface corrosion and paint wear was observed. The valve was original to the facility and had surpassed its expected service life. | 120 | The Forcemain was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken.
112 | The Forcemain was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken. | 121 | The asset was observed to be in good condition.
113 | The exhaust fan was in fair condition. Heavy corrosion on motor of the exhaust fan was observed. | 122 | The asset was observed to be in fair condition. The pump was working but it was near the end of its expected service life. Pump testing was not undertaken as part of this assessment. he operator mentioned that one of pumps is electrically jumpered out. Th
114 | The asset was observed to be in fair condition. The pump was working but it was near the end of its expected service life. Pump testing was not undertaken as part of this assessment. Based on the age of the pumps, replacement is recommended in the next 10 | 123 | The asset was observed to be in poor condition. Heavy corrosion and deterioration was observed on the surface of the valve. The valve was near the end of its expected service life.
115 | The asset was observed to be in poor condition. Heavy corrosion and deterioration was observed on the surface of the valve. The valve was near the end of its expected service life. | 124 | The asset was observed to be in poor condition. Heavy corrosion and deterioration was observed on the surface of the valve. The valve was near the end of its expected service life.
116 | The asset was observed to be in poor condition. Heavy corrosion and deterioration was observed on the surface of the valve. The valve was near the end of its expected service life. | 125 | The asset was observed to be in fair condition. The pump was working but it was near the end of its expected service life. Pump testing was not undertaken as part of this assessment. he operator mentioned that one of pumps is electrically jumpered out. Th
117 | The asset was observed to be in fair condition. The pump was working but it was near the end of its expected service life. Pump testing was not undertaken as part of this assessment. . Based on the age of the pumps, replacement is recommended in the next | 126 | The asset was observed to be in poor condition. Heavy corrosion and deterioration was observed on the surface of the valve. The valve was near the end of its expected service life.
118 | The asset was observed to be in poor condition. Heavy corrosion and deterioration was observed on the surface of the valve. The valve was near the end of its expected service life. | 127 | The asset was observed to be in poor condition. Heavy corrosion and deterioration was observed on the surface of the valve. The valve was near the end of its expected service life.
119 | The asset was observed to be in poor condition. Heavy corrosion and deterioration was observed on the surface of the valve. The valve was near the end of its expected service life. | 128 | The Forcemain was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken.
120 | The Forcemain was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken. | 129 | Poor | Corrosion and deterioration were observed on the surface of the pump. The pump is beyond the end of its expected service life
121 | The asset was observed to be in good condition. | 130 | Dust | Corrosion
122 | The asset was observed to be in fair condition. The pump was working but it was near the end of its expected service life. Pump testing was not undertaken as part of this assessment. he operator mentioned that one of pumps is electrically jumpered out. Th | 131 | The exhaust fan was missing | As per Section 7.2.9 of MOECC's Design Guidelines for Sewage Works, mechanical ventilation is required for below ground surface dry well.
123 | The asset was observed to be in poor condition. Heavy corrosion and deterioration was observed on the surface of the valve. The valve was near the end of its expected service life. | 132 | fair | Deterioration was observed on the surface of the pump and it is beyond the end of its expected service life.
124 | The asset was observed to be in poor condition. Heavy corrosion and deterioration was observed on the surface of the valve. The valve was near the end of its expected service life. | 133 | fair | Corrasion and deterioration was observed on the surface of the valve. The valve is beyond its expected service life.
125 | The asset was observed to be in fair condition. The pump was working but it was near the end of its expected service life. Pump testing was not undertaken as part of this assessment. he operator mentioned that one of pumps is electrically jumpered out. Th | 134 | fair | minor corrosion on casing
126 | The asset was observed to be in poor condition. Heavy corrosion and deterioration was observed on the surface of the valve. The valve was near the end of its expected service life. | 135 | fair | Corrosion and deterioration was observed on the surface of the valve. The valve is beyond its expected service life.
127 | The asset was observed to be in poor condition. Heavy corrosion and deterioration was observed on the surface of the valve. The valve was near the end of its expected service life. | 136 | fair | Corrosion and deterioration was observed on the surface of the valve. The valve is beyond its expected service life.
128 | The Forcemain was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken. | 137 | fair | Deterioration was observed on the surface of the pump and it is beyond the end of its expected service life.
129 | Poor | 138 | fair | Corrasion and deterioration was observed on the surface of the valve. The valve is beyond its expected service life.
129 | Corrosion and deterioration were observed on the surface of the pump. The pump is beyond the end of its expected service life | 139 | fair | minor corrosion on casing
130 | Dust | 140 | fair | Corrosion and deterioration was observed on the surface of the valve. The valve is beyond its expected service life.
130 | Corrosion | 141 | fair | Corrosion and deterioration was observed on the surface of the valve. The valve is beyond its expected service life.
131 | The exhaust fan was missing | 142 | assumed to be in good condition | The pipe is at half of its expected service life.
131 | As per Section 7.2.9 of MOECC's Design Guidelines for Sewage Works, mechanical ventilation is required for below ground surface dry well. | 143 | Poor | Severe corrosion and deterioration were observed on the surface of the pump. The pump was near the end of its expected service life.
132 | fair | 144 | good
132 | Deterioration was observed on the surface of the pump and it is beyond the end of its expected service life. | 145 | As per Section 7.2.9 of MOECC's Design Guidelines for Sewage Works, mechanical ventilation is required for below ground surface dry well.
133 | fair | 146 | Poor | Corrosion and deterioration was observed on the surface of the pump. The pump was near the end of its expected service life.
133 | Corrasion and deterioration was observed on the surface of the valve. The valve is beyond its expected service life. | 147 | Poor | Corrosion and deterioration was observed on the surface of the valve. The valve is near the end of its expected service life.
134 | fair | 148 | Fair | Minor surface corrosion
134 | minor corrosion on casing | 149 | Poor | Corrosion and deterioration was observed on the valve. The valve was near the end of its expected service life.
135 | fair | 150 | Poor | Corrosion and deterioration was observed on the valve. The valve was near the end of its expected service life.
135 | Corrosion and deterioration was observed on the surface of the valve. The valve is beyond its expected service life. | 151 | Poor | Corrosion and deterioration was observed on the surface of the pump. The pump was near the end of its expected service life.
136 | fair | 152 | Poor | Corrosion and deterioration was observed on the surface of the valve. The valve is near the end of its expected service life.
136 | Corrosion and deterioration was observed on the surface of the valve. The valve is beyond its expected service life. | 153 | Fair | Minor surface corrosion and paint wear
137 | fair | 154 | Poor | Corrosion and deterioration was observed on the valve. The valve was near the end of its expected service life.
137 | Deterioration was observed on the surface of the pump and it is beyond the end of its expected service life. | 155 | Poor | Corrosion and deterioration was observed on the valve. The valve was near the end of its expected service life.
138 | fair | 156 | Good
138 | Corrasion and deterioration was observed on the surface of the valve. The valve is beyond its expected service life. | 157 | Poor | Corrosion and deterioration was observed on the surface of the pump. The pump is beyond its expected service life.
139 | fair | 158 | Minor corrosion on nuts
139 | minor corrosion on casing | 159 | Surface corrosion
140 | fair | 160 | fair | Corrosion and deterioration was observed on the surface of the pump. The pump was beyond its expected service life.
140 | Corrosion and deterioration was observed on the surface of the valve. The valve is beyond its expected service life. | 161 | Poor | Moderate corrosion and deterioration was observed on the surface of the valve. The valve was beyond its expected service life.
141 | fair | 162 | fair | paint wear
141 | Corrosion and deterioration was observed on the surface of the valve. The valve is beyond its expected service life. | 163 | Poor | Corrosion and deterioration was observed on the surface of the valve.
142 | assumed to be in good condition | 164 | Poor | Corrosion and deterioration was observed on the surface of the valve.
142 | The pipe is at half of its expected service life. | 165 | Fair | Corrosion and deterioration was observed on the surface of the pump. The pump was beyond its expected service life.
143 | Poor | 166 | Poor | Corrosion and deterioration was observed on the surface of the pump. The pump was beyond its expected service life.
143 | Severe corrosion and deterioration were observed on the surface of the pump. The pump was near the end of its expected service life. | 167 | fair | paint wear
144 | good | 168 | Poor | Corrosion and deterioration was observed on the surface of the valve.
145 | As per Section 7.2.9 of MOECC's Design Guidelines for Sewage Works, mechanical ventilation is required for below ground surface dry well. | 169 | Poor | Corrosion and deterioration was observed on the surface of the valve.
146 | Poor | 170 | assumed to be good | The pipe was at half of its expected service life.
146 | Corrosion and deterioration was observed on the surface of the pump. The pump was near the end of its expected service life. | 171
147 | Poor | 172 | very good
147 | Corrosion and deterioration was observed on the surface of the valve. The valve is near the end of its expected service life. | 173
148 | Fair | 174 | fair | The pump was beyond its expected service life.
148 | Minor surface corrosion | 175 | Poor | Heavy corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
149 | Poor | 176
149 | Corrosion and deterioration was observed on the valve. The valve was near the end of its expected service life. | 177 | Poor | Heavy corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
150 | Poor | 178 | assumed to be fair | The pipe was at half of its expected service life
150 | Corrosion and deterioration was observed on the valve. The valve was near the end of its expected service life. | 179 | fair | Corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
151 | Poor | 180 | nuts were not secured properly | good
151 | Corrosion and deterioration was observed on the surface of the pump. The pump was near the end of its expected service life. | 181 | Paint peeling | fair
152 | Poor | 182 | Fair | Deterioration was observed on the surface of the pump. The pump was near the end of its expected service life.
152 | Corrosion and deterioration was observed on the surface of the valve. The valve is near the end of its expected service life. | 183 | Fair | Corrosion and deterioration was observed on the valve. The pump was near the end of its expected service life.
153 | Fair | 184 | fair | paint wear
153 | Minor surface corrosion and paint wear | 185 | Fair | Corrosion and deterioration was observed on the valve. The pump was near the end of its expected service life.
154 | Poor | 186 | Very Poor | Severe corrosion and deterioration was observed on the valve. The pump was near the end of its expected service life.
154 | Corrosion and deterioration was observed on the valve. The valve was near the end of its expected service life. | 187 | Fair | Deterioration was observed on the surface of the pump. The pump was near the end of its expected service life.
155 | Poor | 188 | fair | expected service life.
155 | Corrosion and deterioration was observed on the valve. The valve was near the end of its expected service life. | 189 | fair | paint wear
156 | Good | 190 | Fair | Corrosion and deterioration was observed on the valve. The pump was near the end of its expected service life.
157 | Poor | 191 | fair | Minor deterioration was observed on the surface of the valve. The valve was near the end of its expected service life.
157 | Corrosion and deterioration was observed on the surface of the pump. The pump is beyond its expected service life. | 192 | assumed to be good
158 | Minor corrosion on nuts | 193 | The asset was observed to be in fair condition. The PLC was obsolete.
159 | Surface corrosion | 194 | The asset was assumed to be in good condition based on its age. Pump testing was not undertaken as part of this assessment; however, no performance issues were identified by the operators.
159 |  | 195 | The asset was observed to be in fair condition. Moderate corrosion on the surface of the valve was observed.
160 | fair | 196 | The asset was observed to be in fair condition. Moderate corrosion on the surface of the valve was observed.
160 | Corrosion and deterioration was observed on the surface of the pump. The pump was beyond its expected service life. | 197 | The asset was observed to be in fair condition. Moderate corrosion on the surface of the valve was observed.
161 | Poor | 198 | The asset was assumed to be in good condition based on its age. Pump testing was not undertaken as part of this assessment; however, no performance issues were identified by the operators.
161 | Moderate corrosion and deterioration was observed on the surface of the valve. The valve was beyond its expected service life. | 199 | The asset was observed to be in fair condition. Moderate corrosion on the surface of the valve was observed.
162 | fair | 200 | The asset was observed to be in fair condition. Moderate corrosion on the surface of the valve was observed.
162 | paint wear | 201 | The asset was observed to be in fair condition. Heavy corrosion and deterioration were observed on the surface of the valve.
163 | Poor | 202 | The asset was observed to be in fair condition. Heavy corrosion and deterioration were observed on the surface of the valve.
163 | Corrosion and deterioration was observed on the surface of the valve. | 203 | The asset was observed to be in good condition.
164 | Poor | 204 | The asset was observed to be in good condition.
164 | Corrosion and deterioration was observed on the surface of the valve. | 205 | The asset was observed to be in good condition. The operator mentioned that overflow level head sometimes receives loss of echo. Further examination of the equipment and its associated equipment is required to investigate this issue.
165 | Fair | 206 | The asset was observed to be in good condition. It was identified by the operator that the level transmitter records erroneous readings. Overflow level head sometimes receives loss of echo. Further examination of the equipment and its associated equipment
165 | Corrosion and deterioration was observed on the surface of the pump. The pump was beyond its expected service life. | 207 | The Forcemain was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken.
166 | Poor | 208 | The asset was observed to be in fair condition. Surface corrosion was observed. The sump pump was beyond its expected service life.
166 | Corrosion and deterioration was observed on the surface of the pump. The pump was beyond its expected service life. | 209 | The asset was observed to be in fair condition. Corrosion was observed.
167 | fair | 210
167 | paint wear | 211 | The asset was missing. | As per Section 7.2.9 of MOECC's Design Guidelines for Sewage Works, mechanical ventilation is required for below ground surface dry well.
168 | Poor | 212 | The asset was observed to be in fair condition. Corrosion and deterioration were observed on the surface of the pump. The pump was original to the facility and had surpassed its expected service life. Pump testing was not undertaken as part of this assess
168 | Corrosion and deterioration was observed on the surface of the valve. | 213 | The asset was observed to be in fair condition. Corrosion and deterioration were observed on the surface of the valve. The valve was near the end of its expected service life.
169 | Poor | 214 | The asset was observed to be in fair condition. Corrosion and deterioration were observed on the surface of the motor. The motor was near the end of its expected service life.
169 | Corrosion and deterioration was observed on the surface of the valve. | 215 | The asset was observed to be in fair condition. Corrosion and deterioration were observed on the surface of the valve. The valve was near the end of its expected service life.
170 | assumed to be good | 216 | The asset was observed to be in fair condition. Corrosion and deterioration were observed on the surface of the valve. The valve was near the end of its expected service life.
170 | The pipe was at half of its expected service life. | 217 | The asset was observed to be in fair condition. Corrosion and deterioration were observed on the surface of the pump. The pump was original to the facility and had surpassed its expected service life. Pump testing was not undertaken as part of this assess
172 | very good | 218 | The asset was observed to be in fair condition. Corrosion and deterioration were observed on the surface of the valve. The valve was near the end of its expected service life.
174 | fair | 219 | The asset was observed to be in fair condition. Deterioration and corrosion were observed on the surface of the motor. The motor was beyond its expected service life.
174 | The pump was beyond its expected service life. | 220 | The asset was observed to be in fair condition. Corrosion and deterioration were observed on the surface of the valve. The valve was near the end of its expected service life.
175 | Poor | 221 | The asset was observed to be in fair condition. Corrosion and deterioration were observed on the surface of the valve. The valve was near the end of its expected service life.
175 | Heavy corrosion was observed on the surface of the pump. The pump was beyond its expected service life. | 222 | The Forcemain was assumed to be in good condition as no performance issues were identified. The pipe passed half of its expected service. Additionally, internal inspection of the piping was not undertaken to confirm its condition.
177 | Poor | 223 | The piping was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken.
177 | Heavy corrosion was observed on the surface of the pump. The pump was beyond its expected service life. | 224 | The piping was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken.
178 | assumed to be fair | 225 | The piping was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken.
178 | The pipe was at half of its expected service life | 226 | The asset was observed to be in poor condition. Heavy corrosion and deterioration were observed on the surface of the piping.
179 | fair | 227 | The asset was in poor condition. Heavy corrosion and deterioration was observed.
179 | Corrosion was observed on the surface of the pump. The pump was beyond its expected service life. | 228 | The asset was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken.
180 | nuts were not secured properly | 229 | Fair | The pipe was over half of its expected service life.
180 | good | 230 | The asset was observed to be in fair condition. Surface corrosion was observed. The pipe was over half of its expected service life. Additionally, internal inspection of the piping was not undertaken to confirm its condition.
181 | Paint peeling | 231
181 | fair | 232 | The asset was observed to be in fair condition. Surface corrosion was observed. The pipe was over half of its expected service life. Additionally, internal inspection of the piping was not undertaken to confirm its condition.
182 | Fair | 233 | The asset was assumed to be in good condition. The pipe was over half of its expected service life. Additionally, internal inspection of the piping was not undertaken to confirm its condition.
182 | Deterioration was observed on the surface of the pump. The pump was near the end of its expected service life. | 234 | The asset was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken.
183 | Fair | 235 | The asset was observed to be in poor condition. Heavy deterioration on the surface piping was observed.
183 | Corrosion and deterioration was observed on the valve. The pump was near the end of its expected service life. | 236 | The asset was observed to be in poor condition. Heavy deterioration on the surface piping was observed.
184 | fair | 237 | Fair | The pipe is at half of its expected service life.
184 | paint wear | 238 | Fair | The pipe is at half of its expected service life.
185 | Fair | 239 | Fair | The bar screen is at half of its expected service life.
185 | Corrosion and deterioration was observed on the valve. The pump was near the end of its expected service life. | 240 | Fair | The pipe is at half of its expected service life.
186 | Very Poor | 241 | Fair | The pipe is at half of its expected service life.
186 | Severe corrosion and deterioration was observed on the valve. The pump was near the end of its expected service life. | 242 | Good
187 | Fair | 243 | Fair | Minor corrosion
187 | Deterioration was observed on the surface of the pump. The pump was near the end of its expected service life. | 244 | fair | corrosion
188 | fair | 245
188 | expected service life. | 246
189 | fair | 247 | Good | The pipe was at half of its expected service life.
189 | paint wear | 248 | Fair | The pipe was at half of its expected service life.
190 | Fair | 249 | good
190 | Corrosion and deterioration was observed on the valve. The pump was near the end of its expected service life. | 250 | Good
191 | fair | 251 | Assumed to be fair | The pipe was at half of its expected service life
191 | Minor deterioration was observed on the surface of the valve. The valve was near the end of its expected service life. | 252 | Poor | Heavy corrosion was observed on the surface of the pipe
192 | assumed to be good | 253 | Poor | Heavy corrosion was observed on the surface of the pipe
193 | The asset was observed to be in fair condition. The PLC was obsolete. | 254 | Good
194 | The asset was assumed to be in good condition based on its age. Pump testing was not undertaken as part of this assessment; however, no performance issues were identified by the operators. | 255
195 | The asset was observed to be in fair condition. Moderate corrosion on the surface of the valve was observed. | 256 | Good
196 | The asset was observed to be in fair condition. Moderate corrosion on the surface of the valve was observed. | 257 | Good
197 | The asset was observed to be in fair condition. Moderate corrosion on the surface of the valve was observed. | 258 | Good
198 | The asset was assumed to be in good condition based on its age. Pump testing was not undertaken as part of this assessment; however, no performance issues were identified by the operators. | 259 | Fair | The pipe was at half of its expected service life.
199 | The asset was observed to be in fair condition. Moderate corrosion on the surface of the valve was observed. | 260 | Poor | Heavy corrosion was observed on the pipe
200 | The asset was observed to be in fair condition. Moderate corrosion on the surface of the valve was observed. | 261 | Poor | Heavy corrosion was observed on the pipe
201 | The asset was observed to be in fair condition. Heavy corrosion and deterioration were observed on the surface of the valve. | 262 | fair | The pipe passed half of its expected service life.
202 | The asset was observed to be in fair condition. Heavy corrosion and deterioration were observed on the surface of the valve. | 263 | Fair | Minor deterioration was observed on the pipe and it passed half of its expected service life.
203 | The asset was observed to be in good condition. | 264 | Fair | Minor deterioration was observed on the pipe and it passed half of its expected service life.
204 | The asset was observed to be in good condition. | 265 | Fair | Minor deterioration was observed on the pipe and it passed half of its expected service life.
205 | The asset was observed to be in good condition. The operator mentioned that overflow level head sometimes receives loss of echo. Further examination of the equipment and its associated equipment is required to investigate this issue. | 266 | assumed to be good
206 | The asset was observed to be in good condition. It was identified by the operator that the level transmitter records erroneous readings. Overflow level head sometimes receives loss of echo. Further examination of the equipment and its associated equipment | 267 | Poor | Heavy corrosion and deterioration was observed
207 | The Forcemain was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken. | 268 | Poor | Heavy corrosion and deterioration was observed
208 | The asset was observed to be in fair condition. Surface corrosion was observed. The sump pump was beyond its expected service life. | 269 | The asset was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken.
209 | The asset was observed to be in fair condition. Corrosion was observed. | 270 | The asset was observed to be in fair condition. Moderate corrosion on the surface of the pipe was observed.
211 | The asset was missing. | 271 | The asset was observed to be in poor condition. Heavy corrosion on the surface of the valve was observed.
211 | As per Section 7.2.9 of MOECC's Design Guidelines for Sewage Works, mechanical ventilation is required for below ground surface dry well. | 272 | The asset was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken.
212 | The asset was observed to be in fair condition. Corrosion and deterioration were observed on the surface of the pump. The pump was original to the facility and had surpassed its expected service life. Pump testing was not undertaken as part of this assess | 273 | The asset was observed to be in fair condition. Minor surface corrosion and deterioration was noted. However, internal inspection of the piping was not undertaken.
213 | The asset was observed to be in fair condition. Corrosion and deterioration were observed on the surface of the valve. The valve was near the end of its expected service life. | 274 | The asset was observed to be in fair condition. Moderate surface corrosion was observed.
214 | The asset was observed to be in fair condition. Corrosion and deterioration were observed on the surface of the motor. The motor was near the end of its expected service life. | 275 | The asset was in good condition.
215 | The asset was observed to be in fair condition. Corrosion and deterioration were observed on the surface of the valve. The valve was near the end of its expected service life. | 276 | The asset was in fair condition. Weathered paint and minor corrosion was observed.
216 | The asset was observed to be in fair condition. Corrosion and deterioration were observed on the surface of the valve. The valve was near the end of its expected service life. | 277 | The asset was in fair condition. Corrosion and pitting noted.
217 | The asset was observed to be in fair condition. Corrosion and deterioration were observed on the surface of the pump. The pump was original to the facility and had surpassed its expected service life. Pump testing was not undertaken as part of this assess | 278 | The asset was in fair condition. Corrosion was noted
218 | The asset was observed to be in fair condition. Corrosion and deterioration were observed on the surface of the valve. The valve was near the end of its expected service life. | 279 | Fair | Surface corrosion on underside
219 | The asset was observed to be in fair condition. Deterioration and corrosion were observed on the surface of the motor. The motor was beyond its expected service life. | 280 | The asset was in fair condition. Surface corrosion on underside was observed.
220 | The asset was observed to be in fair condition. Corrosion and deterioration were observed on the surface of the valve. The valve was near the end of its expected service life. | 281 | The asset was in fair condition. The paint at some locations was missing and corrosion was noted.
221 | The asset was observed to be in fair condition. Corrosion and deterioration were observed on the surface of the valve. The valve was near the end of its expected service life. | 282 | The asset was observed to be in good condition.
222 | The Forcemain was assumed to be in good condition as no performance issues were identified. The pipe passed half of its expected service. Additionally, internal inspection of the piping was not undertaken to confirm its condition. | 283 | The hatch was missing grating. Under Ontario Regulation 213/91 this presents a fall hazard when the hatches are left open. | The asset was observed to be in poor condition. The grating was missing.
223 | The piping was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken. | 284 | The hatch was missing grating. Under Ontario Regulation 213/91 this presents a fall hazard when the hatches are left open. | The asset was observed to be in poor condition as it was missing hatch grating.
224 | The piping was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken. | 285 | The asset was observed to be in good condition.
225 | The piping was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken. | 286 | The asset was observed to be in good condition.
226 | The asset was observed to be in poor condition. Heavy corrosion and deterioration were observed on the surface of the piping. | 287 | The asset was observed to be in fair condition. Corrosion on the platform was observed.
227 | The asset was in poor condition. Heavy corrosion and deterioration was observed. | 288 | The asset was observed to be in fair condition. Corrosion was observed.
228 | The asset was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken. | 289 | The asset was observed to be in fair condition. Brick riser supporting manhole frame was loose.
229 | Fair | 290 | The asset was observed to be in good condition.
229 | The pipe was over half of its expected service life. | 291 | The asset was observed to be in fair condition. Corrosion was observed on top surface.
230 | The asset was observed to be in fair condition. Surface corrosion was observed. The pipe was over half of its expected service life. Additionally, internal inspection of the piping was not undertaken to confirm its condition. | 292 | The asset was observed to be in fair condition. Peeling paint was observed.
232 | The asset was observed to be in fair condition. Surface corrosion was observed. The pipe was over half of its expected service life. Additionally, internal inspection of the piping was not undertaken to confirm its condition. | 293 | The ladder was missing a rung at platform level. Under Ontario Regulation 213/91 this presents a fall hazard. | The asset was observed to be in poor condition as it was missing a rung at platform level.
233 | The asset was assumed to be in good condition. The pipe was over half of its expected service life. Additionally, internal inspection of the piping was not undertaken to confirm its condition. | 294 | The asset was observed to be in fair condition. Surface corrosion on underside was observed.
234 | The asset was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken. | 295 | The asset was observed to be in good condition.
235 | The asset was observed to be in poor condition. Heavy deterioration on the surface piping was observed. | 296 | The asset was observed to be in fair condition. Corrosion was observed.
236 | The asset was observed to be in poor condition. Heavy deterioration on the surface piping was observed. | 297 | The asset was observed to be in good condition.
237 | Fair | 298 | The asset was observed to be in fair condition. The hatch was missing a safety grating. | The Pump Hatch was missing grating. Under Ontario Regulation 213/91 this presents a fall hazard when the hatches are left open.
237 | The pipe is at half of its expected service life. | 299 | The asset was observed to be in good condition.
238 | Fair | 300 | The grating in the wet well was not clipped. | The asset was observed to be in fair condition. The grating in the wet well was not clipped.
238 | The pipe is at half of its expected service life. | 301 | Rust spots noted | Fair
239 | Fair | 302 | Fair | minor corrosion and paint wear
239 | The bar screen is at half of its expected service life. | 303 | fair | minor paint wear
240 | Fair | 304 | Peeling paint on exterior | Fair
240 | The pipe is at half of its expected service life. | 305 | Fair | minor corrosion on the underside
241 | Fair | 306 | good
241 | The pipe is at half of its expected service life. | 307 | Corrosion noted | Fair
242 | Good | 308 | Corrosion noted | Fair
243 | Fair | 309 | Fair | To be inspected yearly | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
243 | Minor corrosion | 310 | The asset was observed to be in fair condition. It is recommended to be inspected yearly. | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
244 | fair | 311 | The asset was observed to be in good condition.
244 | corrosion | 312 | The asset was observed to be in fair condition. It is recommended to inspect the asset yearly. | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
247 | Good | 313 | The asset was observed to be in fair condition. It is recommended to inspect the asset yearly. | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
247 | The pipe was at half of its expected service life. | 314 | The asset was observed to be in fair condition. The grab bar was loose. | The Grab Bar was loose. Under Ontario Regulation 213/91 this presents a fall hazard.
248 | Fair | 315 | The asset was in fair condition. It is unknown when the equipment was last inspected. | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
248 | The pipe was at half of its expected service life. | 316 | Fair | To be inspected yearly
249 | good | 317 | Fair | Minor corrosion and paint wear
250 | Good | 318 | Fair | paint wear
251 | Assumed to be fair | 319 | Fair | To be inspected every year | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
251 | The pipe was at half of its expected service life | 320 | Surface corrosion noted on underside | Fair
252 | Poor | 321 | Fair | To be inspected every year | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
252 | Heavy corrosion was observed on the surface of the pipe | 322 | Bent ladder rung | Fair
253 | Poor | 323 | Corrosion noted | Fair
253 | Heavy corrosion was observed on the surface of the pipe | 324 | Weathered paint on exterior and minor corrosion inside | Fair
254 | Good | 325 | good
256 | Good | 326 | Fair | discoloration of the checker plate
257 | Good | 327 | good
258 | Good | 328 | Fair | weathered paint
259 | Fair | 329 | Fair | Minor corrosion
259 | The pipe was at half of its expected service life. | 330 | Fair based on age
260 | Poor | 331 | Peeling paint on exterior and corrosion | Fair
260 | Heavy corrosion was observed on the pipe | 332 | Fair | To be inspected every year | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
261 | Poor | 333 | good
261 | Heavy corrosion was observed on the pipe | 334 | Staining/corrosion noted | Fair
262 | fair | 335 | Fair | Minor corrosion
262 | The pipe passed half of its expected service life. | 336 | Fair | minor corrosion
263 | Fair | 337 | To be inspected every year. As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year. | Fair
263 | Minor deterioration was observed on the pipe and it passed half of its expected service life. | 338 | Fair
264 | Fair | 339 | Fixed portion of platform grating was noted to be bent | Fair
264 | Minor deterioration was observed on the pipe and it passed half of its expected service life. | 340 | Fair
265 | Fair | 341 | To be inspected every year. As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year. | Fair
265 | Minor deterioration was observed on the pipe and it passed half of its expected service life. | 342 | Fair | corrosion and paint wear
266 | assumed to be good | 343 | Fair | Minor corrosion
267 | Poor | 344 | Flaking/missing on exterior | Fair
267 | Heavy corrosion and deterioration was observed | 345 | Fair | To be inspected every year. As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
268 | Poor | 346 | Good
268 | Heavy corrosion and deterioration was observed | 347 | Pitting noted | Fair
269 | The asset was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken. | 348 | Fair | To be inspected yearly. As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
270 | The asset was observed to be in fair condition. Moderate corrosion on the surface of the pipe was observed. | 349 | Calcium buildup and pitting noted | fair
271 | The asset was observed to be in poor condition. Heavy corrosion on the surface of the valve was observed. | 350 | Fair | paint wear
272 | The asset was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken. | 351 | Fair | minor corrosion
273 | The asset was observed to be in fair condition. Minor surface corrosion and deterioration was noted. However, internal inspection of the piping was not undertaken. | 352 | Fair
274 | The asset was observed to be in fair condition. Moderate surface corrosion was observed. | 353 | Fair | Weathered paint and missing paint on exterior
275 | The asset was in good condition. | 354 | Fair
276 | The asset was in fair condition. Weathered paint and minor corrosion was observed. | 355 | Fair
277 | The asset was in fair condition. Corrosion and pitting noted. | 356 | Fair | Anchors were corroded
278 | The asset was in fair condition. Corrosion was noted | 357 | Fair | minor corrosion and staining
279 | Fair | 358 | Fair | Missing safety grating. The Pump Hatch 1 was missing grating. Under Ontario Regulation 213/91 this presents a fall hazard when the hatches are left open.
279 | Surface corrosion on underside | 359 | Fair | Missing safety grating. The Pump Hatch 1 was missing grating. Under Ontario Regulation 213/91 this presents a fall hazard when the hatches are left open.
280 | The asset was in fair condition. Surface corrosion on underside was observed. | 360 | Calcium buildup and corrosion noted | Fair
281 | The asset was in fair condition. The paint at some locations was missing and corrosion was noted. | 361 | Calcium buildup and corrosion noted | Fair
282 | The asset was observed to be in good condition. | 362 | Gratings now clipped down | Corrosion noted | Fair
283 | The hatch was missing grating. Under Ontario Regulation 213/91 this presents a fall hazard when the hatches are left open. | 363 | Fair | To be inspected every year. As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
283 | The asset was observed to be in poor condition. The grating was missing. | 364 | The asset was observed to be in fair condition. Minor corrosion was observed.
284 | The hatch was missing grating. Under Ontario Regulation 213/91 this presents a fall hazard when the hatches are left open. | 365 | The asset was observed to be in fair condition. Minor corrosion was observed.
284 | The asset was observed to be in poor condition as it was missing hatch grating. | 366 | The asset was observed to be in fair condition. Weathered paint on the exterior was observed.
285 | The asset was observed to be in good condition. | 367 | The asset was observed to be in fair condition. Minor corrosion was observed.
286 | The asset was observed to be in good condition. | 368 | The asset was observed to be in fair condition. Surface corrosion was observed.
286 |  | 369 | The asset was observed to be in fair condition. Surface corrosion was noted.
287 | The asset was observed to be in fair condition. Corrosion on the platform was observed. | 370 | The asset was observed to be in fair condition. It is recommended to be inspected every year. | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
288 | The asset was observed to be in fair condition. Corrosion was observed. | 371 | The asset was observed to be in fair condition. Hatch was hard to open due to corrosion on latch.
289 | The asset was observed to be in fair condition. Brick riser supporting manhole frame was loose. | 372 | The asset was observed to be in good condition.
290 | The asset was observed to be in good condition. | 373 | The asset was observed to be in good condition.
291 | The asset was observed to be in fair condition. Corrosion was observed on top surface. | 374 | The asset was observed to be in fair condition. Calcium buildup was observed.
292 | The asset was observed to be in fair condition. Peeling paint was observed. | 375 | The asset was observed to be in fair condition. Calcium buildup was observed.
293 | The ladder was missing a rung at platform level. Under Ontario Regulation 213/91 this presents a fall hazard. | 376 | The asset was observed to be in fair condition. Calcium buildup noted
293 | The asset was observed to be in poor condition as it was missing a rung at platform level. | 377 | The asset was observed to be in fair condition. Calcium buildup noted
294 | The asset was observed to be in fair condition. Surface corrosion on underside was observed. | 378 | The asset was observed to be in good condition.
295 | The asset was observed to be in good condition. | 379 | The asset was observed to be in good condition. It is unknown when the equipment was last inspected. | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
296 | The asset was observed to be in fair condition. Corrosion was observed. | 380 | The asset was observed to be in good condition.
297 | The asset was observed to be in good condition. | 381 | The asset was assumed to be good as no settlement was observed.
298 | The asset was observed to be in fair condition. The hatch was missing a safety grating. | 382 | Not visible/inspected. Assumed to be good as no settlement was noted. | Good
298 | The Pump Hatch was missing grating. Under Ontario Regulation 213/91 this presents a fall hazard when the hatches are left open. | 383 | Not visible/inspected. Assumed to be good as no settlement was noted.
299 | The asset was observed to be in good condition. | 384 | Not visible/inspected. Assumed to be good as no settlement was noted.
300 | The grating in the wet well was not clipped. | 385 | Not visible/inspected. Assumed to be good as no settlement was noted
300 | The asset was observed to be in fair condition. The grating in the wet well was not clipped. | 386 | The asset was observed to be in fair condition. Surface corrosion on underside was observed.
301 | Rust spots noted | 387 | Good
301 | Fair | 388 | The asset was observed to be in poor condition. Heavy corrosion and deterioration was observed on the service of the valve. The valve was near the end of its expected service life.
302 | Fair | 389 | The asset was observed to be in fair condition. Surface corrosion was observed.
302 | minor corrosion and paint wear | 390 | Poor | The pump was beyond its expected service life
303 | fair | 391 | Very Poor | Severe corrosion was observed on the surface of the valve. The valve was beyond its expected service life.
303 | minor paint wear | 392 | Very Poor | Severe corrosion was observed on the surface of the valve. The valve was beyond its expected service life
304 | Peeling paint on exterior | 393 | Poor | The pump was beyond its expected service life.
304 | Fair | 394 | Very Poor | Severe corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
305 | Fair | 395 | Very Poor | Severe corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
305 | minor corrosion on the underside | 396 | Fair | Minor deterioration was observed on the bar screen.
306 | good | 397 | Poor | The pump was beyond its expected service life.
307 | Corrosion noted | 398 | The asset was observed to be in fair condition. The screen was beyond its expected service life.
307 | Fair | 399 | poor | The pump was beyond its expected service life
308 | Corrosion noted | 400 | Poor | Severe corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
308 | Fair | 401
309 | Fair | 402 | Poor | Heavy corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
309 | To be inspected yearly | 403 | Very Poor | Severe corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
309 | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year. | 404 | Fair | Debris is clogging at the bar screen, which in terms start clogging the inlet pipe.
310 | The asset was observed to be in fair condition. It is recommended to be inspected yearly. | 405 | Poor | Corrosion and deterioration was observed on the surface of the valve. The valve was near the end of its expected service life.
310 | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year. | 406 | Poor | Corrosion and deterioration was observed on the surface of the valve
311 | The asset was observed to be in good condition. | 407
312 | The asset was observed to be in fair condition. It is recommended to inspect the asset yearly. | 408 | The asset was observed to be in good condition.
312 | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year. | 409 | The asset was in good condition.
313 | The asset was observed to be in fair condition. It is recommended to inspect the asset yearly. | 410 | The asset was in good condition.
313 | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year. | 411 | The asset was in good condition.
314 | The asset was observed to be in fair condition. The grab bar was loose. | 412 | The asset was observed to be in fair condition. Corrosion was observed.
314 | The Grab Bar was loose. Under Ontario Regulation 213/91 this presents a fall hazard. | 413
315 | The asset was in fair condition. It is unknown when the equipment was last inspected. | 414 | The asset was observed to be in fair condition. It is approaching the end of its service life and should be replaced.
315 | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year. | 415 | The asset was observed to be in fair condition. Corrosion was observed.
316 | Fair | 416 | The asset was observed to be in good condition.
316 | To be inspected yearly | 417 | The asset was observed to be in good condition.
317 | Fair | 418 | The asset was observed to be in good condition.
317 | Minor corrosion and paint wear | 419 | The asset was observed to be in fair condition.
318 | Fair | 420 | obsolete | minor corrosion
318 | paint wear | 421 | Obsolete | Corrosion
319 | Fair | 422 | good | obsolete
319 | To be inspected every year | 423 | good
319 | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year. | 424 | Dust | good
320 | Surface corrosion noted on underside | 425 | good | Corrosion
320 | Fair | 426 | good | Corrosion
321 | Fair | 427 | good | Corrosion
321 | To be inspected every year | 428 | minor Corrosion
321 | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year. | 429 | good
322 | Bent ladder rung | 430 | good
322 | Fair | 431 | good
323 | Corrosion noted | 432 | good
323 | Fair | 433 | very good
324 | Weathered paint on exterior and minor corrosion inside | 434 | good
324 | Fair | 435 | good | obsolete
325 | good | 436 | good
325 |  | 437 | good
326 | Fair | 438 | good
326 | discoloration of the checker plate | 439 | Good
327 | good | 440 | good
328 | Fair | 441 | good
328 | weathered paint | 442 | good
329 | Fair | 443 | good
329 | Minor corrosion | 444 | good
330 | Fair based on age | 445 | good
331 | Peeling paint on exterior and corrosion | 446 | good | bolts were not secured properly
331 | Fair | 447 | good
332 | Fair | 448 | good
332 | To be inspected every year | 449 | The asset was observed to be in good condition.
332 | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year. | 450 | The asset was observed to be in good condition.
333 | good | 451 | The asset was observed to be in good condition.
334 | Staining/corrosion noted | 452 | The asset was observed to be in good condition.
334 | Fair | 453 | The asset was observed to be in good condition.
335 | Fair | 454 | The asset was observed to be in good condition.
335 | Minor corrosion | 455 | The asset was observed to be in good condition.
336 | Fair | 456 | The asset was observed to be in good condition.
336 | minor corrosion | 457 | The asset was in fair condition. Surface corrosion was observed.
337 | To be inspected every year. As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year. | 458 | The asset was observed to be in good condition. | Shock and arc flash hazard as the existing arc flash label is outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreover, the studies and reports
337 | Fair | 459 | The asset was observed to be in good condition.
338 | Fair | 460 | The asset was observed to be in good condition.
339 | Fixed portion of platform grating was noted to be bent | 461 | The asset was observed to be in good condition. | Shock and arc flash hazard as the existing arc flash label is outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreover, the studies and reports
339 | Fair | 462 | The asset was observed to be in good condition. | Shock and arc flash hazard as the existing arc flash label is outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreover, the studies and reports
340 | Fair | 463 | The asset was observed to be in good condition. | Shock and arc flash hazard as the existing arc flash label is outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreover, the studies and reports
341 | To be inspected every year. As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year. | 464 | The asset was observed to be in good condition.
341 | Fair | 465 | The asset was observed to be in fair condition. Corrosion on fixtures was observed. The lighting should be replaced with LED in next upgrade
342 | Fair | 466 | The asset was in fair condition. Corrosion on the surface of the panels as well as circuit breakers was observed. The panel is to be replaced with NEMA 4X enclosure | Shock and arc flash hazard as the existing arc flash label is outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreover, the studies and reports
342 | corrosion and paint wear | 467 | The asset was observed to be in poor condition. Heavy corrosion was observed.
343 | Fair | 468 | The asset was observed to be in good condition. To be replaced with led in next upgrade.
343 | Minor corrosion | 469 | The asset was observed to be in fair condition. Bottom of the enclosure was heavily corroded and should be replaced with NEMA 3R enclosure.
344 | Flaking/missing on exterior | 470 | The asset was observed to be in good condition. However, the availability of parts and increased maintenance cost will be an issue. It is recommended to replace the pump control within the 10-year plan. Additionally, the Phase converters inside panel shou
344 | Fair | 471 | The asset was observed to be in good condition. However, the availability of parts and increased maintenance cost will be an issue. It is recommended to replace the control panel within the 10-year plan. | Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servicing, or maintenance while
345 | Fair | 472 | The asset was observed to be in good condition. However, the availability of parts and increased maintenance cost will be an issue. It is recommended to replace the receptacle within the 10-year plan.
345 | To be inspected every year. As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year. | 473 | The asset was observed to be in good condition.
345 |  | 474 | The asset was observed to be in good condition. However, the availability of parts and increased maintenance cost will be an issue. It is recommended to replace the main breaker within the 10-year plan. | Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the main breaker which may require examination, adjustment, servicing, or maintenance
346 | Good | 475 | The asset was observed to be in good condition. However, the availability of parts and increased maintenance cost will be an issue. It is recommended to replace the transfer switch within the 10-year plan. | Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the manual transfer switch which may require examination, adjustment, servicing, or ma
347 | Pitting noted | 476 | The asset was observed to be in good condition. However, in order to provide accessibility to hydro personnel, it is recommended to move the meter above ground.
347 | Fair | 477 | The asset was observed to be in good condition. Replace with LED fixture in next upgrade.
348 | Fair | 478 | The asset was observed to be in fair condition. The model has been discontinued. | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the breaker which may require examination, adjustment, servicing, or maintenance while
348 | To be inspected yearly. As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year. | 479 | The asset was observed to be in good condition. The model has been discontinued.
349 | Calcium buildup and pitting noted | 480 | The asset was observed to be in good condition. The model has been discontinued.
349 | fair | 481 | The asset was observed to be in fair condition. Corrosion was observed inside and on surface of the panel. It was missing arc flash labels. | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servicing, or maintenance while e
350 | Fair | 482 | The asset was observed to be in good condition.
350 | paint wear | 483 | The asset was observed to be in fair condition. The panel was corroded.
351 | Fair | 484 | The asset was observed to be in good condition. However, availability of spare parts and increased maintenance cost will be an issue. It is therefore recommended to replace the asset in the next 10-years. | Shock and arc flash hazard as the existing arc flash label is outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreover, the studies and reports
351 | minor corrosion | 485 | good
352 | Fair | 486 | good
352 |  | 487 | good
353 | Fair | 488 | good
353 | Weathered paint and missing paint on exterior | 489 | good | replace with LED fixtures rated for class 1, div 2
354 | Fair | 490 | good | inside the panel is not getting drained properly
355 | Fair | 491 | fair | replace with NEMA 4X panel
356 | Fair | 492 | good
356 | Anchors were corroded | 493 | good | missing arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servicin
357 | Fair | 494 | good
357 | minor corrosion and staining | 495 | good | missing arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the receptacle which may require examination, adjustment, ser
358 | Fair | 496 | good | replace with LED in next upgrade
358 | Missing safety grating. The Pump Hatch 1 was missing grating. Under Ontario Regulation 213/91 this presents a fall hazard when the hatches are left open. | 497 | fair | misplaced arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servic | Pump #1 breaker to be sized and replaced according to OESC-2018
359 | Fair | 498 | good
359 | Missing safety grating. The Pump Hatch 1 was missing grating. Under Ontario Regulation 213/91 this presents a fall hazard when the hatches are left open. | 499 | fair | bottom of interior has corroded | replace with NEMA 3R enclosure in next upgrade
360 | Calcium buildup and corrosion noted | 500 | good | missing arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servicin
360 | Fair | 501 | good
361 | Calcium buildup and corrosion noted | 502 | good | missing arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servicin
361 | Fair | 503 | good | fair | replace with LED fixture in next upgrade. To be rated for class 1, div 2
362 | Gratings now clipped down | 504 | fair | bottom of interior was corroded | missing arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servicin
362 | Corrosion noted | 505 | fair | top surface and doors were corroded | to be replaced with NEMA 3R enclosure
362 | Fair | 506 | good | outdated arc flash label. Shock and arc flash hazard as the existing arc flash label are outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreove
363 | Fair | 507 | good
363 | To be inspected every year. As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year. | 508 | good
364 | The asset was observed to be in fair condition. Minor corrosion was observed. | 509 | good
365 | The asset was observed to be in fair condition. Minor corrosion was observed. | 510 | good | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the switch which may require examination, adjustment, servicing, or maintenance while
366 | The asset was observed to be in fair condition. Weathered paint on the exterior was observed. | 511 | poor | severely corroded
367 | The asset was observed to be in fair condition. Minor corrosion was observed. | 512 | good
368 | The asset was observed to be in fair condition. Surface corrosion was observed. | 513 | good | misplaced and outdated arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the VFD breaker which may require examination,
369 | The asset was observed to be in fair condition. Surface corrosion was noted. | 514 | good
370 | The asset was observed to be in fair condition. It is recommended to be inspected every year. | 515 | good | misplaced and outdated arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the VFD breaker which may require examination,
370 | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year. | 516 | good | misplaced and outdated arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the VFD breaker which may require examination,
371 | The asset was observed to be in fair condition. Hatch was hard to open due to corrosion on latch. | 517 | good
372 | The asset was observed to be in good condition. | 518 | good | replace with LED in next upgrade
373 | The asset was observed to be in good condition. | 519 | fair | to be replaced with LED
374 | The asset was observed to be in fair condition. Calcium buildup was observed. | 520 | fair | to be replaced with LED
375 | The asset was observed to be in fair condition. Calcium buildup was observed. | 521 | good
376 | The asset was observed to be in fair condition. Calcium buildup noted | 522 | fair | to have separate Main DS, MTS, and CP | outdated arc flash label. Shock and arc flash hazard as the existing arc flash label are outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreove
377 | The asset was observed to be in fair condition. Calcium buildup noted | 523 | fair
378 | The asset was observed to be in good condition. | 524 | good
379 | The asset was observed to be in good condition. It is unknown when the equipment was last inspected. | 525 | good
379 | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year. | 526 | good
380 | The asset was observed to be in good condition. | 527 | good
381 | The asset was assumed to be good as no settlement was observed. | 528 | good | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the control panel which may require examination, adjustment, servicing, or maintenance
382 | Not visible/inspected. Assumed to be good as no settlement was noted. | 529 | good | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the control panel which may require examination, adjustment, servicing, or maintenance
382 | Good | 530 | good
383 | Not visible/inspected. Assumed to be good as no settlement was noted. | 531 | fair | one of the lights doesn’t work | to be replaced with LED
384 | Not visible/inspected. Assumed to be good as no settlement was noted. | 532 | fair | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servicing, or maintenance while e
385 | Not visible/inspected. Assumed to be good as no settlement was noted | 533 | fair | it doesn't work
386 | The asset was observed to be in fair condition. Surface corrosion on underside was observed. | 534 | fair | to be replaced with LED
387 | Good | 535 | fair | to be replaced with NEMA 3R enclosure
388 | The asset was observed to be in poor condition. Heavy corrosion and deterioration was observed on the service of the valve. The valve was near the end of its expected service life. | 536 | good
389 | The asset was observed to be in fair condition. Surface corrosion was observed. | 537 | good
390 | Poor | 538 | good
390 | The pump was beyond its expected service life | 539 | good | replace with separate main DS, MTS and CP | Shock and arc flash hazard as the existing arc flash label are outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreover, the studies and reports
391 | Very Poor | 540 | good
391 | Severe corrosion was observed on the surface of the valve. The valve was beyond its expected service life. | 541 | The asset was observed to be in good condition. | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the MTS which may require examination, adjustment, servicing, or maintenance while ene
392 | Very Poor | 542 | The asset was observed to be in good condition.
392 | Severe corrosion was observed on the surface of the valve. The valve was beyond its expected service life | 543 | The asset was observed to be in good condition. | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the MTS which may require examination, adjustment, servicing, or maintenance while ene
393 | Poor | 544 | The asset was observed to be in good condition.
393 | The pump was beyond its expected service life. | 545 | The asset was observed to be in fair condition. It is recommended to replace with led fixtures rated for class 1, div 2.
394 | Very Poor | 546 | The asset was observed to be in fair condition. The panel was aged and minor surface corrosion was observed. | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2. Arc Flash label is required for the panel which may require examination, adjustment, servicing, or maintenance while
394 | Severe corrosion was observed on the surface of the pump. The pump was beyond its expected service life. | 547 | The asset was observed to be in fair condition. The top of the panel was damaged. Some repair work was completed to cover the damaged spots; however, it appears that the damaged spots were not sealed properly.
395 | Very Poor | 548 | The asset was observed to be in good condition.
395 | Severe corrosion was observed on the surface of the pump. The pump was beyond its expected service life. | 549 | The asset was observed to be in good condition. | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the control panel which may require examination, adjustment, servicing, or maintenance
396 | Fair | 550 | The asset was observed to be in good condition. | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the lighting panel which may require examination, adjustment, servicing, or maintenanc
396 | Minor deterioration was observed on the bar screen. | 551 | The asset was observed to be in good condition. Replace with VFD in next upgrade. | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the pump capacitors which may require examination, adjustment, servicing, or maintenan
397 | Poor | 552 | The asset was observed to be in good condition. | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the main breaker which may require examination, adjustment, servicing, or maintenance
397 | The pump was beyond its expected service life. | 553 | The asset was observed to be in good condition.
398 | The asset was observed to be in fair condition. The screen was beyond its expected service life. | 554 | The asset was observed to be in good condition. | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the switch which may require examination, adjustment, servicing, or maintenance while
399 | poor | 555 | The asset was observed to be in good condition.
399 | The pump was beyond its expected service life | 556 | The asset was observed to be in good condition.
400 | Poor | 557 | The asset was observed to be in good condition.
400 | Severe corrosion was observed on the surface of the pump. The pump was beyond its expected service life. | 558 | There was no manual transfer station installed at the station. It is recommended to install the manual transfer switch to ensure the station is being powered by one power source (either hydro or generator). Additionally, the MTS provides a safe mean to sw
402 | Poor | 559 | There was no Generator Connection Receptacle and Manual Transfer Switch located on site. It is recommended to install Generator Connection Receptacle as hardwiring the generator for emergency power parallel power source may cause a severe electrical shoc | Paralleling power sources and severe electrical shock hazard while hardwiring the generator for emergency power
402 | Heavy corrosion was observed on the surface of the pump. The pump was beyond its expected service life. | 560 | There was no main fused disconnect switch installed at the station. It is recommended to install the main disconnect switch to allow operators to safely isolate the station from hydro to install, maintain and repair any electrical equipment (electrical, m
403 | Very Poor | 561 | There was no Power meter installed on site. It is recommended to install a power meter to measure and display power consumption of the station. The power meter should be instated above ground for ease of operation/access and compatibility with industry’s
403 | Severe corrosion was observed on the surface of the pump. The pump was beyond its expected service life. | 562 | There was no manual transfer station installed at the station. It is recommended to install the manual transfer switch to ensure the station is being powered by one power source (either hydro or generator). Additionally, the MTS provides a safe mean to sw
404 | Fair | 563 | There was no main fused disconnect switch installed at the station. It is recommended to install the main disconnect switch to allow operators to safely isolate the station from hydro to install, maintain and repair any electrical equipment (electrical, m
404 | Debris is clogging at the bar screen, which in terms start clogging the inlet pipe. | 564 | There was no Generator Connection Receptacle and Manual Transfer Switch located on site. It is recommended to install Generator Connection Receptacle as hardwiring the generator for emergency power parallel power source may cause a severe electrical shoc | Paralleling power sources and severe electrical shock hazard while hardwiring the generator for emergency power. It is recommended to install generator receptacle above ground to comply with industry practice
405 | Poor | 565 | The asset was in fair condition. Moderate corrosion was observed.
405 | Corrosion and deterioration was observed on the surface of the valve. The valve was near the end of its expected service life. | 566 | The asset was in good condition
406 | Poor | 567 | The asset was in good condition overall. Paint peeling was observed.
406 | Corrosion and deterioration was observed on the surface of the valve | 568
408 | The asset was observed to be in good condition. | 569 | The vent piping was in fair condition. Paint peeling at the portion above the wet well was observed.
409 | The asset was in good condition. | 570 | The asset was observed to be in good condition.
410 | The asset was in good condition. | 571
411 | The asset was in good condition. | 572 | The asset was observed to be in good condition.
412 | The asset was observed to be in fair condition. Corrosion was observed. | 573 | The asset was observed to be in fair condition. Paint peeling was observed.
414 | The asset was observed to be in fair condition. It is approaching the end of its service life and should be replaced. | 574 | The asset was in good condition overall. Staining at the bottom section of the pipe was observed.
414 |  | 575 | good
415 | The asset was observed to be in fair condition. Corrosion was observed. | 576 | Surface corrosion
416 | The asset was observed to be in good condition. | 577 | good
416 |  | 578 | good
417 | The asset was observed to be in good condition. | 579 | good
418 | The asset was observed to be in good condition. | 580 | good
419 | The asset was observed to be in fair condition. | 581 | Severe corrosion
420 | obsolete | 582 | Missing gooseneck vent and bird screen.
420 | minor corrosion | 583 | surface corrosion
421 | Obsolete | 584 | Surface corrosion
421 | Corrosion | 585 | good
422 | good | 586 | good
422 | obsolete | 587 | miscellaneous surface staining
423 | good | 588
423 |  | 589 | good
424 | Dust | 590 | good
424 | good | 591
425 | good | 592 | paint peeling | fair
425 | Corrosion | 593 | good
426 | good | 594 | good
426 | Corrosion | 595 | good
427 | good | 596 | The asset was observed to be in good condition, however, it was approaching the end of its useful service life and should be replaced
427 | Corrosion | 597 | surface corrosion
428 | minor Corrosion | 598 | The asset was observed to be in fair condition. Minor surface corrosion and wear on the casing was observed.
429 | good | 599 | The asset was observed to be in fair condition. Operability of the asset was unknown.
429 |  | 600 | good
430 | good | 601 | good
431 | good | 602 | good
432 | good | 603 | Good
433 | very good | 604 | good
434 | good | 605 | The asset was observed to be in good condition.
435 | good | 606 | The asset was observed to be in good condition.
435 | obsolete | 607 | The asset was observed to be in good condition.
436 | good | 608 | The asset was observed to be in good condition.
437 | good | 609 | There was no yard hydrant located on site. | In accordance with Section 19.8.3 of the Region's Water and Wastewater Design Manual (January 2012), a yard hydrant complete with a backflow preventer with a 37.5mm water service line shall be provided for flushing and cleaning purposes. It is recommended
438 | good | 610 | The asset was observed to be in good condition.
439 | Good | 611 | Good
440 | good | 612 | Good
441 | good | 613 | Good
442 | good | 614 | Good
443 | good | 615 | Good
444 | good | 616 | In accordance with Section 19.8.3 of the Region's Water and Wastewater Design Manual (January 2012), a yard hydrant complete with a backflow preventer with a 37.5mm water service line shall be provided for flushing and cleaning purposes. It is recommended
445 | good | 617 | The asset was observed to be in good condition.
446 | good | 618 | The asset was observed to be in good condition.
446 | bolts were not secured properly | 619 | The asset was observed to be in good condition.
447 | good | 620 | The asset was observed to be in fair condition.
448 | good | 621 | The asset was observed to be in good condition.
449 | The asset was observed to be in good condition. | 622 | Fair | Minor surface rust and defects
450 | The asset was observed to be in good condition. | 623 | In accordance with Section 19.8.3 of the Region's Water and Wastewater Design Manual (January 2012), a yard hydrant complete with a backflow preventer with a 37.5mm water service line shall be provided for flushing and cleaning purposes. It is recommended
451 | The asset was observed to be in good condition. | 624 | The asset was observed to be in good condition.
452 | The asset was observed to be in good condition. | 625 | The asset was observed to be in good condition.
453 | The asset was observed to be in good condition. | 626 | The asset was observed to be in good condition.
454 | The asset was observed to be in good condition. | 627
455 | The asset was observed to be in good condition. | 628
456 | The asset was observed to be in good condition. | 629 | The asset was assumed to be in fair condition based on its age.
456 |  | 630 | The asset was observed to be in good condition. | Shock and arc flash hazard as the existing arc flash label is outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreover, the studies and reports
457 | The asset was in fair condition. Surface corrosion was observed. | 631
458 | The asset was observed to be in good condition. | 632
458 | Shock and arc flash hazard as the existing arc flash label is outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreover, the studies and reports | 633
459 | The asset was observed to be in good condition. | 634
460 | The asset was observed to be in good condition. | 635
461 | The asset was observed to be in good condition. | 636
461 | Shock and arc flash hazard as the existing arc flash label is outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreover, the studies and reports | 637
462 | The asset was observed to be in good condition. | 638
462 | Shock and arc flash hazard as the existing arc flash label is outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreover, the studies and reports | 639
463 | The asset was observed to be in good condition. | 640
463 | Shock and arc flash hazard as the existing arc flash label is outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreover, the studies and reports | 641
464 | The asset was observed to be in good condition. | 642
465 | The asset was observed to be in fair condition. Corrosion on fixtures was observed. The lighting should be replaced with LED in next upgrade | 643
466 | The asset was in fair condition. Corrosion on the surface of the panels as well as circuit breakers was observed. The panel is to be replaced with NEMA 4X enclosure | 644
466 | Shock and arc flash hazard as the existing arc flash label is outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreover, the studies and reports | 645
467 | The asset was observed to be in poor condition. Heavy corrosion was observed. | 646
468 | The asset was observed to be in good condition. To be replaced with led in next upgrade. | 647
469 | The asset was observed to be in fair condition. Bottom of the enclosure was heavily corroded and should be replaced with NEMA 3R enclosure. | 648
470 | The asset was observed to be in good condition. However, the availability of parts and increased maintenance cost will be an issue. It is recommended to replace the pump control within the 10-year plan. Additionally, the Phase converters inside panel shou | 649
471 | The asset was observed to be in good condition. However, the availability of parts and increased maintenance cost will be an issue. It is recommended to replace the control panel within the 10-year plan. | 650
471 | Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servicing, or maintenance while | 651 | Fair | Overgrown vegetation
472 | The asset was observed to be in good condition. However, the availability of parts and increased maintenance cost will be an issue. It is recommended to replace the receptacle within the 10-year plan. | 652 | The asset was in poor condition. Heavy corrosion and deterioration was observed.
473 | The asset was observed to be in good condition. | 653
474 | The asset was observed to be in good condition. However, the availability of parts and increased maintenance cost will be an issue. It is recommended to replace the main breaker within the 10-year plan. | 654
474 | Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the main breaker which may require examination, adjustment, servicing, or maintenance | 655 | The asset was observed to be in fair condition. Minor surface corrosion and deterioration was noted. However, internal inspection of the piping was not undertaken.
475 | The asset was observed to be in good condition. However, the availability of parts and increased maintenance cost will be an issue. It is recommended to replace the transfer switch within the 10-year plan. | 656
475 | Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the manual transfer switch which may require examination, adjustment, servicing, or ma | 657 | The asset was observed to be in good condition. Minor paint wear was observed.
476 | The asset was observed to be in good condition. However, in order to provide accessibility to hydro personnel, it is recommended to move the meter above ground. | 658 | The asset was observed to be in fair condition. Moderate corrosion on the surface of the pipe was observed.
476 |  | 659 | There was no overflow installed at the station. As per the Region’s Water and Wastewater Facilities Design Manual (Halton Region, January 2012) an emergency overflow shall be provided for all wastewater pumping stations.
477 | The asset was observed to be in good condition. Replace with LED fixture in next upgrade. | 660
478 | The asset was observed to be in fair condition. The model has been discontinued. | 661 | The Cathodic Protection was assumed to be in good condition. The installation of the cathodic protection system was assumed to coincide with the installation of the above grade panel.
478 | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the breaker which may require examination, adjustment, servicing, or maintenance while | 662
479 | The asset was observed to be in good condition. The model has been discontinued. | 663 | Fair | Minor corrosion
480 | The asset was observed to be in good condition. The model has been discontinued. | 664
481 | The asset was observed to be in fair condition. Corrosion was observed inside and on surface of the panel. It was missing arc flash labels. | 665 | Fair | Minor corrosion
481 | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servicing, or maintenance while e | 666 | Fair | Corrosion
482 | The asset was observed to be in good condition. | 667 | The Cathodic Protection was assumed to be in good condition. The installation of the cathodic protection system was assumed to coincide with the installation of the above grade panel.
483 | The asset was observed to be in fair condition. The panel was corroded. | 668 | Missing exhaust fan | As per Section 7.2.9 of MOECC's Design Guidelines for Sewage Works, mechanical ventilation is required for below ground surface dry well.
484 | The asset was observed to be in good condition. However, availability of spare parts and increased maintenance cost will be an issue. It is therefore recommended to replace the asset in the next 10-years. | 669 | Not observed
484 | Shock and arc flash hazard as the existing arc flash label is outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreover, the studies and reports | 670 | The asset was assumed to be in fair condition based on its age.
485 | good | 671 | Poor | Heavy corrosion and deterioration was observed
486 | good | 672
487 | good | 673
488 | good | 674
489 | good | 675
489 | replace with LED fixtures rated for class 1, div 2 | 676
490 | good | 677
490 | inside the panel is not getting drained properly | 678
491 | fair | 679
491 | replace with NEMA 4X panel | 680
492 | good | 681
493 | good | 682
493 | missing arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servicin | 683
494 | good | 684
495 | good | 685
495 | missing arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the receptacle which may require examination, adjustment, ser | 686
495 |  | 687
496 | good | 688
496 | replace with LED in next upgrade | 689
497 | fair | 690
497 | misplaced arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servic | 691
497 | Pump #1 breaker to be sized and replaced according to OESC-2018 | 692
498 | good | 693
499 | fair | 694
499 | bottom of interior has corroded | 695
499 | replace with NEMA 3R enclosure in next upgrade | 696
500 | good | 697
500 | missing arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servicin | 698
501 | good | 699
502 | good | 700
502 | missing arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servicin | 701
503 | good | 702
503 | fair | 703
503 | replace with LED fixture in next upgrade. To be rated for class 1, div 2 | 704
504 | fair | 705
504 | bottom of interior was corroded | 706
504 | missing arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servicin | 707
505 | fair | 708
505 | top surface and doors were corroded | 709
505 | to be replaced with NEMA 3R enclosure | 710
506 | good | 711
506 | outdated arc flash label. Shock and arc flash hazard as the existing arc flash label are outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreove | 712
507 | good | 713
508 | good | 714
509 | good | 715
510 | good | 716
510 | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the switch which may require examination, adjustment, servicing, or maintenance while | 717
511 | poor | 718
511 | severely corroded | 719
512 | good | 720
513 | good | 721
513 | misplaced and outdated arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the VFD breaker which may require examination, | 722
514 | good | 723
515 | good | 724
515 | misplaced and outdated arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the VFD breaker which may require examination, | 725
516 | good | 726
516 | misplaced and outdated arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the VFD breaker which may require examination, | 727
517 | good | 728
518 | good | 729
518 | replace with LED in next upgrade | 730
519 | fair | 731
519 | to be replaced with LED | 732
520 | fair | 733
520 | to be replaced with LED | 734
521 | good | 735
522 | fair | 736
522 | to have separate Main DS, MTS, and CP | 737
522 | outdated arc flash label. Shock and arc flash hazard as the existing arc flash label are outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreove | 738
523 | fair | 739
524 | good | 740
525 | good | 741
526 | good | 742
527 | good | 743
528 | good | 744
528 | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the control panel which may require examination, adjustment, servicing, or maintenance | 745
529 | good | 746
529 | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the control panel which may require examination, adjustment, servicing, or maintenance | 747
530 | good | 748
531 | fair | 749
531 | one of the lights doesn’t work | 750
531 | to be replaced with LED | 751
532 | fair | 752
532 | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servicing, or maintenance while e | 753
533 | fair | 754
533 | it doesn't work | 755
534 | fair | 756
534 | to be replaced with LED | 757
535 | fair | 758
535 | to be replaced with NEMA 3R enclosure | 759
536 | good | 760
537 | good | 761
537 |  | 762
538 | good | 763
539 | good | 764
539 | replace with separate main DS, MTS and CP | 765
539 | Shock and arc flash hazard as the existing arc flash label are outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreover, the studies and reports | 766
540 | good | 767
541 | The asset was observed to be in good condition. | 768
541 | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the MTS which may require examination, adjustment, servicing, or maintenance while ene | 769
542 | The asset was observed to be in good condition. | 770
543 | The asset was observed to be in good condition. | 771
543 | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the MTS which may require examination, adjustment, servicing, or maintenance while ene | 772
544 | The asset was observed to be in good condition. | 773
545 | The asset was observed to be in fair condition. It is recommended to replace with led fixtures rated for class 1, div 2. | 774
546 | The asset was observed to be in fair condition. The panel was aged and minor surface corrosion was observed. | 775
546 | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2. Arc Flash label is required for the panel which may require examination, adjustment, servicing, or maintenance while | 776
547 | The asset was observed to be in fair condition. The top of the panel was damaged. Some repair work was completed to cover the damaged spots; however, it appears that the damaged spots were not sealed properly. | 777
548 | The asset was observed to be in good condition. | 778
549 | The asset was observed to be in good condition. | 779
549 | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the control panel which may require examination, adjustment, servicing, or maintenance | 780
550 | The asset was observed to be in good condition. | 781
550 | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the lighting panel which may require examination, adjustment, servicing, or maintenanc | 782
551 | The asset was observed to be in good condition. Replace with VFD in next upgrade. | 783
551 | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the pump capacitors which may require examination, adjustment, servicing, or maintenan | 784
552 | The asset was observed to be in good condition. | 785
552 | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the main breaker which may require examination, adjustment, servicing, or maintenance | 786
553 | The asset was observed to be in good condition. | 787
554 | The asset was observed to be in good condition. | 788
554 | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the switch which may require examination, adjustment, servicing, or maintenance while | 789
555 | The asset was observed to be in good condition. | 790
556 | The asset was observed to be in good condition. | 791
557 | The asset was observed to be in good condition. | 792
558 | There was no manual transfer station installed at the station. It is recommended to install the manual transfer switch to ensure the station is being powered by one power source (either hydro or generator). Additionally, the MTS provides a safe mean to sw | 793
559 | There was no Generator Connection Receptacle and Manual Transfer Switch located on site. It is recommended to install Generator Connection Receptacle as hardwiring the generator for emergency power parallel power source may cause a severe electrical shoc | 794
559 | Paralleling power sources and severe electrical shock hazard while hardwiring the generator for emergency power | 795
560 | There was no main fused disconnect switch installed at the station. It is recommended to install the main disconnect switch to allow operators to safely isolate the station from hydro to install, maintain and repair any electrical equipment (electrical, m | 796
561 | There was no Power meter installed on site. It is recommended to install a power meter to measure and display power consumption of the station. The power meter should be instated above ground for ease of operation/access and compatibility with industry’s | 797
562 | There was no manual transfer station installed at the station. It is recommended to install the manual transfer switch to ensure the station is being powered by one power source (either hydro or generator). Additionally, the MTS provides a safe mean to sw | 798
563 | There was no main fused disconnect switch installed at the station. It is recommended to install the main disconnect switch to allow operators to safely isolate the station from hydro to install, maintain and repair any electrical equipment (electrical, m | 799
564 | There was no Generator Connection Receptacle and Manual Transfer Switch located on site. It is recommended to install Generator Connection Receptacle as hardwiring the generator for emergency power parallel power source may cause a severe electrical shoc | 800
564 | Paralleling power sources and severe electrical shock hazard while hardwiring the generator for emergency power. It is recommended to install generator receptacle above ground to comply with industry practice | 801
565 | The asset was in fair condition. Moderate corrosion was observed. | 802
565 |  | 803
566 | The asset was in good condition | 804
567 | The asset was in good condition overall. Paint peeling was observed. | 805
569 | The vent piping was in fair condition. Paint peeling at the portion above the wet well was observed. | 806
570 | The asset was observed to be in good condition. | 807
572 | The asset was observed to be in good condition. | 808
573 | The asset was observed to be in fair condition. Paint peeling was observed. | 809
574 | The asset was in good condition overall. Staining at the bottom section of the pipe was observed. | 810
575 | good | 811
576 | Surface corrosion | 812
577 | good | 813
578 | good | 814
579 | good | 815
580 | good | 816
580 |  | 817
581 | Severe corrosion | 818
582 | Missing gooseneck vent and bird screen. | 819
583 | surface corrosion | 820
584 | Surface corrosion | 821
585 | good | 822
586 | good | 823
587 | miscellaneous surface staining | 824
589 | good | 825
590 | good | 826
590 |  | 827
592 | paint peeling | 828
592 | fair | 829
593 | good | 830
594 | good | 831
595 | good | 832
596 | The asset was observed to be in good condition, however, it was approaching the end of its useful service life and should be replaced | 833
597 | surface corrosion | 834
598 | The asset was observed to be in fair condition. Minor surface corrosion and wear on the casing was observed. | 835
599 | The asset was observed to be in fair condition. Operability of the asset was unknown. | 836
600 | good | 837
601 | good | 838
602 | good | 839
603 | Good | 840
604 | good | 841
605 | The asset was observed to be in good condition. | 842
606 | The asset was observed to be in good condition. | 843
607 | The asset was observed to be in good condition. | 844
608 | The asset was observed to be in good condition. | 845
608 |  | 846
609 | There was no yard hydrant located on site. | 847
609 | In accordance with Section 19.8.3 of the Region's Water and Wastewater Design Manual (January 2012), a yard hydrant complete with a backflow preventer with a 37.5mm water service line shall be provided for flushing and cleaning purposes. It is recommended | 848
610 | The asset was observed to be in good condition. | 849
610 |  | 850
611 | Good | 851
612 | Good | 852
613 | Good | 853
614 | Good | 854
615 | Good | 855
616 | In accordance with Section 19.8.3 of the Region's Water and Wastewater Design Manual (January 2012), a yard hydrant complete with a backflow preventer with a 37.5mm water service line shall be provided for flushing and cleaning purposes. It is recommended | 856
616 |  | 857
617 | The asset was observed to be in good condition. | 858
617 |  | 859
618 | The asset was observed to be in good condition. | 860
619 | The asset was observed to be in good condition. | 861
620 | The asset was observed to be in fair condition. | 862
620 |  | 863
621 | The asset was observed to be in good condition. | 864
622 | Fair | 865
622 | Minor surface rust and defects | 866
623 | In accordance with Section 19.8.3 of the Region's Water and Wastewater Design Manual (January 2012), a yard hydrant complete with a backflow preventer with a 37.5mm water service line shall be provided for flushing and cleaning purposes. It is recommended | 867
624 | The asset was observed to be in good condition. | 868
625 | The asset was observed to be in good condition. | 869
626 | The asset was observed to be in good condition. | 870
629 | The asset was assumed to be in fair condition based on its age. | 871
630 | The asset was observed to be in good condition. | 872
630 | Shock and arc flash hazard as the existing arc flash label is outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreover, the studies and reports | 873
651 | Fair | 874
651 | Overgrown vegetation | 875
652 | The asset was in poor condition. Heavy corrosion and deterioration was observed. | 876
655 | The asset was observed to be in fair condition. Minor surface corrosion and deterioration was noted. However, internal inspection of the piping was not undertaken. | 877
657 | The asset was observed to be in good condition. Minor paint wear was observed. | 878
658 | The asset was observed to be in fair condition. Moderate corrosion on the surface of the pipe was observed. | 879
659 | There was no overflow installed at the station. As per the Region’s Water and Wastewater Facilities Design Manual (Halton Region, January 2012) an emergency overflow shall be provided for all wastewater pumping stations. | 880
661 | The Cathodic Protection was assumed to be in good condition. The installation of the cathodic protection system was assumed to coincide with the installation of the above grade panel. | 881
663 | Fair | 882
663 | Minor corrosion | 883
665 | Fair | 884
665 | Minor corrosion | 885
666 | Fair | 886
666 | Corrosion | 887
667 | The Cathodic Protection was assumed to be in good condition. The installation of the cathodic protection system was assumed to coincide with the installation of the above grade panel. | 888
668 | Missing exhaust fan | 889
668 | As per Section 7.2.9 of MOECC's Design Guidelines for Sewage Works, mechanical ventilation is required for below ground surface dry well. | 890
669 | Not observed | 891
670 | The asset was assumed to be in fair condition based on its age. | 892
671 | Poor | 893
671 | Heavy corrosion and deterioration was observed | 894
895
896
897
898
899
900
901
902
903
904
905
906
907
908
909
910
911
912
913
914
915
916
917
918
919
920
921
922
923
924
925
926
927
928
929
930
931
932
933
934
935
936
937
938
939
940
941
942
943
944
945
946
947
948
949
950
951
952
953
954
955
956
957
958
959
960
961
962
963
964
965
966
967
968
969
970
971
972
973
974
975
976
977
978
979
980
981
982
983
984
985
986
987
988
989
990
991
992
993
994
995
996
997
998
999
1000
1001
1002
1003
1004
1005
1006
1007
1008
1009
1010
1011
1012
1013
1014
1015
1016
1017
1018
1019
1020
1021
1022
1023
1024
1025
1026
1027
1028
1029
1030
1031
1032
1033
1034
1035
1036
1037
1038
1039
1040
1041
1042
1043
1044
1045
1046
1047
1048
1049
1050
1051
1052
1053
1054
1055
1056
1057
1058
1059
1060
1061
1062
1063
1064
1065
1066
1067
1068
1069
1070
1071
1072
1073
1074
1075
1076
1077
1078
1079
1080
1081
1082
1083
1084
1085
1086
1087
1088
1089
1090
1091
1092
1093
1094
1095
1096
1097
1098
1099
1100
1101
1102
1103
1104
1105
1106
1107
1108
1109
1110
1111
1112
1113
1114
1115
1116
1117
1118
1119
1120
1121
1122
1123
1124
1125
1126
1127
1128
1129
1130
1131
1132
1133
1134
1135
1136
1137
1138
1139
1140
1141
1142
1143
1144
1145
1146
1147
1148
1149
1150
1151
1152
1153
1154
1155
1156
1157
1158
1159
1160
1161
1162
1163
1164
1165
1166
1167
1168
1169
1170
1171
1172
1173
1174
1175
1176
1177
1178
1179
1180
1181
1182
1183
1184
1185
1186
1187
1188
1189
1190
1191
1192
1193
1194
1195
1196
1197
1198
1199
1200
1201
1202