## Main
ParentID | Condition | Comment1
1 | 2 | The asset was observed to be in good condition. Very minor localized corrosion was observed.
2 | 2 | The asset was observed to be in good condition.
3 | 3 | The asset was observed to be in fair condition. Although the system is recently installed, SCADA Pack is an outdated model. We recommend the Region to eventually transition toward Allen-Bradley Compactlogix as per Region's standard. The enclosure and ducts can be reused for another 10 years.
4 | 2 | The asset was observed to be in good condition.
5 | 2 | The asset was observed to be in good condition. Corroded bolts were observed.
6 | 2 | The asset was observed to be in good condition.
7 | 3 | The asset was assumed to be in fair condition.
8 | 2 | The asset was observed to be in good condition. Dust was observed.
9 | 2 | The asset was observed to be in good condition.
10 | 2 | The asset was observed to be in good condition. The tanks appeared to be empty at the time of inspection. The tanks should remain within the containment wall, although the existing containment area appears too small to fit all tanks.
11 | 2 | The asset was observed to be in good condition. Minor surface corrosion was noted.
12 | 2 | The asset was observed to be in good condition.
13 | 2 | The asset was observed to be in good condition.
14 | 2 | The asset was observed to be in good condition.
15 | 2 | The asset was observed to be in good condition.
16 | 2 | The asset was observed to be in good condition.
17 | 2 | The asset was observed to be in good condition.
18 | 2 | The asset was observed to be in good condition.
19 | 3 | The asset was assumed to be in fair condition as it might be a potential duplicate asset.
20 | 2 | The asset was observed to be in good condition.
21 | 2 | The asset was observed to be in good condition.
22 | 3 | The asset was observed to be in fair condition as corrosion was noted.
23 | 3 | The asset was observed to be in fair condition as corrosion was noted.
24 | 2 | The asset was observed to be in good condition. This entry is for the valve only. The actuator is inventoried separately under Process Electrical assets
25 | 3 | The asset was observed to be in fair condition. Corroded bolts were observed.
26 | 3 | The asset was observed to be in fair condition. Minor corrosion was observed on the flanges.
27 | 2 | The asset was observed to be in good condition.
28 | 2 | The asset was observed to be in good condition.
29 | 2 | The asset was observed to be in good condition.
30 | 2 | The asset was observed to be in good condition.
31 | 2 | The asset was observed to be in good condition.
32 | 2 | The asset was observed to be in good condition.
33 | 2 | The asset was observed to be in good condition.
34 | 2 | The asset was observed to be in good condition.
35 | 2 | The asset was assumed to be in good condition. This particular air relief valve could not be identified due to a lack of tags, but all air relief valves were the same age.
36 | 2 | The asset was observed to be in good condition.
37 | 2 | The asset was observed to be in good condition.
38 | 2 | The asset was observed to be in good condition.
39 | 2 | The asset was observed to be in good condition.
40 | 4 | The pressure transmitter was in poor condition with corrosion observed. It should to be replaced within the next year.
41 | 3 | The asset was observed to be in fair condition. Corrosion was noted.
42 | 2 | The asset was observed to be in good condition.
43 | 3 | The asset was assumed to be in fair condition.
44 | 2 | The asset was observed to be in good condition.
45 | 3 | The asset was assumed to be in fair condition.
46 | 3 | The asset was observed to be in fair condition. Minor surface corrosion was noted.
47 | 3 | The asset was assumed to be in fair conditoin as it was not located on site.
48 | 2 | The asset was observed to be in good condition.
49 | 2 | The asset was observed to be in good condition.
50 | 2 | The asset was observed to be in good condition.
51 | 2 | The asset was observed to be in good condition.
52 | 3 | The asset was assumed to be in fair condition.
53 | 3 | The asset was assumed to be in fair condition.
54 | 3 | The asset was observed to be in fair condition. Minor surface corrosion was observed.
55 | 3 | The asset was observed to be in fair condition. It was outdated.
56 | 2 | The asset was observed to be in good condition.
57 | 3 | The asset was observed to be in fair condition. There was an incident that the HVAC in generator room has failed and high temperature generated by the standby generator has caused the conduits to bend.
58 | 2 | The asset was observed to be in good condition.
59 | 1 | The asset was assumed to be in very good condition based on its age.
60 | 3 | The asset was observed to be in fair condition. Minor surface corrosion was noted.
61 | 2 | The asset was observed to be in good condition.
62 | 2 | The asset was observed to be in good condition.
63 | 2 | The asset was observed to be in good condition.
64 | 2 | The asset was observed to be in good condition.
65 | 2 | The asset was observed to be in good condition.
66 | 2 | The asset was observed to be in good condition.
67 | 2 | The asset was observed to be in good condition.
68 | 2 | The asset was observed to be in good condition.
69 | 3 | The asset was observed to be in fair condition. Corrosion was observed on sampling tubes.
70 | 2 | The asset was observed to be in good condition.
71 | 3 | The asset was observed to be in fair condition. Minor surface corrosion on valve and bolts was observed.
72 | 3 | The asset was observed to be in good condition. Minor surface corrosion was noted and the bolts were moderately corroded.
73 | 2 | The asset was observed to be in good condition.
74 | 2 | The asset was observed to be in good condition.
75 | 2 | The asset was observed to be in good condition.
76 | 2 | The asset was observed to be in good condition. Dust was noted.
77 | 2 | The asset was observed to be in good condition. Dust was noted.
78 | 2 | The asset was observed to be in good condition.
79 | 3 | The asset was observed to be in fair condition. Corrosion was noted.
80 | 3 | The asset was observed to be in fair condition. Corrosion was noted.
81 | 3 | The asset was assumed to be in fair condition based on its age. The pump was not accessible as it was submerged.
82 | 2 | The asset was observed to be in good condition.
83 | 2 | The asset was observed to be in good condition.
84 | 2 | The asset was observed to be in good condition. The bolts were severely corroded.
85 | 2 | The assset was observed to be in good condition. The tanks appeared to be empty at the time of inspection. The tanks should remain within the containment wall, although the existing containment area appears too small to fit all tanks.
86 | 2 | The asset was observed to be in good condition. Minor surface corrosion was noted.
87 | 2 | The asset was observed to be in good condition.
88 | 2 | The asset was observed to be in good condition.
89 | 2 | The asset was observed to be in good condition.
90 | 2 | The asset was observed to be in good condition. Minor surface deposits were noted.
91 | 3 | The asset was observed to be in fair condition. Surface corrosion was noted.
92 | 3 | The asset was observed to be in fair condition. Minor surface corrosion was noted.
93 | 2 | The asset was observed to be in good condition.
94 | 3 | The asset was observed to be in fair condition. Moderate corrosion was noted and the pump was spraying droplets onto the floor. It was last serviced May 2011 by Advanced Pump Repair Service in Cambridge
95 | 2 | The asset was observed to be in good condition. The pump was last serviced August 2020 by Advanced Pump Repair Service in Cambridge
96 | 3 | The asset was observed to be in fair condition. It was removed for service at the time of inspection. The blind flange on the suction side was leaking.
97 | 1 | The asset was observed to be in very good condition.
98 | 2 | The asset was observed to be in good condition. It appeared to be relatively new compared to the age of the facility. This model was released in 2010, so the installation year was assumed to be 2010.
99 | 2 | The asset was observed to be in good condition.
100 | 2 | The asset was observed to be in good condition.
101 | 2 | The asset was observed to be in good condition.
102 | 2 | The asset was observed to be in good condition.
103 | 2 | The asset was observed to be in good condition.
104 | 3 | The asset was observed to be in fair condition. Minor surface corrosion was noted.
105 | 2 | The asset was observed to be in good condition.
106 | 2 | The asset was observed to be in good condition.
107 | 2 | The asset was observed to be in good condition.
108 | 2 | The asset was observed to be in good condition.
109 | 2 | The asset was observed to be in good condition.
110 | 2 | The asset was observed to be in good condition.
111 | 3 | The asset was observed to be in fair condition. Surface cracks and differential settling were observed. A portion of the driveway on the North side of the lot was recently repaved and was in very good condition.
112 | 2 | The asset was observed to be in good condition. Minor corrosion was observed at the base.
113 | 2 | The asset was observed to be in good condition. Minor rust was observed at the base.
114 | 2 | The asset was observed to be in good condition.
115 | 3 | The asset was observed to be in fair condition. The wire was disconnected from the posts at some sections and needs to be re-fastened.
116 | 2 | The asset was observed to be in good condition.
117 | 2 | The asset was asumed to be in good condition based on the portion that was visible and the condition of the other retaining wall on site.
118 | 2 | The asset was observed to be in good condition.
119 | 2 | The asset was assumed to be in good condition based on its age.
120 | 2 | The asset was assumed to be in good condition based on its age.
121 | 3 | The asset was assumed to be in fair to good condition. The portion visible from the pumping station basement hase moderate surface rusting.
122 | 2 | The asset was assumed to be in good condition based on its age.
123 | 2 | The asset was assumed to be in good condition based on its age.
124 | 2 | The asset was assumed to be in good condition based on its age.
125 | 2 | The asset was assumed to be in good condition based on its age. The catchbasin was inaccessible due to the overgrowth.
126 | 2 | The asset was assumed to be in good condition based on its age.
127 | 2 | The asset was assumed to be in good condition based on its age.
128 | 2 | The asset was assumed to be in good condition based on its age.
129 | 2 | The asset was assumed to be in good condition based on its age.
130 | 2 | The asset was observed to be in good condition.
131 | 2 | The asset was observed to be in good condition.
132 | 2 | The asset was observed to be in good condition. Dust was observed.
133 | 2 | The asset was observed to be in good condition.
134 | 2 | The asset was observed to be in good condition.
135 | 2 | The asset was observed to be in good condition.
136 | 2 | The asset was observed to be in good condition.
137 | 2 | The asset was observed to be in good condition.
138 | 2 | The asset was observed to be in good condition.
139 | 2 | The asset was observed to be in good condition.
140 | 2 | The asset was observed to be in good condition.
141 | 3 | The asset was observed to be in fair condition based on its age.
142 | 3 | The asset was observed to be in fair condition based on its age.
143 | 3 | The asset was in fair condition. It was out of service.
144 | 3 | The asset was observed to be in fair condition based on its age.
145 | 3 | The asset was to be removed from the station.
146 | 2 | The asset was observed to be in good condition.
147 | 2 | The asset was observed to be in good condition.
148 | 2 | The asset was observed to be in good condition.
149 | 2 | The asset was observed to be in good condition.
150 | 2 | The asset was observed to be in good condition.
151 | 4 | The asset was in poor condition. Severe corrosion on the bottom of junction box.
152 | 2 | The asset was observed to be in good condition. It's to be replaced with LED fixtures in the next upgrade.
153 | 2 | The asset was observed to be in good condition. It's to be replaced with LED fixtures in the next upgrade.
154 | 2 | The asset was observed to be in good condition. It's to be replaced with LED fixtures in the next upgrade.
155 | 2 | The asset was observed to be in good condition. It's to be replaced with LED fixtures in the next upgrade.
156 | 2 | The asset was observed to be in good condition. It's to be replaced with LED fixtures in the next upgrade.
157 | 2 | The asset was observed to be in good condition.
159 | 3 | The asset was observed to be in fair condition. Paint peeling was observed at the door base. Moderate corrosion was noted at the base of the door frame.
161 | 4 | The asset was observed to be in poor condition. The exterior door had no weather stripping. Damaged sweeper and through-rust was observed at the base of the door frame. Additionally, severe paint peeling, minor surface rust on doors, and worn wood trim were noted.
162 | 3 | The asset was observed to be in fair condition. Paint peeling was observed at the door base. Localized brick spalling (approx. 1 sq m), localized mortar loss (approx. 2 m), and step cracking at southwest corner (approx 5 m) were noted.
163 | 3 | The asset was observed to be in fair condition. Minor surface rust was noted.
164 | 3 | The asset was observed to be in fair condition. Localized paint wear was noted.
165 | 2 | The asset was observed to be in good condition.
166 | 3 | The asset was observed to be in fair condition. Localized paint wear and damage (bending) was noted.
167 | 2 | The asset was observed to be in good condition.
168 | 3 | The asset was observed to be in fiar condition. Localized spalling at edges were noted.
169 | 2 | The asset was observed to be in good condition.
170 | 2 | The asset was observed to be in good condition.
171 | 2 | The asset was observed to be in good condition; however, even thought it was not a structural concern, poor concrete finishing on exposed interior face was noted.
172 | 2 | The asset was observed to be in good condition.
173 | 2 | The asset was observed to be in good condition.
174 | 3 | The asset was observed to be in fair condition. Minor localized staining was noted.
175 | 3 | The asset was observed to be in fair condition. Localized step cracking at generator room wall (behind electrical panels) was noted. The defects should be repaired next time the electrical panels are removed from the walls (likely at the end of their service life).
176 | 3 | The asset was observed to be in fair condition. Shallow spalling (approx 5 sq m) and severe staining along floor gutter were observed at the top face. Previously repaired holes and cracks (below sodium hypo) was noted. A new crack at hatch corner (approx. 4 lm) was also noted.
177 | 2 | The asset was observed to be in good condition.
178 | 4 | The asset was observed to be in poor condition. Heavy corrosion and discolouration were noted.
179 | 2 | The asset was observed to be in good condition.
180 | 3 | The asset was observed to be in fair condition. Localized paint wear and surface rust were noted.
181 | 3 | The asset was observed to be in good condition. The hoist was last inspected in February of 2010. The Region may consider having another inspection done to ensure proper operation.
182 | 2 | The asset was observed to be in good condition. Based on the condition of the enclosed floor slab (from below), the Region is recommended to consider adding a protective coating to the interior wall faces within the containment area.
183 | 3 | The asset was observed to be in fair condition. Localized wear and discolouration (approximately 10% of total area) were noted.
184 | 3 | The asset was observed to be in fair condition. Minor surface wear was noted.
185 | 2 | The guardrail was in good condition; however, kick plates were missing. Missing kick plates are a health and safety issue as tools/ other objects could fall from the upper level to an occupied space below.
186 | 2 | The asset was observed to be in good condition.
187 | 2 | The asset was observed to be in good condition.
188 | 3 | The asset was observed to be in fair condition. Localized cracks with signs of active leakage (approx. 3 lm) was noted. Poor concrete finishing on exposed interior face was noted; however, it was not a structural concern.
189 | 4 | The asset was observed to be in poor condition. Staining, localized missing paint, and general wear (approximately 30% of total area) were noted.
190 | 2 | The asset was observed to be in good condition. Poor concrete finishing on exposed interior face was noted; however, it was not a structural concern.
191 | 3 | The asset was observed to be in fair condition. Severe honeycombing at east end of south beam (approx. 1 sq m) was noted.
192 | 3 | The asset was observed to be in fair condition. Minor cracking and surface wear were noted.
193 | 2 | The asset was observed to be in good condition.
194 | 3 | The asset was observed to be in fair condition. General surface wear was noted.
195 | 3 | The asset was observed to be in fair condition. Large deep localized spalling (approx. 1 sq m) and localized cracking with signs of leakage (approx. 5 lm) were noted. It is recommended to have this entity inspected from within the tank.
196 | 3 | The asset was assumed to be in fair condition. It is recommended to have this entity inspected from within the tank.
197 | 3 | The asset was observed to be in fair condition. Surface corrosion on post base anchors was noted.
198 | 3 | The asset was observed to be in fair condition. Minor surface rust was noted on bolts
199 | 2 | The asset was observed to be in good condition.
200 | 3 | The asset was observed to be in fair condition. The hatches were only visible from the top. East hatch did not appear to close all the way. Minor corrosion on south hatches.
201 | 2 | The asset was observed to be in good condition.
202 | 3 | The asset was assumed to be in fair to poor condition based on its age as the waterproofing membrane was not able to be observed.
203 | 4 | The asset was observed to be in poor condition. Localized damage at south-west corner of the building was noted.
204 | 2 | The asset was observed to be in good condition.
205 | 4 | The asset was in poor condition based on age and information provided by operations. Since one of the ladders was removed in 2005 due to corrosion, it is likely that the three remaining ladders are in poor condition.
206 | 3 | The asset was assumed to be in fair condition. It is recommended to have this entity inspected from within the tank.
207 | 3 | The asset was assumed to be in fair condition. It is recommended to have this entity inspected from within the tank.
209 | 3 | The asset was assumed to be in fair condition. It is recommended to have this entity inspected from within the tank.
210 | 3 | The asset was assumed to be in fair condition. It is recommended to have this entity inspected from within the tank.
211 | 3 | The asset was assumed to be in fair condition. It is recommended to have this entity inspected from within the tank.
212 | 2 | The asset was in observed to be in good condition.
213 | 2 | The asset was assumed to be in good condition based on its age
214 | 2 | The asset was in observed to be in good condition.
215 | 2 | The asset was observed to be in good condition. It is clear the asset is not original to the facility so the installation year has been approximated to be 2010.
216 | 2 | The asset was in observed to be in good condition.
217 | 2 | The asset was in observed to be in good condition.
218 | 2 | The asset was in observed to be in good condition.
219 | 2 | The asset was in observed to be in good condition.
220 | 2 | The asset was in observed to be in good condition.
221 | 2 | The asset was in observed to be in good condition.
222 | 2 | The asset was in observed to be in good condition.
223 | 2 | The asset was in observed to be in good condition.
224 | 2 | The asset was in observed to be in good condition.
225 | 2 | The asset was in observed to be in good condition.
226 | 2 | The asset was in observed to be in good condition.
227 | 1 | The asset was in observed to be in very good condition.
228 | 2 | The asset was in observed to be in good condition.
229 | 2 | The asset was in observed to be in good condition.
230 | 2 | The asset was in observed to be in good condition.
231 | 2 | The asset was in observed to be in good condition.
232 | 3 | The asset was observed to be in fair condition. The limited portion visible from the basement level of the pumping station was observed to have moderate rust. Based on the age, it is assumed that the portion of the piping within the reservoir is a similar
233 | 3 | The asset was observed to be in fair condition. The limited portion visible from the basement level of the pumping station was observed to have moderate rust. Based on the age, it is assumed that the portion of the piping within the reservoir is a similar
234 | 3 | The asset was observed to be in fair condition. The limited portion visible from the basement level of the pumping station was observed to have moderate rust. Based on the age, it is assumed that the portion of the piping within the reservoir is a similar
235 | 3 | The asset was observed to be in fair condition. The limited portion visible from the basement level of the pumping station was observed to have moderate rust. Based on the age, it is assumed that the portion of the piping within the reservoir is a similar
236 | 3 | The asset was observed to be in fair condition. The limited portion visible from the basement level of the pumping station was observed to have moderate rust. Based on the age, it is assumed that the portion of the piping within the reservoir is a similar
237 | 3 | The asset was observed to be in fair condition. The limited portion visible from the basement level of the pumping station was observed to have moderate rust. Based on the age, it is assumed that the portion of the piping within the reservoir is a similar
238 | 2 | The asset was observed to be in good condition.

## Sheet1
ParentID | Comment1 | Comment2 | Comment3 | Comment4 | Comment5 | Comment6 | Comment7 | Comment8 | Comment9 | Comment10
1 | very minor localized corrosion | very minor localized corrosion
2 | Good
3 | Although the system is recently installed, SCADAPack is an outdated model. We recommend the Region to eventually transition toward Allen-Bradley Compactlogix as per Region's standard. The enclosure and ducts can be reused for another 10 years. | dust | Although the system is recently installed, SCADAPack is an outdated model. We recommend the Region to eventually transition toward Allen-Bradley Compactlogix as per Region's standard. The enclosure and ducts can be reused for another 10 years. | dust
4 | Good
5 | corroded bolts | corroded bolts
6 | Good
7
8 | dust | dust
9 | Good
10 | Good | The tanks appeared to be empty at the time of inspection. The tanks should remain within the containment wall, although the existing containment area appears too small to fit all tanks. | Good
11 | minor surface corrosion
12 | Good | Good
13 | Good
14 | Good
15 | good
16 | Good
17 | Good
18 | good
19 | Potential Duplicate Asset
20 | good
21 | Good
22 | Corrosion
23 | Corrosion | Corrosion
24 | This entry is for the valve only. The actuator is inventoried separately under Process Electrical assets | Good | Good
25 | corroded bolts
26 | Minor corrosion of flanges
27 | Good
28 | Good | Good
29 | Good
30 | Good | Good
31 | Good | Good
32 | Good
33 | Good
34 | Good
35 | The asset was assumed to be in good condition. This particular air relief valve could not be identified due to a lack of tags, but all air relief valves were the same age.
36 | Good | Good
37 | Good
38 | Good | Good
39 | Good
40 | The pressure transmitter was in poor condition with corrosion observed. It should to be replaced within the next year. | The pressure transmitter was in poor condition with corrosion observed. It should to be replaced within the next year.
41 | Corrosion | The flow meter was in poor condition and is an outdated model. It should be replaced in the next year.
42 | Good
43
44 | good
45
46 | The asset was observed to be in fair condition. Minor surface corrosion was noted.
47 | This asset was not located on site. All identified check valves were accounted for
48 | Good
49 | Good
50 | Good | Good
51 | Good | Good
52
53
54 | The asset was observed to be in fair condition. Minor surface corrosion was observed.
55 | outdated | outdated
56 | Good | Good
57 | There was an incident that the HVAC in generator room has failed and high temperature generated by the standby generator has caused the conduits to bend. | good
58 | Good
59 | The asset was assumed to be in very good condition based on its age. | Good
60 | The asset was observed to be in fair condition. Minor surface corrosion was noted. | The asset was observed to be in fair condition. Minor surface corrosion was noted.
61 | Good
62 | Good
63 | Good
64 | Good | Good
65 | good
66 | Good
67 | Good
68 | Good
69 | corrosion on sampling tubes
70 | Good | This asset was not located but is assumed to be the same as the other unit heaters within the SCPS.
71 | The asset was observed to be in fair condition. Minor surface corrosion on valve and bolts was observed. | The asset was observed to be in fair condition. Minor surface corrosion on valve and bolts was observed.
72 | The asset was observed to be in good condition. Minor surface corrosion was noted and the bolts were moderately corroded. | The asset was observed to be in good condition. Minor surface corrosion was noted and the bolts were moderately corroded.
73 | Good | The asset did not appear to be original to the facility but the installation date was unknown.
74 | Good | This asset was on a switch leveled Motor Damper 2
75 | Good | This asset was not located but is assumed to be the same as the other unit heaters within the SCPS.
76 | dust
77 | dust | dust
78 | good | good
79 | corrosion | corrosion
80 | corrosion | corrosion
81 | The asset was assumed to be in fair condition based on its age. The pump was not accessible as it was submerged.
82 | Good
83 | Good
84 | The asset was observed to be in good condition. The bolts were severely corroded. | The asset was observed to be in good condition. The bolts were severely corroded.
85 | The tanks appeared to be empty at the time of inspection. The tanks should remain within the containment wall, although the existing containment area appears too small to fit all tanks. | Good | Good
86 | The asset was observed to be in good condition. Minor surface corrosion was noted. | The asset was observed to be in good condition. Minor surface corrosion was noted.
87 | Good | Good
88 | good
89 | Good
90 | The asset was observed to be in good condition. Minor surface deposits were noted. | The asset was observed to be in good condition. Minor surface deposits were noted.
91 | The asset was observed to be in fair condition. Surface corrosion was noted.
92 | minor surface corrosion | minor surface corrosion
93 | Good | Good
94 | The pump was last serviced May 2011 by Advanced Pump Repair Service in Cambridge | The asset was observed to be in fair condition. Moderate corrosion was noted and the pump was spraying droplets onto the floor. | The asset was observed to be in fair condition. Moderate corrosion was noted and the pump was spraying droplets onto the floor. | The pump was last serviced May 2011 by Advanced Pump Repair Service in Cambridge
95 | The pump was last serviced August 2020 by Advanced Pump Repair Service in Cambridge | The pump was last serviced August 2020 by Advanced Pump Repair Service in Cambridge | Good | Good
96 | This asset was removed for service at the time of inspection. The blind flange on the suction side was leaking. | This asset was removed for service at the time of inspection. The blind flange on the suction side was leaking.
97 | Very good | The pump was last serviced in June 2020 by Advanced Pump Repair Service in Cambridge Ontario. | Very good | The pump was last serviced in June 2020 by Advanced Pump Repair Service in Cambridge Ontario.
98 | The dosing pump appears to be relatively new compared to the age of the facility. This model was released in 2010, so the installation year was assumed to be 2010 | good | good | The dosing pump appears to be relatively new compared to the age of the facility. This model was released in 2010, so the installation year was assumed to be 2010
99 | Good | The dosing pump appears to be relatively new compared to the age of the facility. This model was released in 2010, so the installation year was assumed to be 2010
100 | Good
101 | Good | Good
102 | Good | Good
103 | Good | Good
104 | minor surface corrosion | minor surface corrosion
105 | Good | Good
106 | Good | Good
107 | Good | Good
108 | Good | Good
109 | Good | Very good
110 | Good | Good
111 | The asset was observed to be in fair condition. Surface cracks and differential settling were observed. A portion of the driveway on the North side of the lot was recently repaved and was in very good condition.
112 | The asset was observed to be in good condition. Minor corrosion was observed at the base.
113 | The asset was observed to be in good condition. Minor rust was observed at the base.
114 | The asset was observed to be in good condition.
115 | The asset was observed to be in fair condition. The wire was disconnected from the posts at some sections and needs to be re-fastened.
116 | The asset was observed to be in good condition
117 | The asset was asumed to be in good condition based on the portion that was visible and the condition of the other retaining wall on site.
118 | See Drawing C1135-030 | The asset was observed to be in good condition
119 | The asset was assumed to be in good condition based on its age | See Drawing C1135-030 | See Drawing C1135-030 | See Drawing C1135-030. New 450x400 reducer with approx. 2 m of new 400 mm PVC watermain was installed in 2018 off this line to tie into existing 400 mm inlet. | The asset was assumed to be in good condition.
120 | See Drawing C1135-030 | See Drawing C1135-030 | The asset was assumed to be in good condition based on its age | See Drawing C1135-030 | The asset was assumed to be in good condition.
121 | The asset was assumed to be in fair to good condition. The portion visible from the pumping station basement hase moderate surface rusting. | See Drawing C1135-030 | See Drawing C1135-030 | The asset was assumed to be in good condition based on its age | See Drawing C1135-030
122 | See Drawing C1135-030 | The asset was assumed to be in good condition based on its age | See Drawing C1135-030 | The asset was assumed to be in good condition based on its age | See Drawing C1135-030
123 | See Drawing C1135-030 | See Drawing C1135-030 | The asset was assumed to be in good condition based on its age
124 | See Drawing C1135-030 | See Drawing C1135-030 | The asset was assumed to be in good condition based on its age
125 | The asset was assumed to be in good condition based on its age. The catchbasin was inaccessible due to the overgrowth. | See Drawing C1135-030 | See Drawing C1135-030
126 | The asset was assumed to be in good condition based on its age | See Drawing C1135-030 | See Drawing C1135-030
127 | See Drawing C1135-030 | See Drawing C1135-030 | The asset was assumed to be in good condition based on its age
128 | See Drawing C1135-030 | The asset was assumed to be in good condition based on its age | See Drawing C1135-030
129 | See Drawing C1135-030 | See Drawing C1135-030 | The asset was assumed to be in good condition based on its age
130 | Good
131 | Good | Good
132 | Dust
133 | Good
134 | Good | Good
135 | good | good
136 | good | good
137 | good | good
138 | good | good
139 | good | good
140 | good | good
141 | fair | fair
142 | fair | fair
143 | out of service | fair | fair | out of service
144 | fair | fair
145 | to be removed from station
146 | good | good
147 | good | good
148 | good | good
149 | good | good
150 | No performance issues were observed or reported | good
151 | poor | severe corrosion on the bottom of junction box
152 | good | to be replaced with LED fixtures in the next upgrade
153 | to be replaced with LED fixtures in the next upgrade | good
154 | to be replaced with LED fixtures in the next upgrade | good
155 | to be replaced with LED fixtures in the next upgrade | good
156 | to be replaced with LED fixtures in the next upgrade | good
157 | good
158
159 | Paint peeling at door base | moderate corrosion at base of door frame
160
161 | Fair | Generator Room Exterior Door - no weather stripping, damaged sweeper, and through-rust at base of door frame. | Severe paint peeling, minor surface rust on doors, worn wood trim.
162 | Fair | Localized brick spalling (approx. 1 sq m) Localized mortar loss (approx. 2 lm) Steph cracking at southwest corner (approx 5 lm)
163 | Fair | Minor surface rust
164 | Fair | localized paint wear
165 | Good
166 | Fair | Localized paint wear and damage (bending)
167 | Good
168 | Localized spalling at edges | Fair
169 | Good
170 | Good
171 | Good | Poor concrete finishing on exposed interior face - not a structural concern
172 | Good
173 | Good
174 | Fair | Minor localized staining
175 | Fair | Localized step cracking at generator room wall (behind electrical panels). This should be repaired next time the electrical panels are removed from the walls (likely at the end of their service life).
176 | Fair | Top face - shallow spalling (approx 5 sq m) and severe staining along floor gutter. Bottom face - previously repaired holes and cracks (below sodium hypo), new crack at hatch corner (approx. 4 lm).
177 | Good
178 | Poor | Heavy corrosion and discolouration
179 | Good
180 | Fair | localized paint wear and surface rust
181 | Good, The hoist was last inspected in February of 2010. The Region may consider having another inspection done to ensure proper operation.
182 | Good, Based on the condition of the enclosed floor slab (from below), consider adding a protective coating to the interior wall faces within the containment area.
183 | Fair | Localized wear and discolouration (approximately 10% of total area)
184 | Fair | Minor surface wear
185 | The guardrail was in good condition, however kick plates were missing. Missing kick plates are a health and safety issue as tools/ other objects could fall from the upper level to an occupied space below.
186 | Good
187 | Good
188 | Fair | localized cracks with signs of active leakage (approx. 3 lm) Poor concrete finishing on exposed interior face - not a structural concern.
189 | Staining, localized missing paint, and general wear (approximately 30% of total area) | Poor
190 | Good | Poor concrete finishing on exposed interior face - not a structural concern.
191 | Fair | Severe honeycombing at east end of south beam (approx. 1 sq m)
192 | Fair | Minor cracking and surface wear
193 | Good
194 | Fair | General surface wear
195 | Large deep localized spalling (approx. 1 sq m). Localized cracking with signs of leakage (approx. 5 lm). | It is recommended to have this entity inspected from within the tank. | Poor
196 | Fair (age-based) - this entity was not observable on site. | It is recommended to have this entity inspected from within the tank.
197 | Fair | surface corrosion on post base anchors
198 | Fair | Minor surface rust on bolts
199 | Good
200 | Fair | East hatch did not appear to close all the way. Minor corrosion on south hatches. Hatches were only visible from the top.
201 | Good | Good
202 | The waterproofing membrane was not able to be observed, and was assumed to be in fair to poor condition based on its age.
203 | Localized damage at south-west corner of the building. | Poor
204 | Good
205 | Since one of the ladders was removed in 2005 due to corrosion, it is likely that the three remaining ladders are in poor condition. | Poor (based on age and information provided by operations)
206 | Fair (age-based) - this entity was not observable on site. | It is recommended to have this entity inspected from within the tank.
207 | Fair (age-based) - this entity was not observable on site. | It is recommended to have this entity inspected from within the tank.
208
209 | Fair (age-based) - this entity was not observable on site. | It is recommended to have this entity inspected from within the tank.
210 | Fair (age-based) - this entity was not observable on site.
211 | Fair (age-based) - this entity was not observable on site. | It is recommended to have this entity inspected from within the tank.
212 | Dust
213 | The asset was assumed to be in good condition based on its age | See Drawing C1135-030, located southeast of Pumphouse.
214 | Good
215 | The asset was observed to be in good condition. It is clear the asset is not original to the facility so the installation year has been approximated to be 2010.
216 | Good
217 | Good | The backflow preventer was last tested February 2020
218 | Good
219 | Good
220 | Good
221 | Good
222 | Good
223 | Good
224 | Good
225 | Good
226 | Good
227 | Very Good
228 | Good
229 | Good | No performance issues were observed or reported.
230 | Good
231 | Good
232 | The asset was observed to be in fair condition. The limited portion visible from the basement level of the pumping station was observed to have moderate rust. Based on the age, it is assumed that the portion of the piping within the reservoir is a similar
233 | The asset was observed to be in fair condition. The limited portion visible from the basement level of the pumping station was observed to have moderate rust. Based on the age, it is assumed that the portion of the piping within the reservoir is a similar
234 | The asset was observed to be in fair condition. The limited portion visible from the basement level of the pumping station was observed to have moderate rust. Based on the age, it is assumed that the portion of the piping within the reservoir is a similar
235 | The asset was observed to be in fair condition. The limited portion visible from the basement level of the pumping station was observed to have moderate rust. Based on the age, it is assumed that the portion of the piping within the reservoir is a similar
236 | The asset was observed to be in fair condition. The limited portion visible from the basement level of the pumping station was observed to have moderate rust. Based on the age, it is assumed that the portion of the piping within the reservoir is a similar
237 | The asset was observed to be in fair condition. The limited portion visible from the basement level of the pumping station was observed to have moderate rust. Based on the age, it is assumed that the portion of the piping within the reservoir is a similar
238 | Good
239
240
241
242
243
244
245
246
247
248
249
250
251
252
253
254
255
256
257
258
259
260
261
262
263
264
265
266
267
268
269
270
271
272
273
274
275
276
277
278
279
280
281
282
283
284
285
286
287
288
289
290
291
292
293
294
295
296
297
298
299
300
301
302
303
304 | Fair
305 | Fair | minor corrosion on the underside
306 | good
307 | Corrosion noted | Fair
308 | Corrosion noted | Fair
309 | Fair | To be inspected yearly | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
310 | The asset was observed to be in fair condition. It is recommended to be inspected yearly. | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
311 | The asset was observed to be in good condition.
312 | The asset was observed to be in fair condition. It is recommended to inspect the asset yearly. | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
313 | The asset was observed to be in fair condition. It is recommended to inspect the asset yearly. | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
314 | The asset was observed to be in fair condition. The grab bar was loose. | The Grab Bar was loose. Under Ontario Regulation 213/91 this presents a fall hazard.
315 | The asset was in fair condition. It is unknown when the equipment was last inspected. | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
316 | Fair | To be inspected yearly
317 | Fair | Minor corrosion and paint wear
318 | Fair | paint wear
319 | Fair | To be inspected every year | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
320 | Surface corrosion noted on underside | Fair
321 | Fair | To be inspected every year | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
322 | Bent ladder rung | Fair
323 | Corrosion noted | Fair
324 | Weathered paint on exterior and minor corrosion inside | Fair
325 | good
326 | Fair | discoloration of the checker plate
327 | good
328 | Fair | weathered paint
329 | Fair | Minor corrosion
330 | Fair based on age
331 | Peeling paint on exterior and corrosion | Fair
332 | Fair | To be inspected every year | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
333 | good
334 | Staining/corrosion noted | Fair
335 | Fair | Minor corrosion
336 | Fair | minor corrosion
337 | To be inspected every year. As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year. | Fair
338 | Fair
339 | Fixed portion of platform grating was noted to be bent | Fair
340 | Fair
341 | To be inspected every year. As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year. | Fair
342 | Fair | corrosion and paint wear
343 | Fair | Minor corrosion
344 | Flaking/missing on exterior | Fair
345 | Fair | To be inspected every year. As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
346 | Good
347 | Pitting noted | Fair
348 | Fair | To be inspected yearly. As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
349 | Calcium buildup and pitting noted | fair
350 | Fair | paint wear
351 | Fair | minor corrosion
352 | Fair
353 | Fair | Weathered paint and missing paint on exterior
354 | Fair
355 | Fair
356 | Fair | Anchors were corroded
357 | Fair | minor corrosion and staining
358 | Fair | Missing safety grating. The Pump Hatch 1 was missing grating. Under Ontario Regulation 213/91 this presents a fall hazard when the hatches are left open.
359 | Fair | Missing safety grating. The Pump Hatch 1 was missing grating. Under Ontario Regulation 213/91 this presents a fall hazard when the hatches are left open.
360 | Calcium buildup and corrosion noted | Fair
361 | Calcium buildup and corrosion noted | Fair
362 | Gratings now clipped down | Corrosion noted | Fair
363 | Fair | To be inspected every year. As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
364 | The asset was observed to be in fair condition. Minor corrosion was observed.
365 | The asset was observed to be in fair condition. Minor corrosion was observed.
366 | The asset was observed to be in fair condition. Weathered paint on the exterior was observed.
367 | The asset was observed to be in fair condition. Minor corrosion was observed.
368 | The asset was observed to be in fair condition. Surface corrosion was observed.
369 | The asset was observed to be in fair condition. Surface corrosion was noted.
370 | The asset was observed to be in fair condition. It is recommended to be inspected every year. | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
371 | The asset was observed to be in fair condition. Hatch was hard to open due to corrosion on latch.
372 | The asset was observed to be in good condition.
373 | The asset was observed to be in good condition.
374 | The asset was observed to be in fair condition. Calcium buildup was observed.
375 | The asset was observed to be in fair condition. Calcium buildup was observed.
376 | The asset was observed to be in fair condition. Calcium buildup noted
377 | The asset was observed to be in fair condition. Calcium buildup noted
378 | The asset was observed to be in good condition.
379 | The asset was observed to be in good condition. It is unknown when the equipment was last inspected. | As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
380 | The asset was observed to be in good condition.
381 | The asset was assumed to be good as no settlement was observed.
382 | Not visible/inspected. Assumed to be good as no settlement was noted. | Good
383 | Not visible/inspected. Assumed to be good as no settlement was noted.
384 | Not visible/inspected. Assumed to be good as no settlement was noted.
385 | Not visible/inspected. Assumed to be good as no settlement was noted
386 | The asset was observed to be in fair condition. Surface corrosion on underside was observed.
387 | Good
388 | The asset was observed to be in poor condition. Heavy corrosion and deterioration was observed on the service of the valve. The valve was near the end of its expected service life.
389 | The asset was observed to be in fair condition. Surface corrosion was observed.
390 | Poor | The pump was beyond its expected service life
391 | Very Poor | Severe corrosion was observed on the surface of the valve. The valve was beyond its expected service life.
392 | Very Poor | Severe corrosion was observed on the surface of the valve. The valve was beyond its expected service life
393 | Poor | The pump was beyond its expected service life.
394 | Very Poor | Severe corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
395 | Very Poor | Severe corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
396 | Fair | Minor deterioration was observed on the bar screen.
397 | Poor | The pump was beyond its expected service life.
398 | The asset was observed to be in fair condition. The screen was beyond its expected service life.
399 | poor | The pump was beyond its expected service life
400 | Poor | Severe corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
401
402 | Poor | Heavy corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
403 | Very Poor | Severe corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
404 | Fair | Debris is clogging at the bar screen, which in terms start clogging the inlet pipe.
405 | Poor | Corrosion and deterioration was observed on the surface of the valve. The valve was near the end of its expected service life.
406 | Poor | Corrosion and deterioration was observed on the surface of the valve
407
408 | The asset was observed to be in good condition.
409 | The asset was in good condition.
410 | The asset was in good condition.
411 | The asset was in good condition.
412 | The asset was observed to be in fair condition. Corrosion was observed.
413
414 | The asset was observed to be in fair condition. It is approaching the end of its service life and should be replaced.
415 | The asset was observed to be in fair condition. Corrosion was observed.
416 | The asset was observed to be in good condition.
417 | The asset was observed to be in good condition.
418 | The asset was observed to be in good condition.
419 | The asset was observed to be in fair condition.
420 | obsolete | minor corrosion
421 | Obsolete | Corrosion
422 | good | obsolete
423 | good
424 | Dust | good
425 | good | Corrosion
426 | good | Corrosion
427 | good | Corrosion
428 | minor Corrosion
429 | good
430 | good
431 | good
432 | good
433 | very good
434 | good
435 | good | obsolete
436 | good
437 | good
438 | good
439 | Good
440 | good
441 | good
442 | good
443 | good
444 | good
445 | good
446 | good | bolts were not secured properly
447 | good
448 | good
449 | The asset was observed to be in good condition.
450 | The asset was observed to be in good condition.
451 | The asset was observed to be in good condition.
452 | The asset was observed to be in good condition.
453 | The asset was observed to be in good condition.
454 | The asset was observed to be in good condition.
455 | The asset was observed to be in good condition.
456 | The asset was observed to be in good condition.
457 | The asset was in fair condition. Surface corrosion was observed.
458 | The asset was observed to be in good condition. | Shock and arc flash hazard as the existing arc flash label is outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreover, the studies and reports
459 | The asset was observed to be in good condition.
460 | The asset was observed to be in good condition.
461 | The asset was observed to be in good condition. | Shock and arc flash hazard as the existing arc flash label is outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreover, the studies and reports
462 | The asset was observed to be in good condition. | Shock and arc flash hazard as the existing arc flash label is outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreover, the studies and reports
463 | The asset was observed to be in good condition. | Shock and arc flash hazard as the existing arc flash label is outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreover, the studies and reports
464 | The asset was observed to be in good condition.
465 | The asset was observed to be in fair condition. Corrosion on fixtures was observed. The lighting should be replaced with LED in next upgrade
466 | The asset was in fair condition. Corrosion on the surface of the panels as well as circuit breakers was observed. The panel is to be replaced with NEMA 4X enclosure | Shock and arc flash hazard as the existing arc flash label is outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreover, the studies and reports
467 | The asset was observed to be in poor condition. Heavy corrosion was observed.
468 | The asset was observed to be in good condition. To be replaced with led in next upgrade.
469 | The asset was observed to be in fair condition. Bottom of the enclosure was heavily corroded and should be replaced with NEMA 3R enclosure.
470 | The asset was observed to be in good condition. However, the availability of parts and increased maintenance cost will be an issue. It is recommended to replace the pump control within the 10-year plan. Additionally, the Phase converters inside panel shou
471 | The asset was observed to be in good condition. However, the availability of parts and increased maintenance cost will be an issue. It is recommended to replace the control panel within the 10-year plan. | Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servicing, or maintenance while
472 | The asset was observed to be in good condition. However, the availability of parts and increased maintenance cost will be an issue. It is recommended to replace the receptacle within the 10-year plan.
473 | The asset was observed to be in good condition.
474 | The asset was observed to be in good condition. However, the availability of parts and increased maintenance cost will be an issue. It is recommended to replace the main breaker within the 10-year plan. | Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the main breaker which may require examination, adjustment, servicing, or maintenance
475 | The asset was observed to be in good condition. However, the availability of parts and increased maintenance cost will be an issue. It is recommended to replace the transfer switch within the 10-year plan. | Shock and arc flash hazard as no arc flash label was installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the manual transfer switch which may require examination, adjustment, servicing, or ma
476 | The asset was observed to be in good condition. However, in order to provide accessibility to hydro personnel, it is recommended to move the meter above ground.
477 | The asset was observed to be in good condition. Replace with LED fixture in next upgrade.
478 | The asset was observed to be in fair condition. The model has been discontinued. | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the breaker which may require examination, adjustment, servicing, or maintenance while
479 | The asset was observed to be in good condition. The model has been discontinued.
480 | The asset was observed to be in good condition. The model has been discontinued.
481 | The asset was observed to be in fair condition. Corrosion was observed inside and on surface of the panel. It was missing arc flash labels. | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servicing, or maintenance while e
482 | The asset was observed to be in good condition.
483 | The asset was observed to be in fair condition. The panel was corroded.
484 | The asset was observed to be in good condition. However, availability of spare parts and increased maintenance cost will be an issue. It is therefore recommended to replace the asset in the next 10-years. | Shock and arc flash hazard as the existing arc flash label is outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreover, the studies and reports
485 | good
486 | good
487 | good
488 | good
489 | good | replace with LED fixtures rated for class 1, div 2
490 | good | inside the panel is not getting drained properly
491 | fair | replace with NEMA 4X panel
492 | good
493 | good | missing arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servicin
494 | good
495 | good | missing arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the receptacle which may require examination, adjustment, ser
496 | good | replace with LED in next upgrade
497 | fair | misplaced arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servic | Pump #1 breaker to be sized and replaced according to OESC-2018
498 | good
499 | fair | bottom of interior has corroded | replace with NEMA 3R enclosure in next upgrade
500 | good | missing arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servicin
501 | good
502 | good | missing arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servicin
503 | good | fair | replace with LED fixture in next upgrade. To be rated for class 1, div 2
504 | fair | bottom of interior was corroded | missing arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servicin
505 | fair | top surface and doors were corroded | to be replaced with NEMA 3R enclosure
506 | good | outdated arc flash label. Shock and arc flash hazard as the existing arc flash label are outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreove
507 | good
508 | good
509 | good
510 | good | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the switch which may require examination, adjustment, servicing, or maintenance while
511 | poor | severely corroded
512 | good
513 | good | misplaced and outdated arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the VFD breaker which may require examination,
514 | good
515 | good | misplaced and outdated arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the VFD breaker which may require examination,
516 | good | misplaced and outdated arc flash label. Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the VFD breaker which may require examination,
517 | good
518 | good | replace with LED in next upgrade
519 | fair | to be replaced with LED
520 | fair | to be replaced with LED
521 | good
522 | fair | to have separate Main DS, MTS, and CP | outdated arc flash label. Shock and arc flash hazard as the existing arc flash label are outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreove
523 | fair
524 | good
525 | good
526 | good
527 | good
528 | good | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the control panel which may require examination, adjustment, servicing, or maintenance
529 | good | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the control panel which may require examination, adjustment, servicing, or maintenance
530 | good
531 | fair | one of the lights doesn’t work | to be replaced with LED
532 | fair | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the panel which may require examination, adjustment, servicing, or maintenance while e
533 | fair | it doesn't work
534 | fair | to be replaced with LED
535 | fair | to be replaced with NEMA 3R enclosure
536 | good
537 | good
538 | good
539 | good | replace with separate main DS, MTS and CP | Shock and arc flash hazard as the existing arc flash label are outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreover, the studies and reports
540 | good
541 | The asset was observed to be in good condition. | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the MTS which may require examination, adjustment, servicing, or maintenance while ene
542 | The asset was observed to be in good condition.
543 | The asset was observed to be in good condition. | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the MTS which may require examination, adjustment, servicing, or maintenance while ene
544 | The asset was observed to be in good condition.
545 | The asset was observed to be in fair condition. It is recommended to replace with led fixtures rated for class 1, div 2.
546 | The asset was observed to be in fair condition. The panel was aged and minor surface corrosion was observed. | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2. Arc Flash label is required for the panel which may require examination, adjustment, servicing, or maintenance while
547 | The asset was observed to be in fair condition. The top of the panel was damaged. Some repair work was completed to cover the damaged spots; however, it appears that the damaged spots were not sealed properly.
548 | The asset was observed to be in good condition.
549 | The asset was observed to be in good condition. | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the control panel which may require examination, adjustment, servicing, or maintenance
550 | The asset was observed to be in good condition. | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the lighting panel which may require examination, adjustment, servicing, or maintenanc
551 | The asset was observed to be in good condition. Replace with VFD in next upgrade. | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the pump capacitors which may require examination, adjustment, servicing, or maintenan
552 | The asset was observed to be in good condition. | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the main breaker which may require examination, adjustment, servicing, or maintenance
553 | The asset was observed to be in good condition.
554 | The asset was observed to be in good condition. | Shock and arc flash hazard as no arc flash label were installed. As per (Ontario Electrical Safety Code (OESC)) Section2-306.1 & 2-306.2 Arc Flash label is required for the switch which may require examination, adjustment, servicing, or maintenance while
555 | The asset was observed to be in good condition.
556 | The asset was observed to be in good condition.
557 | The asset was observed to be in good condition.
558 | There was no manual transfer station installed at the station. It is recommended to install the manual transfer switch to ensure the station is being powered by one power source (either hydro or generator). Additionally, the MTS provides a safe mean to sw
559 | There was no Generator Connection Receptacle and Manual Transfer Switch located on site. It is recommended to install Generator Connection Receptacle as hardwiring the generator for emergency power parallel power source may cause a severe electrical shoc | Paralleling power sources and severe electrical shock hazard while hardwiring the generator for emergency power
560 | There was no main fused disconnect switch installed at the station. It is recommended to install the main disconnect switch to allow operators to safely isolate the station from hydro to install, maintain and repair any electrical equipment (electrical, m
561 | There was no Power meter installed on site. It is recommended to install a power meter to measure and display power consumption of the station. The power meter should be instated above ground for ease of operation/access and compatibility with industry’s
562 | There was no manual transfer station installed at the station. It is recommended to install the manual transfer switch to ensure the station is being powered by one power source (either hydro or generator). Additionally, the MTS provides a safe mean to sw
563 | There was no main fused disconnect switch installed at the station. It is recommended to install the main disconnect switch to allow operators to safely isolate the station from hydro to install, maintain and repair any electrical equipment (electrical, m
564 | There was no Generator Connection Receptacle and Manual Transfer Switch located on site. It is recommended to install Generator Connection Receptacle as hardwiring the generator for emergency power parallel power source may cause a severe electrical shoc | Paralleling power sources and severe electrical shock hazard while hardwiring the generator for emergency power. It is recommended to install generator receptacle above ground to comply with industry practice
565 | The asset was in fair condition. Moderate corrosion was observed.
566 | The asset was in good condition
567 | The asset was in good condition overall. Paint peeling was observed.
568
569 | The vent piping was in fair condition. Paint peeling at the portion above the wet well was observed.
570 | The asset was observed to be in good condition.
571
572 | The asset was observed to be in good condition.
573 | The asset was observed to be in fair condition. Paint peeling was observed.
574 | The asset was in good condition overall. Staining at the bottom section of the pipe was observed.
575 | good
576 | Surface corrosion
577 | good
578 | good
579 | good
580 | good
581 | Severe corrosion
582 | Missing gooseneck vent and bird screen.
583 | surface corrosion
584 | Surface corrosion
585 | good
586 | good
587 | miscellaneous surface staining
588
589 | good
590 | good
591
592 | paint peeling | fair
593 | good
594 | good
595 | good
596 | The asset was observed to be in good condition, however, it was approaching the end of its useful service life and should be replaced
597 | surface corrosion
598 | The asset was observed to be in fair condition. Minor surface corrosion and wear on the casing was observed.
599 | The asset was observed to be in fair condition. Operability of the asset was unknown.
600 | good
601 | good
602 | good
603 | Good
604 | good
605 | The asset was observed to be in good condition.
606 | The asset was observed to be in good condition.
607 | The asset was observed to be in good condition.
608 | The asset was observed to be in good condition.
609 | There was no yard hydrant located on site. | In accordance with Section 19.8.3 of the Region's Water and Wastewater Design Manual (January 2012), a yard hydrant complete with a backflow preventer with a 37.5mm water service line shall be provided for flushing and cleaning purposes. It is recommended
610 | The asset was observed to be in good condition.
611 | Good
612 | Good
613 | Good
614 | Good
615 | Good
616 | In accordance with Section 19.8.3 of the Region's Water and Wastewater Design Manual (January 2012), a yard hydrant complete with a backflow preventer with a 37.5mm water service line shall be provided for flushing and cleaning purposes. It is recommended
617 | The asset was observed to be in good condition.
618 | The asset was observed to be in good condition.
619 | The asset was observed to be in good condition.
620 | The asset was observed to be in fair condition.
621 | The asset was observed to be in good condition.
622 | Fair | Minor surface rust and defects
623 | In accordance with Section 19.8.3 of the Region's Water and Wastewater Design Manual (January 2012), a yard hydrant complete with a backflow preventer with a 37.5mm water service line shall be provided for flushing and cleaning purposes. It is recommended
624 | The asset was observed to be in good condition.
625 | The asset was observed to be in good condition.
626 | The asset was observed to be in good condition.
627
628
629 | The asset was assumed to be in fair condition based on its age.
630 | The asset was observed to be in good condition. | Shock and arc flash hazard as the existing arc flash label is outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreover, the studies and reports
631
632
633
634
635
636
637
638
639
640
641
642
643
644
645
646
647
648
649
650
651 | Fair | Overgrown vegetation
652 | The asset was in poor condition. Heavy corrosion and deterioration was observed.
653
654
655 | The asset was observed to be in fair condition. Minor surface corrosion and deterioration was noted. However, internal inspection of the piping was not undertaken.
656
657 | The asset was observed to be in good condition. Minor paint wear was observed.
658 | The asset was observed to be in fair condition. Moderate corrosion on the surface of the pipe was observed.
659 | There was no overflow installed at the station. As per the Region’s Water and Wastewater Facilities Design Manual (Halton Region, January 2012) an emergency overflow shall be provided for all wastewater pumping stations.
660
661 | The Cathodic Protection was assumed to be in good condition. The installation of the cathodic protection system was assumed to coincide with the installation of the above grade panel.
662
663 | Fair | Minor corrosion
664
665 | Fair | Minor corrosion
666 | Fair | Corrosion
667 | The Cathodic Protection was assumed to be in good condition. The installation of the cathodic protection system was assumed to coincide with the installation of the above grade panel.
668 | Missing exhaust fan | As per Section 7.2.9 of MOECC's Design Guidelines for Sewage Works, mechanical ventilation is required for below ground surface dry well.
669 | Not observed
670 | The asset was assumed to be in fair condition based on its age.
671 | Poor | Heavy corrosion and deterioration was observed
672
673
674
675
676
677
678
679
680
681
682
683
684
685
686
687
688
689
690
691
692
693
694
695
696
697
698
699
700
701
702
703
704
705
706
707
708
709
710
711
712
713
714
715
716
717
718
719
720
721
722
723
724
725
726
727
728
729
730
731
732
733
734
735
736
737
738
739
740
741
742
743
744
745
746
747
748
749
750
751
752
753
754
755
756
757
758
759
760
761
762
763
764
765
766
767
768
769
770
771
772
773
774
775
776
777
778
779
780
781
782
783
784
785
786
787
788
789
790
791
792
793
794
795
796
797
798
799
800
801
802
803
804
805
806
807
808
809
810
811
812
813
814
815
816
817
818
819
820
821
822
823
824
825
826
827
828
829
830
831
832
833
834
835
836
837
838
839
840
841
842
843
844
845
846
847
848
849
850
851
852
853
854
855
856
857
858
859
860
861
862
863
864
865
866
867
868
869
870
871
872
873
874
875
876
877
878
879
880
881
882
883
884
885
886
887
888
889
890
891
892
893
894
895
896
897
898
899
900
901
902
903
904
905
906
907
908
909
910
911
912
913
914
915
916
917
918
919
920
921
922
923
924
925
926
927
928
929
930
931
932
933
934
935
936
937
938
939
940
941
942
943
944
945
946
947
948
949
950
951
952
953
954
955
956
957
958
959
960
961
962
963
964
965
966
967
968
969
970
971
972
973
974
975
976
977
978
979
980
981
982
983
984
985
986
987
988
989
990
991
992
993
994
995
996
997
998
999
1000
1001
1002
1003
1004
1005
1006
1007
1008
1009
1010
1011
1012
1013
1014
1015
1016
1017
1018
1019
1020
1021
1022
1023
1024
1025
1026
1027
1028
1029
1030
1031
1032
1033
1034
1035
1036
1037
1038
1039
1040
1041
1042
1043
1044
1045
1046
1047
1048
1049
1050
1051
1052
1053
1054
1055
1056
1057
1058
1059
1060
1061
1062
1063
1064
1065
1066
1067
1068
1069
1070
1071
1072
1073
1074
1075
1076
1077
1078
1079
1080
1081
1082
1083
1084
1085
1086
1087
1088
1089
1090
1091
1092
1093
1094
1095
1096
1097
1098
1099
1100
1101
1102
1103
1104
1105
1106
1107
1108
1109
1110
1111
1112
1113
1114
1115
1116
1117
1118
1119
1120
1121
1122
1123
1124
1125
1126
1127
1128
1129
1130
1131
1132
1133
1134
1135
1136
1137
1138
1139
1140
1141
1142
1143
1144
1145
1146
1147
1148
1149
1150
1151
1152
1153
1154
1155
1156
1157
1158
1159
1160
1161
1162
1163
1164
1165
1166
1167
1168
1169
1170
1171
1172
1173
1174
1175
1176
1177
1178
1179
1180
1181
1182
1183
1184
1185
1186
1187
1188
1189
1190
1191
1192
1193
1194
1195
1196
1197
1198
1199
1200
1201
1202

## import
ParentID | CommentType | Comment
1 | Condition Comment | The asset was observed to be in good condition. Very minor localized corrosion was observed.
2 | Condition Comment | The asset was observed to be in good condition.
3 | Condition Comment | The asset was observed to be in fair condition. Although the system is recently installed, SCADA Pack is an outdated model. We recommend the Region to eventually transition toward Allen-Bradley Compactlogix as per Region's standard. The enclosure and ducts can be reused for another 10 years.
4 | Condition Comment | The asset was observed to be in good condition.
5 | Condition Comment | The asset was observed to be in good condition. Corroded bolts were observed.
6 | Condition Comment | The asset was observed to be in good condition.
7 | Condition Comment | The asset was assumed to be in fair condition.
8 | Condition Comment | The asset was observed to be in good condition. Dust was observed.
9 | Condition Comment | The asset was observed to be in good condition.
10 | Condition Comment | The asset was observed to be in good condition. The tanks appeared to be empty at the time of inspection. The tanks should remain within the containment wall, although the existing containment area appears too small to fit all tanks.
11 | Condition Comment | The asset was observed to be in good condition. Minor surface corrosion was noted.
12 | Condition Comment | The asset was observed to be in good condition.
13 | Condition Comment | The asset was observed to be in good condition.
14 | Condition Comment | The asset was observed to be in good condition.
15 | Condition Comment | The asset was observed to be in good condition.
16 | Condition Comment | The asset was observed to be in good condition.
17 | Condition Comment | The asset was observed to be in good condition.
18 | Condition Comment | The asset was observed to be in good condition.
19 | Condition Comment | The asset was assumed to be in fair condition as it might be a potential duplicate asset.
20 | Condition Comment | The asset was observed to be in good condition.
21 | Condition Comment | The asset was observed to be in good condition.
22 | Condition Comment | The asset was observed to be in fair condition as corrosion was noted.
23 | Condition Comment | The asset was observed to be in fair condition as corrosion was noted.
24 | Condition Comment | The asset was observed to be in good condition. This entry is for the valve only. The actuator is inventoried separately under Process Electrical assets
25 | Condition Comment | The asset was observed to be in fair condition. Corroded bolts were observed.
26 | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed on the flanges.
27 | Condition Comment | The asset was observed to be in good condition.
28 | Condition Comment | The asset was observed to be in good condition.
29 | Condition Comment | The asset was observed to be in good condition.
30 | Condition Comment | The asset was observed to be in good condition.
31 | Condition Comment | The asset was observed to be in good condition.
32 | Condition Comment | The asset was observed to be in good condition.
33 | Condition Comment | The asset was observed to be in good condition.
34 | Condition Comment | The asset was observed to be in good condition.
35 | Condition Comment | The asset was assumed to be in good condition. This particular air relief valve could not be identified due to a lack of tags, but all air relief valves were the same age.
36 | Condition Comment | The asset was observed to be in good condition.
37 | Condition Comment | The asset was observed to be in good condition.
38 | Condition Comment | The asset was observed to be in good condition.
39 | Condition Comment | The asset was observed to be in good condition.
40 | Condition Comment | The pressure transmitter was in poor condition with corrosion observed. It should to be replaced within the next year.
41 | Condition Comment | The asset was observed to be in fair condition. Corrosion was noted.
42 | Condition Comment | The asset was observed to be in good condition.
43 | Condition Comment | The asset was assumed to be in fair condition.
44 | Condition Comment | The asset was observed to be in good condition.
45 | Condition Comment | The asset was assumed to be in fair condition.
46 | Condition Comment | The asset was observed to be in fair condition. Minor surface corrosion was noted.
47 | Condition Comment | The asset was assumed to be in fair condition as it was not located on site.
48 | Condition Comment | The asset was observed to be in good condition.
49 | Condition Comment | The asset was observed to be in good condition.
50 | Condition Comment | The asset was observed to be in good condition.
51 | Condition Comment | The asset was observed to be in good condition.
52 | Condition Comment | The asset was assumed to be in fair condition.
53 | Condition Comment | The asset was assumed to be in fair condition.
54 | Condition Comment | The asset was observed to be in fair condition. Minor surface corrosion was observed.
55 | Condition Comment | The asset was observed to be in fair condition. It was outdated.
56 | Condition Comment | The asset was observed to be in good condition.
57 | Condition Comment | The asset was observed to be in fair condition. There was an incident that the HVAC in generator room has failed and high temperature generated by the standby generator has caused the conduits to bend.
58 | Condition Comment | The asset was observed to be in good condition.
59 | Condition Comment | The asset was assumed to be in very good condition based on its age.
60 | Condition Comment | The asset was observed to be in fair condition. Minor surface corrosion was noted.
61 | Condition Comment | The asset was observed to be in good condition.
62 | Condition Comment | The asset was observed to be in good condition.
63 | Condition Comment | The asset was observed to be in good condition.
64 | Condition Comment | The asset was observed to be in good condition.
65 | Condition Comment | The asset was observed to be in good condition.
66 | Condition Comment | The asset was observed to be in good condition.
67 | Condition Comment | The asset was observed to be in good condition.
68 | Condition Comment | The asset was observed to be in good condition.
69 | Condition Comment | The asset was observed to be in fair condition. Corrosion was observed on sampling tubes.
70 | Condition Comment | The asset was observed to be in good condition.
71 | Condition Comment | The asset was observed to be in fair condition. Minor surface corrosion on valve and bolts was observed.
72 | Condition Comment | The asset was observed to be in good condition. Minor surface corrosion was noted and the bolts were moderately corroded.
73 | Condition Comment | The asset was observed to be in good condition.
74 | Condition Comment | The asset was observed to be in good condition.
75 | Condition Comment | The asset was observed to be in good condition.
76 | Condition Comment | The asset was observed to be in good condition. Dust was noted.
77 | Condition Comment | The asset was observed to be in good condition. Dust was noted.
78 | Condition Comment | The asset was observed to be in good condition.
79 | Condition Comment | The asset was observed to be in fair condition. Corrosion was noted.
80 | Condition Comment | The asset was observed to be in fair condition. Corrosion was noted.
81 | Condition Comment | The asset was assumed to be in fair condition based on its age. The pump was not accessible as it was submerged.
82 | Condition Comment | The asset was observed to be in good condition.
83 | Condition Comment | The asset was observed to be in good condition.
84 | Condition Comment | The asset was observed to be in good condition. The bolts were severely corroded.
85 | Condition Comment | The asset was observed to be in good condition. The tanks appeared to be empty at the time of inspection. The tanks should remain within the containment wall, although the existing containment area appears too small to fit all tanks.
86 | Condition Comment | The asset was observed to be in good condition. Minor surface corrosion was noted.
87 | Condition Comment | The asset was observed to be in good condition.
88 | Condition Comment | The asset was observed to be in good condition.
89 | Condition Comment | The asset was observed to be in good condition.
90 | Condition Comment | The asset was observed to be in good condition. Minor surface deposits were noted.
91 | Condition Comment | The asset was observed to be in fair condition. Surface corrosion was noted.
92 | Condition Comment | The asset was observed to be in fair condition. Minor surface corrosion was noted.
93 | Condition Comment | The asset was observed to be in good condition.
94 | Condition Comment | The asset was observed to be in fair condition. Moderate corrosion was noted and the pump was spraying droplets onto the floor. It was last serviced May 2011 by Advanced Pump Repair Service in Cambridge
95 | Condition Comment | The asset was observed to be in good condition. The pump was last serviced August 2020 by Advanced Pump Repair Service in Cambridge
96 | Condition Comment | The asset was observed to be in fair condition. It was removed for service at the time of inspection. The blind flange on the suction side was leaking.
97 | Condition Comment | The asset was observed to be in very good condition.
98 | Condition Comment | The asset was observed to be in good condition. It appeared to be relatively new compared to the age of the facility. This model was released in 2010, so the installation year was assumed to be 2010.
99 | Condition Comment | The asset was observed to be in good condition.
100 | Condition Comment | The asset was observed to be in good condition.
101 | Condition Comment | The asset was observed to be in good condition.
102 | Condition Comment | The asset was observed to be in good condition.
103 | Condition Comment | The asset was observed to be in good condition.
104 | Condition Comment | The asset was observed to be in fair condition. Minor surface corrosion was noted.
105 | Condition Comment | The asset was observed to be in good condition.
106 | Condition Comment | The asset was observed to be in good condition.
107 | Condition Comment | The asset was observed to be in good condition.
108 | Condition Comment | The asset was observed to be in good condition.
109 | Condition Comment | The asset was observed to be in good condition.
110 | Condition Comment | The asset was observed to be in good condition.
111 | Condition Comment | The asset was observed to be in fair condition. Surface cracks and differential settling were observed. A portion of the driveway on the North side of the lot was recently repaved and was in very good condition.
112 | Condition Comment | The asset was observed to be in good condition. Minor corrosion was observed at the base.
113 | Condition Comment | The asset was observed to be in good condition. Minor rust was observed at the base.
114 | Condition Comment | The asset was observed to be in good condition.
115 | Condition Comment | The asset was observed to be in fair condition. The wire was disconnected from the posts at some sections and needs to be re-fastened.
116 | Condition Comment | The asset was observed to be in good condition.
117 | Condition Comment | The asset was assumed to be in good condition based on the portion that was visible and the condition of the other retaining wall on site.
118 | Condition Comment | The asset was observed to be in good condition.
119 | Condition Comment | The asset was assumed to be in good condition based on its age.
120 | Condition Comment | The asset was assumed to be in good condition based on its age.
121 | Condition Comment | The asset was assumed to be in fair to good condition. The portion visible from the pumping station basement hase moderate surface rusting.
122 | Condition Comment | The asset was assumed to be in good condition based on its age.
123 | Condition Comment | The asset was assumed to be in good condition based on its age.
124 | Condition Comment | The asset was assumed to be in good condition based on its age.
125 | Condition Comment | The asset was assumed to be in good condition based on its age. The catchbasin was inaccessible due to the overgrowth.
126 | Condition Comment | The asset was assumed to be in good condition based on its age.
127 | Condition Comment | The asset was assumed to be in good condition based on its age.
128 | Condition Comment | The asset was assumed to be in good condition based on its age.
129 | Condition Comment | The asset was assumed to be in good condition based on its age.
130 | Condition Comment | The asset was observed to be in good condition.
131 | Condition Comment | The asset was observed to be in good condition.
132 | Condition Comment | The asset was observed to be in good condition. Dust was observed.
133 | Condition Comment | The asset was observed to be in good condition.
134 | Condition Comment | The asset was observed to be in good condition.
135 | Condition Comment | The asset was observed to be in good condition.
136 | Condition Comment | The asset was observed to be in good condition.
137 | Condition Comment | The asset was observed to be in good condition.
138 | Condition Comment | The asset was observed to be in good condition.
139 | Condition Comment | The asset was observed to be in good condition.
140 | Condition Comment | The asset was observed to be in good condition.
141 | Condition Comment | The asset was observed to be in fair condition based on its age.
142 | Condition Comment | The asset was observed to be in fair condition based on its age.
143 | Condition Comment | The asset was in fair condition. It was out of service.
144 | Condition Comment | The asset was observed to be in fair condition based on its age.
145 | Condition Comment | The asset was to be removed from the station.
146 | Condition Comment | The asset was observed to be in good condition.
147 | Condition Comment | The asset was observed to be in good condition.
148 | Condition Comment | The asset was observed to be in good condition.
149 | Condition Comment | The asset was observed to be in good condition.
150 | Condition Comment | The asset was observed to be in good condition.
151 | Condition Comment | The asset was in poor condition. Severe corrosion on the bottom of junction box.
152 | Condition Comment | The asset was observed to be in good condition. It's to be replaced with LED fixtures in the next upgrade.
153 | Condition Comment | The asset was observed to be in good condition. It's to be replaced with LED fixtures in the next upgrade.
154 | Condition Comment | The asset was observed to be in good condition. It's to be replaced with LED fixtures in the next upgrade.
155 | Condition Comment | The asset was observed to be in good condition. It's to be replaced with LED fixtures in the next upgrade.
156 | Condition Comment | The asset was observed to be in good condition. It's to be replaced with LED fixtures in the next upgrade.
157 | Condition Comment | The asset was observed to be in good condition.
159 | Condition Comment | The asset was observed to be in fair condition. Paint peeling was observed at the door base. Moderate corrosion was noted at the base of the door frame.
161 | Condition Comment | The asset was observed to be in poor condition. The exterior door had no weather stripping. Damaged sweeper and through-rust was observed at the base of the door frame. Additionally, severe paint peeling, minor surface rust on doors, and worn wood trim were noted.
162 | Condition Comment | The asset was observed to be in fair condition. Paint peeling was observed at the door base. Localized brick spalling (approx. 1 sq m), localized mortar loss (approx. 2 m), and step cracking at southwest corner (approx 5 m) were noted.
163 | Condition Comment | The asset was observed to be in fair condition. Minor surface rust was noted.
164 | Condition Comment | The asset was observed to be in fair condition. Localized paint wear was noted.
165 | Condition Comment | The asset was observed to be in good condition.
166 | Condition Comment | The asset was observed to be in fair condition. Localized paint wear and damage (bending) was noted.
167 | Condition Comment | The asset was observed to be in good condition.
168 | Condition Comment | The asset was observed to be in fair condition. Localized spalling at edges were noted.
169 | Condition Comment | The asset was observed to be in good condition.
170 | Condition Comment | The asset was observed to be in good condition.
171 | Condition Comment | The asset was observed to be in good condition; however, even thought it was not a structural concern, poor concrete finishing on exposed interior face was noted.
172 | Condition Comment | The asset was observed to be in good condition.
173 | Condition Comment | The asset was observed to be in good condition.
174 | Condition Comment | The asset was observed to be in fair condition. Minor localized staining was noted.
175 | Condition Comment | The asset was observed to be in fair condition. Localized step cracking at generator room wall (behind electrical panels) was noted. The defects should be repaired next time the electrical panels are removed from the walls (likely at the end of their service life).
176 | Condition Comment | The asset was observed to be in fair condition. Shallow spalling (approx 5 sq m) and severe staining along floor gutter were observed at the top face. Previously repaired holes and cracks (below sodium hypo) was noted. A new crack at hatch corner (approx. 4 lm) was also noted.
177 | Condition Comment | The asset was observed to be in good condition.
178 | Condition Comment | The asset was observed to be in poor condition. Heavy corrosion and discolouration were noted.
179 | Condition Comment | The asset was observed to be in good condition.
180 | Condition Comment | The asset was observed to be in fair condition. Localized paint wear and surface rust were noted.
181 | Condition Comment | The asset was observed to be in good condition. The hoist was last inspected in February of 2010. The Region may consider having another inspection done to ensure proper operation.
182 | Condition Comment | The asset was observed to be in good condition. Based on the condition of the enclosed floor slab (from below), the Region is recommended to consider adding a protective coating to the interior wall faces within the containment area.
183 | Condition Comment | The asset was observed to be in fair condition. Localized wear and discolouration (approximately 10% of total area) were noted.
184 | Condition Comment | The asset was observed to be in fair condition. Minor surface wear was noted.
185 | Condition Comment | The guardrail was in good condition; however, kick plates were missing. Missing kick plates are a health and safety issue as tools/ other objects could fall from the upper level to an occupied space below.
186 | Condition Comment | The asset was observed to be in good condition.
187 | Condition Comment | The asset was observed to be in good condition.
188 | Condition Comment | The asset was observed to be in fair condition. Localized cracks with signs of active leakage (approx. 3 lm) was noted. Poor concrete finishing on exposed interior face was noted; however, it was not a structural concern.
189 | Condition Comment | The asset was observed to be in poor condition. Staining, localized missing paint, and general wear (approximately 30% of total area) were noted.
190 | Condition Comment | The asset was observed to be in good condition. Poor concrete finishing on exposed interior face was noted; however, it was not a structural concern.
191 | Condition Comment | The asset was observed to be in fair condition. Severe honeycombing at east end of south beam (approx. 1 sq m) was noted.
192 | Condition Comment | The asset was observed to be in fair condition. Minor cracking and surface wear were noted.
193 | Condition Comment | The asset was observed to be in good condition.
194 | Condition Comment | The asset was observed to be in fair condition. General surface wear was noted.
195 | Condition Comment | The asset was observed to be in fair condition. Large deep localized spalling (approx. 1 sq m) and localized cracking with signs of leakage (approx. 5 lm) were noted. It is recommended to have this entity inspected from within the tank.
196 | Condition Comment | The asset was assumed to be in fair condition. It is recommended to have this entity inspected from within the tank.
197 | Condition Comment | The asset was observed to be in fair condition. Surface corrosion on post base anchors was noted.
198 | Condition Comment | The asset was observed to be in fair condition. Minor surface rust was noted on bolts
199 | Condition Comment | The asset was observed to be in good condition.
200 | Condition Comment | The asset was observed to be in fair condition. The hatches were only visible from the top. East hatch did not appear to close all the way. Minor corrosion on south hatches.
201 | Condition Comment | The asset was observed to be in good condition.
202 | Condition Comment | The asset was assumed to be in fair to poor condition based on its age as the waterproofing membrane was not able to be observed.
203 | Condition Comment | The asset was observed to be in poor condition. Localized damage at south-west corner of the building was noted.
204 | Condition Comment | The asset was observed to be in good condition.
205 | Condition Comment | The asset was in poor condition based on age and information provided by operations. Since one of the ladders was removed in 2005 due to corrosion, it is likely that the three remaining ladders are in poor condition.
206 | Condition Comment | The asset was assumed to be in fair condition. It is recommended to have this entity inspected from within the tank.
207 | Condition Comment | The asset was assumed to be in fair condition. It is recommended to have this entity inspected from within the tank.
209 | Condition Comment | The asset was assumed to be in fair condition. It is recommended to have this entity inspected from within the tank.
210 | Condition Comment | The asset was assumed to be in fair condition. It is recommended to have this entity inspected from within the tank.
211 | Condition Comment | The asset was assumed to be in fair condition. It is recommended to have this entity inspected from within the tank.
212 | Condition Comment | The asset was in observed to be in good condition.
213 | Condition Comment | The asset was assumed to be in good condition based on its age
214 | Condition Comment | The asset was in observed to be in good condition.
215 | Condition Comment | The asset was observed to be in good condition. It is clear the asset is not original to the facility so the installation year has been approximated to be 2010.
216 | Condition Comment | The asset was in observed to be in good condition.
217 | Condition Comment | The asset was in observed to be in good condition.
218 | Condition Comment | The asset was in observed to be in good condition.
219 | Condition Comment | The asset was in observed to be in good condition.
220 | Condition Comment | The asset was in observed to be in good condition.
221 | Condition Comment | The asset was in observed to be in good condition.
222 | Condition Comment | The asset was in observed to be in good condition.
223 | Condition Comment | The asset was in observed to be in good condition.
224 | Condition Comment | The asset was in observed to be in good condition.
225 | Condition Comment | The asset was in observed to be in good condition.
226 | Condition Comment | The asset was in observed to be in good condition.
227 | Condition Comment | The asset was in observed to be in very good condition.
228 | Condition Comment | The asset was in observed to be in good condition.
229 | Condition Comment | The asset was in observed to be in good condition.
230 | Condition Comment | The asset was in observed to be in good condition.
231 | Condition Comment | The asset was in observed to be in good condition.
232 | Condition Comment | The asset was observed to be in fair condition. The limited portion visible from the basement level of the pumping station was observed to have moderate rust. Based on the age, it is assumed that the portion of the piping within the reservoir is a similar
233 | Condition Comment | The asset was observed to be in fair condition. The limited portion visible from the basement level of the pumping station was observed to have moderate rust. Based on the age, it is assumed that the portion of the piping within the reservoir is a similar
234 | Condition Comment | The asset was observed to be in fair condition. The limited portion visible from the basement level of the pumping station was observed to have moderate rust. Based on the age, it is assumed that the portion of the piping within the reservoir is a similar
235 | Condition Comment | The asset was observed to be in fair condition. The limited portion visible from the basement level of the pumping station was observed to have moderate rust. Based on the age, it is assumed that the portion of the piping within the reservoir is a similar
236 | Condition Comment | The asset was observed to be in fair condition. The limited portion visible from the basement level of the pumping station was observed to have moderate rust. Based on the age, it is assumed that the portion of the piping within the reservoir is a similar
237 | Condition Comment | The asset was observed to be in fair condition. The limited portion visible from the basement level of the pumping station was observed to have moderate rust. Based on the age, it is assumed that the portion of the piping within the reservoir is a similar
238 | Condition Comment | The asset was observed to be in good condition.