## Final
AssetID | ParentID | AssetName | CoF | AssetDescription | Owner | Status | SiteName | FacilityName | LocationName | AssetCategory | CustomClientCategory | Manufacturer | Model | SerialNumber | InspectionType | AssessmentYear | InstallYear | AvgESL | ReplaceYear | PhotoName | VisualCondition | PerformanceCondition | PoF | TempComments1 | TempComments2 | TempComments3 | TempRehabComment | TempRehabYear | TempRehabCost
113 | 631 | Wet Well Exhaust Fan | 1 | built-in explosion-proof ventilation fan, motor capacity: 0.5 HP | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Building Mechanical | Building Services | N/A | N/A | N/A |  | 2020 | 1988 |  |  | HR-BAES-010 |  |  |  | heavy corrosion
569 | 631 | Wet Well Gooseneck Ventilation Pipes | 1 | Two 4 inch diameter aluminum vents with bird screen | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Building Mechanical | Process Mechanical Equipment | [5 empty] | 1988 |  |  | HR-BAES-002 |  |  |  | paint peeling at the portion above the wet well |  |  | Repaint the ventilation pipes | 2023 | 500
608 | 18 | Yard Hydrant | 1 |  | Halton | In Service | Belaire Dr. PS | WWPS | Site | Site Works | Site Works | [5 empty] | 1988 |  | 2035 | HR-BAES-002 |  |  |  |  | Good
19 | 631 | Wet Well Concrete Structure | 2 | Belaire Dr. PS Wet Well | Halton | In Service | Belaire Dr. PS | WWPS | Process Structural | Process Structural | Building and Process Structural | [5 empty] | 1988 |  | 2048 | HR-BAES-051 |  |  |  | Fair | Concrete spalling and exposed corroded reinforcement |  | Remove loose concrete, clean reinforcement and apply rust inhibiting paint and patch with cementitous repair mortar | 2025 | 2000
288 | 631 | Aluminum Guardrails | 2 |  | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1988 |  | 2048 | HR-BAES-051 |  |  |  | corosion | Fair
287 | 631 | Aluminum Platform | 2 |  | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1988 |  | 2048 | HR-BAES-051 |  |  |  | Fair | corosion on the platform
286 | 631 | Access Ladder | 2 | Platform to wet well base | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1988 |  | 2048 | HR-BAES-051 |  |  |  |  | fair
285 | 631 | Access Ladder | 2 | Entrance to platform | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1988 |  | 2048 | HR-BAES-051 |  |  |  | fair
282 | 631 | Access Hatch | 1 | Belaire Dr. PS Wet Well | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1988 |  | 2048 | HR-BAES-002 |  |  |  | good
228 | 18 | Emergency By-Pass Piping | 3 | 100mm Diameter Ductile Iron Riser piping with end threaded to accpet cap in a junction box. Approx. 3.6m. | Halton | In Service | Belaire Dr. PS | Belaire Dr. PS | Site | Process Mechanical | Process Piping |  |  |  |  | 0 | 1988 | [6 empty] | assumed to be fair
227 | 631 | Pump 2 Discharge Piping | 3 | 100mm Diameter, approx. 2.5m, Class 52 Ductile Iron discharge piping connected to 100mm PVC forcemain | Halton | In Service | Belaire Dr. PS | Belaire Dr. PS | Wet Well | Process Mechanical | Process Piping |  |  |  |  | 0 | 1988 |  |  | HR-BAES-015 |  |  |  | Heavy corrosion | Heavy corrosion and deterioration was observed on the piping
120 | 18 | FORCEMAIN | 4 | 100mm diameter, approx. 73.15m PVC forcemain | Halton | In Service | Belaire Dr. PS | Belaire Dr. PS | Site | Process Mechanical | Process Piping |  |  |  |  | 2020 | 1988 | [6 empty] | assumed to be good
652 | 631 | Pump 1 Discharge Piping | 3 | 100mm Diameter, approx. 2.5m, Class 52 Ductile Iron discharge piping connected to 100mm PVC forcemain | Halton | In Service | Belaire Dr. PS | Belaire Dr. PS | Wet Well | Process Mechanical | Process Piping | [5 empty] | 1988 |  |  | HR-BAES-015 |  |  |  | poor | Heavy corrosion and deterioration was observed on the piping
283 | 631 | Pump Hatch 1 | 1 | Belaire Dr. PS Wet Well | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1988 |  | 2048 | HR-BAES-002 |  |  |  | Fair | HS: Missing hatch grating |  | Install safety grating | 2021 | 1000
314 | 631 | Grab Bar | 2 | Belaire Dr. PS Wet Well | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1988 |  | 2048 | HR-BAES-002 |  |  |  | Fair | HS: Grab bar is loose |  | Tighten as required | 2021 | 100
284 | 631 | Pump Hatch 2 | 1 | Belaire Dr. PS Wet Well | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1988 |  | 2048 | HR-BAES-002 |  |  |  | Fair | HS: Missing hatch grating |  | Install safety grating | 2021 | 1000
313 | 631 | Davit Socket Base | 2 | Belaire Dr. PS Wet Well | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1988 |  | 2048 | HR-BAES-002 |  |  |  | Fair | To be inspected yearly |  | conduct inspection | 2021 | 500
474 | 18 | Main Breaker | 2 | Main Breaker; Westinghouse; Series C FDB; ; 600V, 60A-2P | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Process Electrical | Process Electrical | [5 empty] | 1988 |  | 2030 | IMG_20200702_083922 |  |  |  | good
473 | 18 | Power Meter | 2 | Power Meter; ; ; ; | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Process Electrical | Process Electrical | [5 empty] | 2010 |  | 2040 | IMG_20200702_083914 |  |  |  | good
472 | 18 | Generator Receptacle | 2 | Generator Receptacle; ; ; ; | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Process Electrical | Process Electrical | [5 empty] | 1988 |  |  | IMG_20200702_082805 |  |  |  | good
471 | 18 | Control Logic Panel | 2 | Control Logic Panel; ; ; ; | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Process Electrical | Process Electrical | [5 empty] | 1988 |  | 2030 | IMG_20200702_082805 |  |  |  | good
470 | 18 | Pump Duplex Control | 2 | Pump Duplex Control with Disconnect switch; ; ; ; 120/240V, 3.9HP | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Process Electrical | Process Electrical | [5 empty] | 1988 |  | 2030 | IMG_20200702_083731 |  |  |  | good | phase converters inside panel to be replaced with VFDs
469 | 18 | Electrical Outdoor Enclosure | 2 | Outdoor Enclosure; ; ; ; | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Process Electrical | Process Electrical | [5 empty] | 1988 |  | 2030 | IMG_20200702_082737 |  |  |  | fair | bottom of the enclosre is severly corroded | to be replaced with NEMA 3R enclosure
467 | 631 | Wet Well Lighting | 1 | Lighting; ; ; ; | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Building Electrical | Building Services | [5 empty] | 1988 |  | 2022 | HR-BAES-040 |  |  |  | poor | heaviliy corroded
475 | 18 | Manual Transfer Switch | 2 | Manual Transfer Switch; GE; ; ; 600V, 60A | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Process Electrical | Process Electrical | [5 empty] | 1988 |  | 2030 | IMG_20200702_083922 |  |  |  | good
468 | 18 | Panel Outdoor Light | 1 | Pole Light; ; ; ; | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Building Electrical | Building Services | [5 empty] | 1988 |  | 2030 | IMG_20200702_082700 |  |  |  | good | to be replaced with LED in next upgrade
416 | 631 | Wet Well Level Transmitter | 2 | Wet Well Level Transmitter; Siemens Milltronics; Multiranger 200; ; ; | Halton | In Service | Belaire Dr. PS | WWPS | Site | Process Instrumentation | Process Instrumentation | [5 empty] | 2014 |  | 2030 | HR-BAES-054 |  |  |  |  | Dust
418 | 631 | Wet Well Floats | 2 | Wet Well Floats; ; ; ; ; | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Process Instrumentation | Process Instrumentation | [5 empty] | 2016 |  | 2030 | HR-BAES-036 |  |  |  | Corrosion
417 | 18 | Remote Signals Telephone Transmitter | 1 | Remote Signals Telephone Transmitter; Pribusin; IUC-X9-TXC; ; ; | Halton | In Service | Belaire Dr. PS | WWPS | Site | Process Instrumentation | Process Instrumentation | [5 empty] | 2016 |  | 2030 | HR-BAES-055 |  |  |  | Dust
119 | 631 | SEWAGE LIFT PUMP #2 DISCHARGE VALVE | 2 | Gate Valve #1 with Handwheel;;;;100 mm | Halton | In Service | Belaire Dr. PS | Belaire Dr. PS | Wet Well | Process Mechanical | Process Mechanical Equipment | CRANE | GATE VALVE | N/A |  | 2020 | 1988 |  |  | HR-BAES-006 |  |  |  | Poor | Heavy corrosion and deterioration was observed on the service of the valve. The valve was near the end of its expected service life.
115 | 631 | SEWAGE LIFT PUMP #1 CHECK VALVE | 2 | Check Valve #1;;;;100 mm | Halton | In Service | Belaire Dr. PS | Belaire Dr. PS | Wet Well | Process Mechanical | Process Mechanical Equipment | JENKINS-McAVITY | N/A | N/A |  | 2020 | 1988 |  |  | HR-BAES-009 |  |  |  | Poor | Heavy corrosion and deterioration was observed on the service of the valve. The valve was near the end of its expected service life.
388 | 19 | VALVE DISCHARGE FORCEMAIN | 2 | Gate Valve #3 with Handwheel;;;;100 mm | Halton | In Service | Belaire Dr. PS | Belaire Dr. PS | Wet Well |  | Process Mechanical Equipment | [5 empty] | 1988 |  |  | HR-BAES-005 |  |  |  | Poor | Severe corrosion and deterioration was observed on the service of the valve. The valve was near the end of its expected service life.
117 | 631 | SEWAGE LIFT PUMP #2 | 2 | Sewage Pump #1;Flygt;CP 3085;;6.3 L/s at 4.7 m TDH 2 HP | Halton | In Service | Belaire Dr. PS | Belaire Dr. PS | Wet Well | Process Mechanical | Process Mechanical Equipment | FLYGT | C3102-180 | L07288 |  | 2020 | 1988 |  |  | HR-BAES-015 |  |  |  | Poor | The pump is working but it is near the end of its expected service life.
116 | 631 | SEWAGE LIFT PUMP #1 DISCHARGE VALVE | 2 | Gate Valve #1 with Handwheel;;;;100 mm | Halton | In Service | Belaire Dr. PS | Belaire Dr. PS | Wet Well | Process Mechanical | Process Mechanical Equipment | CRANE | GATE VALVE | N/A |  | 2020 | 1988 |  |  | HR-BAES-008 |  |  |  | Poor | Heavy corrosion and deterioration was observed on the service of the valve. The valve was near the end of its expected service life.
118 | 631 | SEWAGE LIFT PUMP #2 CHECK VALVE | 2 | Check Valve #1;;;;100 mm | Halton | In Service | Belaire Dr. PS | Belaire Dr. PS | Wet Well | Process Mechanical | Process Mechanical Equipment | MCAVITY | SWING CHECK | N/A |  | 2020 | 1988 |  |  | HR-BAES-007 |  |  |  | Poor | Heavy corrosion and deterioration was observed on the service of the valve. The valve was near the end of its expected service life.
226 | 631 | Discharge Header | 3 | 100mm Diameter, approx. 5m, Class 52 Ductile Iron discharge piping connected to 100mm PVC forcemain | Halton | In Service | Belaire Dr. PS | Belaire Dr. PS | Wet Well | Process Mechanical | Process Piping |  |  |  |  | 0 | 1988 |  |  | HR-BAES-026 |  |  |  | Poor | Heavy corrosion and deterioration was observed on the piping
114 | 631 | SEWAGE LIFT PUMP #1 | 2 | Sewage Pump #1;Flygt;CP 3085;;6.3 L/s at 4.7 m TDH 2 HP | Halton | In Service | Belaire Dr. PS | Belaire Dr. PS | Wet Well | Process Mechanical | Process Mechanical Equipment | FLYGT | C3102-180.1307 | L07283188 |  | 2020 | 1988 |  |  | HR-BAES-018 |  |  |  | Fair. | The pump is working but it is near the end of its expected service life.
631 | 2 | Wet Well | 3 |  | Halton |  | Belaire Dr. PS |  |  | Process Structural | Building and Process Structural
572 | 635 | Dry Well Portable Heater | 1 | Installation year assumed to be 1972 | Halton | In Service | Carrington Place PS | WWPS | Dry Well | Building Mechanical | Building Services | [5 empty] | 1972 |  |  | HR-CRTN-045 |  |  |  | good
571 | 20 | Dry Well Sump Pump | 1 | Installation year assumed to be 1970 | Halton | In Service | Carrington Place PS | Carrington Place PS | Dry Well | Building Mechanical | Building Services | [5 empty] | 1970 |  |  | HR-CARD-145
573 |  | Wet Well Gooseneck Ventilation Pipes | 1 | Two 4 inches diameter steel pipe vents with bird screen | Halton | In Service | Carrington Place PS | WWPS | We Well | Building Mechanical | Process Mechanical Equipment | [5 empty] | 1972 |  |  | HR-CRTN-033 |  |  |  | paint peeling
599 | 635 | Dry Well Thermostat | 1 | Installation year assumed to be 1972 | Halton | In Service | Carrington Place PS | WWPS | We Well | Building Mechanical | Building Services | [5 empty] | 1972 |  |  | HR-CRTN-124 |  |  |  | operability of the asset was unknown
570 | 635 | Dry Well Dehumidifier | 1 | Installation year assumed to be 1970 | Halton | In Service | Carrington Place PS | WWPS | Dry Well | Building Mechanical | Building Services | [5 empty] | 1970 |  |  | HR-CARD-123 |  |  |  | good
609 | 21 | Yard Hydrant (New Asset) | 1 |  | Halton |  | Carrington Place PS | WWPS | Site | Site Works | Site Works | [12 empty] | There was no yard hydrant | In accordance with Section 19.8.3 of the Region's Water and Wastewater Design Manual (January 2012), a yard hydrant complete with a backflow preventer with a 37.5mm water service line shall be provided for flushing and cleaning purposes. It is recommended
219 | 635 | SEWAGE LIFT PUMP #2 MOTOR DRIVE | 2 | 15.0 HP | Halton | In Service | Carrington Place PS | Carrington Place PS | Dry Well | Process Mechanical | Process Electrical | BROOK ELECTRIC | N/A | X608521 |  | 2020 | 1972 | [6 empty] | fair | Deterioration and corrosion was obeserved on the surface of the motor. The motor was beyond its expected service life.
386 | 289 | Manhole Frame and Cover | 2 |  | Halton | In Service | Carrington Place PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2032 |  |  |  |  | Fair | Surface corrosion on underside
290 | 635 | Dry Well Access Ladder | 2 | Carrington Place PS Dry Well | Halton | In Service | Carrington Place PS | WWPS | Dry Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2032 | HR-CRTN-035 |  |  |  | Fair
291 | 635 | Dry Well Access Hatch | 2 | Carrington Place PS Dry Well | Halton | In Service | Carrington Place PS | WWPS | Dry Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2032 | HR-CRTN-033 |  |  |  | Fair | Corrosion on top surface |  | Clean and touch up paint | 2021 | 300
292 | 635 | Protective Paint | 2 | Carrington Place PS Dry Well | Halton | In Service | Carrington Place PS | WWPS | Dry Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2032 | HR-CRTN-035 |  |  |  | Fair | Peeling paint noted
293 | 636 | Wet Well Access Ladder | 2 |  | Halton | In Service | Carrington Place PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2032 | HR-CRTN-001 |  |  |  | Fair | HS: Missing rung at platform level |  | Install missing run | 2021 | 500
294 | 636 | Manhole Frame and Cover | 1 |  | Halton | In Service | Carrington Place PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2032 | HR-CRTN-001 |  |  |  | Fair | Surface corrosion on underside
295 | 636 | Wet Well Aluminum Grating | 2 |  | Halton | In Service | Carrington Place PS | WWPS | Dry Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2032 | HR-CRTN-036 |  |  |  | Fair
296 | 636 | Wet Well Aluminum Platform | 2 | Carrington Place PS Dry Well | Halton | In Service | Carrington Place PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2025 | HR-CRTN-080 |  |  |  | Fair to poor | Corrosion noted
312 | 635 | Davit Socket Base | 2 | Carrington Place PS Dry Well | Halton | In Service | Carrington Place PS | WWPS | Dry Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2032 | HR-CRTN-004 |  |  |  | Fair | To be inspected yearly
20 | 635 | Dry Well Structure | 2 | Carrington Place PS Dry Well | Halton | In Service | Carrington Place PS | WWPS | Dry Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2032 | HR-CRTN-036 |  |  |  | Fair | Corrosion noted |  | Grind to bare metal and touch up paint | 2021 | 2000
289 | 636 | Wet Well Concrete Structure | 2 | Carrington Place PS Dry Well | Halton | In Service | Carrington Place PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2032 | HR-CRTN-001 |  |  |  | Fair | Brick riser supporting manhole frame is loose |  | Reparge brick riser | 2021 | 500
564 | 21 | Generator Connect Recept (New Asset) | 2 | New Gen Connect Recept; ; ; ; ;600V, 50A | Halton | In Service | Carrington Place PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2021 |  |  | IMG_20200629_125113 |  |  |  | There was no Generator Connection Receptical and Manual Transfer Switch located on site. Paralleling power sources and severe electrical shock hazard while hardwiring the generator for emergency power | to be installed (above ground) to comply with industry practice
478 | 20 | Main Breaker | 2 | Main Breaker; Moeller; 6-63/62-u; ; 600V, 60A | Halton | In Service | Carrington Place PS | Carrington Place PS | Dry Well | Process Electrical | Process Electrical | [5 empty] | 1972 |  | 2025 | IMG_20200629_125233 |  |  |  |  | good | discountinued
481 | 20 | Power Panel | 2 | Power Panel indluding Pump relays; Moeller; ; ; ; | Halton | In Service | Carrington Place PS | WWPS | Dry Well | Process Electrical | Process Electrical | [5 empty] | 1972 |  | 2030 | IMG_20200629_125113 |  |  |  | fair | corrosion was observed in different inside and surface of panel | missing Arc Flash Labels
563 | 20 | Main Disconnect Switch | 2 | New main DS; ; ; ; ;600V, 50A | Halton | In Service | Carrington Place PS | WWPS | Dry Well | Process Electrical | Process Electrical | [5 empty] | 2021 |  | 2021 | IMG_20200629_125113 |  |  |  | fair | to be installed (above ground) to comply with industry practice
480 | 20 | Pump #2 Breaker | 2 | Pump #2 Breaker; Moeller; NZM 6-63/62-u; ; 600V, 50A | Halton | In Service | Carrington Place PS | Carrington Place PS | Dry Well | Process Electrical | Process Electrical | [5 empty] | 1972 |  | 2025 | 00000IMG_00000_BURST20200629125320236_COVER |  |  |  | good
479 | 20 | Pump #1 Breaker | 2 | Pump #1 Breaker; Moeller; NZM 6-63/62-u; ; 600V, 36A | Halton | In Service | Carrington Place PS | Carrington Place PS | Dry Well | Process Electrical | Process Electrical | [5 empty] | 1972 |  | 2025 | 00000IMG_00000_BURST20200629125326278_COVER |  |  |  | good | discountinued
562 | 20 | Manual Transfer Switch | 2 | MTS; ; ; ; ;600V, 50A | Halton | In Service | Carrington Place PS | WWPS | Dry Well | Process Electrical | Process Electrical | [5 empty] | 2021 |  |  | IMG_20200629_125113 |  |  |  | Fair | to be installed (above ground) to comply with industry practice
477 | 635 | Drywell Lights | 1 | Drywell Lights; ; ; ; 2 fixture, class 1, div 2 rated | Halton | In Service | Carrington Place PS | WWPS | Dry Well | Building Electrical | Building Services | [5 empty] | 1972 |  | 2025 | 00100lrPORTRAIT_00100_BURST20200629125448497_COVER |  |  |  | good | replace with LED fixture in next upgrade
476 | 635 | Power Meter | 2 | Power Meter; ; ; ; | Halton | In Service | Carrington Place PS | WWPS | Dry Well | Process Electrical | Process Electrical | [5 empty] | 2011 |  | 2041 | IMG_20200629_125120 |  |  |  | good | move it above ground
414 | 636 | Wet Well Floats | 2 | Wet Well Floats; ; ; ; ; | Halton | In Service | Carrington Place PS | WWPS | Wet Well | Process Instrumentation | Process Instrumentation | [5 empty] | 2008 |  | 2030 | HR-CRTN-080 |  |  |  |  | good
412 | 635 | Sump Float | 2 | Sump Float; ; ; ; | Halton | In Service | Carrington Place PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation | [5 empty] | 2008 |  | 2030 | HR-CRTN-018 |  |  |  | Corrrosion | fair
415 |  | Discharge Flow Meter | 2 | Discharge Flow Meter; Siemens; Strans F; ; ; | Halton | Not In Service | Carrington Place PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation | [5 empty] | 2008 |  | 2030 | HR-CRTN-020 |  |  |  | fair | Corrosion
209 | 636 | TRANSMITTER LEVEL WET WELL #1 | 2 | Wet Well Level Transmitter; Siemens Milltronics; Multiranger 200; | Halton | In Service | Carrington Place PS | Carrington Place PS | Dry Well | Process Instrumentation | Process Instrumentation | MILLTRONICS | MULTIRANGER PLUS | 09873860-0 |  | 2020 | 2008 |  | 2030 | HR-CRTN-137 |  |  |  | Corrosion | good
222 | 21 | FORCEMAIN | 4 | 200mm diameter, Ductile Iron, approx. 800m | Halton | In Service | Carrington Place PS | Carrington Place PS | Site | Process Mechanical | Process Piping |  |  |  |  | 2020 | 1972 | [6 empty] | Fair | The pipe passed half of its expected service life
213 | 635 | SEWAGE LIFT PUMP #1 CHECK VALVE | 2 | Check Valve #1;Swing-Flex;;;100 mm dia | Halton | In Service | Carrington Place PS | WWPS | Dry Well | Process Mechanical | Process Mechanical Equipment | SWING FLEX | 504 |  |  | 2020 | 1972 |  |  | HR-CRTN-010 |  |  |  | fair | Corrosion and deterioration was observed on the surface of the valve. The valve was beyond its expected service life.
220 | 635 | SEWAGE LIFT PUMP #2 INLET VALVE | 2 | Inlet Gate Valve #1;;;;200 mm dia | Halton | In Service | Carrington Place PS | Carrington Place PS | Dry Well | Process Mechanical | Process Mechanical Equipment | RED WHITE | N/A | N/A |  | 2020 | 1972 |  |  | HR-CRTN-016 |  |  |  | Poor | Corrosion and deterioratino was observed on the valve. The valve was beyond its expected service life.
218 | 635 | SEWAGE LIFT PUMP #2 CHECK VALVE | 2 | Check Valve #1;Swing-Flex;;;100 mm dia | Halton | In Service | Carrington Place PS | Carrington Place PS | Dry Well | Process Mechanical | Process Mechanical Equipment | SWING FLEX | 504 |  |  | 2020 | 1972 |  |  | HR-CRTN-014 |  |  |  | fair | Corrosion and deterioration was observed on the surface of the valve. The valve was beyond its expected service life.
217 | 635 | SEWAGE LIFT PUMP #2 | 2 | Sewage Lift Pump #1;Smith & Loveless;;;15 HP | Halton | In Service | Carrington Place PS | Carrington Place PS | Dry Well | Process Mechanical | Process Mechanical Equipment | NAPANEE |  |  |  | 2020 | 1972 |  |  | HR-CRTN-015 |  |  |  | fair | Deterioration and corrosion was obeserved on the surface of the pump. The pump was beyond its expected service life.
212 | 635 | SEWAGE LIFT PUMP #1 | 2 | Sewage Lift Pump #1;Smith & Loveless;;;15 HP | Halton | In Service | Carrington Place PS | Carrington Place PS | Dry Well | Process Mechanical | Process Mechanical Equipment | NAPANEE |  |  |  | 2020 | 1972 |  | 2026 | HR-CRTN-008 |  |  |  | fair | Deterioration and corrosion was obeserved on the surface of the pump. The pump was beyond its expected service life.
215 | 635 | SEWAGE LIFT PUMP #1 INLET VALVE | 2 | Inlet Gate Valve #1;;;;200 mm dia | Halton | In Service | Carrington Place PS | Carrington Place PS | Dry Well | Process Mechanical | Process Mechanical Equipment | RED WHITE | N/A | N/A |  | 2020 | 1972 |  |  | HR-CRTN-006 |  |  |  | fair | Corrosion and deterioratino was observed on the valve. The valve was beyond its expected service life.
216 | 635 | SEWAGE LIFT PUMP #1 DISCHARGE VALVE | 2 | Discharge Gate Valve #1;;;;100 mm dia | Halton | In Service | Carrington Place PS | Carrington Place PS | Dry Well | Process Mechanical | Process Mechanical Equipment | KV | N/A | N/A |  | 2020 | 1972 | [6 empty] | fair | Corrosion and deterioratino was observed on the valve. The valve was beyond its expected service life.
398 | 636 | Bar Screen | 2 | Bar Screen;;;; | Halton | In Service | Carrington Place PS | WWPS | Wet Well | Process Mechanical | Process Mechanical Equipment | [5 empty] | 1972 | [6 empty] | fair | The screen was beyond its expected service life.
233 | 21 | Overflow Piping | 2 | 200mm Diameter, Concrete C14 Piping, approx. 50m | Halton | In Service | Carrington Place PS | Carrington Place PS | Site | Process Mechanical | Process Piping |  |  |  |  | 0 | 1972 | [6 empty] | Fair | The pipe was over half of its expected service life.
208 | 635 | PUMP #1 SUMP | 1 | Sump Pump;Little Giant;;; | Halton | In Service | Carrington Place PS | Carrington Place PS | Dry Well | Building Mechanical | Process Mechanical Equipment | LITTLE GIANT | N/A | N/A |  | 2020 | 1972 |  |  | HR-CARD-145 |  |  |  | The sump pump was beyond its expected service life. | fair
221 | 635 | SEWAGE LIFT PUMP #2 DISCHARGE VALVE | 2 | Discharge Gate Valve #1;;;;100 mm dia | Halton | In Service | Carrington Place PS | Carrington Place PS | Dry Well | Process Mechanical | Process Mechanical Equipment | NEWMAN HATTERSLEY | FIG.#T504 | N/A |  | 2020 | 1972 |  |  | HR-CRTN-016 |  |  |  | fair | Corrosion and deterioratino was observed on the valve. The valve was beyond its expected service life.
230 | 635 | Pump 1 Piping | 3 | 200mm (8") Diameter, Ductile Iron Piping, approx. 3m | Halton | In Service | Carrington Place PS | Carrington Place PS | Dry Well | Process Mechanical | Process Piping |  |  |  |  | 0 | 1972 | [6 empty] | fair | The pipe was over half of its expected service life.
232 | 635 | Pump 2 Piping | 3 | 200mm Diameter, Ductile Iron, approx. 5 m | Halton | In Service | Carrington Place PS | WWPS | Dry Well | Process Mechanical | Process Piping |  |  |  |  | 0 | 1972 | [6 empty] | fair | The pipe was over half of its expected service life.
211 | 635 | FAN EXHAUST #1 | 1 | 115 VOLTS | Halton | Missing | Carrington Place PS | Carrington Place PS | Dry Well | Building Mechanical | Building Services | N/A | N/A | N/A |  | 2020 | 1972 | [6 empty] | CC: As per Section 7.2.9 of MOECC's Design Guidelines for Sewage Works, mechanical ventilation is required for below ground surface dry well. | missing
210 | 20 | CONTROL PROCESS FLOW CAR PLACE | 2 |  | Halton |  | Carrington Place PS | Carrington Place PS | Dry Well | Process Electrical | Process Electrical | SIEMENS -CONTROLOTRON | 1010NR-T2KGS-S2 | U23428 |  | 2020
214 | 635 | MOTOR DRIVE SEWAGE LIFT PUMP #1 | 2 | 15.0 HP | Halton | In Service | Carrington Place PS | WWPS | Dry Well | Process Mechanical | Process Electrical | BROOK ELECTRIC MOTORS | N/A | X663787 |  | 2020 | 1972 | [6 empty] | Deterioration and corrosion was obeserved on the surface of the motor. The motor was beyond its expected service life. | fair
574 | 637 | Wet Well Gooseneck Ventilation Pipes | 1 | Two 3 inches diameter steel pipe vents | Halton | In Service | Cedarberry Court PS | WWPS | Wet Well | Building Mechanical | Building Services | [5 empty] | 1972 |  |  | HR-CBRY-019 |  |  |  | Staining at the bottom section of the pipe
610 | 22 | Yard Hydrant | 1 |  | Halton | In Service | Cedarberry Court PS | WWPS | Site | Site Works | Site Works | [5 empty] | 1977 |  | 2035 | HR-CBRY-025 |  |  |  |  | Good
311 | 637 | Grab Bar | 1 | Cedarberry Court PS Wet Well | Halton | In Service | Cedarberry Court PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1976 |  | 2036 | HR-CBRY-025 |  |  |  | Fair
310 | 637 | Davit Socket Base | 1 | Cedarberry Court PS Wet Well | Halton | In Service | Cedarberry Court PS | WWPS | Wet Well | Building Structural | Building and Process Structural | [5 empty] | 1976 |  | 2036 | HR-CBRY-025 |  |  |  | Fair | To be inspected yearly
300 | 637 | Aluminum Platform | 2 | Cedarberry Court PS Wet Well | Halton | In Service | Cedarberry Court PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1976 |  | 2036 | HR-CBRY-044 |  |  |  | Fair | HS: Grating not clipped
299 | 637 | Access Ladder | 1 | Cedarberry Court PS Wet Well | Halton | In Service | Cedarberry Court PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1976 |  | 2036 | HR-CBRY-044 |  |  |  | Fair
298 | 637 | Pump Hatch | 1 | Cedarberry Court PS Wet Well | Halton | In Service | Cedarberry Court PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1976 |  | 2036 | HR-CBRY-025 |  |  |  | Fair | HS: Missing safety grating |  | Install safety grating | 2021 | 1000
297 | 637 | Access Hatch | 1 | Cedarberry Court PS Wet Well | Halton | In Service | Cedarberry Court PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1976 |  | 2036 | HR-CBRY-025 |  |  |  | Fair
23 | 637 | Wet Well Concrete Structure | 3 | Cedarberry Court PS Wet Well | Halton | In Service | Cedarberry Court PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1976 |  | 2036 | HR-CBRY-044 |  |  |  | Fair | Concrete spalling on roof, rust spots and concrete spalling at pipe penetration |  | Cut back rust spots, remove loose concrete, clean reinforcement and coat with rust inhibiting paint and patch with cementitous repair mortar | 2025 | 5000
484 | 22 | Control Panel | 2 | Control Panel; ; ; ; | Halton | In Service | Cedarberry Court PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 1977 |  | 2025 | IMG_2861 |  |  |  | good | arc flash hazard label was painted on
561 | 22 | Power meter (New Asset) | 2 | New Power meter; ; ; ; 240V, 60A | Halton | In Service | Cedarberry Court PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2021 | [6 empty] | to be installed to comply with industry practice
560 | 4 | Fused Disconnect Switch (New Asset) | 1 | New fused DS; ; ; ; 240V, 60A | Halton | In Service | Cedarberry Court PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2021 | [6 empty] | to be installed to comply with industry practice
559 | 22 | Generator Connect Recept (New Asset) | 2 | New Generaor Connect Recept ; ; ; 240V, 60A | Halton | In Service | Cedarberry Court PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2021 | [6 empty] | HS: There was no Generator Connection Receptical and Manual Transfer Switch located on site. Paralleling power sources and severe electrical shock hazard while hardwiring the generator for emergency power | to be installed to comply with industry practice
558 | 22 | Manual Transfer Switch (New Asset) | 2 | New Manual Transfer Switch; ; ; ; 240V, 60A | Halton | In Service | Cedarberry Court PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2021 | [6 empty] | to be installed to comply with industry practice
483 | 4 | Outdoor Enclosure | 2 | Outdoor Enclosure; ; ; ; | Halton | In Service | Cedarberry Court PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 1977 |  | 2025 | IMG_2849 |  |  |  | fair | bottom interior of panel was corroded | Replace with NEMA 3R enclosure
482 | 22 | Panel Flood Light | 1 | Panel Flood Light; ; ; ; | Halton | In Service | Cedarberry Court PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 1977 |  | 2025 | IMG_2850 |  |  |  | good
419 | 637 | Wet Well Floats | 2 | Wet Well Floats; ; ; ; ; | Halton | In Service | Cedarberry Court PS | WWPS | Wet Well | Process Instrumentation | Process Instrumentation | [5 empty] | 2016 |  | 2018 | HR-CBRY-034 |  |  | 2 | Corrosion
121 | 637 | TRANSMITTER LEVEL - WETWELL | 2 | Wet Well Level Transmitter; Siemens Milltronics; Multiranger 200; ; ; | Halton | In Service | Cedarberry Court PS | Cedarberry Court PS | Wet Well | Process Instrumentation | Process Instrumentation | MILLTRONICS | MULTIRANGER 100 | PBD-T4180482 XB |  | 2020 | 2014 |  | 2030 | HR-CBRY-053 |  |  | 2 | good
234 | 22 | Overflow Piping | 3 | 200mm diameter, 6.4 m | Halton |  | Cedarberry Court PS | Cedarberry Court PS | Site | Process Mechanical | Process Piping |  |  |  |  | 0 | 1977
235 | 122 | Pump 1 Piping | 3 | 100mm diameter, approx. 5 m discharge piping | Halton | In Service | Cedarberry Court PS | Cedarberry Court PS | Wet Well | Process Mechanical | Process Piping |  |  |  |  | 0 | 1977 |  |  | HR-CBRY-048 |  |  |  | Poor | Severe deterioration was observed on the service piping
127 | 125 | SEWAGE LIFT PUMP #2 DISCHARGE VALVE | 2 | Gate Valve No.2 with Handwheel;;;;100 mm dia | Halton | In Service | Cedarberry Court PS | Cedarberry Court PS | Wet Well | Process Mechanical | Process Mechanical Equipment | TRUELINE | KNIFE GATE | N/A |  | 2020 | 1977 |  |  | HR-CBRY-002 |  |  |  | Poor | Corrosion and deterioration was observed on the surface of the valve and it is near the end of its expected service life.
128 | 22 | FORCEMAIN | 4 | 100mm diamter, approx. 73 m, PVC forcemain | Halton | In Service | Cedarberry Court PS | Cedarberry Court PS | Site | Process Mechanical | Process Piping |  |  |  |  | 2020 | 1977 | [6 empty] | Good
125 | 637 | SEWAGE LIFT PUMP #2 | 2 | Sewage Lift Pump #2;Flygt;CP3085;;6.3 L/s at 4.7 m TDH 2HP | Halton | In Service | Cedarberry Court PS | Cedarberry Court PS | Wet Well | Process Mechanical | Process Mechanical Equipment | FLYGT | 3082 | 9082 180 73166 |  | 2020 | 1977 |  |  | HR-CBRY-016 |  |  |  | Poor | The pump works but it's near the end of its expected service life.
124 | 122 | SEWAGE LIFT PUMP #1 DISCHARGE VALVE | 2 | Gate Valve No.1 with Handwheel;;;;100 mm dia | Halton | In Service | Cedarberry Court PS | Cedarberry Court PS | Wet Well | Process Mechanical | Process Mechanical Equipment | TRUELINE | KNIFE GATE | N/A |  | 2020 | 1977 |  |  | HR-CBRY-001 |  |  |  | Poor | Deterioration was observed on the surface of the valve and it is near the end of its expected service life.
123 | 122 | SEWAGE LIFT PUMP #1 CHECK VALVE | 2 | Check Valve No.1;Swing-Flex;;;100 mm dia | Halton | In Service | Cedarberry Court PS | Cedarberry Court PS | Wet Well | Process Mechanical | Process Mechanical Equipment | VALMATIC | SWING FLEX | N/A |  | 2020 | 1977 |  |  | HR-CBRY-004 |  |  |  | Poor | Corrosion and serious deterioration was observed on the valve
122 | 637 | PUMP #1 SEWAGE LIFT | 2 | Sewage Lift Pump #1;Flygt;CP3085;;6.3 L/s at 4.7 m TDH 2HP | Halton | In Service | Cedarberry Court PS | Cedarberry Court PS | Wet Well | Process Mechanical | Process Mechanical Equipment | FLYGT | 3082 | 3082 180 73167 |  | 2020 | 1977 |  |  | HR-CBRY-015 |  |  |  | Poor | The pump works but it's near the end of its expected service life.
126 | 125 | SEWAGE LIFT PUMP #2 CHECK VALVE | 2 | Check Valve No.2;Swing-Flex;;;100 mm dia | Halton | In Service | Cedarberry Court PS | Cedarberry Court PS | Wet Well | Process Mechanical | Process Mechanical Equipment | VALMATIC | SWING FLEX | N/A |  | 2020 | 1977 |  |  | HR-CBRY-006 |  |  |  | Poor | Corrosion and serious deterioration was observed on the valve
389 | 637 | Bar Screen | 2 | Bar Screen;;;; | Halton | In Service | Cedarberry Court PS | WWPS | Wet Well | Process Mechanical | Process Mechanical Equipment | [5 empty] | 1977 |  |  | HR-CBRY-007 |  |  |  | Good
236 | 125 | Pump 2 discharge piping | 3 | 100mm diameter, approx. 2.6m discharge piping | Halton | In Service | Cedarberry Court PS | Cedarberry Court PS | Wet Well | Process Mechanical | Process Piping |  |  |  |  | 0 | 1977 | [6 empty] | Poor | Severe deterioration was observed on the service piping
620 | 48 | Exterior metal platform | 2 |  | Halton |  | Rock Point Dr PS | WWPS | Site | Site Works | Site Works | [5 empty] | 2007 |  |  | HR-JOSH-158 |  |  |  |  | Good
621 | 48 | Exterior Metal Platform Handrails | 2 |  | Halton | In Service | Rock Point Dr PS | WWPS | Site | Site Works | Site Works | [5 empty] | 2007 |  | 2035 | HR-JOSH-158 |  |  |  | Good
618 | 48 | Concrete Pedestal | 1 |  | Halton | In Service | Rock Point Dr PS | WWPS | Site | Site Works | Site Works | [5 empty] | 2007 |  |  | HR-JOSH-160 |  |  |  | Good
617 | 48 | Yard Hydrant | 1 |  | Halton | In Service | Rock Point Dr PS | WWPS | Site | Site Works | Site Works | [5 empty] | 2007 |  |  | HR-JOSH-094 |  |  |  |  | Good
619 | 48 | Metal Guard Railing | 2 |  | Halton | In Service | Rock Point Dr PS | WWPS | Site | Site Works | Site Works | [5 empty] | 2007 |  |  | HR-JOSH-160 |  |  |  | Good
378 | 634 | Exterior Aluminum Platform | 2 | Rock Point Dr PS Wet Well | Halton | In Service | Rock Point Dr PS | WWPS | Site | Process Structural | Building and Process Structural | [5 empty] | 2006 |  |  | HR-JOSH-158 |  |  |  | Good
49 | 634 | Wet Well Concrete Structure | 3 | Rock Point Dr PS Wet Well | Halton | In Service | Rock Point Dr PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 2006 |  |  | HR-JOSH-091 |  |  |  | Good | Rust spots noted typically |  | Cut back rust spots, clean and patch with cementitous repair mortar | 2035 | 500
379 | 634 | Davit Socket Base | 1 | Rock Point Dr PS Wet Well | Halton | In Service | Rock Point Dr PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 2006 |  |  | HR-JOSH-081 |  |  |  | Good
377 | 634 | Aluminum Guardrail | 2 | Rock Point Dr PS Wet Well | Halton |  | Rock Point Dr PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [8 empty] | HR-JOSH-091 |  |  |  | Fair | Calcium buildup noted
376 | 634 | Aluminum Platform | 2 | Rock Point Dr PS Wet Well | Halton |  | Rock Point Dr PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [8 empty] | HR-JOSH-091 |  |  |  | Fair | Calcium buildup noted
375 | 634 | Access Ladder | 1 | Platform to wet well base | Halton | In Service | Rock Point Dr PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 2006 |  |  | HR-JOSH-091 |  |  |  | Fair | Calcium buildup noted
374 | 634 | Access Ladder | 1 | Exterior to platform | Halton | In Service | Rock Point Dr PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 2006 |  |  | HR-JOSH-091 |  |  |  | Fair | Calcium buildup noted
373 | 634 | Pump Hatch 2 | 1 | Rock Point Dr PS Wet Well | Halton | In Service | Rock Point Dr PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 2006 |  |  | HR-JOSH-085 |  |  |  | Good
372 | 634 | Pump Hatch 1 | 1 | Rock Point Dr PS Wet Well | Halton | In Service | Rock Point Dr PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 2006 |  |  | HR-JOSH-085 |  |  |  | good
371 | 634 | Access Hatch | 1 | Rock Point Dr PS Wet Well | Halton | In Service | Rock Point Dr PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 2006 |  | 2066 | HR-JOSH-085 |  |  |  | Fair | Hatch hard to open due to corrosion on latch |  | Repair/replace latch | 2021 | 500
380 | 634 | Grab Bar | 1 | Rock Point Dr PS Wet Well | Halton | In Service | Rock Point Dr PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 2006 |  |  | HR-JOSH-081 |  |  |  | Good
547 | 48 | Outdoor Enclosure | 2 | Outdoor Enclosure | Halton | In Service | Rock Point Dr PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2005 |  | 2035 | IMG_2774 |  |  |  | good | top of control panel enclosure was damaged and was insulated
548 | 48 | Site Light | 1 | Site Light | Halton | In Service | Rock Point Dr PS | WWPS | Site | Building Electrical | Process Electrical | [5 empty] | 2005 |  | 2035 | IMG_2780 |  |  |  | good
549 | 48 | Duplex Pump Control Panel | 2 | Duplex Pump Control Panel; Cutler Hammer; ; ; 240V | Halton | In Service | Rock Point Dr PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2005 |  | 2035 | IMG_2793 |  |  |  | good
550 | 13 | Lighting Panel | 2 | Lighting Panel; Cutler Hammer; PL1A; 120/240V, 225A, 18CCT | Halton | In Service | Rock Point Dr PS | WWPS | Site | Building Electrical | Process Electrical | [5 empty] | 2005 |  | 2035 | IMG_2796 |  |  |  | good
551 | 48 | Pump Capacitors | 2 | Pump Capacitors; ; ; | Halton | In Service | Rock Point Dr PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2005 |  | 2035 | IMG_2806 |  |  |  | good | replace with VFD in next upgrade
557 | 48 | Generator Transformer | 2 | Generator Transformer; BEMAG; ;600V-120/240V, 50kVA | Halton | In Service | Rock Point Dr PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2005 |  | 2035 | IMG_2843 |  |  |  | good
556 | 48 | Power Meter | 2 | Power Meter; ; ; | Halton | In Service | Rock Point Dr PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2005 |  | 2035 | IMG_2824 |  |  |  | good
555 | 48 | Generator Connect Receptacle | 2 | Gen Connect Recept; ; ; 600V | Halton | In Service | Rock Point Dr PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2005 |  | 2035 | IMG_2815 |  |  |  | good
554 | 48 | Manual Transfer Switch | 2 | MTS; Eaton; ; 240V, 200A | Halton | In Service | Rock Point Dr PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2005 |  | 2035 | IMG_2815 |  |  |  | good
553 | 48 | Surge Protection Device | 2 | Surge Protection Device; Eaton; Clipper VL; | Halton | In Service | Rock Point Dr PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2005 |  | 2035 | IMG_2812 |  |  |  | good
552 | 48 | Main Breaker | 2 | Main Breaker; Eaton; ;240V, 200A | Halton | In Service | Rock Point Dr PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2005 |  | 2035 | IMG_2808 |  |  |  | good
205 | 634 | BY -PASS FLOW TRANSMITTER | 2 | Bypass Flow Meter; Siemens Milltronics; MultiRanger 100; 030305108VX; ; | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Site | Process Instrumentation | Process Instrumentation | SIEMENS | MR-100 | 030305108VX |  | 2020 | 2010 |  |  | HR-JOSH-212 |  |  |  | good
204 | 48 | JOSHUA CREEK UP#1 - | 2 | PLC Panel UPS; Eaton; Powerware 9120 700; RW513A0198 ; 700VA-3000VA; | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Site | Process Instrumentation | Process Instrumentation | POWER WARE | PW 9120 700 | RW513A0198 |  | 2020 | 2006 |  | 2025 | HR-JOSH-214 |  |  |  | Corrosion
206 | 634 | WET WELL LEVEL TRANSMITTER | 2 | Wet Well Level Transmitter; Siemens Milltronics; Multiranger 100; 030205142VX; ; | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Dry Well | Process Instrumentation | Process Instrumentation | SIEMENS | MR-100 | 030205142VX |  | 2020 | 2010 |  | 2030 | HR-JOSH-198 |  |  |  | good
454 | 634 | Wet Well Floats | 2 | Wet Well Floats; ; ; ; ; | Halton | In Service | Rock Point Dr PS | WWPS | Wet Well | Process Instrumentation | Process Instrumentation | [5 empty] | 2006 |  | 2025 | HR-JOSH-109 |  |  |  | good
455 | 634 | Wet Well Level Transmitter* Wet Well Level Transmitter | 2 | Wet Well Level Transmitter; Siemens Milltronics; Multiranger 200; ; ; | Halton | In Service | Rock Point Dr PS | WWPS | Wet Well | Process Instrumentation | Process Instrumentation | [5 empty] | 2014 |  | 2030 | HR-JOSH-198 |  |  |  | good
193 | 48 | PLC #1 - ROCK POINT DR. - E16RT01 | 2 | Panel, Control/PLC; Allen-Bradley; SLC 05; 1747-L552 ; ; | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Site | Process Instrumentation | Process Instrumentation | Rockwell Automation/Allen-Brad | 1747-L552 | N/A |  | 2020 | 2005 |  | 2025 | HR-JOSH-209 |  |  |  | fair. | obselete
408 | 49 | Trash Basket | 2 | Trash Basket;;;; | Halton | In Service | Rock Point Dr PS | WWPS | Wet Well | Process Mechanical | Process Mechanical Equipment | [5 empty] | 2006 |  |  | HR-JOSH-89 |  |  |  | Good
201 | 207 | DISCHARGE HEADER ISOLATION VALVE #2 | 2 | Knife Gate Valve #2;;;;100 mm dia | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Wet Well | Process Mechanical | Process Mechanical Equipment | TRUELINE | F8112 | N/A |  | 2020 | 2006 |  |  | HR-JOSH-098 |  |  |  | Fair | Heavy corrosion and deterioration was observed on the surface of the valve.
202 | 207 | DISCH. HEADER BYPASS ISOL. VALVE#3 | 2 | Knife Gate Valve #3;;;;100 mm dia | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Wet Well | Process Mechanical | Process Mechanical Equipment | TRUELINE | F8112 | N/A |  | 2020 | 2006 |  |  | HR-JOSH-097 |  |  |  | Fair | Heavy corrosion and deterioration was observed on the surface of the valve.
194 | 13 | SEWAGE LIFT PUMP #1 | 2 | Sewage Lift Pump #1;Flygt;3127.090;0510181;7.5 L/s at 15 m TDH 7.5 HP | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Wet Well | Process Mechanical | Process Mechanical Equipment | FLYGT | 3127.090 | 0510181 |  | 2020 | 2006 |  |  | HR-JOSH-101 |  |  |  | Good.
195 | 194 | SEWAGE LIFT PUMP #1 CHECK VALVE | 2 | Check Valve #1;;;;100 mm dia | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Wet Well | Process Mechanical | Process Mechanical Equipment | HILLEN DELELIE | N/A | N/A |  | 2020 | 2006 |  |  | HR-JOSH-101 |  |  |  | Fair | Heavy corrosion was observed on the surface of the valve
207 | 13 | FORCEMAIN | 4 | 100mm diameter, approx. 390m PVC forcemain | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Site | Process Mechanical | Process Piping |  |  |  |  | 2020 | 2006 | [6 empty] | Good
199 | 198 | SEWAGE LIFT PUMP #2 CHECK VALVE | 2 | Check Valve #2;;;;100 mm dia | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Wet Well | Process Mechanical | Process Mechanical Equipment | HILLEN DELELIE | N/A | N/A |  | 2020 | 2006 |  |  | HR-JOSH-107 |  |  |  | Fair | Heavy corrosion and deterioration was observed on the surface of the valve.
196 | 194 | SEWAGE LIFT PUMP #1 DISCHARGE VALVE | 2 | Gate Valve #1;;;;100 mm dia | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Wet Well | Process Mechanical | Process Mechanical Equipment | AVK | N/A | 23-100-4702630029 |  | 2020 | 2006 |  |  | HR-JOSH-099 |  |  |  | Fair | Heavy corrosion was observed on the surface of the valve
200 | 198 | SEWAGE LIFT PUMP #2 DISCHARGE VALVE | 2 | Gate Valve #2;;;;100 mm dia | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Wet Well | Process Mechanical | Process Mechanical Equipment | AVK | N/A | 23-100-4702630029 |  | 2020 | 2006 |  |  | HR-JOSH-106 |  |  |  | Fair | Heavy corrosion and deterioration was observed on the surface of the valve.
197 | 207 | DISCHARGE HEADER ISOLATION VALVE #1 | 2 | Knife Gate Valve #1;;;;100 mm dia | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Wet Well | Process Mechanical | Process Mechanical Equipment | TRUELINE | F8112 | N/A |  | 2020 | 2006 |  |  | HR-JOSH-115 |  |  |  | Fair | Heavy corrosion and deterioration was observed on the surface of the valve.
407 | 49 | Overflow Piping | 3 | 200mm diameter, approx. 7m PVC SDR 35 | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Wet Well |  | Process Piping | [5 empty] | 2006
271 | 207 | Air Release Valve #1 | 2 | Air Release Valve #1;;;;50 mm dia | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Wet Well | Process Mechanical | Process Piping |  |  |  |  | 0 | 2006 |  |  | HR-JOSH-118 |  |  |  | poor | Heavy corrosion was observed on the surface of the valve
270 | 194 | Pump 1 Discharge Piping | 3 | 100mm diameter, approx. 10m SS pipe | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Wet Well | Process Mechanical | Process Piping |  |  |  |  | 0 | 2006 |  |  | HR-JOSH-116 |  |  |  | Fair | Heavy corrosion was observed on the surface of the pipe
269 | 634 | Overflow Piping | 3 | 200mm diameter, approx. 7m PVC SDR 35 | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Wet Well | Process Mechanical | Process Piping |  |  |  |  | 0 | 2006 | [6 empty] | Good
198 | 13 | SEWAGE LIFT PUMP #2 | 2 | Sewage Lift Pump #2;Flygt;3127.090;0510181;7.5 L/s at 15 m TDH 7.5 HP | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Wet Well | Process Mechanical | Process Mechanical Equipment | FLYGT | 3127.090 | 0510182 |  | 2020 | 2006 |  |  | HR-JOSH-109 |  |  |  | Good
657 | 634 | Wet Well Vent Piping | 1 | 1/4 HP | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Wet Well | Building Mechanical | Building Services | [5 empty] | 2006 |  |  | HR-JOSH-095 |  |  |  | good | Minor painr wear |  | Resurface and repaint | 2022 | 250
658 | 198 | Pump 2 Discharge Piping | 3 | 100mm diameter, approx. 10m SS pipe | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Wet Well | Process Mechanical | Process Piping | [5 empty] | 2006 |  |  | HR-JOSH-116 |  |  |  | Fair | Heavy corrosion was observed on the surface of the pipe
203 | 634 | FAN EXHAUST #1 | 1 | 1/4 HP | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Wet Well | Building Mechanical | Building Services | PENN POWER VENTILATOR | REX 10Q | N/A |  | 2020 | 2006 |  |  | HR-JOSH-092 |  |  |  | good
605 |  | Dry Wall Thermostat | 1 | Installation year assumed to be 1972 | Halton |  | Weaver Avenue PS | WWPS | Dry Well | Building Mechanical | Building Services | [5 empty] | 1972 |  |  | HR-WEAV-005 |  |  |  | good
604 |  | Dry Wall Humidistat | 1 | Installation year assumed to be 1972 | Halton |  | Weaver Avenue PS | WWPS | Dry Well | Building Mechanical | Building Services | [5 empty] | 1972 |  |  | HR-WEAV-005 |  |  |  | good
598 | 649 | Dry Wall Portable Dehumidifier | 1 | Installation year assumed to be 1972 | Halton |  | Weaver Avenue PS | WWPS | Dry Well | Building Mechanical | Building Services | [5 empty] | 1972 |  |  | HR-WEAV-007 |  |  |  | good
597 | 649 | Dry Wall Sump Pump | 1 |  | Halton |  | Weaver Avenue PS | WWPS | Dry Well | Building Mechanical | Building Services | [5 empty] | 1972 |  |  | HR-WEAV-012 |  |  |  | surface corrosion
596 | 649 | Dry Wall Portable Heater | 1 | Installation year assumed to be 1972 | Halton |  | Weaver Avenue PS | WWPS | Dry Well | Building Mechanical | Building Services | [5 empty] | 1972 |  |  | HR-WEAV-010 |  |  |  | good
626 | 51 | Brick pathway | 1 |  | Halton |  | Weaver Avenue PS | WWPS | Site | Site Works | Site Works | [5 empty] | 1972 |  | 2035 | HR-WEAV-002 |  |  |  | Good
624 | 51 | Yard Hydrant | 1 |  | Halton | In Service | Weaver Avenue PS | WWPS | Site | Site Works | Site Works | [5 empty] | 1972 |  | 2035 | HR-WEAV-024 |  |  |  | Good
625 | 51 | Oveflow Structure | 2 |  | Halton | In Service | Weaver Avenue PS | WWPS | Site | Site Works | Site Works | [5 empty] | 1972 |  | 2035 | HR-WEAV-003 |  |  |  | Good
52 | 650 | Wet Well Structure | 3 | 7 foot inside diameter precast concrete | Halton | In Service | Weaver Avenue PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2032 | HR-WEAV-001 |  |  |  | Fair | Rust spots noted typically |  | Cut back rust spot, clean and patch with cementitous repair mortar | 2025 | 500
366 | 649 | Protective Paint | 1 | Weaver Avenue PS Dry Well | Halton | In Service | Weaver Avenue PS | WWPS | Dry Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2032 | HR-WEAV-107 |  |  |  | Fair | Weathered paint on exterior
50 | 649 | Dry Well Structure | 3 | Steel drywell by Smith & Loveless | Halton | In Service | Weaver Avenue PS | WWPS | Dry Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2032 | HR-WEAV-112 |  |  |  | Fair | Missing paint/corrosion noted |  | Grind to bare metal and touch up paint | 2021 | 500
370 | 649 | Davit Socket Base | 1 | Weaver Avenue PS Dry Well | Halton | In Service | Weaver Avenue PS | WWPS | Dry Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2032 | HR-WEAV-112 |  |  |  | Fair | To be inspected every eyar
365 | 649 | Access Ladder | 1 | Weaver Avenue PS Dry Well | Halton | In Service | Weaver Avenue PS | WWPS | Dry Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2040 | HR-WEAV-107 |  |  |  | Fair
367 | 650 | Access Ladder | 1 | Weaver Avenue PS Wet Well | Halton | In Service | Weaver Avenue PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2040 | HR-WEAV-001 |  |  |  | Fair
368 | 650 | Checker Plate Platform | 1 | Weaver Avenue PS Wet Well | Halton | In Service | Weaver Avenue PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2032 | HR-WEAV-001 |  |  |  | Fair | Surface corrosion noted
369 | 650 | Manhole Frame and Cover | 1 | Weaver Avenue PS Wet Well | Halton | In Service | Weaver Avenue PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2032 | HR-WEAV-002 |  |  |  | Fair
381 | 649 | Concrete Foundation | 1 | Weaver Avenue PS Dry Well | Halton | In Service | Weaver Avenue PS | WWPS | Dry Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2040 |  |  |  |  | Not accessible/inspected. Assumed to be good as no settlement was noted
364 | 650 | Access Hatch | 1 | Weaver Avenue PS Dry Well | Halton | In Service | Weaver Avenue PS | WWPS | Dry Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2040 | HR-WEAV-112 |  |  |  | Fair | Minor corrosion noted
90 | 88 | SEWAGE LIFT PUMP #1 MOTOR DRIVE | 1 | 7.5 HP; | Halton | In Service | Weaver Avenue PS | Weaver Avenue PS | Dry Well | Process Mechanical | Process Mechanical Equipment | ROBBIN & MYERS | N-BPM4 | YF7773-1 |  | 2020 | 1972 |  |  | HR-WEAV-014 |  |  |  | Fair | Deterioration was observed on the valve. The valve was beyond its expected service life.
543 | 649 | Main Transfer Switch | 2 | MTS; Square D; ; ; 600V, 60A | Halton | In Service | Weaver Avenue PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2007 |  | 2037 | HR-WEAV-038 |  |  |  | good
95 | 50 | SEWAGE LIFT PUMP #2 MOTOR DRIVE | 2 | 7.5 HP; Westinghouse; Model J; ;600v, 10HP | Halton |  | Weaver Avenue PS | Weaver Avenue PS | Dry Well | Process Mechanical | Process Electrical | ROBBIN & MYERS | N-BPM4 | YF7773-2 |  | 2020 | 1972 | [6 empty] | Fair | Deterioration was observed on the surface of the pump. The pump was beyond its expected service life.
544 | 649 | Gennerator Connect Receptacle | 2 | Gen Connect Recept; ; ; ; 600V, 60A | Halton | In Service | Weaver Avenue PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2007 |  | 2037 | HR-WEAV-042 |  |  |  | good
541 | 649 | Main Diwsconnect Switch | 2 | Main DS; Square D; ; ; 600V, 60A | Halton | In Service | Weaver Avenue PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2007 |  | 2037 | HR-WEAV-030 |  |  |  | good
456 | 649 | Outdoor Enclosure | 2 | Outdoor Enclosure; | Halton | In Service | Weaver Avenue PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2007 |  | 2037 | HR-WEAV-025 |  |  |  |  | good
545 | 649 | Drywell Lights | 1 | Drywell Lights; ; ; ; Fluorescent | Halton | In Service | Weaver Avenue PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 1972 |  | 2025 | HR-WEAV-047 |  |  |  | fair | to be replaced with LED fixtures rated for Class 1, div 2
546 | 649 | Control Panel | 2 | Control Panel; S&L; ; ; | Halton | In Service | Weaver Avenue PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 1972 |  | 2025 | HR-WEAV-004 |  |  |  | fair
542 | 649 | Power Meter | 2 | Power Meter; elster; ; ; 600V | Halton | In Service | Weaver Avenue PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2007 |  | 2037 | HR-WEAV-034 |  |  |  | good
86 | 649 | TRANSMITTER LEVEL - DRY WELL | 2 | Wet Well Level Transmitter; Siemens; Sitrans LUC500; ; ; | Halton | In Service | Weaver Avenue PS | Weaver Avenue PS | Dry Well | Process Instrumentation | Process Instrumentation | SIEMENS/MILLTRONICS | MULTIRANGER PLUS | PBD/W6120004 |  | 2020 | 2009 |  | 2030 | HR-WEAV-011 |  |  |  | Dust
85 | 650 | TRANSMITTER LEVEL WET WELL #1 | 2 | 100" Wet Well Level Transmitter; Siemens Milltronics; Multiranger Plus; ; ; | Halton | Not In Service | Weaver Avenue PS | Weaver Avenue PS | Dry Well | Process Instrumentation | Process Instrumentation | MILLTRONICS | MULTIRANGER PLUS | 011491 091-18 |  | 2020 | 2009 |  | 2030 | HR-WEAV-009 |  |  |  | good | nuts were not secured properly
452 | 649 | Sump Float | 2 | Sump Float; ; ; ; ; | Halton | In Service | Weaver Avenue PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation | [5 empty] | 2009 |  | 2030 | HR-WEAV-012 |  |  |  | good
451 | 649 | Exhaust Fan Timer | 2 | Exhaust Fan Timer; Paragon; ; ; ; | Halton | In Service | Weaver Avenue PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation | [5 empty] | 2009 |  | 2030 | HR-WEAV-005 |  |  |  | good
450 | 649 | Dry Well Temperature Controller | 2 | Dry Well Temperature Controller; Penn; ; ; ; | Halton | In Service | Weaver Avenue PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation | [5 empty] | 2009 |  | 2030 | HR-WEAV-005 |  |  |  | good
449 | 649 | Dry Well Humidity Controller | 2 | Dry Well Humidity Controller; Penn; ; ; | Halton | In Service | Weaver Avenue PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation | [5 empty] | 2009 |  | 2009 | HR-WEAV-005 |  |  |  | good
453 | 51 | Remote Signals Telephone Transmitter | 1 | Remote Signals Telephone Transmitter; Pribusin; IUC-X9-TXC; ; ; | Halton | In Service | Weaver Avenue PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation | [5 empty] | 2016 |  | 2030 | HR-WEAV-068 |  |  |  | good
84 | 649 | PUMP #1 SUMP | 2 | Sump Pump;;;; | Halton | In Service | Weaver Avenue PS | Weaver Avenue PS | Dry Well | Building Mechanical | Building Services | LITTLE GIANT | GE-CIA-SFC | GE-CIA-RFSN |  | 2020 | 1972 |  |  | HR-WEAV-012 |  |  |  | Very Poor | Severe corrosion was observed on the pump. The pump was beyond its expected service life.
88 | 50 | SEWAGE LIFT PUMP #1 | 2 | Sewage Lift Pump #1;Smith&Loveless;4B2;;30.3 L/s at 11.3 m TDH 7 HP | Halton | In Service | Weaver Avenue PS | WWPS | Dry Well | Process Mechanical | Process Mechanical Equipment | SMITH AND LOVELESS | N/A | 7210773-2 |  | 2020 | 1972 |  |  | HR-WEAV-014 |  |  |  | Fair | Corrosion was observed on the surface of the pump. No performance issues were identified, however; the pump was beyond its expected service life.
89 | 88 | SEWAGE LIFT PUMP #1 CHECK VALVE | 2 | Check Valve #1;Swing-Flex;504A;;100 mm dia | Halton | In Service | Weaver Avenue PS | Weaver Avenue PS | Dry Well | Process Mechanical | Process Mechanical Equipment | VALMATIC | SWING FLEX | N/A |  | 2020 | 1972 |  |  | HR-WEAV-015 |  |  |  | Fair | Deterioration was observed on the valve. The valve was beyond its expected service life.
91 | 88 | SEWAGE LIFT PUMP #1 INLET VALVE | 2 | Inlet Knife Gate Valve #1;;;;150 mm dia | Halton | In Service | Weaver Avenue PS | Weaver Avenue PS | Dry Well | Process Mechanical | Process Mechanical Equipment | IOWA | N/A | N/A |  | 2020 | 1972 |  |  | HR-WEAV-013 |  |  |  | Fair | Minor deterioration was observed on the surface of the valve but the valve was beyond its expected service life.
92 | 88 | SEWAGE LIFT PUMP #1 DISCHARGE VALVE | 2 | Discharge Knife Gate Valve #1;;;;150 mm dia | Halton | In Service | Weaver Avenue PS | Weaver Avenue PS | Dry Well | Process Mechanical | Process Mechanical Equipment | IOWA | N/A | N/A |  | 2020 | 1972 |  |  | HR-WEAV-016 |  |  |  | Fair | Corrosion and deterioration was observed on the surface of the valve. The valve was beyond its expected service life.
93 | 14 | SEWAGE LIFT PUMP #2 | 2 | Sewage Lift Pump 21;Smith&Loveless;4B2;;30.3 L/s at 11.3 m TDH 7 HP | Halton | In Service | Weaver Avenue PS | Weaver Avenue PS | Dry Well | Process Mechanical | Process Mechanical Equipment | SMITH AND LOVELESS | N/A | 7210773-2 |  | 2020 | 1972 |  |  | HR-WEAV-020 |  |  |  | Fair | Deterioration was observed on the surface of the pump. The pump was beyond its expected service life.
94 | 93 | SEWAGE LIFT PUMP #2 CHECK VALVE | 2 | Check Valve #2;Swing-Flex;504A;;100 mm dia | Halton | In Service | Weaver Avenue PS | Weaver Avenue PS | Dry Well | Process Mechanical | Process Mechanical Equipment | VALMATIC | SWING FLEX | N/A |  | 2020 | 1972 |  |  | HR-WEAV-019 |  |  |  | Fair | Deterioration was observed on the valve. The valve was beyond its expected service life.
97 | 93 | SEWAGE LIFT PUMP #2 DISCHARGE VALVE | 2 | Discharge Knife Gate Valve #1;;;;150 mm dia | Halton |  | Weaver Avenue PS | Weaver Avenue PS | Dry Well | Process Mechanical | Process Mechanical Equipment | TRUELINE | 316 SS KNIFE GATE | N/A |  | 2020 |  |  |  | HR-WEAV-018 |  |  |  | Fair | Minor deterioration was observed on the surface of the valve but the valve was beyond its expected service life.
272 | 650 | Overflow Piping | 3 | 300mm diameter, approx. 9m corrugated metal pipe | Halton | In Service | Weaver Avenue PS | Weaver Avenue PS | Wet Well | Process Mechanical | Process Piping |  |  |  |  | 0 | 1972 | [6 empty] | Fair | The pipe passed half of its expected service life.
98 | 51 | FORCEMAIN | 4 | 150mm diameter, approx. 153m ductile iron pipe | Halton | In Service | Weaver Avenue PS | Weaver Avenue PS | Site | Process Mechanical | Process Piping |  |  |  |  | 2020 | 1972 | [6 empty] | Fair | The pipe passed half of its expected service life.
274 | 650 | Bar Screen | 2 | Bar Screen;;;; | Halton | In Service | Weaver Avenue PS | Weaver Avenue PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  |  |  |  | 0 | 1972 | [6 empty] | Fair | The bar screen passed half of its expected service life.
273 | 88 | Pump 1 Piping | 3 | 150mm diameter, approx. 5 m ductile iron pipe | Halton | In Service | Weaver Avenue PS | Weaver Avenue PS | Wet Well | Process Mechanical | Process Piping |  |  |  |  | 0 | 1972 |  |  | HR-WEAV-022 |  |  |  | Fair | The pipe passed half of its expected service life.
96 | 93 | SEWAGE LIFT PUMP #2 INLET VALVE | 2 | Inlet Knife Gate Valve #2;;;;150 mm dia | Halton |  | Weaver Avenue PS | Weaver Avenue PS | Dry Well | Process Mechanical | Process Mechanical Equipment | IOWA | N/A | N/A |  | 2020 |  |  |  | HR-WEAV-021 |  |  |  | Fair | Minor deterioration was observed on the surface of the valve but the valve was beyond its expected service life.
87 | 50 | FAN EXHAUST #1 | 1 | 115 VOLTS | Halton |  | Weaver Avenue PS | Weaver Avenue PS | Dry Well | Building Mechanical | Building Services | N/A | N/A | N/A |  | 2020
655 | 93 | Pump 2 Piping | 3 | 150mm diameter, approx. 5 m ductile iron pipe | Halton | In Service | Weaver Avenue PS | Weaver Avenue PS | Wet Well | Process Mechanical | Process Piping | [5 empty] | 1972 |  |  | HR-WEAV-022 |  |  |  | Fair | The pipe passed half of its expected service life.

## r_tblAsset
AssetID | ParentID | AssetName | CoF | AssetDescription | Owner | Status | SiteName | FacilityName | LocationName | AssetCategory | CustomClientCategory | Manufacturer | Model | SerialNumber | InspectionType | AssessmentYear | InstallYear | AvgESL | ReplaceYear | PhotoName | VisualCondition | PerformanceCondition | PoF | TempComments1 | TempComments2 | TempComments3 | TempRehabComment | TempRehabYear | TempRehabCost
113 | 631 | Wet Well Exhaust Fan | 1 | built-in explosion-proof ventilation fan, motor capacity: 0.5 HP | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Building Mechanical | Building Services | N/A | N/A | N/A |  | 2020 | 1988 |  |  | HR-BAES-010 |  |  |  | heavy corrosion
569 | 631 | Wet Well Gooseneck Ventilation Pipes | 1 | Two 4 inch diameter aluminum vents with bird screen | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Building Mechanical | Process Mechanical Equipment | [5 empty] | 1988 |  |  | HR-BAES-002 |  |  |  | paint peeling at the portion above the wet well |  |  | Repaint the ventilation pipes | 2023 | 500
608 | 18 | Yard Hydrant | 1 |  | Halton | In Service | Belaire Dr. PS | WWPS | Site | Site Works | Site Works | [5 empty] | 1988 |  | 2035 | HR-BAES-002 |  |  |  |  | Good
19 | 631 | Wet Well Concrete Structure | 2 | Belaire Dr. PS Wet Well | Halton | In Service | Belaire Dr. PS | WWPS | Process Structural | Process Structural | Building and Process Structural | [5 empty] | 1988 |  | 2048 | HR-BAES-051 |  |  |  | Fair | Concrete spalling and exposed corroded reinforcement |  | Remove loose concrete, clean reinforcement and apply rust inhibiting paint and patch with cementitous repair mortar | 2025 | 2000
288 | 631 | Aluminum Guardrails | 2 |  | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1988 |  | 2048 | HR-BAES-051 |  |  |  | corosion | Fair
287 | 631 | Aluminum Platform | 2 |  | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1988 |  | 2048 | HR-BAES-051 |  |  |  | Fair | corosion on the platform
286 | 631 | Access Ladder | 2 | Platform to wet well base | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1988 |  | 2048 | HR-BAES-051 |  |  |  |  | fair
285 | 631 | Access Ladder | 2 | Entrance to platform | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1988 |  | 2048 | HR-BAES-051 |  |  |  | fair
282 | 631 | Access Hatch | 1 | Belaire Dr. PS Wet Well | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1988 |  | 2048 | HR-BAES-002 |  |  |  | good
228 | 18 | Emergency By-Pass Piping | 3 | 100mm Diameter Ductile Iron Riser piping with end threaded to accpet cap in a junction box. Approx. 3.6m. | Halton | In Service | Belaire Dr. PS | Belaire Dr. PS | Site | Process Mechanical | Process Piping |  |  |  |  | 0 | 1988 | [6 empty] | assumed to be fair
227 | 631 | Pump 2 Discharge Piping | 3 | 100mm Diameter, approx. 2.5m, Class 52 Ductile Iron discharge piping connected to 100mm PVC forcemain | Halton | In Service | Belaire Dr. PS | Belaire Dr. PS | Wet Well | Process Mechanical | Process Piping |  |  |  |  | 0 | 1988 |  |  | HR-BAES-015 |  |  |  | Heavy corrosion | Heavy corrosion and deterioration was observed on the piping
120 | 18 | FORCEMAIN | 4 | 100mm diameter, approx. 73.15m PVC forcemain | Halton | In Service | Belaire Dr. PS | Belaire Dr. PS | Site | Process Mechanical | Process Piping |  |  |  |  | 2020 | 1988 | [6 empty] | assumed to be good
652 | 631 | Pump 1 Discharge Piping | 3 | 100mm Diameter, approx. 2.5m, Class 52 Ductile Iron discharge piping connected to 100mm PVC forcemain | Halton | In Service | Belaire Dr. PS | Belaire Dr. PS | Wet Well | Process Mechanical | Process Piping | [5 empty] | 1988 |  |  | HR-BAES-015 |  |  |  | poor | Heavy corrosion and deterioration was observed on the piping
283 | 631 | Pump Hatch 1 | 1 | Belaire Dr. PS Wet Well | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1988 |  | 2048 | HR-BAES-002 |  |  |  | Fair | HS: Missing hatch grating |  | Install safety grating | 2021 | 1000
314 | 631 | Grab Bar | 2 | Belaire Dr. PS Wet Well | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1988 |  | 2048 | HR-BAES-002 |  |  |  | Fair | HS: Grab bar is loose |  | Tighten as required | 2021 | 100
284 | 631 | Pump Hatch 2 | 1 | Belaire Dr. PS Wet Well | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1988 |  | 2048 | HR-BAES-002 |  |  |  | Fair | HS: Missing hatch grating |  | Install safety grating | 2021 | 1000
313 | 631 | Davit Socket Base | 2 | Belaire Dr. PS Wet Well | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1988 |  | 2048 | HR-BAES-002 |  |  |  | Fair | To be inspected yearly |  | conduct inspection | 2021 | 500
474 | 18 | Main Breaker | 2 | Main Breaker; Westinghouse; Series C FDB; ; 600V, 60A-2P | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Process Electrical | Process Electrical | [5 empty] | 1988 |  | 2030 | IMG_20200702_083922 |  |  |  | good
473 | 18 | Power Meter | 2 | Power Meter; ; ; ; | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Process Electrical | Process Electrical | [5 empty] | 2010 |  | 2040 | IMG_20200702_083914 |  |  |  | good
472 | 18 | Generator Receptacle | 2 | Generator Receptacle; ; ; ; | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Process Electrical | Process Electrical | [5 empty] | 1988 |  |  | IMG_20200702_082805 |  |  |  | good
471 | 18 | Control Logic Panel | 2 | Control Logic Panel; ; ; ; | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Process Electrical | Process Electrical | [5 empty] | 1988 |  | 2030 | IMG_20200702_082805 |  |  |  | good
470 | 18 | Pump Duplex Control | 2 | Pump Duplex Control with Disconnect switch; ; ; ; 120/240V, 3.9HP | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Process Electrical | Process Electrical | [5 empty] | 1988 |  | 2030 | IMG_20200702_083731 |  |  |  | good | phase converters inside panel to be replaced with VFDs
469 | 18 | Electrical Outdoor Enclosure | 2 | Outdoor Enclosure; ; ; ; | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Process Electrical | Process Electrical | [5 empty] | 1988 |  | 2030 | IMG_20200702_082737 |  |  |  | fair | bottom of the enclosre is severly corroded | to be replaced with NEMA 3R enclosure
467 | 631 | Wet Well Lighting | 1 | Lighting; ; ; ; | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Building Electrical | Building Services | [5 empty] | 1988 |  | 2022 | HR-BAES-040 |  |  |  | poor | heaviliy corroded
475 | 18 | Manual Transfer Switch | 2 | Manual Transfer Switch; GE; ; ; 600V, 60A | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Process Electrical | Process Electrical | [5 empty] | 1988 |  | 2030 | IMG_20200702_083922 |  |  |  | good
468 | 18 | Panel Outdoor Light | 1 | Pole Light; ; ; ; | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Building Electrical | Building Services | [5 empty] | 1988 |  | 2030 | IMG_20200702_082700 |  |  |  | good | to be replaced with LED in next upgrade
416 | 631 | Wet Well Level Transmitter | 2 | Wet Well Level Transmitter; Siemens Milltronics; Multiranger 200; ; ; | Halton | In Service | Belaire Dr. PS | WWPS | Site | Process Instrumentation | Process Instrumentation | [5 empty] | 2014 |  | 2030 | HR-BAES-054 |  |  |  |  | Dust
418 | 631 | Wet Well Floats | 2 | Wet Well Floats; ; ; ; ; | Halton | In Service | Belaire Dr. PS | WWPS | Wet Well | Process Instrumentation | Process Instrumentation | [5 empty] | 2016 |  | 2030 | HR-BAES-036 |  |  |  | Corrosion
417 | 18 | Remote Signals Telephone Transmitter | 1 | Remote Signals Telephone Transmitter; Pribusin; IUC-X9-TXC; ; ; | Halton | In Service | Belaire Dr. PS | WWPS | Site | Process Instrumentation | Process Instrumentation | [5 empty] | 2016 |  | 2030 | HR-BAES-055 |  |  |  | Dust
119 | 631 | SEWAGE LIFT PUMP #2 DISCHARGE VALVE | 2 | Gate Valve #1 with Handwheel;;;;100 mm | Halton | In Service | Belaire Dr. PS | Belaire Dr. PS | Wet Well | Process Mechanical | Process Mechanical Equipment | CRANE | GATE VALVE | N/A |  | 2020 | 1988 |  |  | HR-BAES-006 |  |  |  | Poor | Heavy corrosion and deterioration was observed on the service of the valve. The valve was near the end of its expected service life.
115 | 631 | SEWAGE LIFT PUMP #1 CHECK VALVE | 2 | Check Valve #1;;;;100 mm | Halton | In Service | Belaire Dr. PS | Belaire Dr. PS | Wet Well | Process Mechanical | Process Mechanical Equipment | JENKINS-McAVITY | N/A | N/A |  | 2020 | 1988 |  |  | HR-BAES-009 |  |  |  | Poor | Heavy corrosion and deterioration was observed on the service of the valve. The valve was near the end of its expected service life.
388 | 19 | VALVE DISCHARGE FORCEMAIN | 2 | Gate Valve #3 with Handwheel;;;;100 mm | Halton | In Service | Belaire Dr. PS | Belaire Dr. PS | Wet Well |  | Process Mechanical Equipment | [5 empty] | 1988 |  |  | HR-BAES-005 |  |  |  | Poor | Severe corrosion and deterioration was observed on the service of the valve. The valve was near the end of its expected service life.
117 | 631 | SEWAGE LIFT PUMP #2 | 2 | Sewage Pump #1;Flygt;CP 3085;;6.3 L/s at 4.7 m TDH 2 HP | Halton | In Service | Belaire Dr. PS | Belaire Dr. PS | Wet Well | Process Mechanical | Process Mechanical Equipment | FLYGT | C3102-180 | L07288 |  | 2020 | 1988 |  |  | HR-BAES-015 |  |  |  | Poor | The pump is working but it is near the end of its expected service life.
116 | 631 | SEWAGE LIFT PUMP #1 DISCHARGE VALVE | 2 | Gate Valve #1 with Handwheel;;;;100 mm | Halton | In Service | Belaire Dr. PS | Belaire Dr. PS | Wet Well | Process Mechanical | Process Mechanical Equipment | CRANE | GATE VALVE | N/A |  | 2020 | 1988 |  |  | HR-BAES-008 |  |  |  | Poor | Heavy corrosion and deterioration was observed on the service of the valve. The valve was near the end of its expected service life.
118 | 631 | SEWAGE LIFT PUMP #2 CHECK VALVE | 2 | Check Valve #1;;;;100 mm | Halton | In Service | Belaire Dr. PS | Belaire Dr. PS | Wet Well | Process Mechanical | Process Mechanical Equipment | MCAVITY | SWING CHECK | N/A |  | 2020 | 1988 |  |  | HR-BAES-007 |  |  |  | Poor | Heavy corrosion and deterioration was observed on the service of the valve. The valve was near the end of its expected service life.
226 | 631 | Discharge Header | 3 | 100mm Diameter, approx. 5m, Class 52 Ductile Iron discharge piping connected to 100mm PVC forcemain | Halton | In Service | Belaire Dr. PS | Belaire Dr. PS | Wet Well | Process Mechanical | Process Piping |  |  |  |  | 0 | 1988 |  |  | HR-BAES-026 |  |  |  | Poor | Heavy corrosion and deterioration was observed on the piping
114 | 631 | SEWAGE LIFT PUMP #1 | 2 | Sewage Pump #1;Flygt;CP 3085;;6.3 L/s at 4.7 m TDH 2 HP | Halton | In Service | Belaire Dr. PS | Belaire Dr. PS | Wet Well | Process Mechanical | Process Mechanical Equipment | FLYGT | C3102-180.1307 | L07283188 |  | 2020 | 1988 |  |  | HR-BAES-018 |  |  |  | Fair. | The pump is working but it is near the end of its expected service life.
631 | 2 | Wet Well | 3 |  | Halton |  | Belaire Dr. PS |  |  | Process Structural | Building and Process Structural
572 | 635 | Dry Well Portable Heater | 1 | Installation year assumed to be 1972 | Halton | In Service | Carrington Place PS | WWPS | Dry Well | Building Mechanical | Building Services | [5 empty] | 1972 |  |  | HR-CRTN-045 |  |  |  | good
571 | 20 | Dry Well Sump Pump | 1 | Installation year assumed to be 1970 | Halton | In Service | Carrington Place PS | Carrington Place PS | Dry Well | Building Mechanical | Building Services | [5 empty] | 1970 |  |  | HR-CARD-145
573 |  | Wet Well Gooseneck Ventilation Pipes | 1 | Two 4 inches diameter steel pipe vents with bird screen | Halton | In Service | Carrington Place PS | WWPS | We Well | Building Mechanical | Process Mechanical Equipment | [5 empty] | 1972 |  |  | HR-CRTN-033 |  |  |  | paint peeling
599 | 635 | Dry Well Thermostat | 1 | Installation year assumed to be 1972 | Halton | In Service | Carrington Place PS | WWPS | We Well | Building Mechanical | Building Services | [5 empty] | 1972 |  |  | HR-CRTN-124 |  |  |  | operability of the asset was unknown
570 | 635 | Dry Well Dehumidifier | 1 | Installation year assumed to be 1970 | Halton | In Service | Carrington Place PS | WWPS | Dry Well | Building Mechanical | Building Services | [5 empty] | 1970 |  |  | HR-CARD-123 |  |  |  | good
609 | 21 | Yard Hydrant (New Asset) | 1 |  | Halton |  | Carrington Place PS | WWPS | Site | Site Works | Site Works | [12 empty] | There was no yard hydrant | In accordance with Section 19.8.3 of the Region's Water and Wastewater Design Manual (January 2012), a yard hydrant complete with a backflow preventer with a 37.5mm water service line shall be provided for flushing and cleaning purposes. It is recommended
219 | 635 | SEWAGE LIFT PUMP #2 MOTOR DRIVE | 2 | 15.0 HP | Halton | In Service | Carrington Place PS | Carrington Place PS | Dry Well | Process Mechanical | Process Electrical | BROOK ELECTRIC | N/A | X608521 |  | 2020 | 1972 | [6 empty] | fair | Deterioration and corrosion was obeserved on the surface of the motor. The motor was beyond its expected service life.
386 | 289 | Manhole Frame and Cover | 2 |  | Halton | In Service | Carrington Place PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2032 |  |  |  |  | Fair | Surface corrosion on underside
290 | 635 | Dry Well Access Ladder | 2 | Carrington Place PS Dry Well | Halton | In Service | Carrington Place PS | WWPS | Dry Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2032 | HR-CRTN-035 |  |  |  | Fair
291 | 635 | Dry Well Access Hatch | 2 | Carrington Place PS Dry Well | Halton | In Service | Carrington Place PS | WWPS | Dry Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2032 | HR-CRTN-033 |  |  |  | Fair | Corrosion on top surface |  | Clean and touch up paint | 2021 | 300
292 | 635 | Protective Paint | 2 | Carrington Place PS Dry Well | Halton | In Service | Carrington Place PS | WWPS | Dry Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2032 | HR-CRTN-035 |  |  |  | Fair | Peeling paint noted
293 | 636 | Wet Well Access Ladder | 2 |  | Halton | In Service | Carrington Place PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2032 | HR-CRTN-001 |  |  |  | Fair | HS: Missing rung at platform level |  | Install missing run | 2021 | 500
294 | 636 | Manhole Frame and Cover | 1 |  | Halton | In Service | Carrington Place PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2032 | HR-CRTN-001 |  |  |  | Fair | Surface corrosion on underside
295 | 636 | Wet Well Aluminum Grating | 2 |  | Halton | In Service | Carrington Place PS | WWPS | Dry Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2032 | HR-CRTN-036 |  |  |  | Fair
296 | 636 | Wet Well Aluminum Platform | 2 | Carrington Place PS Dry Well | Halton | In Service | Carrington Place PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2025 | HR-CRTN-080 |  |  |  | Fair to poor | Corrosion noted
312 | 635 | Davit Socket Base | 2 | Carrington Place PS Dry Well | Halton | In Service | Carrington Place PS | WWPS | Dry Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2032 | HR-CRTN-004 |  |  |  | Fair | To be inspected yearly
20 | 635 | Dry Well Structure | 2 | Carrington Place PS Dry Well | Halton | In Service | Carrington Place PS | WWPS | Dry Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2032 | HR-CRTN-036 |  |  |  | Fair | Corrosion noted |  | Grind to bare metal and touch up paint | 2021 | 2000
289 | 636 | Wet Well Concrete Structure | 2 | Carrington Place PS Dry Well | Halton | In Service | Carrington Place PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2032 | HR-CRTN-001 |  |  |  | Fair | Brick riser supporting manhole frame is loose |  | Reparge brick riser | 2021 | 500
564 | 21 | Generator Connect Recept (New Asset) | 2 | New Gen Connect Recept; ; ; ; ;600V, 50A | Halton | In Service | Carrington Place PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2021 |  |  | IMG_20200629_125113 |  |  |  | There was no Generator Connection Receptical and Manual Transfer Switch located on site. Paralleling power sources and severe electrical shock hazard while hardwiring the generator for emergency power | to be installed (above ground) to comply with industry practice
478 | 20 | Main Breaker | 2 | Main Breaker; Moeller; 6-63/62-u; ; 600V, 60A | Halton | In Service | Carrington Place PS | Carrington Place PS | Dry Well | Process Electrical | Process Electrical | [5 empty] | 1972 |  | 2025 | IMG_20200629_125233 |  |  |  |  | good | discountinued
481 | 20 | Power Panel | 2 | Power Panel indluding Pump relays; Moeller; ; ; ; | Halton | In Service | Carrington Place PS | WWPS | Dry Well | Process Electrical | Process Electrical | [5 empty] | 1972 |  | 2030 | IMG_20200629_125113 |  |  |  | fair | corrosion was observed in different inside and surface of panel | missing Arc Flash Labels
563 | 20 | Main Disconnect Switch | 2 | New main DS; ; ; ; ;600V, 50A | Halton | In Service | Carrington Place PS | WWPS | Dry Well | Process Electrical | Process Electrical | [5 empty] | 2021 |  | 2021 | IMG_20200629_125113 |  |  |  | fair | to be installed (above ground) to comply with industry practice
480 | 20 | Pump #2 Breaker | 2 | Pump #2 Breaker; Moeller; NZM 6-63/62-u; ; 600V, 50A | Halton | In Service | Carrington Place PS | Carrington Place PS | Dry Well | Process Electrical | Process Electrical | [5 empty] | 1972 |  | 2025 | 00000IMG_00000_BURST20200629125320236_COVER |  |  |  | good
479 | 20 | Pump #1 Breaker | 2 | Pump #1 Breaker; Moeller; NZM 6-63/62-u; ; 600V, 36A | Halton | In Service | Carrington Place PS | Carrington Place PS | Dry Well | Process Electrical | Process Electrical | [5 empty] | 1972 |  | 2025 | 00000IMG_00000_BURST20200629125326278_COVER |  |  |  | good | discountinued
562 | 20 | Manual Transfer Switch | 2 | MTS; ; ; ; ;600V, 50A | Halton | In Service | Carrington Place PS | WWPS | Dry Well | Process Electrical | Process Electrical | [5 empty] | 2021 |  |  | IMG_20200629_125113 |  |  |  | Fair | to be installed (above ground) to comply with industry practice
477 | 635 | Drywell Lights | 1 | Drywell Lights; ; ; ; 2 fixture, class 1, div 2 rated | Halton | In Service | Carrington Place PS | WWPS | Dry Well | Building Electrical | Building Services | [5 empty] | 1972 |  | 2025 | 00100lrPORTRAIT_00100_BURST20200629125448497_COVER |  |  |  | good | replace with LED fixture in next upgrade
476 | 635 | Power Meter | 2 | Power Meter; ; ; ; | Halton | In Service | Carrington Place PS | WWPS | Dry Well | Process Electrical | Process Electrical | [5 empty] | 2011 |  | 2041 | IMG_20200629_125120 |  |  |  | good | move it above ground
414 | 636 | Wet Well Floats | 2 | Wet Well Floats; ; ; ; ; | Halton | In Service | Carrington Place PS | WWPS | Wet Well | Process Instrumentation | Process Instrumentation | [5 empty] | 2008 |  | 2030 | HR-CRTN-080 |  |  |  |  | good
412 | 635 | Sump Float | 2 | Sump Float; ; ; ; | Halton | In Service | Carrington Place PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation | [5 empty] | 2008 |  | 2030 | HR-CRTN-018 |  |  |  | Corrrosion | fair
415 |  | Discharge Flow Meter | 2 | Discharge Flow Meter; Siemens; Strans F; ; ; | Halton | Not In Service | Carrington Place PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation | [5 empty] | 2008 |  | 2030 | HR-CRTN-020 |  |  |  | fair | Corrosion
209 | 636 | TRANSMITTER LEVEL WET WELL #1 | 2 | Wet Well Level Transmitter; Siemens Milltronics; Multiranger 200; | Halton | In Service | Carrington Place PS | Carrington Place PS | Dry Well | Process Instrumentation | Process Instrumentation | MILLTRONICS | MULTIRANGER PLUS | 09873860-0 |  | 2020 | 2008 |  | 2030 | HR-CRTN-137 |  |  |  | Corrosion | good
222 | 21 | FORCEMAIN | 4 | 200mm diameter, Ductile Iron, approx. 800m | Halton | In Service | Carrington Place PS | Carrington Place PS | Site | Process Mechanical | Process Piping |  |  |  |  | 2020 | 1972 | [6 empty] | Fair | The pipe passed half of its expected service life
213 | 635 | SEWAGE LIFT PUMP #1 CHECK VALVE | 2 | Check Valve #1;Swing-Flex;;;100 mm dia | Halton | In Service | Carrington Place PS | WWPS | Dry Well | Process Mechanical | Process Mechanical Equipment | SWING FLEX | 504 |  |  | 2020 | 1972 |  |  | HR-CRTN-010 |  |  |  | fair | Corrosion and deterioration was observed on the surface of the valve. The valve was beyond its expected service life.
220 | 635 | SEWAGE LIFT PUMP #2 INLET VALVE | 2 | Inlet Gate Valve #1;;;;200 mm dia | Halton | In Service | Carrington Place PS | Carrington Place PS | Dry Well | Process Mechanical | Process Mechanical Equipment | RED WHITE | N/A | N/A |  | 2020 | 1972 |  |  | HR-CRTN-016 |  |  |  | Poor | Corrosion and deterioratino was observed on the valve. The valve was beyond its expected service life.
218 | 635 | SEWAGE LIFT PUMP #2 CHECK VALVE | 2 | Check Valve #1;Swing-Flex;;;100 mm dia | Halton | In Service | Carrington Place PS | Carrington Place PS | Dry Well | Process Mechanical | Process Mechanical Equipment | SWING FLEX | 504 |  |  | 2020 | 1972 |  |  | HR-CRTN-014 |  |  |  | fair | Corrosion and deterioration was observed on the surface of the valve. The valve was beyond its expected service life.
217 | 635 | SEWAGE LIFT PUMP #2 | 2 | Sewage Lift Pump #1;Smith & Loveless;;;15 HP | Halton | In Service | Carrington Place PS | Carrington Place PS | Dry Well | Process Mechanical | Process Mechanical Equipment | NAPANEE |  |  |  | 2020 | 1972 |  |  | HR-CRTN-015 |  |  |  | fair | Deterioration and corrosion was obeserved on the surface of the pump. The pump was beyond its expected service life.
212 | 635 | SEWAGE LIFT PUMP #1 | 2 | Sewage Lift Pump #1;Smith & Loveless;;;15 HP | Halton | In Service | Carrington Place PS | Carrington Place PS | Dry Well | Process Mechanical | Process Mechanical Equipment | NAPANEE |  |  |  | 2020 | 1972 |  | 2026 | HR-CRTN-008 |  |  |  | fair | Deterioration and corrosion was obeserved on the surface of the pump. The pump was beyond its expected service life.
215 | 635 | SEWAGE LIFT PUMP #1 INLET VALVE | 2 | Inlet Gate Valve #1;;;;200 mm dia | Halton | In Service | Carrington Place PS | Carrington Place PS | Dry Well | Process Mechanical | Process Mechanical Equipment | RED WHITE | N/A | N/A |  | 2020 | 1972 |  |  | HR-CRTN-006 |  |  |  | fair | Corrosion and deterioratino was observed on the valve. The valve was beyond its expected service life.
216 | 635 | SEWAGE LIFT PUMP #1 DISCHARGE VALVE | 2 | Discharge Gate Valve #1;;;;100 mm dia | Halton | In Service | Carrington Place PS | Carrington Place PS | Dry Well | Process Mechanical | Process Mechanical Equipment | KV | N/A | N/A |  | 2020 | 1972 | [6 empty] | fair | Corrosion and deterioratino was observed on the valve. The valve was beyond its expected service life.
398 | 636 | Bar Screen | 2 | Bar Screen;;;; | Halton | In Service | Carrington Place PS | WWPS | Wet Well | Process Mechanical | Process Mechanical Equipment | [5 empty] | 1972 | [6 empty] | fair | The screen was beyond its expected service life.
233 | 21 | Overflow Piping | 2 | 200mm Diameter, Concrete C14 Piping, approx. 50m | Halton | In Service | Carrington Place PS | Carrington Place PS | Site | Process Mechanical | Process Piping |  |  |  |  | 0 | 1972 | [6 empty] | Fair | The pipe was over half of its expected service life.
208 | 635 | PUMP #1 SUMP | 1 | Sump Pump;Little Giant;;; | Halton | In Service | Carrington Place PS | Carrington Place PS | Dry Well | Building Mechanical | Process Mechanical Equipment | LITTLE GIANT | N/A | N/A |  | 2020 | 1972 |  |  | HR-CARD-145 |  |  |  | The sump pump was beyond its expected service life. | fair
221 | 635 | SEWAGE LIFT PUMP #2 DISCHARGE VALVE | 2 | Discharge Gate Valve #1;;;;100 mm dia | Halton | In Service | Carrington Place PS | Carrington Place PS | Dry Well | Process Mechanical | Process Mechanical Equipment | NEWMAN HATTERSLEY | FIG.#T504 | N/A |  | 2020 | 1972 |  |  | HR-CRTN-016 |  |  |  | fair | Corrosion and deterioratino was observed on the valve. The valve was beyond its expected service life.
230 | 635 | Pump 1 Piping | 3 | 200mm (8") Diameter, Ductile Iron Piping, approx. 3m | Halton | In Service | Carrington Place PS | Carrington Place PS | Dry Well | Process Mechanical | Process Piping |  |  |  |  | 0 | 1972 | [6 empty] | fair | The pipe was over half of its expected service life.
232 | 635 | Pump 2 Piping | 3 | 200mm Diameter, Ductile Iron, approx. 5 m | Halton | In Service | Carrington Place PS | WWPS | Dry Well | Process Mechanical | Process Piping |  |  |  |  | 0 | 1972 | [6 empty] | fair | The pipe was over half of its expected service life.
211 | 635 | FAN EXHAUST #1 | 1 | 115 VOLTS | Halton | Missing | Carrington Place PS | Carrington Place PS | Dry Well | Building Mechanical | Building Services | N/A | N/A | N/A |  | 2020 | 1972 | [6 empty] | CC: As per Section 7.2.9 of MOECC's Design Guidelines for Sewage Works, mechanical ventilation is required for below ground surface dry well. | missing
210 | 20 | CONTROL PROCESS FLOW CAR PLACE | 2 |  | Halton |  | Carrington Place PS | Carrington Place PS | Dry Well | Process Electrical | Process Electrical | SIEMENS -CONTROLOTRON | 1010NR-T2KGS-S2 | U23428 |  | 2020
214 | 635 | MOTOR DRIVE SEWAGE LIFT PUMP #1 | 2 | 15.0 HP | Halton | In Service | Carrington Place PS | WWPS | Dry Well | Process Mechanical | Process Electrical | BROOK ELECTRIC MOTORS | N/A | X663787 |  | 2020 | 1972 | [6 empty] | Deterioration and corrosion was obeserved on the surface of the motor. The motor was beyond its expected service life. | fair
574 | 637 | Wet Well Gooseneck Ventilation Pipes | 1 | Two 3 inches diameter steel pipe vents | Halton | In Service | Cedarberry Court PS | WWPS | Wet Well | Building Mechanical | Building Services | [5 empty] | 1972 |  |  | HR-CBRY-019 |  |  |  | Staining at the bottom section of the pipe
610 | 22 | Yard Hydrant | 1 |  | Halton | In Service | Cedarberry Court PS | WWPS | Site | Site Works | Site Works | [5 empty] | 1977 |  | 2035 | HR-CBRY-025 |  |  |  |  | Good
311 | 637 | Grab Bar | 1 | Cedarberry Court PS Wet Well | Halton | In Service | Cedarberry Court PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1976 |  | 2036 | HR-CBRY-025 |  |  |  | Fair
310 | 637 | Davit Socket Base | 1 | Cedarberry Court PS Wet Well | Halton | In Service | Cedarberry Court PS | WWPS | Wet Well | Building Structural | Building and Process Structural | [5 empty] | 1976 |  | 2036 | HR-CBRY-025 |  |  |  | Fair | To be inspected yearly
300 | 637 | Aluminum Platform | 2 | Cedarberry Court PS Wet Well | Halton | In Service | Cedarberry Court PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1976 |  | 2036 | HR-CBRY-044 |  |  |  | Fair | HS: Grating not clipped
299 | 637 | Access Ladder | 1 | Cedarberry Court PS Wet Well | Halton | In Service | Cedarberry Court PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1976 |  | 2036 | HR-CBRY-044 |  |  |  | Fair
298 | 637 | Pump Hatch | 1 | Cedarberry Court PS Wet Well | Halton | In Service | Cedarberry Court PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1976 |  | 2036 | HR-CBRY-025 |  |  |  | Fair | HS: Missing safety grating |  | Install safety grating | 2021 | 1000
297 | 637 | Access Hatch | 1 | Cedarberry Court PS Wet Well | Halton | In Service | Cedarberry Court PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1976 |  | 2036 | HR-CBRY-025 |  |  |  | Fair
23 | 637 | Wet Well Concrete Structure | 3 | Cedarberry Court PS Wet Well | Halton | In Service | Cedarberry Court PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1976 |  | 2036 | HR-CBRY-044 |  |  |  | Fair | Concrete spalling on roof, rust spots and concrete spalling at pipe penetration |  | Cut back rust spots, remove loose concrete, clean reinforcement and coat with rust inhibiting paint and patch with cementitous repair mortar | 2025 | 5000
484 | 22 | Control Panel | 2 | Control Panel; ; ; ; | Halton | In Service | Cedarberry Court PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 1977 |  | 2025 | IMG_2861 |  |  |  | good | arc flash hazard label was painted on
561 | 22 | Power meter (New Asset) | 2 | New Power meter; ; ; ; 240V, 60A | Halton | In Service | Cedarberry Court PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2021 | [6 empty] | to be installed to comply with industry practice
560 | 4 | Fused Disconnect Switch (New Asset) | 1 | New fused DS; ; ; ; 240V, 60A | Halton | In Service | Cedarberry Court PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2021 | [6 empty] | to be installed to comply with industry practice
559 | 22 | Generator Connect Recept (New Asset) | 2 | New Generaor Connect Recept ; ; ; 240V, 60A | Halton | In Service | Cedarberry Court PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2021 | [6 empty] | HS: There was no Generator Connection Receptical and Manual Transfer Switch located on site. Paralleling power sources and severe electrical shock hazard while hardwiring the generator for emergency power | to be installed to comply with industry practice
558 | 22 | Manual Transfer Switch (New Asset) | 2 | New Manual Transfer Switch; ; ; ; 240V, 60A | Halton | In Service | Cedarberry Court PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2021 | [6 empty] | to be installed to comply with industry practice
483 | 4 | Outdoor Enclosure | 2 | Outdoor Enclosure; ; ; ; | Halton | In Service | Cedarberry Court PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 1977 |  | 2025 | IMG_2849 |  |  |  | fair | bottom interior of panel was corroded | Replace with NEMA 3R enclosure
482 | 22 | Panel Flood Light | 1 | Panel Flood Light; ; ; ; | Halton | In Service | Cedarberry Court PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 1977 |  | 2025 | IMG_2850 |  |  |  | good
419 | 637 | Wet Well Floats | 2 | Wet Well Floats; ; ; ; ; | Halton | In Service | Cedarberry Court PS | WWPS | Wet Well | Process Instrumentation | Process Instrumentation | [5 empty] | 2016 |  | 2018 | HR-CBRY-034 |  |  | 2 | Corrosion
121 | 637 | TRANSMITTER LEVEL - WETWELL | 2 | Wet Well Level Transmitter; Siemens Milltronics; Multiranger 200; ; ; | Halton | In Service | Cedarberry Court PS | Cedarberry Court PS | Wet Well | Process Instrumentation | Process Instrumentation | MILLTRONICS | MULTIRANGER 100 | PBD-T4180482 XB |  | 2020 | 2014 |  | 2030 | HR-CBRY-053 |  |  | 2 | good
234 | 22 | Overflow Piping | 3 | 200mm diameter, 6.4 m | Halton |  | Cedarberry Court PS | Cedarberry Court PS | Site | Process Mechanical | Process Piping |  |  |  |  | 0 | 1977
235 | 122 | Pump 1 Piping | 3 | 100mm diameter, approx. 5 m discharge piping | Halton | In Service | Cedarberry Court PS | Cedarberry Court PS | Wet Well | Process Mechanical | Process Piping |  |  |  |  | 0 | 1977 |  |  | HR-CBRY-048 |  |  |  | Poor | Severe deterioration was observed on the service piping
127 | 125 | SEWAGE LIFT PUMP #2 DISCHARGE VALVE | 2 | Gate Valve No.2 with Handwheel;;;;100 mm dia | Halton | In Service | Cedarberry Court PS | Cedarberry Court PS | Wet Well | Process Mechanical | Process Mechanical Equipment | TRUELINE | KNIFE GATE | N/A |  | 2020 | 1977 |  |  | HR-CBRY-002 |  |  |  | Poor | Corrosion and deterioration was observed on the surface of the valve and it is near the end of its expected service life.
128 | 22 | FORCEMAIN | 4 | 100mm diamter, approx. 73 m, PVC forcemain | Halton | In Service | Cedarberry Court PS | Cedarberry Court PS | Site | Process Mechanical | Process Piping |  |  |  |  | 2020 | 1977 | [6 empty] | Good
125 | 637 | SEWAGE LIFT PUMP #2 | 2 | Sewage Lift Pump #2;Flygt;CP3085;;6.3 L/s at 4.7 m TDH 2HP | Halton | In Service | Cedarberry Court PS | Cedarberry Court PS | Wet Well | Process Mechanical | Process Mechanical Equipment | FLYGT | 3082 | 9082 180 73166 |  | 2020 | 1977 |  |  | HR-CBRY-016 |  |  |  | Poor | The pump works but it's near the end of its expected service life.
124 | 122 | SEWAGE LIFT PUMP #1 DISCHARGE VALVE | 2 | Gate Valve No.1 with Handwheel;;;;100 mm dia | Halton | In Service | Cedarberry Court PS | Cedarberry Court PS | Wet Well | Process Mechanical | Process Mechanical Equipment | TRUELINE | KNIFE GATE | N/A |  | 2020 | 1977 |  |  | HR-CBRY-001 |  |  |  | Poor | Deterioration was observed on the surface of the valve and it is near the end of its expected service life.
123 | 122 | SEWAGE LIFT PUMP #1 CHECK VALVE | 2 | Check Valve No.1;Swing-Flex;;;100 mm dia | Halton | In Service | Cedarberry Court PS | Cedarberry Court PS | Wet Well | Process Mechanical | Process Mechanical Equipment | VALMATIC | SWING FLEX | N/A |  | 2020 | 1977 |  |  | HR-CBRY-004 |  |  |  | Poor | Corrosion and serious deterioration was observed on the valve
122 | 637 | PUMP #1 SEWAGE LIFT | 2 | Sewage Lift Pump #1;Flygt;CP3085;;6.3 L/s at 4.7 m TDH 2HP | Halton | In Service | Cedarberry Court PS | Cedarberry Court PS | Wet Well | Process Mechanical | Process Mechanical Equipment | FLYGT | 3082 | 3082 180 73167 |  | 2020 | 1977 |  |  | HR-CBRY-015 |  |  |  | Poor | The pump works but it's near the end of its expected service life.
126 | 125 | SEWAGE LIFT PUMP #2 CHECK VALVE | 2 | Check Valve No.2;Swing-Flex;;;100 mm dia | Halton | In Service | Cedarberry Court PS | Cedarberry Court PS | Wet Well | Process Mechanical | Process Mechanical Equipment | VALMATIC | SWING FLEX | N/A |  | 2020 | 1977 |  |  | HR-CBRY-006 |  |  |  | Poor | Corrosion and serious deterioration was observed on the valve
389 | 637 | Bar Screen | 2 | Bar Screen;;;; | Halton | In Service | Cedarberry Court PS | WWPS | Wet Well | Process Mechanical | Process Mechanical Equipment | [5 empty] | 1977 |  |  | HR-CBRY-007 |  |  |  | Good
236 | 125 | Pump 2 discharge piping | 3 | 100mm diameter, approx. 2.6m discharge piping | Halton | In Service | Cedarberry Court PS | Cedarberry Court PS | Wet Well | Process Mechanical | Process Piping |  |  |  |  | 0 | 1977 | [6 empty] | Poor | Severe deterioration was observed on the service piping
620 | 48 | Exterior metal platform | 2 |  | Halton |  | Rock Point Dr PS | WWPS | Site | Site Works | Site Works | [5 empty] | 2007 |  |  | HR-JOSH-158 |  |  |  |  | Good
621 | 48 | Exterior Metal Platform Handrails | 2 |  | Halton | In Service | Rock Point Dr PS | WWPS | Site | Site Works | Site Works | [5 empty] | 2007 |  | 2035 | HR-JOSH-158 |  |  |  | Good
618 | 48 | Concrete Pedestal | 1 |  | Halton | In Service | Rock Point Dr PS | WWPS | Site | Site Works | Site Works | [5 empty] | 2007 |  |  | HR-JOSH-160 |  |  |  | Good
617 | 48 | Yard Hydrant | 1 |  | Halton | In Service | Rock Point Dr PS | WWPS | Site | Site Works | Site Works | [5 empty] | 2007 |  |  | HR-JOSH-094 |  |  |  |  | Good
619 | 48 | Metal Guard Railing | 2 |  | Halton | In Service | Rock Point Dr PS | WWPS | Site | Site Works | Site Works | [5 empty] | 2007 |  |  | HR-JOSH-160 |  |  |  | Good
378 | 634 | Exterior Aluminum Platform | 2 | Rock Point Dr PS Wet Well | Halton | In Service | Rock Point Dr PS | WWPS | Site | Process Structural | Building and Process Structural | [5 empty] | 2006 |  |  | HR-JOSH-158 |  |  |  | Good
49 | 634 | Wet Well Concrete Structure | 3 | Rock Point Dr PS Wet Well | Halton | In Service | Rock Point Dr PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 2006 |  |  | HR-JOSH-091 |  |  |  | Good | Rust spots noted typically |  | Cut back rust spots, clean and patch with cementitous repair mortar | 2035 | 500
379 | 634 | Davit Socket Base | 1 | Rock Point Dr PS Wet Well | Halton | In Service | Rock Point Dr PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 2006 |  |  | HR-JOSH-081 |  |  |  | Good
377 | 634 | Aluminum Guardrail | 2 | Rock Point Dr PS Wet Well | Halton |  | Rock Point Dr PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [8 empty] | HR-JOSH-091 |  |  |  | Fair | Calcium buildup noted
376 | 634 | Aluminum Platform | 2 | Rock Point Dr PS Wet Well | Halton |  | Rock Point Dr PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [8 empty] | HR-JOSH-091 |  |  |  | Fair | Calcium buildup noted
375 | 634 | Access Ladder | 1 | Platform to wet well base | Halton | In Service | Rock Point Dr PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 2006 |  |  | HR-JOSH-091 |  |  |  | Fair | Calcium buildup noted
374 | 634 | Access Ladder | 1 | Exterior to platform | Halton | In Service | Rock Point Dr PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 2006 |  |  | HR-JOSH-091 |  |  |  | Fair | Calcium buildup noted
373 | 634 | Pump Hatch 2 | 1 | Rock Point Dr PS Wet Well | Halton | In Service | Rock Point Dr PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 2006 |  |  | HR-JOSH-085 |  |  |  | Good
372 | 634 | Pump Hatch 1 | 1 | Rock Point Dr PS Wet Well | Halton | In Service | Rock Point Dr PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 2006 |  |  | HR-JOSH-085 |  |  |  | good
371 | 634 | Access Hatch | 1 | Rock Point Dr PS Wet Well | Halton | In Service | Rock Point Dr PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 2006 |  | 2066 | HR-JOSH-085 |  |  |  | Fair | Hatch hard to open due to corrosion on latch |  | Repair/replace latch | 2021 | 500
380 | 634 | Grab Bar | 1 | Rock Point Dr PS Wet Well | Halton | In Service | Rock Point Dr PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 2006 |  |  | HR-JOSH-081 |  |  |  | Good
547 | 48 | Outdoor Enclosure | 2 | Outdoor Enclosure | Halton | In Service | Rock Point Dr PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2005 |  | 2035 | IMG_2774 |  |  |  | good | top of control panel enclosure was damaged and was insulated
548 | 48 | Site Light | 1 | Site Light | Halton | In Service | Rock Point Dr PS | WWPS | Site | Building Electrical | Process Electrical | [5 empty] | 2005 |  | 2035 | IMG_2780 |  |  |  | good
549 | 48 | Duplex Pump Control Panel | 2 | Duplex Pump Control Panel; Cutler Hammer; ; ; 240V | Halton | In Service | Rock Point Dr PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2005 |  | 2035 | IMG_2793 |  |  |  | good
550 | 13 | Lighting Panel | 2 | Lighting Panel; Cutler Hammer; PL1A; 120/240V, 225A, 18CCT | Halton | In Service | Rock Point Dr PS | WWPS | Site | Building Electrical | Process Electrical | [5 empty] | 2005 |  | 2035 | IMG_2796 |  |  |  | good
551 | 48 | Pump Capacitors | 2 | Pump Capacitors; ; ; | Halton | In Service | Rock Point Dr PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2005 |  | 2035 | IMG_2806 |  |  |  | good | replace with VFD in next upgrade
557 | 48 | Generator Transformer | 2 | Generator Transformer; BEMAG; ;600V-120/240V, 50kVA | Halton | In Service | Rock Point Dr PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2005 |  | 2035 | IMG_2843 |  |  |  | good
556 | 48 | Power Meter | 2 | Power Meter; ; ; | Halton | In Service | Rock Point Dr PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2005 |  | 2035 | IMG_2824 |  |  |  | good
555 | 48 | Generator Connect Receptacle | 2 | Gen Connect Recept; ; ; 600V | Halton | In Service | Rock Point Dr PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2005 |  | 2035 | IMG_2815 |  |  |  | good
554 | 48 | Manual Transfer Switch | 2 | MTS; Eaton; ; 240V, 200A | Halton | In Service | Rock Point Dr PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2005 |  | 2035 | IMG_2815 |  |  |  | good
553 | 48 | Surge Protection Device | 2 | Surge Protection Device; Eaton; Clipper VL; | Halton | In Service | Rock Point Dr PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2005 |  | 2035 | IMG_2812 |  |  |  | good
552 | 48 | Main Breaker | 2 | Main Breaker; Eaton; ;240V, 200A | Halton | In Service | Rock Point Dr PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2005 |  | 2035 | IMG_2808 |  |  |  | good
205 | 634 | BY -PASS FLOW TRANSMITTER | 2 | Bypass Flow Meter; Siemens Milltronics; MultiRanger 100; 030305108VX; ; | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Site | Process Instrumentation | Process Instrumentation | SIEMENS | MR-100 | 030305108VX |  | 2020 | 2010 |  |  | HR-JOSH-212 |  |  |  | good
204 | 48 | JOSHUA CREEK UP#1 - | 2 | PLC Panel UPS; Eaton; Powerware 9120 700; RW513A0198 ; 700VA-3000VA; | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Site | Process Instrumentation | Process Instrumentation | POWER WARE | PW 9120 700 | RW513A0198 |  | 2020 | 2006 |  | 2025 | HR-JOSH-214 |  |  |  | Corrosion
206 | 634 | WET WELL LEVEL TRANSMITTER | 2 | Wet Well Level Transmitter; Siemens Milltronics; Multiranger 100; 030205142VX; ; | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Dry Well | Process Instrumentation | Process Instrumentation | SIEMENS | MR-100 | 030205142VX |  | 2020 | 2010 |  | 2030 | HR-JOSH-198 |  |  |  | good
454 | 634 | Wet Well Floats | 2 | Wet Well Floats; ; ; ; ; | Halton | In Service | Rock Point Dr PS | WWPS | Wet Well | Process Instrumentation | Process Instrumentation | [5 empty] | 2006 |  | 2025 | HR-JOSH-109 |  |  |  | good
455 | 634 | Wet Well Level Transmitter* Wet Well Level Transmitter | 2 | Wet Well Level Transmitter; Siemens Milltronics; Multiranger 200; ; ; | Halton | In Service | Rock Point Dr PS | WWPS | Wet Well | Process Instrumentation | Process Instrumentation | [5 empty] | 2014 |  | 2030 | HR-JOSH-198 |  |  |  | good
193 | 48 | PLC #1 - ROCK POINT DR. - E16RT01 | 2 | Panel, Control/PLC; Allen-Bradley; SLC 05; 1747-L552 ; ; | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Site | Process Instrumentation | Process Instrumentation | Rockwell Automation/Allen-Brad | 1747-L552 | N/A |  | 2020 | 2005 |  | 2025 | HR-JOSH-209 |  |  |  | fair. | obselete
408 | 49 | Trash Basket | 2 | Trash Basket;;;; | Halton | In Service | Rock Point Dr PS | WWPS | Wet Well | Process Mechanical | Process Mechanical Equipment | [5 empty] | 2006 |  |  | HR-JOSH-89 |  |  |  | Good
201 | 207 | DISCHARGE HEADER ISOLATION VALVE #2 | 2 | Knife Gate Valve #2;;;;100 mm dia | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Wet Well | Process Mechanical | Process Mechanical Equipment | TRUELINE | F8112 | N/A |  | 2020 | 2006 |  |  | HR-JOSH-098 |  |  |  | Fair | Heavy corrosion and deterioration was observed on the surface of the valve.
202 | 207 | DISCH. HEADER BYPASS ISOL. VALVE#3 | 2 | Knife Gate Valve #3;;;;100 mm dia | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Wet Well | Process Mechanical | Process Mechanical Equipment | TRUELINE | F8112 | N/A |  | 2020 | 2006 |  |  | HR-JOSH-097 |  |  |  | Fair | Heavy corrosion and deterioration was observed on the surface of the valve.
194 | 13 | SEWAGE LIFT PUMP #1 | 2 | Sewage Lift Pump #1;Flygt;3127.090;0510181;7.5 L/s at 15 m TDH 7.5 HP | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Wet Well | Process Mechanical | Process Mechanical Equipment | FLYGT | 3127.090 | 0510181 |  | 2020 | 2006 |  |  | HR-JOSH-101 |  |  |  | Good.
195 | 194 | SEWAGE LIFT PUMP #1 CHECK VALVE | 2 | Check Valve #1;;;;100 mm dia | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Wet Well | Process Mechanical | Process Mechanical Equipment | HILLEN DELELIE | N/A | N/A |  | 2020 | 2006 |  |  | HR-JOSH-101 |  |  |  | Fair | Heavy corrosion was observed on the surface of the valve
207 | 13 | FORCEMAIN | 4 | 100mm diameter, approx. 390m PVC forcemain | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Site | Process Mechanical | Process Piping |  |  |  |  | 2020 | 2006 | [6 empty] | Good
199 | 198 | SEWAGE LIFT PUMP #2 CHECK VALVE | 2 | Check Valve #2;;;;100 mm dia | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Wet Well | Process Mechanical | Process Mechanical Equipment | HILLEN DELELIE | N/A | N/A |  | 2020 | 2006 |  |  | HR-JOSH-107 |  |  |  | Fair | Heavy corrosion and deterioration was observed on the surface of the valve.
196 | 194 | SEWAGE LIFT PUMP #1 DISCHARGE VALVE | 2 | Gate Valve #1;;;;100 mm dia | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Wet Well | Process Mechanical | Process Mechanical Equipment | AVK | N/A | 23-100-4702630029 |  | 2020 | 2006 |  |  | HR-JOSH-099 |  |  |  | Fair | Heavy corrosion was observed on the surface of the valve
200 | 198 | SEWAGE LIFT PUMP #2 DISCHARGE VALVE | 2 | Gate Valve #2;;;;100 mm dia | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Wet Well | Process Mechanical | Process Mechanical Equipment | AVK | N/A | 23-100-4702630029 |  | 2020 | 2006 |  |  | HR-JOSH-106 |  |  |  | Fair | Heavy corrosion and deterioration was observed on the surface of the valve.
197 | 207 | DISCHARGE HEADER ISOLATION VALVE #1 | 2 | Knife Gate Valve #1;;;;100 mm dia | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Wet Well | Process Mechanical | Process Mechanical Equipment | TRUELINE | F8112 | N/A |  | 2020 | 2006 |  |  | HR-JOSH-115 |  |  |  | Fair | Heavy corrosion and deterioration was observed on the surface of the valve.
407 | 49 | Overflow Piping | 3 | 200mm diameter, approx. 7m PVC SDR 35 | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Wet Well |  | Process Piping | [5 empty] | 2006
271 | 207 | Air Release Valve #1 | 2 | Air Release Valve #1;;;;50 mm dia | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Wet Well | Process Mechanical | Process Piping |  |  |  |  | 0 | 2006 |  |  | HR-JOSH-118 |  |  |  | poor | Heavy corrosion was observed on the surface of the valve
270 | 194 | Pump 1 Discharge Piping | 3 | 100mm diameter, approx. 10m SS pipe | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Wet Well | Process Mechanical | Process Piping |  |  |  |  | 0 | 2006 |  |  | HR-JOSH-116 |  |  |  | Fair | Heavy corrosion was observed on the surface of the pipe
269 | 634 | Overflow Piping | 3 | 200mm diameter, approx. 7m PVC SDR 35 | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Wet Well | Process Mechanical | Process Piping |  |  |  |  | 0 | 2006 | [6 empty] | Good
198 | 13 | SEWAGE LIFT PUMP #2 | 2 | Sewage Lift Pump #2;Flygt;3127.090;0510181;7.5 L/s at 15 m TDH 7.5 HP | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Wet Well | Process Mechanical | Process Mechanical Equipment | FLYGT | 3127.090 | 0510182 |  | 2020 | 2006 |  |  | HR-JOSH-109 |  |  |  | Good
657 | 634 | Wet Well Vent Piping | 1 | 1/4 HP | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Wet Well | Building Mechanical | Building Services | [5 empty] | 2006 |  |  | HR-JOSH-095 |  |  |  | good | Minor painr wear |  | Resurface and repaint | 2022 | 250
658 | 198 | Pump 2 Discharge Piping | 3 | 100mm diameter, approx. 10m SS pipe | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Wet Well | Process Mechanical | Process Piping | [5 empty] | 2006 |  |  | HR-JOSH-116 |  |  |  | Fair | Heavy corrosion was observed on the surface of the pipe
203 | 634 | FAN EXHAUST #1 | 1 | 1/4 HP | Halton | In Service | Rock Point Dr PS | Rock Point Dr PS | Wet Well | Building Mechanical | Building Services | PENN POWER VENTILATOR | REX 10Q | N/A |  | 2020 | 2006 |  |  | HR-JOSH-092 |  |  |  | good
605 |  | Dry Wall Thermostat | 1 | Installation year assumed to be 1972 | Halton |  | Weaver Avenue PS | WWPS | Dry Well | Building Mechanical | Building Services | [5 empty] | 1972 |  |  | HR-WEAV-005 |  |  |  | good
604 |  | Dry Wall Humidistat | 1 | Installation year assumed to be 1972 | Halton |  | Weaver Avenue PS | WWPS | Dry Well | Building Mechanical | Building Services | [5 empty] | 1972 |  |  | HR-WEAV-005 |  |  |  | good
598 | 649 | Dry Wall Portable Dehumidifier | 1 | Installation year assumed to be 1972 | Halton |  | Weaver Avenue PS | WWPS | Dry Well | Building Mechanical | Building Services | [5 empty] | 1972 |  |  | HR-WEAV-007 |  |  |  | good
597 | 649 | Dry Wall Sump Pump | 1 |  | Halton |  | Weaver Avenue PS | WWPS | Dry Well | Building Mechanical | Building Services | [5 empty] | 1972 |  |  | HR-WEAV-012 |  |  |  | surface corrosion
596 | 649 | Dry Wall Portable Heater | 1 | Installation year assumed to be 1972 | Halton |  | Weaver Avenue PS | WWPS | Dry Well | Building Mechanical | Building Services | [5 empty] | 1972 |  |  | HR-WEAV-010 |  |  |  | good
626 | 51 | Brick pathway | 1 |  | Halton |  | Weaver Avenue PS | WWPS | Site | Site Works | Site Works | [5 empty] | 1972 |  | 2035 | HR-WEAV-002 |  |  |  | Good
624 | 51 | Yard Hydrant | 1 |  | Halton | In Service | Weaver Avenue PS | WWPS | Site | Site Works | Site Works | [5 empty] | 1972 |  | 2035 | HR-WEAV-024 |  |  |  | Good
625 | 51 | Oveflow Structure | 2 |  | Halton | In Service | Weaver Avenue PS | WWPS | Site | Site Works | Site Works | [5 empty] | 1972 |  | 2035 | HR-WEAV-003 |  |  |  | Good
52 | 650 | Wet Well Structure | 3 | 7 foot inside diameter precast concrete | Halton | In Service | Weaver Avenue PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2032 | HR-WEAV-001 |  |  |  | Fair | Rust spots noted typically |  | Cut back rust spot, clean and patch with cementitous repair mortar | 2025 | 500
366 | 649 | Protective Paint | 1 | Weaver Avenue PS Dry Well | Halton | In Service | Weaver Avenue PS | WWPS | Dry Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2032 | HR-WEAV-107 |  |  |  | Fair | Weathered paint on exterior
50 | 649 | Dry Well Structure | 3 | Steel drywell by Smith & Loveless | Halton | In Service | Weaver Avenue PS | WWPS | Dry Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2032 | HR-WEAV-112 |  |  |  | Fair | Missing paint/corrosion noted |  | Grind to bare metal and touch up paint | 2021 | 500
370 | 649 | Davit Socket Base | 1 | Weaver Avenue PS Dry Well | Halton | In Service | Weaver Avenue PS | WWPS | Dry Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2032 | HR-WEAV-112 |  |  |  | Fair | To be inspected every eyar
365 | 649 | Access Ladder | 1 | Weaver Avenue PS Dry Well | Halton | In Service | Weaver Avenue PS | WWPS | Dry Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2040 | HR-WEAV-107 |  |  |  | Fair
367 | 650 | Access Ladder | 1 | Weaver Avenue PS Wet Well | Halton | In Service | Weaver Avenue PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2040 | HR-WEAV-001 |  |  |  | Fair
368 | 650 | Checker Plate Platform | 1 | Weaver Avenue PS Wet Well | Halton | In Service | Weaver Avenue PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2032 | HR-WEAV-001 |  |  |  | Fair | Surface corrosion noted
369 | 650 | Manhole Frame and Cover | 1 | Weaver Avenue PS Wet Well | Halton | In Service | Weaver Avenue PS | WWPS | Wet Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2032 | HR-WEAV-002 |  |  |  | Fair
381 | 649 | Concrete Foundation | 1 | Weaver Avenue PS Dry Well | Halton | In Service | Weaver Avenue PS | WWPS | Dry Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2040 |  |  |  |  | Not accessible/inspected. Assumed to be good as no settlement was noted
364 | 650 | Access Hatch | 1 | Weaver Avenue PS Dry Well | Halton | In Service | Weaver Avenue PS | WWPS | Dry Well | Process Structural | Building and Process Structural | [5 empty] | 1972 |  | 2040 | HR-WEAV-112 |  |  |  | Fair | Minor corrosion noted
90 | 88 | SEWAGE LIFT PUMP #1 MOTOR DRIVE | 1 | 7.5 HP; | Halton | In Service | Weaver Avenue PS | Weaver Avenue PS | Dry Well | Process Mechanical | Process Mechanical Equipment | ROBBIN & MYERS | N-BPM4 | YF7773-1 |  | 2020 | 1972 |  |  | HR-WEAV-014 |  |  |  | Fair | Deterioration was observed on the valve. The valve was beyond its expected service life.
543 | 649 | Main Transfer Switch | 2 | MTS; Square D; ; ; 600V, 60A | Halton | In Service | Weaver Avenue PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2007 |  | 2037 | HR-WEAV-038 |  |  |  | good
95 | 50 | SEWAGE LIFT PUMP #2 MOTOR DRIVE | 2 | 7.5 HP; Westinghouse; Model J; ;600v, 10HP | Halton |  | Weaver Avenue PS | Weaver Avenue PS | Dry Well | Process Mechanical | Process Electrical | ROBBIN & MYERS | N-BPM4 | YF7773-2 |  | 2020 | 1972 | [6 empty] | Fair | Deterioration was observed on the surface of the pump. The pump was beyond its expected service life.
544 | 649 | Gennerator Connect Receptacle | 2 | Gen Connect Recept; ; ; ; 600V, 60A | Halton | In Service | Weaver Avenue PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2007 |  | 2037 | HR-WEAV-042 |  |  |  | good
541 | 649 | Main Diwsconnect Switch | 2 | Main DS; Square D; ; ; 600V, 60A | Halton | In Service | Weaver Avenue PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2007 |  | 2037 | HR-WEAV-030 |  |  |  | good
456 | 649 | Outdoor Enclosure | 2 | Outdoor Enclosure; | Halton | In Service | Weaver Avenue PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2007 |  | 2037 | HR-WEAV-025 |  |  |  |  | good
545 | 649 | Drywell Lights | 1 | Drywell Lights; ; ; ; Fluorescent | Halton | In Service | Weaver Avenue PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 1972 |  | 2025 | HR-WEAV-047 |  |  |  | fair | to be replaced with LED fixtures rated for Class 1, div 2
546 | 649 | Control Panel | 2 | Control Panel; S&L; ; ; | Halton | In Service | Weaver Avenue PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 1972 |  | 2025 | HR-WEAV-004 |  |  |  | fair
542 | 649 | Power Meter | 2 | Power Meter; elster; ; ; 600V | Halton | In Service | Weaver Avenue PS | WWPS | Site | Process Electrical | Process Electrical | [5 empty] | 2007 |  | 2037 | HR-WEAV-034 |  |  |  | good
86 | 649 | TRANSMITTER LEVEL - DRY WELL | 2 | Wet Well Level Transmitter; Siemens; Sitrans LUC500; ; ; | Halton | In Service | Weaver Avenue PS | Weaver Avenue PS | Dry Well | Process Instrumentation | Process Instrumentation | SIEMENS/MILLTRONICS | MULTIRANGER PLUS | PBD/W6120004 |  | 2020 | 2009 |  | 2030 | HR-WEAV-011 |  |  |  | Dust
85 | 650 | TRANSMITTER LEVEL WET WELL #1 | 2 | 100" Wet Well Level Transmitter; Siemens Milltronics; Multiranger Plus; ; ; | Halton | Not In Service | Weaver Avenue PS | Weaver Avenue PS | Dry Well | Process Instrumentation | Process Instrumentation | MILLTRONICS | MULTIRANGER PLUS | 011491 091-18 |  | 2020 | 2009 |  | 2030 | HR-WEAV-009 |  |  |  | good | nuts were not secured properly
452 | 649 | Sump Float | 2 | Sump Float; ; ; ; ; | Halton | In Service | Weaver Avenue PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation | [5 empty] | 2009 |  | 2030 | HR-WEAV-012 |  |  |  | good
451 | 649 | Exhaust Fan Timer | 2 | Exhaust Fan Timer; Paragon; ; ; ; | Halton | In Service | Weaver Avenue PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation | [5 empty] | 2009 |  | 2030 | HR-WEAV-005 |  |  |  | good
450 | 649 | Dry Well Temperature Controller | 2 | Dry Well Temperature Controller; Penn; ; ; ; | Halton | In Service | Weaver Avenue PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation | [5 empty] | 2009 |  | 2030 | HR-WEAV-005 |  |  |  | good
449 | 649 | Dry Well Humidity Controller | 2 | Dry Well Humidity Controller; Penn; ; ; | Halton | In Service | Weaver Avenue PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation | [5 empty] | 2009 |  | 2009 | HR-WEAV-005 |  |  |  | good
453 | 51 | Remote Signals Telephone Transmitter | 1 | Remote Signals Telephone Transmitter; Pribusin; IUC-X9-TXC; ; ; | Halton | In Service | Weaver Avenue PS | WWPS | Dry Well | Process Instrumentation | Process Instrumentation | [5 empty] | 2016 |  | 2030 | HR-WEAV-068 |  |  |  | good
84 | 649 | PUMP #1 SUMP | 2 | Sump Pump;;;; | Halton | In Service | Weaver Avenue PS | Weaver Avenue PS | Dry Well | Building Mechanical | Building Services | LITTLE GIANT | GE-CIA-SFC | GE-CIA-RFSN |  | 2020 | 1972 |  |  | HR-WEAV-012 |  |  |  | Very Poor | Severe corrosion was observed on the pump. The pump was beyond its expected service life.
88 | 50 | SEWAGE LIFT PUMP #1 | 2 | Sewage Lift Pump #1;Smith&Loveless;4B2;;30.3 L/s at 11.3 m TDH 7 HP | Halton | In Service | Weaver Avenue PS | WWPS | Dry Well | Process Mechanical | Process Mechanical Equipment | SMITH AND LOVELESS | N/A | 7210773-2 |  | 2020 | 1972 |  |  | HR-WEAV-014 |  |  |  | Fair | Corrosion was observed on the surface of the pump. No performance issues were identified, however; the pump was beyond its expected service life.
89 | 88 | SEWAGE LIFT PUMP #1 CHECK VALVE | 2 | Check Valve #1;Swing-Flex;504A;;100 mm dia | Halton | In Service | Weaver Avenue PS | Weaver Avenue PS | Dry Well | Process Mechanical | Process Mechanical Equipment | VALMATIC | SWING FLEX | N/A |  | 2020 | 1972 |  |  | HR-WEAV-015 |  |  |  | Fair | Deterioration was observed on the valve. The valve was beyond its expected service life.
91 | 88 | SEWAGE LIFT PUMP #1 INLET VALVE | 2 | Inlet Knife Gate Valve #1;;;;150 mm dia | Halton | In Service | Weaver Avenue PS | Weaver Avenue PS | Dry Well | Process Mechanical | Process Mechanical Equipment | IOWA | N/A | N/A |  | 2020 | 1972 |  |  | HR-WEAV-013 |  |  |  | Fair | Minor deterioration was observed on the surface of the valve but the valve was beyond its expected service life.
92 | 88 | SEWAGE LIFT PUMP #1 DISCHARGE VALVE | 2 | Discharge Knife Gate Valve #1;;;;150 mm dia | Halton | In Service | Weaver Avenue PS | Weaver Avenue PS | Dry Well | Process Mechanical | Process Mechanical Equipment | IOWA | N/A | N/A |  | 2020 | 1972 |  |  | HR-WEAV-016 |  |  |  | Fair | Corrosion and deterioration was observed on the surface of the valve. The valve was beyond its expected service life.
93 | 14 | SEWAGE LIFT PUMP #2 | 2 | Sewage Lift Pump 21;Smith&Loveless;4B2;;30.3 L/s at 11.3 m TDH 7 HP | Halton | In Service | Weaver Avenue PS | Weaver Avenue PS | Dry Well | Process Mechanical | Process Mechanical Equipment | SMITH AND LOVELESS | N/A | 7210773-2 |  | 2020 | 1972 |  |  | HR-WEAV-020 |  |  |  | Fair | Deterioration was observed on the surface of the pump. The pump was beyond its expected service life.
94 | 93 | SEWAGE LIFT PUMP #2 CHECK VALVE | 2 | Check Valve #2;Swing-Flex;504A;;100 mm dia | Halton | In Service | Weaver Avenue PS | Weaver Avenue PS | Dry Well | Process Mechanical | Process Mechanical Equipment | VALMATIC | SWING FLEX | N/A |  | 2020 | 1972 |  |  | HR-WEAV-019 |  |  |  | Fair | Deterioration was observed on the valve. The valve was beyond its expected service life.
97 | 93 | SEWAGE LIFT PUMP #2 DISCHARGE VALVE | 2 | Discharge Knife Gate Valve #1;;;;150 mm dia | Halton |  | Weaver Avenue PS | Weaver Avenue PS | Dry Well | Process Mechanical | Process Mechanical Equipment | TRUELINE | 316 SS KNIFE GATE | N/A |  | 2020 |  |  |  | HR-WEAV-018 |  |  |  | Fair | Minor deterioration was observed on the surface of the valve but the valve was beyond its expected service life.
272 | 650 | Overflow Piping | 3 | 300mm diameter, approx. 9m corrugated metal pipe | Halton | In Service | Weaver Avenue PS | Weaver Avenue PS | Wet Well | Process Mechanical | Process Piping |  |  |  |  | 0 | 1972 | [6 empty] | Fair | The pipe passed half of its expected service life.
98 | 51 | FORCEMAIN | 4 | 150mm diameter, approx. 153m ductile iron pipe | Halton | In Service | Weaver Avenue PS | Weaver Avenue PS | Site | Process Mechanical | Process Piping |  |  |  |  | 2020 | 1972 | [6 empty] | Fair | The pipe passed half of its expected service life.
274 | 650 | Bar Screen | 2 | Bar Screen;;;; | Halton | In Service | Weaver Avenue PS | Weaver Avenue PS | Wet Well | Process Mechanical | Process Mechanical Equipment |  |  |  |  | 0 | 1972 | [6 empty] | Fair | The bar screen passed half of its expected service life.
273 | 88 | Pump 1 Piping | 3 | 150mm diameter, approx. 5 m ductile iron pipe | Halton | In Service | Weaver Avenue PS | Weaver Avenue PS | Wet Well | Process Mechanical | Process Piping |  |  |  |  | 0 | 1972 |  |  | HR-WEAV-022 |  |  |  | Fair | The pipe passed half of its expected service life.
96 | 93 | SEWAGE LIFT PUMP #2 INLET VALVE | 2 | Inlet Knife Gate Valve #2;;;;150 mm dia | Halton |  | Weaver Avenue PS | Weaver Avenue PS | Dry Well | Process Mechanical | Process Mechanical Equipment | IOWA | N/A | N/A |  | 2020 |  |  |  | HR-WEAV-021 |  |  |  | Fair | Minor deterioration was observed on the surface of the valve but the valve was beyond its expected service life.
87 | 50 | FAN EXHAUST #1 | 1 | 115 VOLTS | Halton |  | Weaver Avenue PS | Weaver Avenue PS | Dry Well | Building Mechanical | Building Services | N/A | N/A | N/A |  | 2020
655 | 93 | Pump 2 Piping | 3 | 150mm diameter, approx. 5 m ductile iron pipe | Halton | In Service | Weaver Avenue PS | Weaver Avenue PS | Wet Well | Process Mechanical | Process Piping | [5 empty] | 1972 |  |  | HR-WEAV-022 |  |  |  | Fair | The pipe passed half of its expected service life.

## r_defects
DefectID | ParentID | DefectType | DefectExtent | DefectComment | OPEXType | RehabComment | RehabYear | RehabUnitMaterialCost | RehabQuantity | RehabQuantityUnits | TotalRehabMarkup | Recurring | WorkFrequency | DBNotes
2 | 17 | Leaking | At Joints | Leakage at joint | Maintenance | Polyurethane crack injection | 2021 | 5000 | 1 | ea. | 1 | FALSE | 0
3 | 19 | Exposed Rebar |  | Exposed corroded reinforcement and concrete spalling | Maintenance | Remove loose concrete, clean reinforcement and apply rust inhibiting paint and patch with cementitous repair mortar | 2025 | 2000 | 1 | ea. | 1 | FALSE | 0
4 | 20 | Rusting |  | Corrosion | Maintenance | Grind to bare metal and touch up paint | 2021 | 2000 | 1 | ea. | 1 | FALSE | 0
5 | 23 | Exposed Rebar | Minor | Exposed corroded reinforcement and rust spots | Maintenance | Cut back rust spots, remove loose concrete, clean reinforcement and coat with rust inhibiting paint and patch with cementitous repair mortar | 2025 | 5000 | 1 | ea. | 1 | FALSE | 0
7 | 26 | Corrosion |  | Minor corrosion | Maintenance | Remove loose paint, grind to bare metal and touch up paint | 2030 | 3000 | 1 | ea. | 1 | FALSE | 0
8 | 28 | Exposed Rebar |  | Exposed corroded reinforcement | Maintenance | Remove loose concrete, clean reinforcement and paint with rust inhibiting paint and patch with cementitous repair mortar | 2030 | 2000 | 1 | ea. | 1 | FALSE | 0
9 | 31 | Spalling / Exposed Aggregates / Exposed Granular |  | Leakage/spalling at joint | Maintenance | Polyurethane crack injection and remove loose concrete and patch with cementitous repair material | 2025 | 5000 | 1 | ea. | 1 | FALSE | 0
10 | 34 | Exposed Rebar |  | Exposed corroded reinforcement, rust spots and spalling at joint | Maintenance | Remove loose concrete, clean rebar and apply rust inhibiting paint and patch with cementitous repair mortar | 2025 | 3000 | 1 | ea. | 1 | FALSE | 0
11 | 41 | Exposed Rebar |  | Rust spots | Maintenance | Cut back rust spots, clean and patch with cementitous repair mortar | 2025 | 500 | 5 | ea. | 1 | FALSE | 0
12 | 46 | Exposed Rebar |  | Exposed corroded reinforcement and concrete spalling | Maintenance | Remove loose concrete, clean exposed corroded reinforcement and apply rust inhibiting paint and patch area with cementitous repair mortar | 2025 | 5000 | 1 | ea. | 1 | FALSE | 0
13 | 49 | Exposed Rebar |  | Rust spots | Maintenance | Cut back rust spots, clean and patch with cementitous repair mortar | 2035 | 500 | 10 | ea. | 1 | FALSE | 0
14 | 50 | Corrosion | Moderate | Corrosion noted at mount for scada equipment | Maintenance | Grind to bare metal and touch up paint | 2021 | 500 | 1 | ea. | 1 | FALSE | 0
15 | 52 | Exposed Rebar |  | Rust spots noted | Maintenance | Cut back rust spot, clean and patch with cementitous repair mortar | 2025 | 500 | 10 | ea. | 1 | FALSE | 0
16 | 283 | Missing Components |  | Missing safety grating | Maintenance | Install safety grating | 2021 | 1000 | 1 | ea. | 1 | FALSE | 0 | 283_merge
17 | 284 | Missing Components |  | Missing safety grating | Maintenance | Install safety grating | 2021 | 1000 | 1 | ea. | 1 | FALSE | 0 | 284_merge
18 | 289 | Displaced / Detached | Riser | Brick riser is loose | Maintenance | Reparge brick riser | 2021 | 500 | 1 | ea. | 1 | FALSE | 0 | 289_merge
19 | 291 | Corrosion |  | Corrosion on top surface | Maintenance | Clean and touch up paint | 2021 | 300 | 1 | ea. | 1 | FALSE | 0 | 291_merge
20 | 293 | Performance Issues |  | Missing rung | Maintenance | Install missing run | 2021 | 500 | 1 | ea. | 1 | FALSE | 0 | 293_merge
21 | 298 | Missing Components |  | Missing safety grating | Maintenance | Install safety grating | 2021 | 1000 | 1 | ea. | 1 | FALSE | 0 | 299_merge
22 | 301 | Exposed Rebar |  | Rust spots | Maintenance | Cut back rust spot, clean and patch with cementitous repair mortar | 2025 | 500 | 5 | ea. | 1 | FALSE | 0 | 302_merge
23 | 304 | Staining / Discoloration / Fading |  | peeling paint on exterior | Maintenance | Remove loose paint and touch up paint | 2021 | 500 | 1 | ea. | 1 | FALSE | 0 | 305_merge
24 | 314 | Performance Issues |  | Grab bar is loose | Maintenance | Tighten as required | 2021 | 100 | 1 | ea. | 1 | FALSE | 0 | 317_merge
25 | 322 | Performance Issues |  | Bent ladder rung | Maintenance | Replace bent ladder rung | 2021 | 500 | 1 | ea. | 1 | FALSE | 0 | 325_merge
26 | 331 | Aging / Wear / Weathering / Deterioration | Exteior | Peeling paint | Maintenance | Remove loose paint, clean and touch up paint | 2021 | 500 | 1 | ea. | 1 | FALSE | 0 | 334_merge
27 | 344 | Aging / Wear / Weathering / Deterioration | Exterior | Missing paint on exterior | Maintenance | Remove loose paint, clean surface and touch up paint | 2021 | 100 | 5 | ea. | 1 | FALSE | 0 | 347_merge
28 | 353 | Aging / Wear / Weathering / Deterioration |  | Weathered and missing paint on exterior | Maintenance | Remove loose paint and touch up paint | 2021 | 500 | 1 | ea. | 1 | FALSE | 0 | 356_merge
29 | 356 | Performance Issues |  | Corroded anchors | Maintenance | Replace anchors | 2021 | 300 | 1 | ea. | 1 | FALSE | 0 | 359_merge
30 | 371 | Performance Issues |  | Hard to open | Maintenance | Repair/replace latch | 2021 | 500 | 1 | ea. | 1 | FALSE | 0 | 374_merge
93 | 569 | Staining / Discoloration / Fading |  |  |  | Repaint the ventilation pipes | 2023 | 500 | 1 | ea. | 1 | FALSE | 0 | 280_merge
94 | 591 |  |  |  |  | Install gooseneck section and bird screen. | 2023 | 200 | 1 | ea. | 1 | FALSE | 0 | 309_merge
95 | 592 |  |  |  |  | Repaint the gooseneck pipe vent | 2023 | 100 | 1 | ea. | 1 | FALSE | 0 | 310_merge
96 | 315 | Other Defects |  | It is unknown when the equipment was last inspected. | Maintenance | conduct yearly inspections | 2021 | 500 | 1 | ea. | 1 | FALSE | 1
97 | 276 | Aging / Wear / Weathering / Deterioration | Minor | Weathered paint and minor corrosion was observed. | Maintenance | Resurface and repaint | 2022 | 500 | 1 | ea. | 1 | FALSE | 0
100 | 281 | Corrosion | Minor | The paint at some locations was missing and corrosion was noted. | Maintenance | Grind to bare metal and touch up paint | 2022 | 3000 | 1 | ea. | 1 | FALSE | 0
101 | 103 | Missing Components | Minor | One of the bolts was missing | Maintenance | Install missing bolt | 2021 | 100 | 1 | ea. | 1 | FALSE | 0
102 | 458 |  |  | Shock and arc flash hazard as the existing arc flash label is outdated. | Maintenance | Update and install arc flash hazard label | 2020 |  | 1 | ea. | 1 | FALSE | 0
105 | 461 |  |  | Shock and arc flash hazard as the existing arc flash label is outdated. | Maintenance | Update and install arc flash hazard label | 2020 |  | 1 | ea. | 1 | FALSE | 0
106 | 462 |  |  | Shock and arc flash hazard as the existing arc flash label is outdated. | Maintenance | Update and install arc flash hazard label | 2020 |  | 1 | ea. | 1 | FALSE | 0
107 | 463 |  |  | Shock and arc flash hazard as the existing arc flash label is outdated. | Maintenance | Update and install arc flash hazard label | 2020 |  | 1 | ea. | 1 | FALSE | 0
108 | 466 |  |  | Shock and arc flash hazard as the existing arc flash label is outdated. | Maintenance | Update and install arc flash hazard label | 2020 |  | 1 | ea. | 1 | FALSE | 0
109 | 630 |  |  | Shock and arc flash hazard as the existing arc flash label is outdated. | Maintenance | Update and install arc flash hazard label | 2020 |  | 1 | ea. | 1 | FALSE | 0
110 | 622 | Corrosion | Minor | Minor surface rust and defects | Maintenance | Resurface and repaint | 2022 | 400 | 1 | ea. | 1 | FALSE | 0
111 | 313 | MISCELLANEOUS |  | To be inspected yearly | Maintenance | conduct inspection |  | 500 | 1 | ea. | 1 | FALSE | 0
112 | 657 | Aging / Wear / Weathering / Deterioration | Minor | Minor paint wear | Maintenance | Resurface and repaint | 2022 | 250 | 1 | ea. | 1 | FALSE | 0

## p_comments
ParentID | Comment1 | Comment2 | Comment3 | Comment4 | Comment5 | Comment6 | Comment7 | Comment8 | Comment9 | Comment10
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15 | The asset was in fair condition. Typical corrosion was noted throughout
16
17 | The asset was in fair condition. Leakage was noted at joints. Concrete spalling was also noted at concrete parging of joints
18
19 | Fair | Concrete spalling and exposed corroded reinforcement
20 | Fair | Corrosion noted
21
22
23 | Fair | Concrete spalling on roof, rust spots and concrete spalling at pipe penetration
24 | Good | Minor corrosion noted
25
26 | Good | Minor corrosion noted throughout
27
28 | Fair | Exposed corroded reinforcement
29 | Fair | Corrosion noted throughout
30
31 | Fair | Efflorescence deposits/leak at joint. Concrete delamination/spalling at joint
32
33
34 | Fair | Exposed corroded reinforcement, rust spots and concrete parging spalling was noted at joints
35
36 | Fair | Corrosion noted throghout
37
38 | Fair
39
40
41 | Fair | Rust spots noted
42 | Fair | Corrosion was noted at the base
43
44 | Fair | Exposed corroded reinforcement and concrete spalling noted
45
46 | Fair | Exposed corroded reinforcement and concrete spalling was noted at the pipe penetration
47
48
49 | Good | Rust spots noted typically
50 | Fair | Missing paint/corrosion noted
51
52 | Fair | Rust spots noted typically
53 | Poor | The pump was near the end of its expected life.
54 | Very Poor | Severe corrosion was observed on the valve.
55 | Very Poor | Severe corrosion was observed on the valve.
56
57 | Poor | The pump was near the end of its expected service life
58 | Very Poor | Severe corrosion was observed on the surface of the valve
59 | Very Poor | Severe corrosio was observed on the valve
60 | Fair | The pipe was at half of its expected service life.
61 | Surface staining on exhaust fan pipe
62 | Fair | The pump was near the end of its expected service life.
63 | Very Poor | Servere corrosion was observed on the surface of the valve
64 | Very Poor | Servere corrosion was observed on the surface of the valve
65 | Fair | The pump was near the end of its expected service life.
66 | Very Poor | Severe corrosion was observed on the surface of the valve.
67 | Very Poor | Severe corrosion was observed on the surface of the valve
68 | Good
69 | Moderate surface corrosion | Poor | Corrosion and deterioration was observed on the surface of the pump. The pump was beyond its expected service life.
70 | good
71 | paint peeling
72 | Poor | Deterioratino was observed on the surface of the pump. The pump was beyond its expected service life.
73 | Poor | Deterioration was observed on the surface of the valve. The valve was beyond its expected service life
74
75 | Poor | Corrosion and deterioration was observed on the surface of the valve. The valve was beyond its expected service life.
76 | Deterioration was observed on the surface of the valve. The valve was beyond its expected service life. | Poor
77
78 | Poor | Deterioratino was observed on the surface of the pump. The pump was beyond its expected service life.
79 | Poor | Deterioration and corrosion was observed on the surface of the valve. The valve was beyond its expected service life
80
81 | Poor | Corrosion was observed on the surface of the valve. The valve was beyond its expected service life.
82 | Fair | Minor d eterioration was observed on the surface of the valve. The valve was beyond its expected service life.
83 | Fair | The pipe passed half of its expected service life.
84 | Very Poor | Severe corrosion was observed on the pump. The pump was beyond its expected service life.
85 | good | nuts were not secured properly
86 | Dust
87
88 | Fair | Corrosion was observed on the surface of the pump. No performance issues were identified, however; the pump was beyond its expected service life.
89 | Fair | Deterioration was observed on the valve. The valve was beyond its expected service life.
90 | Fair | Deterioration was observed on the valve. The valve was beyond its expected service life.
91 | Fair | Minor deterioration was observed on the surface of the valve but the valve was beyond its expected service life.
92 | Fair | Corrosion and deterioration was observed on the surface of the valve. The valve was beyond its expected service life.
93 | Fair | Deterioration was observed on the surface of the pump. The pump was beyond its expected service life.
94 | Fair | Deterioration was observed on the valve. The valve was beyond its expected service life.
95 | Fair | Deterioration was observed on the surface of the pump. The pump was beyond its expected service life.
96 | Fair | Minor deterioration was observed on the surface of the valve but the valve was beyond its expected service life.
97 | Fair | Minor deterioration was observed on the surface of the valve but the valve was beyond its expected service life.
98 | Fair | The pipe passed half of its expected service life.
99 | The asset was in fair condition. Moderate corrosion was observed.
100 | The asset was observed to be in good condition. Dust was observed.
101 | CC: As per Section 7.2.9 of MOECC's Design Guidelines for Sewage Works, mechanical ventilation is required for below ground surface dry well. | Exhaust Fan 1 was missing during the assessment.
102 | The asset was observed to be in fair condition. Surface corrosion and paint wear was observed. The pump was original to the facility and had surpassed its expected service life. Pump testing was not undertaken as part of this assessment. Based on the age
103 | The asset was observed to be in fair condition. Surface corrosion and paint wear was observed. One of the bolts on the valve was also missing. The valve was original to the facility and had surpassed its expected service life. Pump testing was not underta
104 | The asset was observed to be in fair condition. Surface corrosion and paint wear was observed. The motor was original to the facility and had surpassed its expected service life. Pump testing was not undertaken as part of this assessment. Based on the age
105 | The asset was observed to be in fair condition. Surface corrosion and paint wear was observed. The valve was original to the facility and had surpassed its expected service life. Pump testing was not undertaken as part of this assessment. Based on the age
106 | The asset was observed to be in fair condition. Surface corrosion and paint wear was observed. The valve was original to the facility and had surpassed its expected service life. Pump testing was not undertaken as part of this assessment. Based on the age
107 | The asset was observed to be in fair condition. Surface corrosion and paint wear was observed. The pump was original to the facility and had surpassed its expected service life. Pump testing was not undertaken as part of this assessment. Based on the age
108 | The asset was observed to be in fair condition. Surface corrosion and paint wear was observed. The valve was original to the facility and had surpassed its expected service life. Pump testing was not undertaken as part of this assessment. Based on the age
109 | The asset was observed to be in fair condition. Surface corrosion and paint wear was observed. The motor was original to the facility and had surpassed its expected service life. Pump testing was not undertaken as part of this assessment. Based on the age
110 | The asset was observed to be in fair condition. Surface corrosion and paint wear was observed. The valve was original to the facility and had surpassed its expected service life. Pump testing was not undertaken as part of this assessment. Based on the age
111 | The asset was observed to be in fair condition. Surface corrosion and paint wear was observed. The valve was original to the facility and had surpassed its expected service life. Pump testing was not undertaken as part of this assessment. Based on the age
112 | The Forcemain was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken.
113 | heavy corrosion
114 | Fair. | The pump is working but it is near the end of its expected service life.
115 | Poor | Heavy corrosion and deterioration was observed on the service of the valve. The valve was near the end of its expected service life.
116 | Poor | Heavy corrosion and deterioration was observed on the service of the valve. The valve was near the end of its expected service life.
117 | Poor | The pump is working but it is near the end of its expected service life.
118 | Poor | Heavy corrosion and deterioration was observed on the service of the valve. The valve was near the end of its expected service life.
119 | Poor | Heavy corrosion and deterioration was observed on the service of the valve. The valve was near the end of its expected service life.
120 | assumed to be good
121 | good
122 | Poor | The pump works but it's near the end of its expected service life.
123 | Poor | Corrosion and serious deterioration was observed on the valve
124 | Poor | Deterioration was observed on the surface of the valve and it is near the end of its expected service life.
125 | Poor | The pump works but it's near the end of its expected service life.
126 | Poor | Corrosion and serious deterioration was observed on the valve
127 | Poor | Corrosion and deterioration was observed on the surface of the valve and it is near the end of its expected service life.
128 | Good
129 | Poor | Corrosion and deterioratino were observed on the surface of the pump. The pump is beyond the end of its expected service life
130 | Dust | Corrosion
131
132 | Poor | Deterioration was observed on the surface of the pump and it is beyond the end of its expected service life.
133 | Poor | Corrision and deterioration was observed on the surface of the valve. The valve is beyond its expected service life.
134
135 | Poor | Corrosion and deterioration was observed on the surface of the valve. The valve is beyond its expected service life.
136 | Poor | Corrosion and deterioration was observed on the surface of the valve. The valve is beyond its expected service life.
137 | Poor | Deterioration was observed on the surface of the pump and it is beyond the end of its expected service life.
138 | Poor | Corrision and deterioration was observed on the surface of the valve. The valve is beyond its expected service life.
139
140 | Poor | Corrosion and deterioration was observed on the surface of the valve. The valve is beyond its expected service life.
141 | Poor | Corrosion and deterioration was observed on the surface of the valve. The valve is beyond its expected service life.
142 | Fair | The pipe is at half of its expected service life.
143 | Severe corrosion and deterioratino were observed on the surface of the pump. The pump was near the end of its expected service life. | Poor
144 | good
145 | As per Section 7.2.9 of MOECC's Design Guidelines for Sewage Works, mechanical ventilation is required for below ground surface dry well.
146 | Poor | Corrosion and deterioration was observed on the surface of the pump. The pump was near the end of its expected service life.
147 | Poor | Corrosion and deterioration was observed on the surface of the valve. The valve is near the end of its expected service life.
148
149 | Poor | Corrosion and deterioration was observed on the valve. The valve was near the end of its expected service life.
150 | Poor | Corrosion and deterioration was observed on the valve. The valve was near the end of its expected service life.
151 | Poor | Corrosion and deterioration was observed on the surface of the pump. The pump was near the end of its expected service life.
152 | Poor | Corrosion and deterioration was observed on the surface of the valve. The valve is near the end of its expected service life.
153
154 | Poor | Corrosion and deterioration was observed on the valve. The valve was near the end of its expected service life.
155 | Poor | Corrosion and deterioration was observed on the valve. The valve was near the end of its expected service life.
156 | Good | Good
157 | Poor | Corrosion and deterioration was observed on the surface of the pump. The pump is beyond its expected service life.
158 | Minor corrosion on nuts
159 | Surface corrosion
160 | Poor | Corrosion and deterioration was observed on the surface of the pump. The pump was beyond its expected service life.
161 | Very Poor | Severe corrosion and deterioration was observed on the surface of the valve. The valve was beyond its expected service life.
162
163 | Poor | Corrosion and deterioration was observed on the surface of the valve.
164 | Poor | Corrosion and deterioration was observed on the surface of the valve.
165 | Poor | Corrosion and deterioration was observed on the surface of the pump. The pump was beyond its expected service life.
166 | Poor | Corrosion and deterioration was observed on the surface of the pump. The pump was beyond its expected service life.
167
168 | Poor | Corrosion and deterioration was observed on the surface of the valve.
169 | Poor | Corrosion and deterioration was observed on the surface of the valve.
170 | Fair | The pipe was at half of its expected service life.
171
172 | very good
173
174 | Poor | The pump was beyond its expected service life.
175 | Very Poor | Severe corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
176
177 | Very Poor | Severe corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
178 | Fair | The pipe was at half of its expected service life
179 | Poor | Corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
180 | nuts were not secured properly | good
181 | Paint peeling
182 | Fair | Deterioration was observed on the surface of the pump. The pump was near the end of its expected service life.
183 | Fair | Corrosoin and deterioration was observed on the valve. The pump was near the end of its expected service life.
184
185 | Fair | Corrosoin and deterioration was observed on the valve. The pump was near the end of its expected service life.
186 | Very Poor | Severe corrosoin and deterioration was observed on the valve. The pump was near the end of its expected service life.
187 | Fair | Deterioration was observed on the surface of the pump. The pump was near the end of its expected service life.
188 | Poor | expected service life.
189
190 | Poor | Corrosoin and deterioration was observed on the valve. The pump was near the end of its expected service life.
191 | fair | Minor deteriorartion was observed on the surface of the valve. The valve was near the end of its expected service life.
192 | Good
193 | fair. | obselete
194 | Good.
195 | Fair | Heavy corrosion was observed on the surface of the valve
196 | Fair | Heavy corrosion was observed on the surface of the valve
197 | Fair | Heavy corrosion and deterioration was observed on the surface of the valve.
198 | Good
199 | Fair | Heavy corrosion and deterioration was observed on the surface of the valve.
200 | Fair | Heavy corrosion and deterioration was observed on the surface of the valve.
201 | Fair | Heavy corrosion and deterioration was observed on the surface of the valve.
202 | Fair | Heavy corrosion and deterioration was observed on the surface of the valve.
203 | good
204 | Corrosion
205 | good
206 | good
207 | Good
208 | The sump pump was beyond its expected service life. | fair
209 | Corrosion | good
210
211 | CC: As per Section 7.2.9 of MOECC's Design Guidelines for Sewage Works, mechanical ventilation is required for below ground surface dry well. | missing
212 | fair | Deterioration and corrosion was obeserved on the surface of the pump. The pump was beyond its expected service life.
213 | fair | Corrosion and deterioration was observed on the surface of the valve. The valve was beyond its expected service life.
214 | Deterioration and corrosion was obeserved on the surface of the motor. The motor was beyond its expected service life. | fair
215 | fair | Corrosion and deterioratino was observed on the valve. The valve was beyond its expected service life.
216 | fair | Corrosion and deterioratino was observed on the valve. The valve was beyond its expected service life.
217 | fair | Deterioration and corrosion was obeserved on the surface of the pump. The pump was beyond its expected service life.
218 | fair | Corrosion and deterioration was observed on the surface of the valve. The valve was beyond its expected service life.
219 | fair | Deterioration and corrosion was obeserved on the surface of the motor. The motor was beyond its expected service life.
220 | Poor | Corrosion and deterioratino was observed on the valve. The valve was beyond its expected service life.
221 | fair | Corrosion and deterioratino was observed on the valve. The valve was beyond its expected service life.
222 | Fair | The pipe passed half of its expected service life
223 | The piping was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken.
224 | The piping was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken.
225 | The piping was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken.
226 | Poor | Heavy corrosion and deterioration was observed on the piping
227 | Heavy corrosion | Heavy corrosion and deterioration was observed on the piping
228 | assumed to be fair
229 | Fair | The pipe was over half of its expected service life.
230 | fair | The pipe was over half of its expected service life.
231
232 | fair | The pipe was over half of its expected service life.
233 | Fair | The pipe was over half of its expected service life.
234
235 | Poor | Severe deterioration was observed on the service piping
236 | Poor | Severe deterioration was observed on the service piping
237 | Fair | The pipe is at half of its expected service life.
238 | Fair | The pipe is at half of its expected service life.
239 | Fair | The bar screen is at half of its expected service life.
240
241
242 | Good
243 | Good
244
245
246
247 | Fair | The pipe was at half of its expected service life.
248 | Fair | The pipe was at half of its expected service life.
249 | Poor | The bar screen was beyond its expected service life
250
251 | Fair | The pipe was at half of its expected service life
252 | Very Poor | Severe corrosion was observed on the surfcae of the pipe
253
254 | Good
255
256 | Good
257
258
259 | Fair | The pipe was at half of its expected service life.
260 | Very Poor | Severe corrosion was observed on the pipe
261
262 | Fair | The pipe passed half of its expected service life.
263 | Fair | Minor deterioration was observed on the pipe and it passed half of its expected service life.
264
265
266 | Good
267
268 | Severe corrision was observed on the surface of the pipe | Very Poor
269 | Good
270 | Fair | Heavy corrosion was observed on the surface of the pipe
271 | poor | Heavy corrosion was observed on the surface of the valve
272 | Fair | The pipe passed half of its expected service life.
273 | Fair | The pipe passed half of its expected service life.
274 | Fair | The bar screen passed half of its expected service life.
275 | The asset was in good condition.
276 | The asset was in fair condition. Weathered paint and minor corrosion was observed.
277 | The asset was in fair condition. Corrosion and pitting noted.
278 | The asset was in fair condition. Corrosion was noted
279 | Fair | Surface corrosion on underside
280 | The asset was in fair condition. Surface corrosion on underside was observed.
281 | The asset was in fair condition. The paint at some locations was missing and corrosion was noted.
282 | good
283 | Fair | HS: Missing hatch grating
284 | Fair | HS: Missing hatch grating
285 | fair
286 |  | fair
287 | Fair | corosion on the platform
288 | corosion | Fair
289 | Fair | Brick riser supporting manhole frame is loose
290 | Fair
291 | Fair | Corrosion on top surface
292 | Fair | Peeling paint noted
293 | Fair | HS: Missing rung at platform level
294 | Fair | Surface corrosion on underside
295 | Fair
296 | Fair to poor | Corrosion noted
297 | Fair
298 | Fair | HS: Missing safety grating
299 | Fair
300 | Fair | HS: Grating not clipped
301 | Fair | Rust spots noted
302 | Fair
303 | Fair
304 | Fair | Peeling paint on exterior
305 | Fair
306 | Fair
307 | Fair | Corrosion noted
308 | Fair | Corrosion noted
309 | Fair | To be inspected yearly
310 | Fair | To be inspected yearly
311 | Fair
312 | Fair | To be inspected yearly
313 | Fair | To be inspected yearly
314 | Fair | HS: Grab bar is loose
315 | The asset was in fair condition. It is unknown when the equipment was last inspected. | HS: As per Occupational Health and Safety Act, R.S.O. 1990, c. O.1 the Davit Socket Base is to be inspected every year.
316 | Fair | To be inspected yearly
317 | Fair
318 | Fair
319 | Fair | To be inspected every year
320 | Surface corrsion noted on underside | Fair
321 | Fair | To be inspected every year
322 | Fair | HS: Bent ladder rung
323 | Corrosion noted | Fair
324 | Fair | Weathered paint on exterior
325 | Fair
326 | Fair
327 | Fair
328 | Fair
329 | Fair
330 | Fair
331 | Fair | Peeling paint on exterior
332 | Fair | To be inspected every year
333 | Fair
334 | Fair | Staining/corrosion noted
335 | Fair
336 | Fair
337 | Fair | HS: To be inspected every year
338 | Fair
339 | Fair | Fixed portion of platform grating was noted to be bent
340 | Fair
341 | Fair | To be inspected every year
342 | Fair
343 | Fair
344 | Fair | Flaking/missing on exterior
345 | Fair | HS: To be inspected every year
346 | Fair
347 | Fair | Pitting noted
348 | Fair | HS: To be inspected yearly
349 | fair | Calcium buildup and pitting noted
350 | Fair
351 | Fair
352 |  | Fair
353 | Fair | Weathered paint and missing paint on exterior
354 | Fair
355 | Fair
356 | Fair | Anchors were corroded
357 | Fair
358 | Fair | HS: Missing safety grating
359 | Fair | HS: Missing safety grating
360 | Fair | Calcium buildup and corrosion noted
361 | Fair | Calcium buildup and corrosion noted
362 | Fair | HS: Gratings now clipped down | Corrosion noted
363 | Fair | To be inspected every year
364 | Fair | Minor corrosion noted
365 | Fair
366 | Fair | Weathered paint on exterior
367 | Fair
368 | Fair | Surface corrosion noted
369 | Fair
370 | Fair | To be inspected every eyar
371 | Fair | Hatch hard to open due to corrosion on latch
372 | good
373 | Good
374 | Fair | Calcium buildup noted
375 | Fair | Calcium buildup noted
376 | Fair | Calcium buildup noted
377 | Fair | Calcium buildup noted
378 | Good
379 | Good
380 | Good
381 | Not accessible/inspected. Assumed to be good as no settlement was noted
382 | Good | Not visible/inspected. Assumed to be good as no settlement was noted.
383 | Not visible/inspected. Assumed to be good as no settlement was noted.
384 | Not visible/inspected. Assumed to be good as no settlement was noted.
385 | Not visibile/inspected. Assumed to be good as no settlement was noted
386 | Fair | Surface corrosion on underside
387 | Good
388 | Poor | Severe corrosion and deterioration was observed on the service of the valve. The valve was near the end of its expected service life.
389 | Good
390 | Poor | The pump was beyond its expected service life
391 | Very Poor | Severe corrosion was observed on the surface of the valve. The valve was beyond its expected service life.
392 | Very Poor | Severe corrosion was observed on the surface of the valve. The valve was beyond its expected service life
393 | The pump was beyond its expected service life. | Poor
394 | Very Poor | Severe corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
395 | Very Poor | Severe corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
396 | Fair | Minor deterioratino was observed on the bar screen.
397 | Poor | The pump was beyond its expected service life.
398 | fair | The screen was beyond its expected service life.
399 | poor | The pump was beyond its expected service life
400 | Poor | Severe corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
401
402 | Very Poor | Severe corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
403 | Very Poor | Severe corrosion was observed on the surface of the pump. The pump was beyond its expected service life.
404 | Fair | Debris is clogging at the bar screen, which in terms start clogging the inlet pipe.
405 | Poor | Corrosion and deterioration was observed on the surface of the valve. The valve was near the end of its expected service life.
406 | Poor | Corrosion and deterioration was observed on the surface of the valve
407
408 | Good
409 | The asset was in good condition.
410 | The asset was in good condition.
411 | The asset was in good condition.
412 | Corrrosion | fair
413
414 |  | good
415 | fair | Corrosion
416 |  | Dust
417 | Dust
418 | Corrosion
419 | Corrosion
420 | obselete | minor corrosion
421 | Obselete | Corrosion
422 | obselete | good
423 |  | good
424 | Dust | good
425 | good | Corrosion
426 | good | Corrosion
427 | good | Corrosion
428 | minor Corrosion
429 |  | good
430 | good
431 | good
432 | good
433 | very good
434 | good
435 | good | obselete
436 | good
437 | good
438 | good
439 | Good
440 | good
441 | good
442 | good
443 | good
444 | good
445 | good
446 | good | bolts were not secured properly
447 | good
448 | good
449 | good
450 | good
451 | good
452 | good
453 | good
454 | good
455 | good
456 |  | good
457 | The asset was in fair condition. Surface corrosion was observed.
458 | The asset was observed to be in good condition. | HS: Shock and arc flash hazard as the existing arc flash label is outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreover, the studies and reports
459 | The asset was observed to be in good condition.
460 | The asset was observed to be in good condition.
461 | The asset was observed to be in good condition. | HS: Shock and arc flash hazard as the existing arc flash label is outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreover, the studies and reports
462 | The asset was observed to be in good condition. | HS: Shock and arc flash hazard as the existing arc flash label is outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreover, the studies and reports
463 | The asset was observed to be in good condition. | HS: Shock and arc flash hazard as the existing arc flash label is outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreover, the studies and reports
464 | The asset was observed to be in good condition.
465 | The asset was observed to be in fair condition. Corrosion on fixtures was observed. The lighting should be replaced with LED in next upgrade
466 | The asset was in fair condition. Corrosion on the surface of the panels as well as circuit breakers was observed. The panel is to be replaced with NEMA 4X enclosure | HS: Shock and arc flash hazard as the existing arc flash label is outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreover, the studies and reports
467 | poor | heaviliy corroded
468 | good | to be replaced with LED in next upgrade
469 | fair | bottom of the enclosre is severly corroded | to be replaced with NEMA 3R enclosure
470 | good | phase converters inside panel to be replaced with VFDs
471 | good
472 | good
473 | good
474 | good
475 | good
476 | good | move it above ground
477 | good | replace with LED fixture in next upgrade
478 |  | good | discountinued
479 | good | discountinued
480 | good
481 | fair | corrosion was observed in different inside and surface of panel | missing Arc Flash Labels
482 | good
483 | fair | bottom interior of panel was corroded | Replace with NEMA 3R enclosure
484 | good | arc flash hazard label was painted on
485 | good
486 | good
487 | good
488 | good
489 | good | replace with LED fixtures rated for class 1, div 2
490 | good | inside the panel is not getting drained properly
491 | fair | replace with NEMA 4X panel
492 | good
493 | good | HS: missing arc flash label
494 | good
495 |  | good | HS: missing arc flash label
496 | good | replace with LED in next upgrade
497 | fair | HS: misplaced arc flash label | Pump #1 breaker to be sized and replaced according to OESC-2018
498 | good
499 | fair | bottom of interior has corroded | replace with NEMA 3R enclosure in next upgrade
500 | good | HS: missing arc flash label
501 | good
502 | good | HS: missing arc flash label
503 | good | fair | replace with LED fixture in next upgrade. To be rated for class 1, div 2
504 | fair | bottom of interior was corroded | HS: missing arc flash label
505 | fair | top surface and doors were corroded | to be replaced with NEMA 3R enclosure
506 | CC: outdated arc flash label | good
507 | good
508 | good
509 | good
510 | good
511 | poor | severly corroded
512 | good
513 | CC: misplaced and outdated arc flash label | good
514 | good
515 | CC: misplaced and outdated arc flash label | good
516 | CC: misplaced and outdated arc flash label | good
517 | good
518 | good | replace with LED in next upgrade
519 | fair | to be raplced with LED
520 | fair | to be replaced with LED
521 | fair
522 | CC: outdated arc flash label | fair | to have separate Main DS, MTS, and CP
523 | fair
524 | good
525 | good
526 | good
527 | good
528 | good
529 | good
530 | good
531 | fair | one of the lights doesn’t work | to be replaced with LED
532 | fair
533 | fair | it doesn't work
534 | fair | to be replaced with LED
535 | to be replaced with NEMA 3R enclosure | fair
536 | good
537 |  | good
538 | good
539 |  | good | replace with separate main DS, MTS and CP
540 | good
541 | good
542 | good
543 | good
544 | good
545 | fair | to be replaced with LED fixtures rated for Class 1, div 2
546 | fair
547 | good | top of control panel enclosure was damaged and was insulated
548 | good
549 | good
550 | good
551 | good | replace with VFD in next upgrade
552 | good
553 | good
554 | good
555 | good
556 | good
557 | good
558 | to be installed to comply with industry practice
559 | HS: There was no Generator Connection Receptical and Manual Transfer Switch located on site. Paralleling power sources and severe electrical shock hazard while hardwiring the generator for emergency power | to be installed to comply with industry practice
560 | to be installed to comply with industry practice
561 | to be installed to comply with industry practice
562 | Fair | to be installed (above ground) to comply with industry practice
563 | fair | to be installed (above ground) to comply with industry practice
564 | There was no Generator Connection Receptical and Manual Transfer Switch located on site. Paralleling power sources and severe electrical shock hazard while hardwiring the generator for emergency power | to be installed (above ground) to comply with industry practice
565 |  | The asset was in fair condition. Moderate corrosion was observed.
566 | The asset was in good condition
567 | The asset was in good condition overall. Paint peeling was observed.
568
569 | paint peeling at the portion above the wet well
570 | good
571
572 | good
573 | paint peeling
574 | Staining at the bottom section of the pipe
575 | good
576 | Surface corrosion
577 | good
578 | good
579 | good
580 | good
581 | Severe corrosion
582 | Missing gooseneck vent and bird screen.
583 | surface corrosion
584 | Surface corrosion
585 | good
586 | good
587 | miscellaneous surface staining
588 | Moderate corrosion
589 | good
590 | good
591 | Missing gooseneck section and bird screen
592 | paint peeling
593 | obsolete
594 | good
595 | good
596 | good
597 | surface corrosion
598 | good
599 | operability of the asset was unknown
600 | good
601 | good
602 | good
603 | Good
604 | good
605 | good
606 | The asset was observed to be in good condition.
607 | The asset was observed to be in good condition.
608 |  | Good
609 | There was no yard hydrant | In accordance with Section 19.8.3 of the Region's Water and Wastewater Design Manual (January 2012), a yard hydrant complete with a backflow preventer with a 37.5mm water service line shall be provided for flushing and cleaning purposes. It is recommended
610 |  | Good
611 | Good
612 | Good
613 | Good
614 | Good
615 | Good
616 |  | In accordance with Section 19.8.3 of the Region's Water and Wastewater Design Manual (January 2012), a yard hydrant complete with a backflow preventer with a 37.5mm water service line shall be provided for flushing and cleaning purposes. It is recommended
617 |  | Good
618 | Good
619 | Good
620 |  | Good
621 | Good
622 | Fair | Minor surface rust and defects
623 | In accordance with Section 19.8.3 of the Region's Water and Wastewater Design Manual (January 2012), a yard hydrant complete with a backflow preventer with a 37.5mm water service line shall be provided for flushing and cleaning purposes. It is recommended
624 | Good
625 | Good
626 | Good
627
628
629 | The asset was assumed to be in fair condition based on its age.
630 | The asset was observed to be in good condition. | HS: Shock and arc flash hazard as the existing arc flash label is outdated. As per (Workplace electrical safety (CSA Z-462-18)), labels need to change as soon as a change has been made to the system affecting fault currents. Moreover, the studies and reports
631
632
633
634
635
636
637
638
639
640
641
642
643
644
645
646
647
648
649
650
651 | Fair | Overgrown vegetation
652 | poor | Heavy corrosion and deterioration was observed on the piping
653
654
655 | Fair | The pipe passed half of its expected service life.
656
657 | good | Minor painr wear
658 | Fair | Heavy corrosion was observed on the surface of the pipe