## Sheet1
seqNum | assetTag | CategoryCode | facility | assetName | COF | Description | installYear | repCost | defect1Input | Process | building | inspectorName | LocationTag | LocationORIGINAL | TransmitterModel | TransducerModel | TransducerSerial | InstMeva | installationDate | remainingESL | InstType | ServiceArea | FacilityType | LifeCycleCategory | SerialNo | Parent | RotatingItem | Site | condition | defect1 | defect2 | defect3 | observations | RehabRepairCost | RehabRepairYear | RehabRepairCost2 | RehabRepairYear2 | photoName | repProjectName | rehabProjectName | rehab2ProjectName | Status | InspectionYear | manufacturer | rehabComment1 | rehabCost1 | rehabComment2 | rehabCost2 | defect2Input | defect3Input
5141 |  | HSS | S | (New) Fire Extinguisher | 1 |  | 2025 | 100 | Missing |  |  |  | 00019610 | [6 empty] | 8 | [8 empty] | 2 |  |  |  | The fire extinguisher was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  |  | Nobleton North ET Capital Project 1 |  |  |  | 2019 |  |  | 0 |  | 0
4996 |  | SW | S | (New) Sanitary Service | 2 | Provide sanitary service for tank. | 2025 | 120000 | No existing sanitary service for tank. |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_20201029_091308 |  |  |  |  | 0 |  | Install sanitary service for building and connect to nearby sanitary sewer. | 75000 |  | 0
4942 |  | SW | S | 300mm Underground Watermain Valve | 3 | 300mm Water valve, in valve box (within Region property line, adjacent to Dalton Road) | 1984 | 10000 | Lid could not be opened |  |  |  | 790900008 | [6 empty] | 2 | [8 empty] | 3 | Lid could not be opened was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. | 0 |  | 0 |  | IMG_20201029_093855 | Sutton ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
4943 |  | SW | S | 300mm Watermain | 5 | 125m of 300mm watermain. Material unknown | 1984 | 137000 |  |  |  |  | 790900008 | [6 empty] | 2 | [8 empty] | 3 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the short term. | 0 |  | 0 |  | IMG_20201029_093855 | Sutton ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
4944 |  | SW | S | 375mm Storm Sewer | 3 | 375mm storm sewer (tank drain/overflow), concrete pipe, approx. length is 120m | 1984 | 120000 |  |  |  |  | 790900008 | [6 empty] | 2 | [8 empty] | 3 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the short term. | 0 |  | 0 |  |  | Sutton ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
4951 |  | SW | S | Access Road | 1 | Access road from Dalton Road to site entrance. Approx length of 90m and 4.0m wide | 1984 | 30000 | Tire ruts and low spots at various locations. |  |  |  | 790900008 | [6 empty] | 6 | [8 empty] | 3 | Tire ruts and low spots at various locations was observed. |  |  | The asset was observed to be in fair condition.Place and compact granular material as required at low spots and tire ruts. Asset to be replaced in the intermediate term. | 7000 |  | 0 |  | IMG_20201029_093755 | Sutton ET Capital Project 1 |  |  |  | 0 |  | Place and compact granular material as required at low spots and tire ruts. | 7000 |  | 0
5128 |  | ES | S | Aircraft Obstruction Lights | 3 | Two warning lights, bulbs replaced in 2016 | 2016 | 5000 | Good |  |  |  | 00019634 | [6 empty] | 21 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_3873 |  |  |  |  | 2019 |  |  | 0 |  | 0
4940 |  | SW | S | Asphalt Driveway | 1 | Paved surface on site, and driveway entrance. Approximately 250m2. | 1984 | 20000 | Asphalt around concrete pad at tank pedestal settled, and damaged. |  |  |  | 790900008 | [6 empty] | 6 | [8 empty] | 3 | Asphalt around concrete pad at tank pedestal settled, and damaged was observed. | Minor asphalt cracking along south edge of driveway entrance was observed. |  | The asset was observed to be in fair condition.Remove and replace asphalt and granulars around pedestal entrance to ensure positive drainage away from entrance. Asset to be replaced in the intermediate term. | 5000 |  | 0 |  | IMG_20201029_092545 | Sutton ET Capital Project 1 |  |  |  | 0 |  | Remove and replace asphalt and granulars around pedestal entrance to ensure positive drainage away from entrance. | 5000 |  | 0 | Minor asphalt cracking along south edge of driveway entrance
4914 | 00025271 | SIC | S | Bell Antenna 1 | 1 | Cellular Antenna, installation year assumed to be 2010 based on its physical condition | 2010 | 10000 | Good |  |  |  | 790900008 | Sutton Elevated Tank | [5 empty] | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Antenna |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3867 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  |  | 0 |  | 0
4915 | 00025272 | SIC | S | Bell Antenna 2 | 1 | Cellular Antenna, installation year assumed to be 2010 based on its physical condition | 2010 | 10000 | Good |  |  |  | 790900008 | Sutton Elevated Tank | [5 empty] | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Antenna |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3867 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  |  | 0 |  | 0
4916 | 00025273 | SIC | S | Bell Antenna 3 | 1 | Cellular Antenna, installation year assumed to be 2010 based on its physical condition | 2010 | 10000 | Good |  |  |  | 790900008 | Sutton Elevated Tank | [5 empty] | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Antenna |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3867 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  |  | 0 |  | 0
4919 | 00025276 | SIC | S | Bell Antenna 4 | 1 | Cellular Antenna, installation year assumed to be 2010 based on its physical condition | 2010 | 10000 | Good |  |  |  | 790900008 | Sutton Elevated Tank | [5 empty] | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Antenna |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3874 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  |  | 0 |  | 0
4939 |  | SW | S | Chainlink Fence | 2 | 1.8m high, chainlink fence, with 3 barbed wires at top. Approx. 165m in length | 1984 | 25000 | Top barbed wire was cut, affecting approximately 10m in length. |  |  |  | 790900008 | [6 empty] | 6 | [8 empty] | 3 | Top barbed wire was cut, affecting approximately 10m in length was observed. |  |  | The asset was observed to be in fair condition.Re-install top barbed wire for section that is damaged. Asset to be replaced in the intermediate term. | 500 |  | 0 |  | IMG_20201029_091640 | Sutton ET Capital Project 1 |  |  |  | 0 |  | Re-install top barbed wire for section that is damaged. | 500 |  | 0
4923 | 00025424 | HSS | S | Chlorine Residual Kit | 2 | Hach II Pocket Colorimeter, Chlorine Residual Kit | 2010 | 700 | Missing |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Health and Safety | ` |  |  | W-WW | 3 | The asset was missing. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | 0 |  |  | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 | M00482 |  | 0 |  | 0
4941 |  | SW | S | Concrete Curb | 1 | Concrete curb at dirveway entrances (both east and west). Approximately 20m in length | 1984 | 2500 | Minor damage and cracking on curb. |  |  |  | 790900008 | [6 empty] | 6 | [8 empty] | 3 | Minor damage and cracking on curb was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_20201029_092855 | Sutton ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
4931 | 00078381 | BM | S | Electric Baseboard Heater | 2 | Baseboard Convection Heater, 120/1/60, Manufacturer: Dimplex, installation year assumed to be 2016 | 2016 | 500 | good |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 26 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Building Mechanical |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_5647 |  |  |  | OPERATING | 2020 | M00366 |  | 0 |  | 0
5129 |  | ES | S | Electrical Conduit System | 3 | Conduit system including conduit for electrical services, installation year assumed to be 2010. | 2010 | 25000 | good |  |  |  |  | Glenway RES Outside Sanitary Pumping Station | [5 empty] | 15 |  | Area 2N Linear Water & Wells | [5 empty] | OPERATING | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | PXL_20201029_134547192 | Sutton ET Capital Project 2 |  |  | W-WW | 2020 |  |  | 0 |  | 0
5049 | 00044398 | AC | S | Elevated Tank Access Double Doors | 1 | Exterior double metal door, installation year assumed to be 1984 | 1984 | 5500 | corrosion at bottom of door frame |  |  |  | 790900008 | Sutton Elevated Tank | [5 empty] | 6 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Architectural |  |  |  | W-WW | 3 | Corrosion was observed at bottom of door frame. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_3836 | Sutton ET Capital Project 1 |  |  | OPERATING | 2020 |  |  | 0 |  | 0
5098 |  | SC | S | Elevated Tank Aluminum Ladder (Ground to Platform) | 4 |  | 1984 | 30000 | good |  |  |  | 790900008 | [6 empty] | 22 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_3845 |  |  |  |  | 0 |  |  | 0 |  | 0
5099 |  | SC | S | Elevated Tank Aluminum Ladder (Platform to Roof) | 4 |  | 1984 | 15000 | good |  |  |  | 790900008 | [6 empty] | 22 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_3857 |  |  |  |  | 0 |  |  | 0 |  | 0
5101 |  | SC | S | Elevated Tank Aluminum Ladder (Platform to Tank Floor Access Hatch) | 4 |  | 1984 | 4000 | good |  |  |  | 790900008 | [6 empty] | 22 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_3853 |  |  |  |  | 0 |  |  | 0 |  | 0
5100 |  | SC | S | Elevated Tank Aluminum Ladder (Roof to Tank) | 4 |  | 1984 | 15000 | failed |  |  |  | 790900008 | [6 empty] | 22 | [8 empty] | 5 | The asset was failed. |  |  | The asset was observed to be in very poor condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_3889 |  |  |  |  | 0 |  |  | 0 |  | 0
5097 |  | SC | S | Elevated Tank Aluminum Platform | 4 |  | 1984 | 50000 | good |  |  |  | 790900008 | [6 empty] | 22 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_3846 |  |  |  |  | 0 |  |  | 0 |  | 0
5107 |  | HSS | S | Elevated Tank Anchor Point | 4 | Platform level | 2007 | 3000 | good |  |  |  | 790900008 | [6 empty] | 8 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_3850 | Sutton ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
4891 | 00004221 | PM | S | Elevated Tank Bypass Line Check Valve | 3 | Diameter: 150mm, Manufacturer: McAvity | 1984 | 1500 | Minor to moderate surface corrosion |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 2 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Process Mechanical |  |  |  | W-WW | 3 | Minor to moderate surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. | 0 |  | 0 |  | IMG_5651 | Sutton ET Capital Project 1 |  |  | OPERATING | 2020 | M00100 |  | 0 |  | 0
4890 | 00004220 | PM | S | Elevated Tank Bypass Line Gate Valve 1 | 3 | Diameter: 150mm, Manufacturer: McAvity | 1984 | 1500 | Minor to moderate surface corrosion |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 2 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Process Mechanical |  |  |  | W-WW | 3 | Minor to moderate surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. | 0 |  | 0 |  | IMG_5568 | Sutton ET Capital Project 1 |  |  | OPERATING | 2020 | M00100 |  | 0 |  | 0
4892 | 00004222 | PM | S | Elevated Tank Bypass Line Gate Valve 2 | 3 | Diameter: 150mm, Manufacturer: McAvity | 1984 | 1500 | Minor surface corrosion |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 2 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Process Mechanical |  |  |  | W-WW | 3 | Minor surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. | 0 |  | 0 |  | IMG_5557 | Sutton ET Capital Project 1 |  |  | OPERATING | 2020 | M00100 |  | 0 |  | 0
4893 | 00004223 | PM | S | Elevated Tank Bypass Line Gate Valve 3 | 3 | Diameter: 150mm, Manufacturer: McAvity | 1984 | 1500 | Minor surface corrosion |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 2 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Process Mechanical |  |  |  | W-WW | 3 | Minor surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. | 0 |  | 0 |  | IMG_5551 | Sutton ET Capital Project 1 |  |  | OPERATING | 2020 | M00100 |  | 0 |  | 0
4894 | 00004224 | PM | S | Elevated Tank Bypass Line Gate Valve 4 | 3 | Diameter: 150mm, Manufacturer: McAvity | 1984 | 1500 | Minor surface corrosion |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 2 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Process Mechanical |  |  |  | W-WW | 3 | Minor surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. | 0 |  | 0 |  | IMG_5550 | Sutton ET Capital Project 1 |  |  | OPERATING | 2020 | M00100 |  | 0 |  | 0
5138 |  | PM | S | Elevated Tank Bypass Line Piping | 4 | Diameter: 150mm, approximate length: 10m | 1984 | 5500 | Moderate surface corrosion |  |  |  | 790900008 | [6 empty] | 2 | [8 empty] | 3 | Moderate surface corrosion was observed. | Couplings installed on the pipe were rusted was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. | 0 |  | 0 |  | IMG_5642 | Sutton ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0 | Couplings installed on the pipe were rusted.
5133 |  | SC | S | Elevated Tank Cathodic Protection | 3 |  | 1984 | 0 | The elevated tank did not have cathodic protection. The Region is planning to have the cathodic protection system installed. | [10 empty] | 22 | [8 empty] | 3 | The elevated tank did not have cathodic protection. the region is planning to have the cathodic protection system installed was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 | [6 empty] | 0 |  |  | 0 |  | 0
4910 | 00017903 | SIC | S | Elevated Tank Chlorine Analyzer | 3 |  | 1984 | 15000 | outdated |  |  |  | 00016061 | Sutton ET Valve Room | CL17 |  |  | Chlorine |  | 2 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control | 30600007459 |  |  | W-WW | 3 | The asset was outdated. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. | 0 |  | 0 |  | PXL_20201029_133942071 | Sutton ET Capital Project 1 |  |  | OPERATING | 2020 | M00482 |  | 0 |  | 0
5093 |  | SC | S | Elevated Tank Concrete Structure | 4 |  | 1984 | 900000 | good |  |  |  | 790900008 | [6 empty] | 22 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 0 | 2030 | 0 |  | IMG_3845 |  | Sutton ET Capital Project 1 |  |  | 0 |  |  | 0 |  | 0
5106 |  | HSS | S | Elevated Tank Davit Base Socket | 4 | Roof | 2007 | 4000 | good |  |  |  | 790900008 | [6 empty] | 8 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_3879 | Sutton ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
5095 |  | SC | S | Elevated Tank Exterior Coating | 3 |  | 1984 | 600000 | fair |  |  |  | 790900008 | [6 empty] | 22 | [8 empty] | 3 |  |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_3835 |  |  |  |  | 0 |  |  | 0 |  | 0
4935 | 00083317 | SIC | S | Elevated Tank Flow Transmitter | 3 | installation year assumed to be 2010 based on its physical condition | 2010 | 10000 | good |  |  |  | 00016061 | Sutton ET Valve Room | 93WA4-18D3/0 | 93WA4 |  | Flow |  | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control | M1027302000 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | PXL_20201029_134330909 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 | M00405 |  | 0 |  | 0
5131 |  | ES | S | Elevated Tank Grounding | 3 | installation year assumed to be 2010 | 2010 | 10000 | good |  |  |  | 790900018 | [6 empty] | 15 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3844 | Sutton ET Capital Project 2 |  |  |  | 0 |  |  | 0 |  | 0
5115 |  | SC | S | Elevated Tank Guardrail | 3 |  | 1984 | 30000 | good |  |  |  | 790900008 | [6 empty] | 22 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_3873 |  |  |  |  | 0 |  |  | 0 |  | 0
5108 |  | SC | S | Elevated Tank Inlet Pipe Support | 3 |  | 1984 | 30000 | good |  |  |  | 790900008 | [6 empty] | 22 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_3845 |  |  |  |  | 0 |  |  | 0 |  | 0
4889 | 00004219 | PM | S | Elevated Tank Inlet/Outlet Line Gate Valve | 3 | Diameter: 300mm, Manufacturer: McAvity | 1984 | 3000 | Leak in packing |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 2 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Process Mechanical |  |  |  | W-WW | 3 | Leak in packing was observed. | Minor to moderate corrosion was observed on valve body. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. | 0 |  | 0 |  | IMG_5556 | Sutton ET Capital Project 1 |  |  | OPERATING | 2020 | M00100 |  | 0 |  | 0 | Minor to moderate corrosion on valve body
5137 |  | PM | S | Elevated Tank Inlet/Outlet Piping | 4 | Diameter: 300mm, approximate length: 35m | 1984 | 40000 | Very minor surface corrosion |  |  |  | 790900008 | [6 empty] | 2 | [8 empty] | 3 | Very minor surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. | 0 |  | 0 |  | IMG_5591 | Sutton ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
5096 |  | SC | S | Elevated Tank Interior Coating | 3 |  | 1984 | 375000 | poor |  |  |  | 790900008 | [6 empty] | 22 | [8 empty] | 3 | Poor was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_3889 |  |  |  |  | 0 |  |  | 0 |  | 0
5130 |  | ES | S | Elevated Tank Lightning Protection System | 3 | 1 lightning air protection terminal | 2004 | 5000 | good |  |  |  | 790900018 | [6 empty] | 9 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_3867 | Sutton ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
4934 | 00083307 | SIC | S | Elevated Tank Network Access Closet | 4 | installation year assumed to be 2010 | 2010 | 25000 | good |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control | 14E-088/SUETDR_NAC |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | PXL_20201029_134521784 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 | M00844 |  | 0 |  | 0
4913 | 00017906 | SIC | S | Elevated Tank Network Radio Modem 1 | 2 | likely installed in the Network Access Closet, installation year assumed to be 2010 | 2010 | 5000 |  |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | SCADA | 831070 |  |  | W-WW | 3 |  | Included in 00083307 was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | 0 |  |  | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 | M01018 |  | 0 |  | 0 | included in 00083307
4912 | 00017905 | SIC | S | Elevated Tank Network Radio Modem 2 | 2 | likely installed in the Network Access Closet, installation year assumed to be 2010 | 2010 | 5000 |  |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | SCADA | 831046 |  |  | W-WW | 3 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the long term. | 0 |  | 0 |  |  | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 | M01018 |  | 0 |  | 0
4905 | 00017896 | SIC | S | Elevated Tank Network UPS 1 | 2 | likely installed in the Network Access Closet, installation year assumed to be 2010 | 2010 | 3000 |  |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | SCADA | JB0241022055R |  |  | W-WW | 3 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the long term. | 0 |  | 0 |  |  | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 | M00183 |  | 0 |  | 0
4928 | 00052825 | SIC | S | Elevated Tank Network UPS 2 | 2 | likely installed in the Network Access Closet, installation year assumed to be 2010 | 2010 | 3000 |  |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | SCADA | GF104A0100 |  |  | W-WW | 3 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the long term. | 0 |  | 0 |  |  | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 | M00728 |  | 0 |  | 0
5109 |  | SC | S | Elevated Tank Outlet Pipe Support | 3 |  | 1984 | 30000 | good |  |  |  | 790900008 | [6 empty] | 22 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_3845 |  |  |  |  | 0 |  |  | 0 |  | 0
5139 |  | PM | S | Elevated Tank Overflow Piping | 4 | Diameter: 150mm, approximate length: 40m | 1984 | 25000 | Moderate surface corrosion |  |  |  | 790900008 | [6 empty] | 2 | [8 empty] | 3 | Moderate surface corrosion was observed. | Couplings installed on the pipe were rusted was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. | 0 |  | 0 |  | IMG_5634 | Sutton ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0 | Couplings installed on the pipe were rusted.
4950 |  | ES | S | Elevated Tank Pedestal Lighting | 2 | 6 NEMA 4 fixtures, installation year assumed to be 2010. | 2010 | 6000 | good |  |  |  | 790900008 | [6 empty] | 15 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | PXL_20201029_135009897 | Sutton ET Capital Project 2 |  |  |  | 0 |  |  | 0 |  | 0
4901 | 00006889 | SIC | S | Elevated Tank Pressure Gauge | 1 |  | 1984 | 500 | Minor surface corrosion |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 6 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control |  |  |  | W-WW | 3 | Minor surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | PXL_20201029_134817672 | Sutton ET Capital Project 1 |  |  | OPERATING | 2020 | M00627 |  | 0 |  | 0
4926 | 00044946 | SIC | S | Elevated Tank Pressure Transmitter | 3 | Installation year assumed to be 2010 based on its physical condition | 2010 | 2000 | good |  |  |  | 00016061 | Sutton ET Valve Room | PMC71 |  |  |  |  | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control | F900091509C |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | PXL_20201029_134314017 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 | M00405 |  | 0 |  | 0
5126 |  | BM | S | Elevated Tank Removable Louvred Vent | 1 |  | 1984 | 5000 | good |  |  |  | 790900018 | [6 empty] | 6 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_3848 | Sutton ET Capital Project 1 |  |  |  | 2019 |  |  | 0 |  | 0
5104 |  | SC | S | Elevated Tank Roof Access Hatch (Access to Tank Interior) | 2 |  | 1984 | 10000 | good |  |  |  | 790900008 | [6 empty] | 22 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_3883 |  |  |  |  | 0 |  |  | 0 |  | 0
5103 |  | SC | S | Elevated Tank Roof Access Hatch (Access Tube to Tank Roof) | 2 |  | 1984 | 10000 | good |  |  |  | 790900008 | [6 empty] | 22 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_3883 |  |  |  |  | 0 |  |  | 0 |  | 0
5105 |  | HSS | S | Elevated Tank Roof Dismount Post | 4 |  | 1984 | 3000 | Moderate surface corrosion |  |  |  | 790900008 | [6 empty] | 2 | [8 empty] | 3 | Moderate surface corrosion was observed. |  |  | The asset was observed to be in fair condition.Surface prep and paint dismount post in safety yellow colour. Asset to be replaced in the short term. | 2000 |  | 0 |  | IMG_3883 | Sutton ET Capital Project 1 |  |  |  | 0 |  | Surface prep and paint dismount post in safety yellow colour. | 2000 |  | 0
5094 |  | SC | S | Elevated Tank Steel Tank | 5 |  | 1984 | 1300000 | good |  |  |  | 790900008 | [6 empty] | 22 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_3835 |  |  |  |  | 0 |  |  | 0 |  | 0
5102 |  | SC | S | Elevated Tank Submarine Floor Access Hatch | 3 |  | 1984 | 3000 | good |  |  |  | 790900008 | [6 empty] | 22 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_3853 |  |  |  |  | 0 |  |  | 0 |  | 0
4937 | 00083320 | SIC | S | Elevated Tank SUETDR Control Panel | 4 | PAC control panel, installation year assumed to be 2017 | 2017 | 80000 | good |  |  |  | 00016062 | Sutton ET Tank Base | [5 empty] | 12 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control | 14E-088/SUETDR_PAC |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | PXL_20201029_134934038 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 | M00844 |  | 0 |  | 0
4932 | 00081400 | SIC | S | Elevated Tank SUETDR Control Panel Ethernet Switch | 2 | likely installed in SUETDR Control Panel, installation year assumed to be 2017 | 2017 | 3000 |  |  |  |  | 00016062 | Sutton ET Tank Base | [5 empty] | 12 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control | FOC2004Z1FF |  |  | W-WW | 3 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the long term. | 0 |  | 0 |  |  | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 | M01002 |  | 0 |  | 0
4938 | 00083386 | SIC | S | Elevated Tank SUETDR Control Panel UPS | 2 | likely installed in SUETDR Control Panel, installation year assumed to be 2017 | 2017 | 3000 |  |  |  |  | 00016062 | Sutton ET Tank Base | [5 empty] | 12 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control | GK053A0127 |  |  | W-WW | 3 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the long term. | 0 |  | 0 |  | PXL_20201029_134934038 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 | M10181 |  | 0 |  | 0
4933 | 00083219 | SIC | S | Elevated Tank SUETDR OIT Panel | 3 | Advantech Monitor Panel, installation year assumed to be 2017 based on its physical condition | 2017 | 10000 | good |  |  |  | 00016062 | Sutton ET Tank Base | [5 empty] | 12 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control | KSA1476816 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | PXL_20201029_134143670 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 | M10189 |  | 0 |  | 0
4936 | 00083318 | SIC | S | Elevated Tank SUETDR OIT Panel CPU | 2 | installed in SUETDR OIT Panel, installation year assumed to be 2017 | 2017 | 1500 |  |  |  |  | 00016062 | Sutton ET Tank Base | [5 empty] | 12 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control | ACG2001486 |  |  | W-WW | 3 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the long term. | 0 |  | 0 |  | PXL_20201029_134143670 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 | M10189 |  | 0 |  | 0
5117 |  | SC | S | Elevated Tank Tank Vent | 3 |  | 1984 | 5000 | good |  |  |  | 790900008 | [6 empty] | 22 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_3879 |  |  |  |  | 0 |  |  | 0 |  | 0
5140 |  | PM | S | Elevated Tank Vent/Vacuum Relief Unit | 3 | Installation year assumed to be 1984. | 1984 | 10000 | Minor surface corrosion on steel collar |  |  |  | 00019817 | [6 empty] | 2 | [8 empty] | 3 | Minor surface corrosion was observed on steel collar. |  |  | The asset was observed to be in fair condition.Surface prep and touch-up vent collar Asset to be replaced in the short term. | 2000 |  |  |  | IMG_3875 | Sutton ET Capital Project 1 |  |  |  | 2019 |  | Surface prep and touch-up vent collar | 2000
4927 | 00045975 | ES | S | Generator Transfer Panel | 3 | Manufacturer: Siemens, Model No.:EQG630D. Installation year assumed to be 1984. | 1984 | 5000 | minor corrosion around the circuit breakers |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 2 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Electrical System | 12167-067 |  |  | W-WW | 3 | Minor corrosion was observed around the circuit breakers. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. | 0 |  | 0 |  | PXL_20201029_134356166 | Sutton ET Capital Project 1 |  |  | OPERATING | 2020 | M00125 |  | 0 |  | 0
4900 | 00006888 | ES | S | Heat Trace Control Panel | 3 |  | 1984 | 5000 | outdated |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 2 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Electrical System |  |  |  | W-WW | 3 | The asset was outdated. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. | 0 |  | 0 |  | PXL_20201029_134021130 | Sutton ET Capital Project 1 |  |  | OPERATING | 2020 |  |  | 0 |  | 0
5127 | 00006888 | ES | S | Inlet/Outlet Riser Heat Trace System | 3 |  | 1984 | 10000 | good |  |  |  | 00016061 | [6 empty] | 6 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_5575 | Sutton ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
4897 | 00084446 | ES | S | Lighting Panel A | 3 | Mannufacturer:Square D; ; serial number: 12398972110010001, 120/240V, 200A, 42CCT; old tag is 00006883. The panel was installed approximately in 2016. | 2016 | 14000 | corrosion on enclosure |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 21 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Electrical System | T3A |  |  | W-WW | 3 | Corrosion was observed on enclosure. | The enclosure was not nema 3r type was observed. | The enclosure to be replaced with nema 3r type was observed. | The asset was observed to be in fair condition.Replace the enclosure with NEMA 3R type. Asset to be replaced at the end of remaining service life. | 4000 |  | 0 |  | PXL_20201029_134229876 |  |  |  | OPERATING | 2020 | M00129 | Replace the enclosure with NEMA 3R type. | 4000 |  | 0 | The enclosure was not NEMA 3R type. | The enclosure to be replaced with NEMA 3R type
4908 | 00017900 | SIC | S | Network Antenna 1 | 2 | Installation year assumed to be 2010 based on its physical condition | 2010 | 10000 | good |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | SCADA |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | PXL_20201029_133504866 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  |  | 0 |  | 0
4909 | 00017901 | SIC | S | Network Antenna 2 | 2 | Installation year assumed to be 2010 based on its physical condition | 2010 | 10000 | good |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | SCADA |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | PXL_20201029_133504866 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  |  | 0 |  | 0
4947 |  | ES | S | Outdoor Lighting Fixture | 1 | 1 LED flood light, installation year assumed to be 2010. | 2010 | 900 | good |  |  |  | 790900008 | [6 empty] | 15 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | PXL_20201029_133518930 | Sutton ET Capital Project 2 |  |  |  | 0 |  |  | 0 |  | 0
5001 | 00044308 | BM | S | Portable Dehumidifier | 2 | Portable dehumidifier by Electrolux Home Products, Model CAD304NWL, 115/60/1; capacity 30 pints/day | 2016 | 300 | good |  |  |  | 00016061 | [6 empty] | 26 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_5623 |  |  |  |  | 0 |  |  | 0 |  | 0
4929 | 00077743 | ES | S | Portable Generator | 3 | Manufacturer: Honda, Model Name: EU3000, specs: 120V, 20A. Installation year assumed to be 2017 | 2017 | 2000 | good |  |  |  | 790900008 | Sutton Elevated Tank | [5 empty] | 22 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Building Mechanical | EAVJ-1144610 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | PXL_20201029_134627924 |  |  |  | OPERATING | 2020 | M00506 |  | 0 |  | 0
4903 | 00012111 | SW | S | Site Drainage (soft surfaces) | 1 | Site drainage on site, including grassed areas. | 1984 | 15000 | Along edge of pavement, tire ruts damaged sod |  |  |  | 790900008 | Sutton Elevated Tank | [5 empty] | 6 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Siteworks |  |  |  | W-WW | 3 | Along edge of pavement, tire ruts damaged sod was observed. | Low spots at various locations around site, not draining storm water properly was observed. |  | The asset was observed to be in fair condition.Remove top soil and sod along edge of pavement, and replace with gravel shoulder. Asset to be replaced in the intermediate term. | 7500 |  | 2000 |  | IMG_20201029_091412 | Sutton ET Capital Project 1 |  |  | OPERATING | 2020 |  | Remove top soil and sod along edge of pavement, and replace with gravel shoulder. | 7500 | Remove and replace sod at low spots of soft surface around site. | 2000 | Low spots at various locations around site, not draining storm water properly
4902 | 00012107 | SW | S | Site Gate | 2 | East, Gate, Double Lockable | 1984 | 3000 | Minor damage |  |  |  | 790900008 | Sutton Elevated Tank | [5 empty] | 6 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Siteworks |  |  |  | W-WW | 3 | Minor damage was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_20201029_092823 | Sutton ET Capital Project 1 |  |  | OPERATING | 2020 |  |  | 0 |  | 0
4930 | 00078380 | SIC | S | Security System | 3 | Three panels in total, installation year assumed to be 2010 based on the physical condition | 2010 | 10000 | good |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Health and Safety |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | PXL_20201029_134421959 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 | M00076 |  | 0 |  | 0
4945 |  | SW | S | Storm Maintenance Hole No. 2 | 2 | Located at Dalton Road ROW, approximately 2.0m deep. | 1984 | 15000 | Damaged maintenance hole adjustment unit for frame. |  |  |  | 790900008 | [6 empty] | 6 | [8 empty] | 3 | Damaged maintenance hole adjustment unit for frame was observed. |  |  | The asset was observed to be in fair condition.Remove and replace adjustment unit for maintenance hole frame. Asset to be replaced in the intermediate term. | 1000 |  | 0 |  | IMG_20201029_094643 | Sutton ET Capital Project 1 |  |  |  | 0 |  | Remove and replace adjustment unit for maintenance hole frame. | 1000 |  | 0
4946 |  | SW | S | Storm Maintenance Hole No.3 | 2 | Located approximately 5m from elevated tank pedestal. Approximately 2.5m deep. | 1984 | 17500 | Maintenance hole was buried below pavement. |  |  |  | 790900008 | [6 empty] | 6 | [8 empty] | 3 | Maintenance hole was buried below pavement was observed. |  |  | The asset was observed to be in fair condition.Excavate around maintenance hole and raise frame/lid to grade. Reinstate asphalt pavement around lid. Asset to be replaced in the intermediate term. | 2500 |  | 0 |  | IMG_20201029_095120 | Sutton ET Capital Project 1 |  |  |  | 0 |  | Excavate around maintenance hole and raise frame/lid to grade. Reinstate asphalt pavement around lid. | 2500 |  | 0
4924 | 00035519 | BM | S | Sump Pump and Drain Piping | 2 | Submersible Sump Pump, by Mastercraft, 120/1/60, 1/3hp, capacity: 10.4 m3/h. The sump pump pumping connected to elevated tank overflow pipe | 1984 | 2000 | good |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 6 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Process Mechanical |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_5618 | Sutton ET Capital Project 1 |  |  | OPERATING | 2020 |  |  | 0 |  | 0
4906 | 00017897 | SIC | S | Sump Pump Float Switch | 2 | installed in the sump pump pit, installation year assumed to be 2010 based on its physical condition. | 2010 | 500 | good |  |  |  | 00016061 | Sutton ET Valve Room |  |  |  | Level |  | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | PXL_20201029_134846156 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  |  | 0 |  | 0
5114 |  | SW | S | Valve Chamber Access Ladder | 3 |  | 1984 | 2500 | good |  |  |  | 790900008 | [6 empty] | 6 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_3913 | Sutton ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
5113 |  | SW | S | Valve Chamber Manhole Frame and Cover | 2 |  | 1984 | 1500 | good |  |  |  | 790900008 | [6 empty] | 6 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_3911 | Sutton ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
5112 |  | SW | S | Valve Chamber Precast Concrete Chamber | 2 |  | 1984 | 50000 | good |  |  |  | 790900008 | [6 empty] | 6 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_3913 | Sutton ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
5111 |  | SC | S | Valve Room Concrete Roof | 4 |  | 1984 | 15000 | good |  |  |  | 00016061 | [6 empty] | 22 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 0 | 2030 | 0 |  | IMG_3905 |  | Sutton ET Capital Project 1 |  |  | 0 |  |  | 0 |  | 0
4949 |  | ES | S | Valve Room Emergency Lighting | 1 | Emergency lighting with 1 battery unit and 1 remote head, a new battery was installed in July 2020. | 2010 | 1000 | good |  |  |  | 00016061 | [6 empty] | 15 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | PXL_20201029_133917415 | Sutton ET Capital Project 2 |  |  |  | 0 |  |  | 0 |  | 0
5048 | 00006879 | AC | S | Valve Room Interior Single Door | 1 | Installation year assumed to be 1984 | 1984 | 3500 | fair |  |  |  | 00016061 | Sutton ET Tank Base | [5 empty] | 6 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Architectural |  |  |  | W-WW | 3 |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_3903 | Sutton ET Capital Project 1 |  |  | OPERATING | 2020 |  |  | 0 |  | 0
4948 |  | ES | S | Valve Room Lighting Fixtures | 1 | 2 NEMA 4 fixtures, installation year assumed to be 2010. | 2010 | 2000 | good |  |  |  | 00016061 | [6 empty] | 15 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | PXL_20201029_134544370 | Sutton ET Capital Project 2 |  |  |  | 0 |  |  | 0 |  | 0
4907 | 00017898 | SIC | S | Valve Room Low Temperature Alarm | 2 | Valve room low temperature alarm, installation year assumed to be 2010 based on its physical condition. | 2010 | 500 | good |  |  |  | 00016061 | Sutton ET Valve Room | T631A1063 |  |  | Temperature |  | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control | NOT AVAILABLE |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | PXL_20201029_134218182 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 | M00076 |  | 0 |  | 0
5110 |  | SC | S | Valve Room Masonry Blockwall | 4 |  | 1984 | 8000 | hairline cracking at corner |  |  |  | 00016061 | [6 empty] | 22 | [8 empty] | 3 | Hairline cracking was observed at corner. |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_3903 |  |  |  |  | 0 |  |  | 0 |  | 0 | fair
5089 |  | AC | S | Valve Room Wall and Ceiling Paint | 1 | Installation year assumed to be 1987 | 1987 | 2000 | good |  |  |  | 00016061 | [6 empty] | 6 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_3905 | Sutton ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
5003 |  | PM | S | Watermain Pipe Extended Stem Gate Valve 1 | 3 | Diameter: 300mm | 2016 | 5000 | Minor corrosion on wrench nut |  |  |  | 790900008 | [6 empty] | 26 | [8 empty] | 3 | Minor corrosion on wrench nut was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_5482 |  |  |  |  | 0 |  |  | 0 |  | 0
5005 |  | PM | S | Watermain Pipe Extended Stem Gate Valve 2 | 3 | Diameter: 300mm | 2016 | 5000 | Minor corrosion on wrench nut |  |  |  | 790900008 | [6 empty] | 26 | [8 empty] | 3 | Minor corrosion on wrench nut was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_5485 |  |  |  |  | 0 |  |  | 0 |  | 0
5004 |  | PM | S | Watermain Pipe Extended Stem Gate Valve 2 | 3 | Diameter: 300mm | 2016 | 5000 | Minor corrosion on wrench nut |  |  |  | 790900008 | [6 empty] | 26 | [8 empty] | 3 | Minor corrosion on wrench nut was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_5489 |  |  |  |  | 0 |  |  | 0 |  | 0
4918 | 00025275 | SIC | S | York Region Antenna 5 | 1 | UHF SCADA Yagi Antenna, installation year assumed to be 2010 based on the physical condition | 2010 | 10000 | Good |  |  |  | 790900008 | Sutton Elevated Tank | [5 empty] | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Antenna |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3869 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  |  | 0 |  | 0
4917 | 00025274 | SIC | S | York Region Antenna 6 | 1 | UHF Yagi Antenna, installation year assumed to be 2010 based on the physical condition | 2010 | 10000 | Good |  |  |  | 790900008 | Sutton Elevated Tank | [5 empty] | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Antenna |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3869 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  |  | 0 |  | 0
4920 | 00025277 | SIC | S | York Region Antenna 7 | 1 | UHF Whip Traffic Antenna, installation year assumed to be 2010 based on the physical condition | 2010 | 10000 | Good |  |  |  | 790900008 | Sutton Elevated Tank | [5 empty] | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Antenna |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3874 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  |  | 0 |  | 0
4921 | 00025278 | SIC | S | York Region Antenna 8 | 1 | UHF Whip Traffic Antenna, installation year assumed to be 2010 based on the physical condition | 2010 | 10000 | Good |  |  |  | 790900008 | Sutton Elevated Tank | [5 empty] | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Antenna |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3874 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  |  | 0 |  | 0
4922 | 00025279 | SIC | S | York Region Antenna 9 | 1 | UHF Whip Traffic Antenna, installation year assumed to be 2010 based on the physical condition | 2010 | 10000 | Good |  |  |  | 790900008 | Sutton Elevated Tank | [5 empty] | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Antenna |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3874 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  |  | 0 |  | 0