## Sheet1
seqNum | assetTag | facility | CategoryCode | COF | assetName | Description | defect1Input | repCost | Process | building | inspectorName | LocationTag | LocationORIGINAL | TransmitterModel | TransducerModel | TransducerSerial | InstMeva | installYear | installationDate | remainingESL | InstType | ServiceArea | FacilityType | LifeCycleCategory | SerialNo | Parent | RotatingItem | Site | condition | defect1 | defect2 | defect3 | observations | RehabRepairCost | RehabRepairYear | RehabRepairCost2 | RehabRepairYear2 | photoName | repProjectName | rehabProjectName | rehab2ProjectName | Status | InspectionYear | manufacturer | rehabComment1 | rehabCost1 | rehabComment2 | rehabCost2 | defect2Input | defect3Input
5051 |  | MAN | AC | 1 | Electrical Room Access Door (Single) |  | good | 3500 |  |  |  | 17169 | [5 empty] | 2004 |  | 6 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_4108 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
5054 |  | MAN | AC | 1 | Electrical Room Wall Paint |  | good | 1000 |  |  |  | 17169 | [5 empty] | 2004 |  | 6 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_6363 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
5047 | 00024565 | MAN | AC | 1 | Exterior Access Door (Double) | double metal door | corrosion at bottom of doors and door frame | 5500 |  |  |  | 17168 | Mt Alberta Noth ET Foyer |  |  |  |  | 2004 |  | 6 |  |  |  | Architectural |  |  |  | W-WW | 3 | Corrosion was observed at bottom of doors and door frame. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_4128 | Mt Albert North ET Capital Project 1 |  |  | OPERATING |  |  |  | 0 |  | 0
5053 |  | MAN | AC | 1 | Foyer Wall Paint |  | peeled paint at bottom | 1000 |  |  |  | 17168 | [5 empty] | 2004 |  | 6 | [8 empty] | 3 | Peeled paint at bottom was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_4107 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
5046 | 00024566 | MAN | AC | 1 | Storage Room Access Door (Single) | single metal door | corrosion at bottom of door frame | 3500 |  |  |  | 17168 | Mt Alberta Noth ET Foyer |  |  |  |  | 2004 |  | 6 |  |  |  | Architectural |  |  |  | W-WW | 3 | Corrosion was observed at bottom of door frame. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_4109 | Mt Albert North ET Capital Project 1 |  |  | OPERATING |  |  |  | 0 |  | 0
5055 |  | MAN | AC | 1 | Storage Room Wall Paint |  | good | 500 |  |  |  | 17169 | [5 empty] | 2004 |  | 6 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_4123 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
5050 | 00024562 | MAN | AC | 1 | Valve Room Access Door (Double) | double metal door | corrosion at bottom of door frame | 5500 |  |  |  | 17166 | Mt Alberta Noth ET Valve Room |  |  |  |  | 2004 |  | 6 |  |  |  | Architectural |  |  |  | W-WW | 3 | Corrosion was observed at bottom of door frame. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_4109 | Mt Albert North ET Capital Project 1 |  |  | OPERATING |  |  |  | 0 |  | 0
5052 |  | MAN | AC | 1 | Valve Room Wall Paint |  | Minor peeled paint | 2000 |  |  |  | 17166 | [5 empty] | 2004 |  | 6 | [8 empty] | 3 | Minor peeled paint was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_4113 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
4981 | 00024559 | MAN | BM | 2 | Electrical Control Room Electric Unit Heater | Electrical Control Room,forced air Heating System, Electric Unit Heater, by Stelpro; 3kW, 240/1/60; | Good | 3000 |  |  |  | 17169 | Mt Alberta Noth ET Electrical Control Room |  |  |  |  | 2004 |  | 14 |  |  |  | Building Mechanical | 40402 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_6361 | Mt Albert North ET Capital Project 2 |  |  | OPERATING |  | M00132 |  | 0 |  | 0
5036 |  | MAN | BM | 1 | Elevated Tank Removable Louvred Vent |  | good | 5000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 14 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_4064 | Mt Albert North ET Capital Project 2 |  |  |  | 2019 |  |  | 0 |  | 0
5037 |  | MAN | BM | 2 | Plumbing and Drainage | 100mm drainage piping for floor drain and future washroom. Piping is connected to 100mm sanitary main. Length(approximately): 20 meters | good | 10000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 14 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_4121 | Mt Albert North ET Capital Project 2 |  |  |  | 2019 |  |  | 0 |  | 0
4974 | 00024545 | MAN | BM | 2 | Storage Room Electric Unit Heater | PAC Room, Unit Heater, forced air Heating System, 5 kW; 240/1/60; by Oullet Model OAS05000T | good | 3000 |  |  |  | 1 | Mt Alberta Noth ET Foyer |  |  |  |  | 2015 |  | 25 |  |  |  | Building Mechanical | 40402 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Storage room electric unit heater to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_6348 |  |  |  | OPERATING |  | M00132 |  | 0 |  | 0
4985 | 00078317 | MAN | BM | 2 | Sump Pump | Submersible centrifugal sump pump | good | 1000 |  |  |  | 17166 | Mt Alberta Noth ET Valve Room |  |  |  |  | 2004 |  | 14 |  |  |  | Process Mechanical |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_6325 | Mt Albert North ET Capital Project 2 |  |  | OPERATING |  |  |  | 0 |  | 0
4976 | 00024548 | MAN | BM | 2 | Valve Room Dehumidifier | Dehumidifier, Air Handling System, by Noma; Installation year assumed to be 2016 | good | 300 |  |  |  | 17166 | Mt Alberta North Elevated Tank |  |  |  |  | 2016 |  | 26 |  |  |  | Building Mechanical |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Valve room dehumidifier to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_6321 |  |  |  | OPERATING |  | M00153 |  | 0 |  | 0
4978 | 00024542 | MAN | BM | 2 | Valve Room Electric Unit Heater | Valve Room, Electric Unit Heater, forced air Heating System, 5 kW; 240/1/60; by Oullet Model OAS05000T | good | 3000 |  |  |  | 17166 | Mt Alberta Noth ET Valve Room |  |  |  |  | 2004 |  | 14 |  |  |  | Building Mechanical |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_6335 | Mt Albert North ET Capital Project 2 |  |  | OPERATING |  | M00132 |  | 0 |  | 0
5033 |  | MAN | ES | 3 | Electrical Duct System and Conduit System | Conduit system inculding conduit, and underground duct for electrical services | good | 15000 |  |  |  | 17316 | Glenway RES Outside Sanitary Pumping Station |  |  |  |  | 2004 |  | 9 |  | Area 2N Linear Water & Wells | [5 empty] | OPERATING | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_4102 | Mt Albert North ET Capital Project 1 |  |  | W-WW | 2020 |  |  | 0 |  | 0
5019 |  | MAN | ES | 2 | Electrical Room Lighting | 1 linear fluorescent lighting fixture and 1 pendent mount | good | 1000 |  |  |  | 17166 | [5 empty] | 2004 |  | 9 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition.Asset to be replaced with LED fixtures rated for wet locations in next upgrade Asset to be replaced in the intermediate term. | 1000 |  | 0 |  | PXL_20201111_141749310 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  | Asset to be replaced with LED fixtures rated for wet locations in next upgrade | 1000 |  | 0
5029 |  | MAN | ES | 3 | Elevated Tank Grounding |  | good | 10000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 9 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_4100 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
5030 |  | MAN | ES | 3 | Elevated Tank Lightning Protection System | 1 lightning air protection terminal | good | 5000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 9 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_4082 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
5032 |  | MAN | ES | 3 | Elevated Tank Obstruction Light | Dual head lights | good | 3100 |  |  |  | 790900018 | [5 empty] | 2004 |  | 9 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_4082 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
5020 |  | MAN | ES | 3 | Elevated Tank Pedestal and Access Tube Lighting | 8 fixtures in total | good | 20000 |  |  |  | 17166 | [5 empty] | 2004 |  | 9 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | PXL_20201111_140004696 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
5014 |  | MAN | ES | 2 | Foyer Lighting Fixtures | 5 lighting fixtrues including 4 incandescent lighting fixtures and 1 emergency lighting fixture. | good | 3000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 9 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition.The incandescent lighting fixtures to be replaced with LED fixtures rated for wet locations in next upgrade Asset to be replaced in the intermediate term. | 2000 |  | 0 |  | PXL_20201111_140000689 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  | The incandescent lighting fixtures to be replaced with LED fixtures rated for wet locations in next upgrade | 2000 |  | 0
5015 | 00086712 | MAN | ES | 3 | Generator Transfer Switch Panel | Siemens Generator Transfer Switch Panel, EQ loadcentre, 120/240V, 30A | good | 5000 |  |  |  | 17169 | [5 empty] | 2004 |  | 9 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | PXL_20201111_141718982 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
4970 | 00024561 | MAN | ES | 3 | Inlet Piping Heat Tracing Control Panel | Heat Tracing and Montoring Control Panel for inlet piping | good | 5000 |  |  |  | 17169 | Mt Alberta Noth ET Electrical Control Room |  |  |  |  | 2004 |  | 9 |  |  |  | Electrical System | 15835 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | PXL_20201111_141759008 | Mt Albert North ET Capital Project 1 |  |  | OPERATING |  |  |  | 0 |  | 0
5028 | 00024561 | MAN | ES | 3 | Inlet Piping Heat Tracing System | Inlet Piping Heat Tracing System | good | 10000 |  |  |  | 17169 | [5 empty] | 2004 |  | 9 |  |  |  |  | 15835 |  |  |  | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_4103 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
4973 | 00024558 | MAN | ES | 3 | Lighting Panel | Siemens Panel Board P1; 120/240V, 1PH, 30CCT, a 100A main breaker is included. | good | 12000 |  |  |  | 17169 | Mt Alberta Noth ET Electrical Control Room |  |  |  |  | 2004 |  | 9 |  |  |  | Electrical System |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | PXL_20201111_142000666 | Mt Albert North ET Capital Project 1 |  |  | OPERATING |  | M00125 |  | 0 |  | 0
5021 |  | MAN | ES | 2 | Outdoor Lighting | 2 fixtures | good | 2400 |  |  |  | 790900018 | [5 empty] | 2004 |  | 9 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition.Asset to be replaced with LED fixtures rated for wet locations in next upgrade. Asset to be replaced in the intermediate term. | 2400 |  | 0 |  | PXL_20201111_134832486 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  | Asset to be replaced with LED fixtures rated for wet locations in next upgrade. | 2400 |  | 0
4961 | 00024560 | MAN | ES | 3 | Outlet Piping Heat Tracing Control Panel | Heat Tracing and Montoring Control Panel for outlet piping | good | 5000 |  |  |  | 17169 | Mt Alberta Noth ET Electrical Control Room |  |  |  |  | 2004 |  | 9 |  |  |  | Electrical System | 15837 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | PXL_20201111_141847648 | Mt Albert North ET Capital Project 1 |  |  | OPERATING |  |  |  | 0 |  | 0
5027 |  | MAN | ES | 3 | Outlet Piping Heat Tracing System | Outlet Piping Heat Tracing System | good | 10000 |  |  |  | 17169 | [5 empty] | 2004 |  | 9 |  |  |  |  | 15837 |  |  |  | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_4103 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
4995 | 00080565 | MAN | ES | 2 | Portable Generator | Portable Gasoline Generator, Manufacturer: Comet | good | 2000 |  |  |  | 790900018 | Mt Alberta North Elevated Tank |  |  |  |  | 2004 |  | 9 |  |  |  | Electrical System | EAAJ 1069727 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | PXL_20201111_142703597 | Mt Albert North ET Capital Project 1 |  |  | OPERATING |  | M00506 |  | 0 |  | 0
5016 |  | MAN | ES | 3 | Surge Protection Device | Surge Protection Device, PTX 160, 120/240V, 30A | good | 6000 |  |  |  | 17169 | [5 empty] | 2004 |  | 9 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | PXL_20201111_142137604 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
5017 |  | MAN | ES | 2 | Valve Room Lighting | 2 linear fluorescent lighting fixtures,1 pendent mount, and 2 emergency lighting fixtures. | good | 6000 |  |  |  | 17166 | [5 empty] | 2004 |  | 9 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition.The valve room lighting to be replaced with LED fixtures in next upgrade project. Asset to be replaced in the intermediate term. | 6000 |  | 0 |  | PXL_20201111_140025870 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  | The valve room lighting to be replaced with LED fixtures in next upgrade project. | 6000 |  | 0
4956 | 00025415 | MAN | HSS | 2 | Chlorine Residual Kit | Hach II Pocket Colorimeter, Chlorine Residual Kit | good | 700 |  |  |  | 17166 | Mt Alberta Noth ET Valve Room |  |  |  |  | 2004 |  | 6 |  |  |  | Health and Safety | 05080C035745 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | PXL_20201111_140445688 | Mt Albert North ET Capital Project 1 |  |  | OPERATING |  | M00482 |  | 0 |  | 0
5087 |  | MAN | HSS | 4 | Elevated Tank Anchor Point (Platform Level) |  | good | 2000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 6 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_4066 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
5088 |  | MAN | HSS | 4 | Elevated Tank Anchor Point (Roof Level) |  | good | 3000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 6 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_4091 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
5070 |  | MAN | HSS | 4 | Elevated Tank Davit Socket Base (Platform Level) |  | good | 4000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 6 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_4101 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
5071 |  | MAN | HSS | 4 | Elevated Tank Davit Socket Base (Roof Level) |  | good | 4000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 6 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_4093 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
5038 | 00078315 | MAN | HSS | 2 | Emergency Eyewash | Emergency Eyewash | good | 600 |  |  |  | 17166 | [5 empty] | 2004 |  | 6 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | PXL_20201111_140206405 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
5040 |  | MAN | HSS | 1 | Fire Extinguisher | 1 Fire Extinguisher | good | 300 |  |  |  | 17169 | [5 empty] | 2004 |  | 6 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | PXL_20201111_140246229 | Mt Albert North ET Capital Project 1 |  |  |  | 2019 |  |  | 0 |  | 0
5039 |  | MAN | HSS | 2 | Smoke Detectors | Smoke Detector (2) | good | 1000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 6 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | PXL_20201111_141747449 | Mt Albert North ET Capital Project 1 |  |  |  | 2019
4962 | 00024535 | MAN | PM | 3 | Elevated Tank Inlet Line Butterfly Valve 1 | 300mm butterfly vavle, manufacturer: Clow Kennedy | Minor surface corrosion | 3000 |  |  |  | 17166 | Mt Alberta Noth ET Valve Room |  |  |  |  | 2004 |  | 14 |  |  |  | Process Mechanical |  |  |  | W-WW | 3 | Minor surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_6257 | Mt Albert North ET Capital Project 2 |  |  | OPERATING |  | M00554 |  | 0 |  | 0
4969 | 00024534 | MAN | PM | 3 | Elevated Tank Inlet Line Butterfly Valve 2 | 300mm butterfly vavle, manufacturer: Clow Kennedy | Minor surface corrosion | 3000 |  |  |  | 17166 | Mt Alberta Noth ET Valve Room |  |  |  |  | 2004 |  | 14 |  |  |  | Process Mechanical |  |  |  | W-WW | 3 | Minor surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_6248 | Mt Albert North ET Capital Project 2 |  |  | OPERATING |  | M00554 |  | 0 |  | 0
4968 | 00024546 | MAN | PM | 4 | Elevated Tank Inlet Line Check Valve | 300mm check valve, manufacturer: Clow Kennedy | Minor surface corrosion | 5000 |  |  |  | 17166 | Mt Alberta Noth ET Valve Room |  |  |  |  | 2004 |  | 14 |  |  |  | Process Mechanical |  |  |  | W-WW | 3 | Minor surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_6260 | Mt Albert North ET Capital Project 2 |  |  | OPERATING |  | M00856 |  | 0 |  | 0
5042 | 691803567 | MAN | PM | 4 | Elevated Tank Inlet Line Piping | Diameter: 300mm, Length(portion in elevated tank): 30 meters | Good | 33000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 14 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_6273 | Mt Albert North ET Capital Project 2 |  |  |  | 0 |  |  | 0 |  | 0
4983 | 00024541 | MAN | PM | 3 | Elevated Tank Inlet/Outlet Line Butterfly Valve | 300mm butterfly vavle, manufacturer: Clow Kennedy | Minor surface corrosion | 3000 |  |  |  | 17166 | Mt Alberta Noth ET Valve Room |  |  |  |  | 2004 |  | 14 |  |  |  | Process Mechanical |  |  |  | W-WW | 3 | Minor surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_6266 | Mt Albert North ET Capital Project 2 |  |  | OPERATING |  | M00554 |  | 0 |  | 0
5013 | 691803565 | MAN | PM | 3 | Elevated Tank Inlet/Outline Gate Valve 1 | 300mm gate valve, installed in outdoor chamber | Good | 3000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 14 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_6422 | Mt Albert North ET Capital Project 2 |  |  |  | 0 |  |  | 0 |  | 0
5011 | 691803566 | MAN | PM | 3 | Elevated Tank Inlet/Outline Gate Valve 2 | 300mm gate valve, installed in outdoor chamber | Good | 3000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 14 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_6408 | Mt Albert North ET Capital Project 2 |  |  |  | 0 |  |  | 0 |  | 0
5012 | 691803567 | MAN | PM | 3 | Elevated Tank Inlet/Outline Gate Valve 3 | 300mm gate valve, installed in outdoor chamber | Good | 3000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 14 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_6385 | Mt Albert North ET Capital Project 2 |  |  |  | 0 |  |  | 0 |  | 0
5041 | 691803567 | MAN | PM | 5 | Elevated Tank Inlet/Outline Piping | Diameter: 300mm, Length(portion in elevated tank): 10 meters | Good | 11000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 14 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_6280 | Mt Albert North ET Capital Project 2 |  |  |  | 0 |  |  | 0 |  | 0
4965 | 00024537 | MAN | PM | 3 | Elevated Tank Outlet Line Butterfly Valve 1 | Outlet Control Isolation Butterfly valve, size: 300mm, manufacturer: Clow Kennedy | minor surface corrosion | 3000 |  |  |  | 17166 | Mt Alberta Noth ET Valve Room |  |  |  |  | 2004 |  | 14 |  |  |  | Process Mechanical |  |  |  | W-WW | 3 | Minor surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_6284 | Mt Albert North ET Capital Project 2 |  |  | OPERATING |  | M00554 |  | 0 |  | 0
4975 | 00024538 | MAN | PM | 3 | Elevated Tank Outlet Line Butterfly Valve 2 | Outlet Control Isolation Butterfly valve, size: 300mm, manufacturer: Clow Kennedy | Minor surface corrosion | 3000 |  |  |  | 17166 | Mt Alberta Noth ET Valve Room |  |  |  |  | 2004 |  | 14 |  |  |  | Process Mechanical |  |  |  | W-WW | 3 | Minor surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_6293 | Mt Albert North ET Capital Project 2 |  |  | OPERATING |  | M00554 |  | 0 |  | 0
4977 | 00024540 | MAN | PM | 3 | Elevated Tank Outlet Line Butterfly Valve 3 | Outlet Control Isolation Butterfly valve, size: 300mm, manufacturer: Clow Kennedy | good | 3000 |  |  |  | 17166 | Mt Alberta Noth ET Valve Room |  |  |  |  | 2004 |  | 14 |  |  |  | Process Mechanical |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_6305 | Mt Albert North ET Capital Project 2 |  |  | OPERATING |  | M00554 |  | 0 |  | 0
4963 | 00024547 | MAN | PM | 4 | Elevated Tank Outlet Line Flow Control Valve | 300 mm solenoid operated flow control valve, manufracturer: Singer Model S106 | Good | 12000 |  |  |  | 17166 | Mt Alberta Noth ET Valve Room |  |  |  |  | 2004 |  | 14 |  |  |  | Process Mechanical | 504-97 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_6313 | Mt Albert North ET Capital Project 2 |  |  | OPERATING |  | M00818 |  | 0 |  | 0
5043 | 691803567 | MAN | PM | 4 | Elevated Tank Outlet Line Piping | Diameter: 300mm, Length(portion in elevated tank): 39 meters | Good | 43000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 14 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_6298 | Mt Albert North ET Capital Project 2 |  |  |  | 0 |  |  | 0 |  | 0
4964 | 00024539 | MAN | PM | 3 | Elevated Tank Overflow Bypass Line Butterfly Valve 1 | 150mm butterfly valve, manufracturer: Clow Kennedy | Good | 2000 |  |  |  | 17166 | Mt Alberta Noth ET Valve Room |  |  |  |  | 2004 |  | 14 |  |  |  | Process Mechanical |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_6295 | Mt Albert North ET Capital Project 2 |  |  | OPERATING |  | M00554 |  | 0 |  | 0
4966 | 00024536 | MAN | PM | 3 | Elevated Tank Overflow Bypass Line Butterfly Valve 2 | 150mm butterfly valve, manufracturer: Clow Kennedy | good | 2000 |  |  |  | 17166 | Mt Alberta North Elevated Tank |  |  |  |  | 2004 |  | 14 |  |  |  | Process Mechanical |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_6244 | Mt Albert North ET Capital Project 2 |  |  | OPERATING |  | M00554 |  | 0 |  | 0
4967 | 00024544 | MAN | PM | 3 | Elevated Tank Overflow Bypass Line Butterfly Valve 3 | 150mm butterfly valve, manufracturer: Clow Kennedy | Minor surface corrosion | 2000 |  |  |  | 17166 | Mt Alberta Noth ET Valve Room |  |  |  |  | 2004 |  | 14 |  |  |  | Process Mechanical |  |  |  | W-WW | 3 | Minor surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_6280 | Mt Albert North ET Capital Project 2 |  |  | OPERATING |  | M00554 |  | 0 |  | 0
5045 | 691803567 | MAN | PM | 3 | Elevated Tank Overflow Bypass Line Piping | Diameter: 150mm, Length(portion in elevated tank): 5 meters | Good | 3000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 14 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_6253 | Mt Albert North ET Capital Project 2 |  |  |  | 0 |  |  | 0 |  | 0
5044 | 691803567 | MAN | PM | 4 | Elevated Tank Overflow Line Piping | Diameter: 300mm, Length(portion in elevated tank): 43 meters | Good | 47000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 14 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_4103 | Mt Albert North ET Capital Project 2 |  |  |  | 0 |  |  | 0 |  | 0
5116 |  | MAN | PM | 3 | Elevated Tank Roof Vent |  | good | 5000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 14 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_4089 | Mt Albert North ET Capital Project 2 |  |  |  | 0 |  |  | 0 |  | 0
5091 |  | MAN | SC | 4 | Electrical Room Composite Roof |  | Good | 10000 |  |  |  | 17169 | [5 empty] | 2004 |  | 44 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Electrical room composite roof to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_4106 |  |  |  |  | 0 |  |  | 0 |  | 0
5061 |  | MAN | SC | 4 | Electrical Room Masonry Blockwalls |  | good | 15000 |  |  |  | 17169 | [5 empty] | 2004 |  | 44 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Electrical room masonry blockwalls to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_4108 |  |  |  |  | 0 |  |  | 0 |  | 0
5063 |  | MAN | SC | 4 | Elevated Tank Aluminum Ladder (Ground to Platform) |  | good | 30000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 44 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Elevated tank aluminum ladder (ground to platform) to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_4103 |  |  |  |  | 0 |  |  | 0 |  | 0
5065 |  | MAN | SC | 4 | Elevated Tank Aluminum Ladder (Platform to Roof) | Platform to roof | Good | 20000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 44 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Elevated tank aluminum ladder (platform to roof) to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_4095 |  |  |  |  | 0 |  |  | 0 |  | 0
5086 |  | MAN | SC | 4 | Elevated Tank Aluminum Ladder (Platform to Tank Bottom Hatch) | Platform to tank hatch | Good | 2500 |  |  |  | 790900018 | [5 empty] | 2004 |  | 44 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Elevated tank aluminum ladder (platform to tank bottom hatch) to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_4065 |  |  |  |  | 0 |  |  | 0 |  | 0
5066 |  | MAN | SC | 4 | Elevated Tank Aluminum Ladder (Roof to Tank) | Roof to tank | poor | 20000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 44 | [8 empty] | 3 | Poor was observed. | Rail slide is bent was observed. |  | The asset was observed to be in fair condition. Elevated tank aluminum ladder (roof to tank) to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_4072 |  |  |  |  | 0 |  |  | 0 |  | 0 | rail slide is bent
5064 |  | MAN | SC | 3 | Elevated Tank Aluminum Platform |  | good | 50000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 44 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Elevated tank aluminum platform to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_4103 |  |  |  |  | 0 |  |  | 0 |  | 0
5056 |  | MAN | SC | 4 | Elevated Tank Concrete Structure |  | good | 900000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 44 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Elevated tank concrete structure to be replaced at the end of remaining service life. | 0 | 2030 | 0 |  | IMG_4103 |  | Mt Albert North ET Capital Project 1 |  |  | 0 |  |  | 0 |  | 0
5073 |  | MAN | SC | 3 | Elevated Tank Exterior Coating |  | good | 780000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 44 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Elevated tank exterior coating to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_4055 |  |  |  |  | 0 |  |  | 0 |  | 0
5084 |  | MAN | SC | 2 | Elevated Tank Inlet Pipe Support |  | good | 30000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 44 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Elevated tank inlet pipe support to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_4103 |  |  |  |  | 0 |  |  | 0 |  | 0
5074 |  | MAN | SC | 3 | Elevated Tank Interior Coating |  | good | 450000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 44 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Elevated tank interior coating to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_4072 |  |  |  |  | 0 |  |  | 0 |  | 0
5085 |  | MAN | SC | 2 | Elevated Tank Outlet Pipe Support |  | good | 30000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 44 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Elevated tank outlet pipe support to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_4103 |  |  |  |  | 0 |  |  | 0 |  | 0
5067 |  | MAN | SC | 3 | Elevated Tank Roof Access Hatch | To Roof | good | 10000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 44 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Elevated tank roof access hatch to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_4089 |  |  |  |  | 0 |  |  | 0 |  | 0
5069 |  | MAN | SC | 3 | Elevated Tank Roof Guardrail |  | good | 25000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 44 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Elevated tank roof guardrail to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_4087 |  |  |  |  | 0 |  |  | 0 |  | 0
5118 |  | MAN | SC | 3 | Elevated Tank Sacrificial Anode Cathodic Protection System | Elevated Tank Sacrificial Anode Cathodic Protection System |  | 30000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 44 | [8 empty] | 3 |  |  |  | The asset was assumed to be in fair condition. Elevated tank sacrificial anode cathodic protection system to be replaced at the end of remaining service life. | 0 |  | 0 | [6 empty] | 2019 |  |  | 0 |  | 0
5057 |  | MAN | SC | 5 | Elevated Tank Steel Tank |  | minor corrosion | 1300000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 44 | [8 empty] | 3 | Minor corrosion was observed. |  |  | The asset was observed to be in fair condition. Elevated tank steel tank to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_4055 |  |  |  |  | 0 |  |  | 0 |  | 0
5068 |  | MAN | SC | 3 | Elevated Tank Tank Access Hatch | To Tank | good | 10000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 44 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Elevated tank tank access hatch to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_4088 |  |  |  |  | 0 |  |  | 0 |  | 0
5072 |  | MAN | SC | 2 | Elevated Tank Tank Hatch (Access from Upper Platform) |  | good | 5000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 44 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Elevated tank tank hatch (access from upper platform) to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_4065 |  |  |  |  | 0 |  |  | 0 |  | 0
5059 |  | MAN | SC | 3 | Foyer Aluminum Guardrails |  | good | 3000 |  |  |  | 17168 | [5 empty] | 2004 |  | 44 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Foyer aluminum guardrails to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_4104 |  |  |  |  | 0 |  |  | 0 |  | 0
5058 |  | MAN | SC | 3 | Foyer Aluminum Staircase |  | good | 6000 |  |  |  | 17168 | [5 empty] | 2004 |  | 44 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Foyer aluminum staircase to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_4107 |  |  |  |  | 0 |  |  | 0 |  | 0
5092 |  | MAN | SC | 3 | Storage Room Composite Roof |  | Good | 5000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 44 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Storage room composite roof to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_4104 |  |  |  |  | 0 |  |  | 0 |  | 0
5062 |  | MAN | SC | 4 | Storage Room Masonry Blockwalls |  | good | 10000 |  |  |  | 1 | [5 empty] | 2004 |  | 44 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Storage room masonry blockwalls to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_4123 |  |  |  |  | 0 |  |  | 0 |  | 0
5090 |  | MAN | SC | 4 | Valve Room Composite Roof |  | Good | 20000 |  |  |  | 17166 | [5 empty] | 2004 |  | 44 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Valve room composite roof to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_4105 |  |  |  |  | 0 |  |  | 0 |  | 0
5060 |  | MAN | SC | 4 | Valve Room Masonry Blockwalls |  | good | 30000 |  |  |  | 17166 | [5 empty] | 2004 |  | 44 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Valve room masonry blockwalls to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_4113 |  |  |  |  | 0 |  |  | 0 |  | 0
4989 | 00078458 | MAN | SIC | 4 | Elevated Tank Remote OIT Panel | MTENTL | good | 30000 |  |  |  | 17166 | Mt Alberta Noth ET Valve Room |  |  |  |  | 2004 |  | 6 |  |  |  | Instrumentation and Control | KSA0868427 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | PXL_20201111_140549229 | Mt Albert North ET Capital Project 1 |  |  | OPERATING |  | M10189 |  | 0 |  | 0
4994 | 00078459 | MAN | SIC | 0 | Elevated Tank Remote OIT Panel Display and Computer | Advantech Computer | good | 5000 |  |  |  | 17166 | Mt Alberta Noth ET Valve Room |  |  |  |  | 2004 |  | 6 |  |  |  | Instrumentation and Control | AFC1000532 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | PXL_20201111_140549229 | Mt Albert North ET Capital Project 1 |  |  | OPERATING |  | M10189 |  | 0 |  | 0
4990 | 00078462 | MAN | SIC | 3 | Elevated Tank Control Panel UPS | Inside of Elevated Tank MTETNL PAC Panel | good | 3000 |  |  |  | 17169 | Mt Alberta Noth ET Electrical Control Room |  |  |  |  | 2004 |  | 6 |  |  |  | Instrumentation and Control | GH442A1091 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_6352 | Mt Albert North ET Capital Project 1 |  |  | OPERATING |  | M10181 |  | 0 |  | 0
5022 | 00042848 | MAN | SIC | 0 | Elevated Tank Flow Transmitter |  | good | 10000 |  |  |  | 17166 | [5 empty] | 2004 |  | 6 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | PXL_20201111_140503354 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
4993 | 00041442 | MAN | SIC | 3 | Elevated Tank Level Indicating Transmitter | MTETNL_TWR_LIT1 | good | 12000 |  |  |  | 790900018 | Mt Alberta North Elevated Tank |  |  |  |  | 2004 |  | 6 |  |  |  | Instrumentation and Control | E904901509C |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | PXL_20201111_140316939 | Mt Albert North ET Capital Project 1 |  |  | OPERATING |  | M00405 |  | 0 |  | 0
5035 | 00078460 | MAN | SIC | 4 | Elevated Tank MTETNL PAC Panel |  | good | 50000 |  |  |  | 17169 | [5 empty] | 2004 |  | 6 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_6352 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
4988 | 00078461 | MAN | SIC | 4 | Elevated Tank NAC Panel | Network Access Closet Panel, Xmtetnl1 | good | 60000 |  |  |  | 17169 | Mt Alberta Noth ET Electrical Control Room |  |  |  |  | 2004 |  | 6 |  |  |  | Instrumentation and Control | 14E-088/MTETNL_NAC |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | PXL_20201111_142225191 | Mt Albert North ET Capital Project 1 |  |  | OPERATING |  | 1002018 |  | 0 |  | 0
4952 | 00017764 | MAN | SIC | 3 | Elevated Tank Outlet Piping Chlorine Analyzer | MTETNL_TWR_AIT1 Free Residual Chlorine Analyzer | good | 15000 |  |  |  | 17166 | Mt Alberta Noth ET Valve Room |  |  |  |  | 2004 |  | 6 |  |  |  | Instrumentation and Control | 40300009396 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | PXL_20201111_140257952 | Mt Albert North ET Capital Project 1 |  |  | OPERATING |  | M00482 |  | 0 |  | 0
5025 | 00076067 | MAN | SIC | 0 | Elevated Tank Overflow Pipe Pressure Transmitter |  | good | 8500 |  |  |  | 17166 | [5 empty] | 2004 |  | 6 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | PXL_20201111_140526897 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
5026 |  | MAN | SIC | 3 | Elevated Tank Security System |  | good | 30000 |  |  |  | 17169 | [5 empty] | 2004 |  | 6 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | PXL_20201111_141948382 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
4991 | 00078396 | MAN | SIC | 3 | NAC Panel Network Ethernet Switch | inside Network Access Closet Panel | good | 5000 |  |  |  | 17169 | Mt Alberta Noth ET Electrical Control Room |  |  |  |  | 2004 |  | 6 |  |  |  | Instrumentation and Control | FOC1847Z2E7 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | PXL_20201111_142225191 | Mt Albert North ET Capital Project 1 |  |  | OPERATING |  | M01002 |  | 0 |  | 0
4992 | 00078463 | MAN | SIC | 3 | NAC Panel Network Radio | Inside NAC Panel | good | 5000 |  |  |  | 17169 | Mt Alberta Noth ET Electrical Control Room |  |  |  |  | 2004 |  | 6 |  |  |  | Instrumentation and Control | 0001966911 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | PXL_20201111_142225191 | Mt Albert North ET Capital Project 1 |  |  | OPERATING |  | M00455 |  | 0 |  | 0
4953 | 00017760 | MAN | SIC | 3 | Network Anthenna 1 | MTNTRAD103 Network Antenna & Cable | good | 10000 |  |  |  | 790900018 | Mt Alberta Noth ET Valve Room |  |  |  |  | 2004 |  | 6 |  |  |  | SCADA |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_4087 | Mt Albert North ET Capital Project 1 |  |  | OPERATING |  |  |  | 0 |  | 0
4954 | 00017761 | MAN | SIC | 0 | Network Anthenna 2 | MTNTRAD104 | good | 10000 |  |  |  | 790900018 | Mt Alberta Noth ET Valve Room |  |  |  |  | 2006 |  | 7 |  |  |  | SCADA |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_4084 | Mt Albert North ET Capital Project 1 |  |  | OPERATING |  |  |  | 0 |  | 0
4955 | 00017766 | MAN | SIC | 3 | Radio Modem | MTNTRAD101, Network, Radio Modem | good | 5000 |  |  |  | 790900018 | Mt Alberta Noth ET Valve Room |  |  |  |  | 2006 |  | 7 |  |  |  | SCADA | 1269550 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_4086 | Mt Albert North ET Capital Project 1 |  |  | OPERATING |  | M01018 |  | 0 |  | 0
4984 | 00078313 | MAN | SIC | 2 | Valve Room Low Temperature Switch | MTT2TSL101 | good | 1000 |  |  |  | 17166 | Mt Alberta Noth ET Valve Room |  |  |  |  | 2004 |  | 6 |  |  |  | Instrumentation and Control |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | PXL_20201111_140439546 | Mt Albert North ET Capital Project 1 |  |  | OPERATING |  | M00076 |  | 0 |  | 0
4999 |  | MAN | SW | 2 | Chainlink Fence | 1.8m high chainlink fence, with barbed wire on top. Approx. total length 180m | Barbed wire wasnot attached to fence along west side of site for approximately 30m. | 25000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 10 | [8 empty] | 3 | Barbed wire wasnot attached to fence along west side of site for approximately 30m was observed. | Fence mesh damaged at sw corner of site was observed. |  | The asset was observed to be in fair condition.Re-attach barbed wire to top of fence. Asset to be replaced in the intermediate term. | 1000 |  | 1000 |  | IMG_20201111_102312 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  | Re-attach barbed wire to top of fence. | 1000 | Install new mesh at location of damaged fence mesh. | 1000 | Fence mesh damaged at SW corner of site.
4997 |  | MAN | SW | 2 | Elevated Tank Ninth Line Access Gate | 6.0m wide double gate located on Ninth Line | Good. | 3000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 10 | [8 empty] | 3 | The asset was good. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_20201111_094635 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
4998 |  | MAN | SW | 1 | Elevated Tank Ridge Gate Cres Access Gate | 6.0m wide double gate for Ridge Gate crescent | Good | 3000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 10 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_20201111_102248 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
5009 |  | MAN | SW | 5 | Elevated Tank Watermain | 300mm watermain, approximately 65m in length |  | 71000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 2 | [8 empty] | 3 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the short term. | 0 |  | 0 |  |  | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
4982 | 00032809 | MAN | SW | 1 | Fire Hydrant | Fire Hydrant and valve | Hydrant valve box settled (and ground around) by approximately 0.5m | 10000 |  |  |  | 790900018 | Mt Alberta North Elevated Tank |  |  |  |  | 2004 |  | 10 |  |  |  | Siteworks |  |  |  | W-WW | 3 | Hydrant valve box settled (and ground around) by approximately 0.5m was observed. |  |  | The asset was observed to be in fair condition.Raise valve box to grade and regrade. Asset to be replaced in the intermediate term. | 1000 |  | 0 |  | IMG_20201111_094823 | Mt Albert North ET Capital Project 1 |  |  | OPERATING |  | M00100 | Raise valve box to grade and regrade. | 1000 |  | 0
5008 |  | MAN | SW | 4 | Overflow piping | 300mm, length: 16.0m |  | 15000 |  |  |  | 790900018 | [5 empty] | 2005 |  | 5 | [8 empty] | 3 |  |  |  | The asset was assumed to be in fair condition.Regrade area around pipe outlet to allow for above grade overflow outlet with grating on pipe. Place riprap at outlet. Asset to be replaced in the short term. | 10000 |  |  |  | IMG_20201111_100602 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  | Regrade area around pipe outlet to allow for above grade overflow outlet with grating on pipe. Place riprap at outlet. | 10000
5007 |  | MAN | SW | 2 | Pavement | Asphalt pavement (incl. granular base) within site, from Ninth line entrance to elevated tank entrance. Approx. 450m2 | Asphalt had cracking for entire length of driveway, with severe damage by elevated tank. | 35000 |  |  |  | 790900018 | [5 empty] | 2024 |  | 24 | [8 empty] | 3 | Asphalt had cracking for entire length of driveway, with severe damage by elevated tank was observed. | Damage of asphalt at entrance of site was observed. |  | The asset was observed to be in fair condition.Conduct pavement evaluation, and confirm if road resurfacing is sufficient or full reconstruction required. Pavement to be replaced at the end of remaining service life. | 15000 |  | 0 |  | IMG_20201111_100101 |  |  |  |  | 0 |  | Conduct pavement evaluation, and confirm if road resurfacing is sufficient or full reconstruction required. | 15000 |  | 0 | Damage of asphalt at entrance of site.
5010 |  | MAN | SW | 3 | Sanitary Sewer | 100mm sanitary sewer, approximately 22m in length |  | 17500 |  |  |  | 790900018 | [5 empty] | 2005 |  | 5 | [8 empty] | 3 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the short term. | 0 |  | 0 |  |  | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
5000 |  | MAN | SW | 1 | Soft Drainage | Soft surfaces throughout site, approximate area 1250m2. | Low spots around fire hydrant | 25000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 10 | [8 empty] | 3 | Low spots around fire hydrant was observed. | Damaged sod was observed at outlet of overflow pipe. |  | The asset was observed to be in fair condition.Regrade area around fire hydrant Asset to be replaced in the intermediate term. | 2500 |  | 7000 |  | IMG_20201111_102456 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  | Regrade area around fire hydrant | 2500 | Remove top soil and sod and place riprap at outlet of overflow pipe, ensure positive drainage towards property line and but away from adjacent property owner. | 7000 | Damaged sod at outlet of overflow pipe.
5081 |  | MAN | SW | 3 | Valve Chamber #1 Access Ladder |  | good | 1500 |  |  |  | 790900018 | [5 empty] | 2004 |  | 10 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_4135 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
5075 |  | MAN | SW | 3 | Valve Chamber #1 Manhole Frame and Cover |  | good | 1500 |  |  |  | 790900018 | [5 empty] | 2004 |  | 10 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_4056 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
5078 |  | MAN | SW | 3 | Valve Chamber #1 Precast Concrete Structure |  | good | 8000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 10 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_4135 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
5082 |  | MAN | SW | 3 | Valve Chamber #2 Access Ladder |  | good | 1500 |  |  |  | 790900018 | [5 empty] | 2004 |  | 10 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_4137 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
5076 |  | MAN | SW | 3 | Valve Chamber #2 Manhole Frame and Cover |  | good | 1500 |  |  |  | 790900018 | [5 empty] | 2004 |  | 10 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_4056 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
5079 |  | MAN | SW | 3 | Valve Chamber #2 Precast Concrete Structure |  | good | 8000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 10 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_4137 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
5083 |  | MAN | SW | 3 | Valve Chamber #3 Access Ladder |  | good | 1500 |  |  |  | 790900018 | [5 empty] | 2004 |  | 10 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_4139 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
5077 |  | MAN | SW | 3 | Valve Chamber #3 Manhole Frame and Cover |  | good | 1500 |  |  |  | 790900018 | [5 empty] | 2004 |  | 10 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_4056 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0
5080 |  | MAN | SW | 3 | Valve Chamber #3 Precast Concrete Structure |  | good | 8000 |  |  |  | 790900018 | [5 empty] | 2004 |  | 10 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | IMG_4139 | Mt Albert North ET Capital Project 1 |  |  |  | 0 |  |  | 0 |  | 0