## Sheet1
seqNum | facility | CategoryCode | assetName | LocationTag | Description | installYear | remainingESL | repCost | InspectionYear | CalcProcess | Process | building | inspectorName | assetTag | LocationORIGINAL | installationDate | condition | COF | defect1 | defect2 | defect3 | observations | RehabRepairCost | RehabRepairYear | RehabRepairCost2 | RehabRepairYear2 | photoName | repProjectName | rehabProjectName | rehab2ProjectName | LifeCycleCategory | TransmitterModel | TransducerModel | TransducerSerial | Status | rehabComment1 | rehabCost1 | rehabComment2 | rehabCost2 | defect1Input | defect2Input | defect3Input | InstType | InstMeva | ServiceArea | FacilityType | SerialNo | Parent | RotatingItem | Site | manufacturer
4464 | SPS1 | SW | Bollard No.1 | 1 |  | 1978 | 6 | 1000 | 0 | [7 empty] | 3 | 2 | Good was observed condition. |  |  | The asset was observed to be in fair condition.Re-paint the surface of the bollard Asset to be replaced in the intermediate term. | 100 |  |  |  | IMG_2011 | SPS1 Capital Project 1 | [7 empty] | Re-paint the surface of the bollard | 100 |  |  | Good condition
4465 | SPS1 | SW | Bollard No.2 | 1 |  | 1978 | 6 | 1000 | 0 | [7 empty] | 3 | 2 | Good was observed condition. |  |  | The asset was observed to be in fair condition.Re-paint the surface of the bollard Asset to be replaced in the intermediate term. | 100 |  |  |  | IMG_2012 | SPS1 Capital Project 1 | [7 empty] | Re-paint the surface of the bollard | 100 |  |  | Good condition
4466 | SPS1 | SW | Bollard No.3 | 1 |  | 1978 | 6 | 1000 | 0 | [7 empty] | 3 | 2 | Minor paint peeling was observed on the surface of the bollard. good condition was observed. |  |  | The asset was observed to be in fair condition.Re-paint the surface of the bollard Asset to be replaced in the intermediate term. | 100 |  |  |  | IMG_2013 | SPS1 Capital Project 1 | [7 empty] | Re-paint the surface of the bollard | 100 |  |  | Minor paint peeling was observed on the surface of the bollard. Good condition.
4467 | SPS1 | SW | Maintenace Hole No.1 | 1 |  | 1978 | 6 | 3600 | 0 | [7 empty] | 3 | 2 | Good was observed condition. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_2018 | SPS1 Capital Project 1 | [11 empty] | Good condition
4468 | SPS1 | SW | Swale | 1 | Approximately 30 m in length, 0.5 m in width, 0.5 m in depth | 1978 | 6 | 3600 | 0 | [7 empty] | 3 | 2 | Debris was observed in the swale. fair condition was observed. |  |  | The asset was observed to be in fair condition.Clear/excavate the debris from the swale. Asset to be replaced in the intermediate term. | 650 |  |  |  | IMG_2023 | SPS1 Capital Project 1 | [7 empty] | Clear/excavate the debris from the swale. | 650 |  |  | Debris was observed in the swale. Fair condition.
4469 | SPS1 | SW | Pavement | 1 | Approximately 160m2 of pavement on site | 1978 | 6 | 20800 | 0 | [7 empty] | 3 | 2 | Minor cracks observed on the pavement. good condition was observed. |  |  | The asset was observed to be in fair condition.Asphalt resurfacing Asset to be replaced in the intermediate term. | 13600 |  | 4900 |  | IMG_2038 | SPS1 Capital Project 1 | [7 empty] | Asphalt resurfacing | 13600 | Minor crack repairs/fills | 4900 | Minor cracks observed on the pavement. Good condition.
4489 | SPS1 | PM | Wastewaster pump #1 | 2 | Submersible, centrifugal wastewater pump, 7.5 kW, 1745 rpm, 575/3/60; by Flygt model 3127-960-20300; explosion proof enclosure (Class 1, Zone 1); | 1978 | 2 | 25000 | 0 | [7 empty] | 3 | 5 | Good was observed condition. | Scheduled maintenance and inspection was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_7132 | SPS1 Capital Project 1 | [11 empty] | Good condition | Scheduled Maintenance and Inspection
4490 | SPS1 | PM | Wastewaster pump #2 | 2 | Submersible, centrifugal wastewater pump, 7.5 kW, 1745 rpm, 575/3/60; by Flygt model 3127-960-20300; explosion proof enclosure (Class 1, Zone 1); | 1978 | 2 | 25000 | 0 | [7 empty] | 3 | 5 | Good was observed condition. | Scheduled maintenance and inspection was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_7131 | SPS1 Capital Project 1 | [11 empty] | Good condition | Scheduled Maintenance and Inspection
4499 | SPS1 | PM | Pump 1 Discharge Gate Valve | 2 | Gate valve, isolation of Pump #1 discharge line, 100 DIA, flanged, manual nut operator, valve box and extended stem. | 1978 | 2 | 3000 | 0 | [7 empty] | 3 | 4 | severely corroded was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_7111 | SPS1 Capital Project 1 | [11 empty] | severely corroded
4500 | SPS1 | PM | Pump 2 Discharge Gate Valve | 2 | Gate valve, isolation of Pump #2 discharge line, 100 DIA, flanged, manual nut operator, valve box and extended stem. | 1978 | 2 | 3000 | 0 | [7 empty] | 3 | 4 | Severely corroded was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_7111 | SPS1 Capital Project 1 | [11 empty] | severely corroded
4501 | SPS1 | PM | Pump 1 Discharge Check Valve | 2 | Check valve, in Pump #1 discharge line, 100 DIA, flanged | 1978 | 2 | 3500 | 0 | [7 empty] | 3 | 4 | Severely corroded was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_7110 | SPS1 Capital Project 1 | [11 empty] | severely corroded
4502 | SPS1 | PM | Pump 2 Discharge Check Valve | 2 | Check valve, in Pump #2 discharge line, 100 DIA, flanged | 1978 | 2 | 3500 | 0 | [7 empty] | 3 | 4 | Severely corroded was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_7110 | SPS1 Capital Project 1 | [11 empty] | severely corroded
4503 | SPS1 | PM | Overflow Pipe | 1 | 375 DIA Overflow pipe to Lake with manual gate to open-close; c/w 15 DIA steel bars at outlet to lake, | 1978 | 2 | 8000 | 0 | [7 empty] | 3 | 3 | Severely corroded and damaged steel bars at the outlet to late was observed. | No backflow preventing mechanism in place, replacement; a backflow preventing mechanism shall be installed at the wet well was observed. | Needs cleaning from deposits was observed. | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_7122 | SPS1 Capital Project 1 | [11 empty] | Severely corroded and damaged steel bars at the outlet to late | no backflow preventing mechanism in place, replacement; a backflow preventing mechanism shall be installed at the wet well. | needs cleaning from deposits
4504 | SPS1 | PM | Discharge Piping | 2 | Pump discharge pipes of 100 DIA and common 150 DIA force main in wet well | 1978 | 2 | 10000 | 0 | [7 empty] | 3 | 4 | severely corroded was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_0814 | SPS1 Capital Project 1 | [11 empty] | severely corroded
4505 | SPS1 | PM | Bypass gate valve | 1 | Pumping station bypass gate valve in MH, 100 DIA flanged c/w 100 DIA, 90 deg elbow (up) and blind flange. | 1978 | 2 | 5000 | 0 | [7 empty] | 3 | 3 | Mh was flooded to view the condition was observed. | Gravity drain c/w backflow preventing mechanism shall be installed from mh to the wet well was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_0882 | SPS1 Capital Project 1 | [11 empty] | MH was flooded to view the condition | Gravity drain c/w backflow preventing mechanism shall be installed from MH to the wet well.
4519 | SPS1 | PM | Gate Valve | 1 | Force main 150 DIA isolation gate valve, located in pass valve MH. | 1978 | 2 | 3000 | 0 | [7 empty] | 3 | 4 | Mh was flooded was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_0882 | SPS1 Capital Project 1 | [11 empty] | MH was flooded
4534 | SPS1 | SIC | PLC RPU601 | 3 | PLC | 2014 | 8 | 60000 | 0 | [7 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_4962 | SPS1 Capital Project 1 | [11 empty] | good
4535 | SPS1 | SIC | outdoor lights | 1 | 3 wall-pack outdoor lights | 2010 | 10 | 1500 | 0 | [7 empty] | 3 | 2 | To be cleaned from debris and spider webs was observed. | To be replaced with led fixtures in next upgrade was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_4956 | SPS1 Capital Project 1 | [11 empty] | to be cleaned from debris and spider webs | to be replaced with LED fixtures in next upgrade
4536 | SPS1 | SIC | Auto Dialer | 3 | Auto Dialer | 2014 | 8 | 6000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_4991 | SPS1 Capital Project 1 | [11 empty] | good
4537 | SPS1 | SIC | Level Transmitter | 3 | level transmitter | 2014 | 8 | 12000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5006 | SPS1 Capital Project 1 | [11 empty] | good
4538 | SPS1 | ES | standby generator | 3 | 15kw, standby generator | 1984 | 2 | 40000 | 0 | [7 empty] | 3 | 3 | The generator model is outdated and needs to be replaced within next decade was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_4960 | SPS1 Capital Project 1 | [11 empty] | the generator model is outdated and needs to be replaced within next decade
4539 | SPS1 | ES | Hydro Meter | 1 | Hydro Meter | 2014 | 18 | 5000 | 0 | [7 empty] | 3 | 3 | To be cleaned from debris and spider webs was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term. |  |  |  |  | IMG_4955 | SPS1 Capital Project 2 | [11 empty] | to be cleaned from debris and spider webs
4540 | SPS1 | ES | outdoor lights | 3 | 3 wall-packs outdoor lights | 2000 | 10 | 1500 | 0 | [7 empty] | 3 | 2 | To be cleaned from debris and spider webs was observed. | To be replaced with leds in next upgrade was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_4956 | SPS1 Capital Project 1 | [11 empty] | to be cleaned from debris and spider webs | to be replaced with LEDs in next upgrade
4541 | SPS1 | ES | Exit sign | 3 | Exit sign | 2014 | 18 | 500 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. |  |  |  |  | IMG_4965 | SPS1 Capital Project 2 | [11 empty] | good
4542 | SPS1 | ES | Automatic Transfer Switch Panel | 3 | 600V, 60A, Automatic Transfer Switch Panel | 1979 | 6 | 30000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_4966 | SPS1 Capital Project 1 | [11 empty] | good
4543 | SPS1 | ES | 600V distribution panel | 3 | 600V, 100A distribution panel | 1979 | 6 | 14000 | 0 | [7 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_4971 | SPS1 Capital Project 1 | [11 empty] | good
4544 | SPS1 | ES | Main Breaker | 3 | 600V, 100A Main Breaker | 1979 | 6 | 10000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_4979 | SPS1 Capital Project 1 | [11 empty] | good
4545 | SPS1 | ES | Pump Control Panel | 3 | Pump Control Panel | 1979 | 6 | 21000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_4982 | SPS1 Capital Project 1 | [11 empty] | good
4546 | SPS1 | ES | Lighting Transformer | 3 | 600-240V, 5KVA Lighting Transformer | 1979 | 6 | 8000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_4989 | SPS1 Capital Project 1 | [11 empty] | good
4547 | SPS1 | ES | Lighting Panel | 3 | 240V, 100A, 12CCT Lighting Panel | 1979 | 6 | 5000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_4992 | SPS1 Capital Project 1 | [11 empty] | good
4548 | SPS1 | ES | Generator Room Lighting | 3 | 3 linear fluroscent fixtures | 1979 | 6 | 1200 | 0 | [7 empty] | 3 | 2 | To be replaced with leds in next upgrade was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_4998 | SPS1 Capital Project 1 | [11 empty] | to be replaced with LEDs in next upgrade
4568 | SPS1 | SIC | Temperature Switch | 3 | temperature switch | 1987 | 6 | 1500 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5010 | SPS1 Capital Project 1 | [11 empty] | good
4577 | SPS1 | SIC | Antenna | 1 | Antenna | 2014 | 8 | 8000 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_4957 | SPS1 Capital Project 1 | [11 empty] | good
4623 | SPS1 | BM | Unit Heater | 3 | heater, stelpro, SHU0563CT, , 5KW, 600V | 2002 | 11 | 3000 | 0 | [7 empty] | 3 | 2 | Cracking in mortar was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term. |  |  |  |  | IMG_6042 | SPS1 Capital Project 2 | [11 empty] | cracking in mortar
4624 | SPS1 | BM | Exhaust Fan | 3 | exhaust fan, greenheck, SDE-12-24-D, 789693, 1/20HP | 1984 | 6 | 2000 | 0 | [7 empty] | 3 | 2 | Fan was still operational but is already at the end of its life expectancy was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_6073 | SPS1 Capital Project 1 | [11 empty] | Fan was still operational but is already at the end of its life expectancy
4625 | SPS1 | BM | Intake Damper | 3 | motorized damper | 1984 | 2 | 2000 | 0 | [7 empty] | 3 | 3 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_6062 | SPS1 Capital Project 1
4626 | SPS1 | BM | Diesel Fuel System | 3 | fuel tank and fuel lines | 2007 | 16 | 20000 | 0 | [7 empty] | 3 | 2 | It was noted on site that the diesel fuel system is not up to current tssa regulations and will need to be upgraded in the future. ab inspection report provided detailed deficiency list was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term. |  |  |  |  | IMG_6054 | SPS1 Capital Project 2 | [11 empty] | It was noted on site that the diesel fuel system is not up to current TSSA regulations and will need to be upgraded in the future. AB inspection report provided detailed deficiency list.
4627 | SPS1 | BM | Sink Eyewash | 3 | eyewash | 2000 | 9 | 1000 | 0 | [7 empty] | 3 | 2 | Emergency eyewashes are required to provide tepid water. no water heater was installed. no instantaneous heater would be required was observed. | Eyewash sink combo looked to be in good condition was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 3000 |  |  |  | IMG_6075 | SPS1 Capital Project 1 | [8 empty] | 3000 |  |  | Emergency eyewashes are required to provide tepid water. No water heater was installed. No instantaneous heater would be required. | Eyewash sink combo looked to be in good condition.
4628 | SPS1 | BM | Backflow preventer | 3 | backflow, Conbraco, , 1" | 2010 | 19 | 2500 | 0 | [7 empty] | 3 | 2 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the long term. |  |  |  |  | IMG_6081 | SPS1 Capital Project 2
4634 | SPS1 | BM | Generator Exhaust | 3 | ductwork and dampers | 1984 | 2 | 7500 | 0 | [7 empty] | 3 | 3 | Exhaust system to be replaced with generator replacement was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_6090 | SPS1 Capital Project 1 | [11 empty] | Exhaust system to be replaced with generator replacement.
4660 | SPS1 | AC | Generator Building Exterior Brick Veneer | 3 |  | 1987 | 6 | 10000 | 0 | [7 empty] | 3 | 1 | Step cracking in mortar typical was observed. | Grafitti noted was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_7142 | SPS1 Capital Project 1 | [11 empty] | step cracking in mortar typical | grafitti noted
4661 | SPS1 | AC | Generator Building Exterior Access Door | 3 |  | 1987 | 6 | 3500 | 0 | [7 empty] | 3 | 1 | Weathered paint was observed on exterior. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_7142 | SPS1 Capital Project 1 | [11 empty] | weathered paint on exterior
4662 | SPS1 | AC | Generator Building Roofing System | 3 |  | 1987 | 6 | 5000 | 0 | [7 empty] | 3 | 2 | Vegetation on roof was observed. | Bubbling paint around roof drain pipe penetration may be due to roof leakage was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_7147 | SPS1 Capital Project 1 | [11 empty] | vegetation on roof | bubbling paint around roof drain pipe penetration may be due to roof leakage
4663 | SPS1 | AC | Generator Building Wall and Ceiling Paint | 3 |  | 1987 | 6 | 3000 | 0 | [7 empty] | 3 | 1 | Bubbling at roof drain pipe penetration was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_7152 | SPS1 Capital Project 1 | [11 empty] | bubbling at roof drain pipe penetration
4664 | SPS1 | SC | Generator Building Concrete Foundation | 3 |  | 1987 | 26 | 30000 | 0 | [7 empty] | 3 | 4 |  |  |  | The asset was observed to be in fair condition. Provisions for structural repairs. Asset to be replaced at the end of remaining service life. |  | 2023 |  | 2038 |  |  | SPS1 Capital Project 1 | SPS1 Capital Project 2 | [9 empty] | fair
4665 | SPS1 | SC | Generator Building Concrete Floor Slab | 3 |  | 1987 | 26 | 8000 | 0 | [7 empty] | 3 | 4 |  |  |  | The asset was observed to be in fair condition. Provisions for structural repairs. Asset to be replaced at the end of remaining service life. |  | 2023 |  | 2038 | IMG_7151 |  | SPS1 Capital Project 1 | SPS1 Capital Project 2 | [9 empty] | fair
4666 | SPS1 | SC | Generator Building Masonry Blockwall | 3 |  | 1987 | 26 | 15000 | 0 | [7 empty] | 3 | 4 |  |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7152 | [12 empty] | fair
4667 | SPS1 | SC | Generator Building Concrete Roof Slab | 3 |  | 1987 | 26 | 10000 | 0 | [7 empty] | 3 | 3 |  |  |  | The asset was observed to be in fair condition. Provisions for structural repairs. Asset to be replaced at the end of remaining service life. |  | 2027 |  | 2038 | IMG_7152 |  | SPS1 Capital Project 1 | SPS1 Capital Project 2 | [9 empty] | fair
4668 | SPS1 | SC | Wet Well Precast Concrete Structure | 2 |  | 1987 | 26 | 130000 | 0 | [7 empty] | 3 | 4 | Concrete parging spall at precast joints, rust spots typical was observed. | Pump not flat on floor due to benching was observed. |  | The asset was observed to be in fair condition. Provisions for structural repairs. Asset to be replaced at the end of remaining service life. |  | 2023 |  | 2038 | IMG_7150 |  | SPS1 Capital Project 1 | SPS1 Capital Project 2 | [9 empty] | concrete parging spall at precast joints, rust spots typical | pump not flat on floor due to benching
4669 | SPS1 | SC | Wet Well Aluminum Platform | 2 |  | 1987 | 26 | 6000 | 0 | [7 empty] | 3 | 3 | Guardrails do not meet current obc was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7150 | [12 empty] | guardrails do not meet current OBC
4670 | SPS1 | SC | Wet Well Access Ladder | 2 | Exterior to platform | 1987 | 26 | 5000 | 0 | [7 empty] | 3 | 3 |  |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7123 | [12 empty] | fair
4671 | SPS1 | SC | Wet Well Access Ladder | 2 | Platform to base | 1987 | 26 | 5000 | 0 | [7 empty] | 3 | 3 |  |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7124 | [12 empty] | fair
4672 | SPS1 | SC | Wet Well Access Hatch | 2 |  | 1987 | 26 | 5000 | 0 | [7 empty] | 3 | 3 |  |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7160 | [12 empty] | fair
4673 | SPS1 | SC | Wet Well Pump Hatch | 2 |  | 1987 | 26 | 5000 | 0 | [7 empty] | 3 | 3 | Missing was observed safety grating. |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7159 | [12 empty] | missing safety grating
4674 | SPS1 | SC | Wet Well Pump Hatch | 2 |  | 1987 | 26 | 5000 | 0 | [7 empty] | 3 | 3 | Missing was observed safety grating. |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7159 | [12 empty] | missing safety grating
4675 | SPS1 | SC | Wet Well Davit Base Socket | 2 |  | 1987 | 26 | 5000 | 0 | [7 empty] | 3 | 2 |  |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7160 | [12 empty] | fair
4676 | SPS1 | SC | Wet Well Davit Base Socket | 2 |  | 1987 | 26 | 5000 | 0 | [7 empty] | 3 | 2 |  |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7161 | [12 empty] | fair