## Sheet1
seqNum | CategoryCode | assetTag | assetName | installYear | COF | repCost | photoName | facility | Description | Process | building | inspectorName | LocationTag | LocationORIGINAL | manufacturer | TransmitterModel | TransducerModel | TransducerSerial | InstMeva | installationDate | remainingESL | InstType | ServiceArea | FacilityType | LifeCycleCategory | SerialNo | Parent | RotatingItem | Site | condition | defect1 | defect2 | defect3 | observations | RehabRepairCost | RehabRepairYear | RehabRepairCost2 | RehabRepairYear2 | repProjectName | rehabProjectName | rehab2ProjectName | Status | InspectionYear | rehabComment1 | rehabCost1 | rehabComment2 | rehabCost2 | defect1Input | defect2Input | defect3Input
5551 | AC |  | Chemical Entry Access Door (Single) | 1984 | 1 | 3500 | IMG_7060 | KWPH |  |  |  |  | 00016088 | [7 empty] | 6 | [8 empty] | 3 | Corrosion was observed at bottom of door frame. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | corrosion at bottom of door frame
5562 | AC |  | Chemical Entry Room Ceiling Paint | 1984 | 1 | 500 | IMG_7062 | KWPH |  |  |  |  | 00016088 | [7 empty] | 6 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | good
5549 | AC |  | Chemical Entry Room Protective Floor Coating | 1984 | 1 | 1000 | IMG_7062 | KWPH |  |  |  |  | 00016088 | [7 empty] | 6 | [8 empty] | 3 | The asset was failed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | failed
5552 | AC |  | Chemical Room Access Door (Single) | 1984 | 1 | 3500 | IMG_7062 | KWPH |  |  |  |  | 00016089 | [7 empty] | 6 | [8 empty] | 3 | Worn paint at bottom was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | worn paint at bottom
5561 | AC |  | Chemical Room Protective Floor Coating | 1984 | 1 | 2000 | IMG_7064 | KWPH |  |  |  |  | 00016089 | [7 empty] | 6 | [8 empty] | 3 | The asset was failed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | failed
5550 | AC |  | Chemical Storage Ceiling Paint | 1984 | 1 | 700 | IMG_7065 | KWPH |  |  |  |  | 00016089 | [7 empty] | 6 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | good
5564 | AC |  | Chlorination Building Exterior Brick Veneer | 1984 | 1 | 10000 | IMG_7052 | KWPH |  |  |  |  | 00006881 | [7 empty] | 6 | [8 empty] | 3 | Localized spalling/erosion at bottom was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | localized spalling/erosion at bottom
5513 | AC | 00011176 | Chlorination Building Louvre Grilles | 1984 | 1 | 1500 | IMG_1321 | KWPH | two (2) in total |  |  |  | 00006881 | West Park Heights Reservoir | [6 empty] | 6 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | good
5512 | AC | 00011174 | Chlorination Building Roofing System | 2014 | 2 | 8000 | IMG_7046 | KWPH |  |  |  |  | 00016086 | West Park Heights Reservoir | [6 empty] | 8 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | good
5565 | AC |  | Electrical Room Access Door (Single) | 1984 | 1 | 3500 | IMG_7053 | KWPH |  |  |  |  | 00016090 | [7 empty] | 6 | [8 empty] | 3 | Corrosion was observed on kick plate at bottom. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | corrosion on kick plate at bottom
5563 | AC |  | Electrical Room Ceiling Paint | 1984 | 1 | 500 | IMG_7055 | KWPH |  |  |  |  | 00016090 | [7 empty] | 6 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | good
5548 | AC |  | Electrical Room Protective Floor Coating | 1984 | 1 | 1000 | IMG_7056 | KWPH |  |  |  |  | 00016090 | [7 empty] | 6 | [8 empty] | 3 | The asset was failed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | failed
5176 | BM | 00004238 | Chemical Entry Room Electric Heater | 2014 | 2 | 1000 | IMG_0477 | KWPH | wall mount convection Heater, by Stelpro, 1 kW, 120/1/60 |  |  |  | 00016088 | West Park Heights Res Chemical Entry Room | M00037 | [5 empty] | 23 |  | Area 3 Water Treatment |  | Building Mechanical |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5177 | BM | 00004239 | Chemical Entry Room Exhaust Fan | 1984 | 2 | 5000 | IMG_0469 | KWPH | Greenheck Model DSQ-100-B-QD; 1/6hp. 115VAC/1/60, 1140 rpm |  |  |  | 00016088 | West Park Heights Res Chemical Storage Room | M00069 | [5 empty] | 6 |  | Area 3 Water Treatment |  | Building Mechanical | 85F04708 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5178 | BM | 00004240 | Chemical Entry Room Motorized Damper | 1984 | 2 | 2000 | IMG_0470 | KWPH | Damper, c/w Honeywell actuator; 120/1/60; |  |  |  | 00016088 | West Park Heights Res Chemical Storage Room | M00076 | [5 empty] | 6 |  | Area 3 Water Treatment |  | Building Mechanical |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5166 | BM | 00004227 | Chemical Room Exhaust Fan | 1984 | 2 | 5000 | IMG_0532 | KWPH | Greenheck Model DSQ-80-DGF-QD; 1550rpm. |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room | M00069 | [5 empty] | 6 |  | Area 3 Water Treatment |  | Building Mechanical | 85E01526 |  |  | W-WW | 3 | Minor surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | Minor surface corrosion
5167 | BM | 00004228 | Chemical Room Motorized Damper | 1984 | 2 | 3000 | IMG_0524 | KWPH | Damper, c/w Honeywell actuator; 120/1/60; |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room | [6 empty] | 6 |  | Area 3 Water Treatment |  | Building Mechanical |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5165 | BM | 00004226 | Chemical Room Unit Heater | 2014 | 2 | 3000 | IMG_0519 | KWPH | wall mount Unit Heater, 3.6 kW, 208/1/60; Ouellet Model OCC4800AM-MO-TB6/CCG4800AM-MO-TB6, the heater appear to be new |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room | M00037 | [5 empty] | 23 |  | Area 3 Water Treatment |  | Building Mechanical |  |  |  | W-WW | 1 | Very good was observed. |  |  | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  |  |  |  | OPERATING | 0 |  | 0 |  | 0 | very good
5247 | BM | 00055015 | Valve Chamber Air Supply ductwork | 2014 | 2 | 1500 | IMG_0554 | KWPH | ducting system: 150DIA PVC c/w thermal insulation in jacket |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | [6 empty] | 23 |  | Area 3 Water Treatment | [5 empty] | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5248 | BM | 00055016 | Valve Chamber Air Supply Fan | 2014 | 2 | 3500 | IMG_0642 | KWPH | Twin City Model DSI-120AAL; 115/1/60; 1/8hp, ODP enclosure |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | [6 empty] | 23 |  | Area 3 Water Treatment |  |  | K12-000000078996 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5190 | BM | 00055017 | Valve Chamber Dehumidifier | 2014 | 2 | 5000 | IMG_0602 | KWPH | Manufacturer: Ebac Inductrial Products Ltd. model 10264CS-US, capacity 17 PPD; 120/1/60; 350 W; built-in controls |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | [6 empty] | 23 |  | Area 3 Water Treatment |  | Building Mechanical | 251000341 |  |  | W-WW | 3 | Moderate corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  |  |  |  | OPERATING | 0 |  | 0 |  | 0 | Moderate corrosion
5612 | BM |  | Valve Chamber Gooseneck Vent | 1984 | 1 | 1000 | IMG_1312 | KWPH |  |  |  |  | 00016091 | [7 empty] | 6 | [8 empty] | 3 | Minor surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | minor surface corrosion
5189 | BM | 00004251 | Valve Chamber Sump Pump | 1984 | 2 | 3000 | IMG_0606 | KWPH | Submersible Centrifugal Pump with associated piping, 120/1/60 |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | [6 empty] | 6 |  | Area 3 Water Treatment |  | Process Mechanical |  |  |  | W-WW | 4 | Severe corrosion was observed. |  |  | The asset was observed to be in poor condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | Severe corrosion
5192 | BM | 00004254 | Valve Chamber Unit heater | 2014 | 2 | 1000 | IMG_0594 | KWPH | Heating System, Convection Heater, wall mount, by Ouellet |  |  |  | 00016091 | West Park Heights Res Control Room | M00037 | [5 empty] | 23 |  | Area 3 Water Treatment |  | Building Mechanical |  |  |  | W-WW | 3 | Minor corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  |  |  |  | OPERATING | 0 |  | 0 |  | 0 | Minor corrosion
5200 | ES | 00006900 | Chlorination Building Emergency Lights | 2002 | 2 | 5000 | IMG_4724 | KWPH | 2 units with battery packs. |  |  |  | 00016086 | West Park Heights Reservoir | M00606 | [5 empty] | 12 |  | Area 3 Water Treatment | W - Storage Reservoir | Electrical System |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 2 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5609 | ES |  | Chlorination Building Indoor Lighting Fixtures | 2002 | 2 | 9000 | IMG_4717 | KWPH | 6 fluroscent fixtures |  |  |  | 00016086 | [7 empty] | 12 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | good
5608 | ES |  | Chlorination Building Outdoor Light Fixture | 2002 | 2 | 1000 | IMG_4698 | KWPH | One (1) in total. Installation year assumed to be 2010. |  |  |  | 00016086 | [7 empty] | 12 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | good
5196 | ES | 00006894 | Chlorine Booster Pump 1 Disconnect Switch | 2002 | 2 | 5000 | img_1302 | KWPH |  |  |  |  | 00016090 | West Park Heights Res Control Room | M00571 | [5 empty] | 12 |  | Area 3 Water Treatment |  | Electrical System |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 2 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5197 | ES | 00006895 | Chlorine Booster Pump 2 Disconnect Switch | 2002 | 2 | 5000 | IMG_1304 | KWPH |  |  |  |  | 00016090 | West Park Heights Res Control Room | M00311 | [5 empty] | 12 |  | Area 3 Water Treatment |  | Electrical System |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 2 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5194 | ES | 00006892 | Enclosed Switch | 2002 | 3 | 6000 | IMG_1300 | KWPH | 125/250V, 100A |  |  |  | 00016090 | West Park Heights Res Control Room | M00129 | [5 empty] | 12 |  | Area 3 Water Treatment |  | Electrical System | T3 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 2 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5193 | ES | 00006891 | Generator Panel | 2002 | 3 | 12000 | img_1295 | KWPH | 24 Circuits |  |  |  | 00016090 | West Park Heights Res Control Room | M00059 | [5 empty] | 12 |  | Area 3 Water Treatment |  | Electrical System | GP3P60-20 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 2 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5195 | ES | 00006893 | Panel Board LP A | 2002 | 3 | 20000 | img_1301 | KWPH |  |  |  |  | 00016090 | West Park Heights Res Control Room | M00129 | [5 empty] | 12 |  | Area 3 Water Treatment |  | Electrical System | T2 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 2 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5261 | ES | 00055029 | Panel Board LP B | 2014 | 3 | 15000 | IMG_4759 | KWPH | LP B, Panel Board, Lighting Panel |  |  |  | 00016090 | West Park Heights Res Control Room | [6 empty] | 18 |  | Area 3 Water Treatment | [5 empty] | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 2 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5613 | ES |  | Valve Chamber Indoor Lighting Fixtures | 2002 | 2 | 6000 | IMG_7076 | KWPH | 4 fluroscent fixtures |  |  |  | 00016091 | [7 empty] | 12 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | good
5245 | HSS | 00044422 | Battery Acid Spill Containment | 2020 | 2 | 100 | img_1297 | KWPH |  |  |  |  | 00006881 | West Park Heights Reservoir | M10266 | [5 empty] | 14 |  | Area 3 Water Treatment | W - Storage Reservoir | Health and Safety |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 2 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5618 | HSS |  | Chlorine Room Smoke Detector | 2014 | 1 | 0 | IMG_1271 | KWPH |  |  |  |  | 00016089 | [7 empty] | 8 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | good
5242 | HSS | 00024557 | Eyewash Station | 2014 | 3 | 600 | IMG_4725 | KWPH |  |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room | M00191 | [5 empty] | 8 |  | Area 3 Water Treatment |  | Health and Safety |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5623 | HSS |  | Fire Extinguisher | 2020 | 1 | 300 | img_1234 | KWPH | Total of 1 |  |  |  | 00016086 | [7 empty] | 14 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | good
5621 | HSS |  | First Aid Kit | 2020 | 1 | 500 | IMG_1280 | KWPH |  |  |  |  | 00016089 | [7 empty] | 14 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | good
5475 | PM |  | Chamber No.1 Watermain Air Release Valve | 2008 | 2 | 3500 | IMG_0744 | KWPH | 50 DIA Combination Air Relief/ Vacuum Valve c/w isolation ball valve, by ARI model D-040-C2 |  |  |  | 00016092 | [7 empty] | 17 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | Good
5472 | PM |  | Chamber No.1 Watermain Butterfly Valve | 2008 | 3 | 20000 | IMG_0686 | KWPH | Diameter: 750mm, with AWWA square operator nut and extension stem |  |  |  | 00016092 | [7 empty] | 17 | [8 empty] | 3 | Minor surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | Minor surface corrosion
5469 | PM |  | Chamber No.2 Watermain Air Release Valve | 2008 | 3 | 3500 | IMG_0730 | KWPH | 50 DIA Combination Air Relief/ Vacuum Valve c/w isolation ball valve, by ARI model D-040-C2 | [11 empty] | 17 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | good
5617 | PM |  | Chamber No.2 Watermain Butterfly Valve 1 | 2008 | 3 | 20000 | IMG_0726 | KWPH | Diameter: 750mm, with AWWA square operator nut and extension stem |  |  |  | 00016092 | [7 empty] | 17 | [8 empty] | 3 | Minor surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | Minor surface corrosion
5471 | PM |  | Chamber No.2 Watermain Butterfly Valve 2 | 2008 | 3 | 20000 | IMG_0725 | KWPH | Diameter: 750mm, with AWWA square operator nut and extension stem | [11 empty] | 17 | [8 empty] | 3 | Minor surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | Minor surface corrosion
5470 | PM |  | Chamber No.2 Watermain Butterfly Valve 3 | 2008 | 3 | 20000 | IMG_0724 | KWPH | Diameter: 750mm, with AWWA square operator nut and extension stem | [11 empty] | 17 | [8 empty] | 3 | Minor surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | minor surface corrosion
5474 | PM |  | Chamber No.2 Watermain Drain Gate Valve 1 | 2008 | 2 | 1500 | IMG_0725 | KWPH | Diameter: 150mm, with 50 mm square operating nut and extension stem |  |  |  | 00016092 | [7 empty] | 17 | [8 empty] | 3 | Minor surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | Minor surface corrosion
5473 | PM |  | Chamber No.2 Watermain Drain Gate Valve 2 | 2008 | 2 | 1500 | IMG_0724 | KWPH | Diameter: 150mm, with 50 mm square operating nut and extension stem |  |  |  | 00016092 | [7 empty] | 17 | [8 empty] | 3 | Minor surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | minor surface corrosion
5170 | PM | 00017994 | Chlorination System 2 | 2002 | 4 | 45000 | IMG_0503 | KWPH | US Filter -Wallce & Tiernan, model V10k |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room | M00899 | [5 empty] | 11 |  | Area 3 Water Treatment |  | Process Mechanical | 234300009501-001887 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 2 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5168 | PM | 00017993 | Chlorination System 1 | 2002 | 4 | 45000 | IMG_0493 | KWPH | US Filter -Wallce & Tiernan, model V10k |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room | M00899 | [5 empty] | 11 |  | Area 3 Water Treatment |  | Process Mechanical | 234300009501-001891 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 2 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5184 | PM | 00004246 | Chlorine Booster Pump 1 | 2002 | 3 | 7500 | IMG_0653 | KWPH | Grundfos Model A96083903P117420003, 15.41 gpm at 90.6 ft, 0.75hp, 3439 rpm; 240VAC/1/60 |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | M00951 | [5 empty] | 11 |  | Area 3 Water Treatment |  | Process Mechanical | 0002 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 2 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5185 | PM | 00004247 | Chlorine Booster Pump 2 | 2002 | 3 | 7500 | IMG_0658 | KWPH | Grundfos Model A96083903P117420002, 15.41 gpm at 90.6 ft, 0.75hp, 3439 rpm |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | M00951 | [5 empty] | 11 |  | Area 3 Water Treatment |  | Process Mechanical | 0003 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 2 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5616 | PM | 00004246 | Chlorine Booster Pump Piping System | 2002 | 3 | 3000 | IMG_0653 | KWPH |  |  |  |  | 00016091 | [7 empty] | 11 |  |  |  |  | 0002 |  |  |  | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | good
5223 | PM | 00017056 | Chlorine Injection System Tubing System | 2002 | 3 | 3000 | IMG_0618 | KWPH | Chlorine system tubing system from valve chamber to chlorine room. |  |  |  | 00016086 | West Park Heights Res Tank | [6 empty] | 11 |  | Area 3 Water Treatment |  | Process Mechanical |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 2 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5466 | PM |  | Drain Chamber Drain Line Butterfly Valve | 1984 | 2 | 8000 | IMG_0417 | KWPH | Diameter: 300mm |  |  |  | 00016086 | [7 empty] | 6 | [8 empty] | 3 | Surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | surface corrosion
5467 | PM |  | Drain Chamber Overflow Line Flap Gate | 1984 | 2 | 6000 | IMG_0417 | KWPH | Diameter: 450mm |  |  |  | 00016092 | [7 empty] | 6 | [8 empty] | 3 | Surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | surface corrosion
5268 | PM | 00055036 | Reserovir Overflow Piping | 1984 | 4 | 12000 | IMG_4697 | KWPH | Diameter: 350mm, above ground,approximately 12 meters. |  |  |  | 00016086 | West Park Heights Res Tank | [6 empty] | 6 |  | Area 3 Water Treatment | [5 empty] | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | Good
5267 | PM | 00055035 | Reservoir Inlet/Outlet Line Piping | 2014 | 5 | 54000 | IMG_0405 | KWPH | Diameter: 450mm, approximately 33 meters. |  |  |  | 00016086 | West Park Heights Res Tank | [6 empty] | 23 |  | Area 3 Water Treatment | [5 empty] | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  |  |  |  | OPERATING | 0 |  | 0 |  | 0 | Good
5614 | PM | 00055035 | Reservoir Mixing System | 2014 | 3 | 35000 | IMG_0405 | KWPH |  |  |  |  | 00016086 | [7 empty] | 23 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 | [5 empty] | 0 |  | 0 |  | 0 | Good
5250 | PM | 00055018 | Valve Chamber Blind Flange | 2014 | 2 | 4000 | IMG_0630 | KWPH | Blind flange for an adandonded pipe line. |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | [6 empty] | 23 |  | Area 3 Water Treatment | [5 empty] | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5259 | PM | 00055027 | Valve Chamber Inlet/Outlet Line Butterfly Valve 1 | 2014 | 3 | 15000 | IMG_0572 | KWPH | Diameter: 450mm, Val-Matic Model 2018XF, electric actuator by Rotork Type IQS-12FA10-B4, 120/1/60 |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | M00926 | [5 empty] | 23 |  | Area 3 Water Treatment | [5 empty] | W-WW | 3 | Surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  |  |  |  | OPERATING | 0 |  | 0 |  | 0 | Surface corrosion
5258 | PM | 00055026 | Valve Chamber Inlet/Outlet Line Butterfly Valve 1 Electric Actuator | 2014 | 3 | 11000 | IMG_0682 | KWPH | Rotork Type IQS-12FA10-B4, 120/1/60 |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | M00120 | [5 empty] | 23 |  | Area 3 Water Treatment |  |  | 0122960102 |  |  | W-WW | 3 | Minor paint peeling was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  |  |  |  | OPERATING | 0 |  | 0 |  | 0 | minor paint peeling
5181 | PM | 00055021 | Valve Chamber Inlet/Outlet Line Butterfly Valve 2 | 1984 | 3 | 15000 | IMG_0588 | KWPH | Main Line, Valve, Butterfly, 450 DIA flanged, Val-Matic Model 2018XF, electric actuator by Rotork Type IQS-12FA10-B4, 120/1/60 |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | [6 empty] | 2 |  | Area 3 Water Treatment |  | Process Mechanical |  |  |  | W-WW | 3 | Minor surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | Minor surface corrosion
5252 | PM | 00055020 | Valve Chamber Inlet/Outlet Line Butterfly Valve 2 Electric Actuator | 2014 | 3 | 11000 | IMG_1398 | KWPH | Diameter: 450mm |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | M00120 | [5 empty] | 23 |  | Area 3 Water Treatment |  |  | 0122960101 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5254 | PM | 00055022 | Valve Chamber Inlet/Outlet Line Flexible Coupling | 2014 | 3 | 5000 | IMG_1396 | KWPH | diameter: 250mm |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | [6 empty] | 23 |  | Area 3 Water Treatment | [5 empty] | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5257 | PM | 00055025 | Valve Chamber Inlet/Outlet Line Piping | 2014 | 3 | 5000 | IMG_0619 | KWPH | Diameter: 250mm, length: 8 meters |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | [6 empty] | 23 |  | Area 3 Water Treatment | [5 empty] | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  |  |  |  | OPERATING | 0 |  | 0 |  | 0 | Good
5607 | PM |  | Valve Chamber Sampling Line | 2002 | 3 | 2000 | IMG_1450 | KWPH |  |  |  |  | 00016091 | [7 empty] | 11 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | good
5578 | SC |  | Chemical Entry Concrete Roof | 1984 | 4 | 6000 | IMG_7062 | KWPH |  |  |  |  | 00016088 | [7 empty] | 22 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 0 | 2031 | 0 |  |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
5511 | SC | 00011171 | Chemical Entry Room Concrete Blockwall | 1984 | 4 | 9000 | IMG_7062 | KWPH |  |  |  |  | 00016088 | West Park Heights Reservoir | [6 empty] | 22 | [8 empty] | 3 | Step cracking in mortar was observed. |  |  | The asset was observed to be in fair condition. Provisions for structural repairs. Asset to be replaced at the end of remaining service life. | 0 | 2023 | 0 | 2038 |  | Keswick West Park Heights Reservoir Capital Project 1 | Keswick West Park Heights Reservoir Capital Project 2 |  | 0 |  | 0 |  | 0 | step cracking in mortar
5553 | SC | 00011171 | Chemical Room Concrete Blockwall | 1984 | 4 | 12000 | IMG_7068 | KWPH |  |  |  |  | 00016089 | [7 empty] | 22 | [8 empty] | 3 | Step cracking in mortar was observed. |  |  | The asset was observed to be in fair condition. Provisions for structural repairs. Asset to be replaced at the end of remaining service life. | 0 | 2023 | 0 | 2038 |  | Keswick West Park Heights Reservoir Capital Project 1 | Keswick West Park Heights Reservoir Capital Project 2 |  | 0 |  | 0 |  | 0 | step cracking in mortar
5572 | SC |  | Chemical Room Concrete Roof | 1984 | 4 | 8000 | IMG_7065 | KWPH |  |  |  |  | 00016089 | [7 empty] | 22 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 0 | 2031 | 0 |  |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
5580 | SC |  | Drain Chamber Access Hatch | 1984 | 3 | 3000 | IMG_7057 | KWPH |  |  |  |  | 00016092 | [7 empty] | 22 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 | [5 empty] | 0 |  | 0 |  | 0 | good
5574 | SC |  | Drain Chamber Access Ladder | 1984 | 3 | 2000 | IMG_7058 | KWPH |  |  |  |  | 00016092 | [7 empty] | 22 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 | [5 empty] | 0 |  | 0 |  | 0 | good
5579 | SC |  | Drain Chamber Concrete Structure | 1984 | 3 | 10000 | IMG_7058 | KWPH |  |  |  |  | 00016092 | [7 empty] | 22 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 0 | 2031 | 0 |  |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
5566 | SC | 00011171 | Electrical Room Concrete Blockwall | 1984 | 4 | 10000 | IMG_7055 | KWPH |  |  |  |  | 00016090 | [7 empty] | 22 | [8 empty] | 3 | Mortar step cracking was observed. |  |  | The asset was observed to be in fair condition. Provisions for structural repairs. Asset to be replaced at the end of remaining service life. | 0 | 2023 | 0 | 2038 |  | Keswick West Park Heights Reservoir Capital Project 1 | Keswick West Park Heights Reservoir Capital Project 2 |  | 0 |  | 0 |  | 0 | mortar step cracking
5573 | SC |  | Electrical Room Concrete Roof | 1984 | 4 | 6000 | IMG_7055 | KWPH |  |  |  |  | 00016090 | [7 empty] | 22 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 0 | 2031 | 0 |  |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
5510 | SC | 00011170 | Reservoir Access Ladder | 2014 | 3 | 10000 | IMG_7011 | KWPH | Metal ladder to the top of Reservoir |  |  |  | 00006881 | West Park Heights Reservoir | [6 empty] | 53 | [8 empty] | 3 | Fall arrest system is not compliant to current csa standards was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 | [5 empty] | 0 |  | 0 |  | 0 | Fall arrest system is not compliant to current CSA standards
5555 | SC |  | Reservoir Exterior Coating | 1984 | 3 | 575000 | IMG_7011 | KWPH |  |  |  |  | 00006881 | [7 empty] | 22 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 | [5 empty] | 0 |  | 0 |  | 0 | good
5567 | SC |  | Reservoir Interior Coating | 1984 | 4 | 750000 | IMG_7014 | KWPH |  |  |  |  | 00006881 | [7 empty] | 22 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 | [5 empty] | 0 |  | 0 |  | 0 | good
5586 | SC |  | Reservoir Roof Guardrail | 2014 | 3 | 10000 | IMG_7037 | KWPH |  |  |  |  | 00006881 | [7 empty] | 53 | [8 empty] | 3 | Localized cracked pipe sleeve was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 | [5 empty] | 0 |  | 0 |  | 0 | localized cracked pipe sleeve
5556 | SC |  | Reservoir Roof Hatch 1 | 1984 | 3 | 5000 | IMG_7038 | KWPH |  |  |  |  | 00006881 | [7 empty] | 22 | [8 empty] | 3 | Covered in roofing material was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 | [5 empty] | 0 |  | 0 |  | 0 | covered in roofing material
5568 | SC |  | Reservoir Roof Hatch 2 | 1984 | 3 | 5000 | IMG_7045 | KWPH |  |  |  |  | 00006881 | [7 empty] | 22 | [8 empty] | 3 | Covered in roofing material was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 | [5 empty] | 0 |  | 0 |  | 0 | covered in roofing material
5588 | SC |  | Reservoir Side Access Hatch 1 | 1984 | 3 | 10000 | IMG_7019 | KWPH |  |  |  |  | 00006881 | [7 empty] | 22 | [8 empty] | 3 | Minor surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 | [5 empty] | 0 |  | 0 |  | 0 | minor surface corrosion
5587 | SC |  | Reservoir Side Access Hatch 2 | 1984 | 3 | 14000 | IMG_7012 | KWPH |  |  |  |  | 00006881 | [7 empty] | 22 | [8 empty] | 3 | Minor surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 | [5 empty] | 0 |  | 0 |  | 0 | Minor surface corrosion
5554 | SC |  | Reservoir Steel Tank | 1984 | 5 | 1500000 | IMG_7031 | KWPH |  |  |  |  | 00006881 | [7 empty] | 22 | [8 empty] | 3 | Leakage staining noted on interior of tank at top of wall was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 | [5 empty] | 0 |  | 0 |  | 0 | leakage staining noted on interior of tank at top of wall
5571 | SC |  | Valve Chamber Access Hatch 1 | 1984 | 3 | 5000 | IMG_7069 | KWPH |  |  |  |  | 00016091 | [7 empty] | 22 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 | [5 empty] | 0 |  | 0 |  | 0 | good
5577 | SC |  | Valve Chamber Access Hatch 2 | 1984 | 3 | 3000 | IMG_7056 | KWPH |  |  |  |  | 00016091 | [7 empty] | 22 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 | [5 empty] | 0 |  | 0 |  | 0 | good
5570 | SC |  | Valve Chamber Access Ladder 1 | 1984 | 3 | 5000 | IMG_7077 | KWPH |  |  |  |  | 00016091 | [7 empty] | 22 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 | [5 empty] | 0 |  | 0 |  | 0 | good
5576 | SC |  | Valve Chamber Access Ladder 2 | 1984 | 3 | 5000 | IMG_7080 | KWPH |  |  |  |  | 00016091 | [7 empty] | 22 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 | [5 empty] | 0 |  | 0 |  | 0 | good
5569 | SC |  | Valve Chamber Concrete Structure | 1984 | 4 | 100000 | IMG_7077 | KWPH |  |  |  |  | 00016091 | [7 empty] | 22 | [8 empty] | 3 | Localized rust spots was observed. |  |  | The asset was observed to be in fair condition. Provisions for structural repairs. Asset to be replaced at the end of remaining service life. | 0 | 2023 | 0 | 2038 |  | Keswick West Park Heights Reservoir Capital Project 1 | Keswick West Park Heights Reservoir Capital Project 2 |  | 0 |  | 0 |  | 0 | localized rust spots
5273 | SIC | 00083304 | Chemical Entry Room Chlorine Gas Detector | 2014 | 2 | 2000 | IMG_4719 | KWPH | KSTKWP_CL2D_GCL21 |  |  |  | 00016088 | West Park Heights Res Chemical Entry Room | M10086 | A-ULTIMAX-PL-18 |  |  | Gas |  | 8 |  | Area 3 Water Treatment |  | Instrumentation and Control | A17-400747637 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5239 | SIC | 00018060 | Chemical Entry Room Temperature Switch | 1984 | 1 | 1000 | IMG_4702 | KWPH | Installtion year assumed to be 1984 |  |  |  | 00016088 | West Park Heights Res Control Room | M00076 | T631A1063 |  |  | Temperature |  | 6 |  | Area 3 Water Treatment |  | Instrumentation and Control | NOT AVAILABLE |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5229 | SIC | 00017992 | Chemical Room Chlorine Gas Detector | 2014 | 0 | 2000 | IMG_1262 | KWPH | KST1CLD101 |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room | M00937 | 50-125 |  |  | Chlorine Gas |  | 8 |  | Area 3 Water Treatment |  | Instrumentation and Control | A17-0023409 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5198 | SIC | 00006896 | Chlorination Building Entry Security System | 2014 | 3 | 10000 | IMG_4701 | KWPH | Security System includind card readerS and password enter panel. |  |  |  | 00016086 | West Park Heights Res Control Room | M00026 | [5 empty] | 8 |  | Area 3 Water Treatment |  | Health and Safety | RANGER 8980 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5610 | SIC | 00006896 | Chlorination Building Security Panels | 2014 | 3 | 20000 | IMG_4753 | KWPH | Three (3) honeywell panels in total |  |  |  | 00016086 | [7 empty] | 8 |  |  |  |  | RANGER 8980 |  |  |  | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | good
5173 | SIC | 00004235 | Chlorine Injection Line 1 Eductor | 2002 | 3 | 3500 | IMG_0510 | KWPH |  |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room | M00899 | [5 empty] | 6 |  | Area 3 Water Treatment |  | Process Mechanical |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5174 | SIC | 00004236 | Chlorine Injection Line 1 Electric Actuator | 2002 | 3 | 3500 | IMG_0510 | KWPH | True Blue Model EBV-65 |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room | M00894 | [5 empty] | 6 |  | Area 3 Water Treatment |  | Process Mechanical | 9373-083 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | Good
5172 | SIC | 00004234 | Chlorine Injection Line 2 Eductor | 2002 | 3 | 3500 | IMG_0510 | KWPH |  |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room | M00899 | [5 empty] | 6 |  | Area 3 Water Treatment |  | Process Mechanical |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5175 | SIC | 00004237 | Chlorine Injection Line 2 Electric Actuator | 2002 | 3 | 3500 | IMG_0510 | KWPH | True Blue Model EBV-65 |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room | M00894 | [5 empty] | 6 |  | Area 3 Water Treatment |  | Process Mechanical | 9373-083 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5213 | SIC | 00006918 | Chlorine System Pressure Gauges | 2002 | 2 | 1000 | IMG_1258 | KWPH | Two (2) in total. |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room | M00924 | [5 empty] | 6 |  | Area 3 Water Treatment |  | Instrumentation and Control |  |  |  | W-WW | 3 | Minor surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | minor surface corrosion
5465 | SIC | 00004230 | Chlorine Weight Scale | 2002 | 3 | 20000 | IMG_0494 | KWPH | Avery Weigh-Tronix |  |  |  | 00016089 | [7 empty] | 2 | [8 empty] | 3 | Minor surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | minor surface corrosion
5611 | SIC |  | Electrical Room Temperature Switch | 2014 | 1 | 1000 | IMG_4771 | KWPH |  |  |  |  | 00016090 | [7 empty] | 8 |  |  |  |  | NOT AVAILABLE |  |  |  | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | good
5206 | SIC | 00083300 | Facility PAC Control Panel | 2014 | 4 | 60000 | img_1313 | KWPH |  |  |  |  | 00016092 | West Park Heights Res Chemical Storage Room | M00899 | [5 empty] | 8 |  | Area 3 Water Treatment |  | Electrical System | 03-01-D |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5269 | SIC | 00080207 | Facility PAC Control Panel 3 Layer Ethernet Switch | 2014 | 2 | 3000 |  | KWPH | KSETWP Ethernet Switch, Inside PAC control Panel |  |  |  | 00006881 | West Park Heights Reservoir | M01002 | [5 empty] | 8 |  | Area 3 Water Treatment | W - Storage Reservoir | Instrumentation and Control | FOC1834Z4H1 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5244 | SIC | 00028277 | Facility PAC Control Panel Network Radio Modem | 2014 | 2 | 3000 |  | KWPH | KST1RAD101,Inside PAC control Panel |  |  |  | 00016090 | West Park Heights Res Control Room | M01018 | [5 empty] | 8 |  | Area 3 Water Treatment |  | SCADA | 831028 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5272 | SIC | 00083302 | Facility PAC Control Panel OIT Computer | 2014 | 2 | 2000 | IMG_4767 | KWPH |  |  |  |  | 00006881 | West Park Heights Reservoir | M10189 | [5 empty] | 8 |  | Area 3 Water Treatment | W - Storage Reservoir | Instrumentation and Control | 14E-088/KSTKWP_PAC |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5271 | SIC | 00083301 | Facility PAC Control Panel OIT Display and Panel | 2014 | 2 | 10000 | IMG_4767 | KWPH |  |  |  |  | 00016090 | West Park Heights Reservoir | M10189 | [5 empty] | 8 |  | Area 3 Water Treatment | W - Storage Reservoir | Instrumentation and Control | KSA1450204 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5243 | SIC | 00028276 | Facility PAC Control Panel RPU | 2014 | 2 | 3000 |  | KWPH | Inside PAC control Panel |  |  |  | 00016090 | West Park Heights Res Control Room | M00020 | [5 empty] | 8 |  | Area 3 Water Treatment |  | SCADA | 32520A39 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5275 | SIC | 00083387 | Facility PAC Control Panel UPS | 2014 | 2 | 3000 |  | KWPH | Inside PAC control Panel |  |  |  | 00006881 | West Park Heights Reservoir | M10181 | [5 empty] | 8 |  | Area 3 Water Treatment | W - Storage Reservoir | Instrumentation and Control | GK053A0118 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5232 | SIC | 00017995 | Free Chlorine Residual Analyzer | 2002 | 0 | 10000 | IMG_4713 | KWPH |  |  |  |  | 00016088 | West Park Heights Res Chemical Entry Room | M00482 | CL17 |  |  | Chlorine |  | 6 |  | Area 3 Water Treatment |  | Instrumentation and Control | 030800008011 |  |  | W-WW | 3 | The asset was outdated. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | outdated.
5238 | SIC | 00018001 | Network Antenna | 2014 | 1 | 10000 | img_7047 | KWPH | Installation year assumed to be 2010 |  |  |  | 00016090 | West Park Heights Res Control Room | [6 empty] | 8 |  | Area 3 Water Treatment |  | SCADA |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5619 | SIC | 00048031 | OMNI Antenna & Cable | 2014 | 1 | 10000 | img_7044 | KWPH |  |  |  |  | 00006881 | Nobleton North ET Tank Roof | [6 empty] | 8 |  | Area 4 Water Treatment |  | SCADA/ Instrumentation/ Control | SC488-SF3SNF |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 2019 |  |  |  |  | Good
5464 | SIC | 00055023 | Reservoir Inlet/Outlet Line Bidirectional Flowmeter | 2014 | 3 | 12000 | IMG_0578 | KWPH | KSTKWP_TWR_LIT1, Endress+Hauser, Promag, diameter: 250mm |  |  |  | 00016091 | [7 empty] | 8 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | Good
5262 | SIC | 00055030 | Reservoir Inlet/Outlet Line Flowmeter Transmitter | 2014 | 3 | 4000 | img_4706 | KWPH | FIT Display |  |  |  | 00016088 | West Park Heights Res Chemical Entry Room | M00405 | [5 empty] | 8 |  | Area 3 Water Treatment |  |  | FA02E916000 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5214 | SIC | 00006919 | Reservoir Pressure-type Level Transmitter | 2014 | 3 | 9000 | IMG_1392 | KWPH | KSTKWP_TWR_LIT1 |  |  |  | 00016090 | West Park Heights Res Control Room | M00020 | [5 empty] | 8 |  | Area 3 Water Treatment |  | Instrumentation and Control | 94A-11316 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5233 | SIC | 00017996 | Total Chlorine Residual Analyzer | 2002 | 3 | 10000 | IMG_4710 | KWPH | Assume to be original |  |  |  | 00016088 | West Park Heights Res Chemical Entry Room | M00482 | CL17 |  |  | Total Chlorine |  | 2 |  | Area 3 Water Treatment |  | Instrumentation and Control | 030800008013 |  |  | W-WW | 3 | The asset was outdated. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | outdated.
5463 | SIC | 00004234 | Vacuum Regulator 1 | 2002 | 3 | 4000 | IMG_4744 | KWPH | Manufacturer: US Filter -Wallce & Tiernan |  |  |  | 00016089 | [7 empty] | 6 |  |  |  |  | BK17251 |  |  |  | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | good
5171 | SIC | 00004235 | Vacuum Regulator 2 | 2002 | 3 | 4000 | IMG_4744 | KWPH | Manufacturer: US Filter -Wallce & Tiernan |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room | M00899 | [5 empty] | 6 |  | Area 3 Water Treatment |  | Process Mechanical | BK17251 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5227 | SIC | 00017988 | Valve Chamber Float Switch | 2002 | 2 | 1000 | IMG_1403 | KWPH |  |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | M00061 | Not available |  |  | Level |  | 6 |  | Area 3 Water Treatment |  | Instrumentation and Control | NOT AVAILABLE |  |  | W-WW | 3 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0
5622 | SIC | 00017988 | Valve Chamber Sump Pit Float Switch | 2002 | 2 | 1000 | IMG_0609 | KWPH |  |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | M00061 | Not available |  |  | Level |  | 6 |  | Area 3 Water Treatment |  | Instrumentation and Control | NOT AVAILABLE |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
5620 | SIC | 00048032 | YAGI Antenna & Cable | 2014 | 1 | 10000 | IMG_7043 | KWPH |  |  |  |  | 00006881 | Nobleton North ET Tank Roof | [6 empty] | 8 |  | Area 4 Water Treatment |  | SCADA/ Instrumentation/ Control | RY-9008 |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 2019 |  |  |  |  | Good
5451 | SW |  | 600mm Watermain | 1984 | 5 | 60000 |  | KWPH | 600mm ductile iron watermain on site. Approx. 20m in length |  |  |  | 00006881 | [7 empty] | 2 | [8 empty] | 3 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the short term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0
5452 | SW |  | 750mm Watermain | 2008 | 5 | 100000 |  | KWPH | 750mm CPP watermain on site. Approx. 30m in length |  |  |  | 00006881 | [7 empty] | 7 | [8 empty] | 3 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0
5443 | SW |  | Asphalt Driveway | 1984 | 2 | 65000 | IMG_20210510_095755 | KWPH | Asphalt driveway, including parking spots andasphalt around tank. |  |  |  | 00006881 | [7 empty] | 6 | [8 empty] | 3 | Large amount of cracking observed at driveway and parking spots was observed. | Edge of asphalt along asphalt around tank is damaged and breaking off was observed. |  | The asset was observed to be in fair condition.Reconstruct or repave asphalt surfaces on site. Asset to be replaced in the intermediate term. | 60000 |  | 15000 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 | Reconstruct or repave asphalt surfaces on site. | 60000 | Remove and replace full depth asphalt at location that is damaged (along the edge). Raise gravel shoulder between tank and asphalt to ensure positive drainage away from tank and across pavement | 15000 | Large amount of cracking observed at driveway and parking spots. | Edge of asphalt along asphalt around tank is damaged and breaking off.
5442 | SW |  | Chainlink Fence | 1984 | 2 | 25000 | IMG_20210510_095527 | KWPH | Chainlink fence around site, approximately 205m. |  |  |  | 00006881 | [7 empty] | 6 | [8 empty] | 3 | Signs of corrosion at various locations of the fence was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | Signs of corrosion at various locations of the fence.
5590 | SW |  | Chamber No.1 Access Hatch | 2008 | 3 | 5000 | IMG_7083 | KWPH |  |  |  |  | 00016092 | [7 empty] | 7 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | good
5585 | SW |  | Chamber No.1 Access Ladder | 2008 | 3 | 5000 | IMG_7084 | KWPH |  |  |  |  | 00016092 | [7 empty] | 7 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | good
5589 | SW |  | Chamber No.1 Concrete Structure | 2008 | 3 | 40000 | IMG_7086 | KWPH |  |  |  |  | 00016092 | [7 empty] | 7 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | good
5581 | SW |  | Chamber No.2 Access Hatch 1 | 2008 | 3 | 5000 | IMG_7072 | KWPH |  |  |  |  | 00016092 | [7 empty] | 7 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | good
5582 | SW |  | Chamber No.2 Access Hatch 2 | 2008 | 3 | 5000 | IMG_7072 | KWPH |  |  |  |  | 00016092 | [7 empty] | 7 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | good
5583 | SW |  | Chamber No.2 Access Ladder 1 | 2008 | 3 | 5000 | IMG_7091 | KWPH |  |  |  |  | 00016092 | [7 empty] | 7 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | good
5584 | SW |  | Chamber No.2 Access Ladder 2 | 2008 | 3 | 5000 | IMG_0722 | KWPH |  |  |  |  | 00016092 | [7 empty] | 7 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | good
5575 | SW |  | Chamber No.2 Concrete Structure | 2008 | 3 | 100000 | IMG_7091 | KWPH |  |  |  |  | 00006881 | [7 empty] | 7 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | good
5448 | SW |  | Reservoir Drain Piping | 1984 | 4 | 10000 |  | KWPH | 300mm reservoir drain from reservoir to drain chamber, length: 8 meters |  |  |  | 00006881 | [7 empty] | 2 | [8 empty] | 3 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the short term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0
5449 | SW |  | Reservoir Overflow Pipe | 1984 | 4 | 17500 |  | KWPH | 450mm ductile iron overflow pipe from reservoir to drain chamber. Approx. 8.0m in length |  |  |  | 00006881 | [7 empty] | 2 | [8 empty] | 3 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the short term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0
5216 | SW | 00011149 | Site Drainage (soft surfaces) | 1984 | 1 | 20000 | IMG_20210510_100127 | KWPH | Site drainage on soft surfaces |  |  |  | 00006881 | West Park Heights Reservoir | [6 empty] | 6 |  | Area 3 Water Treatment | W - Storage Reservoir | Siteworks |  |  |  | W-WW | 3 | Various locations damaged by tires or animals was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | Various locations damaged by tires or animals.
5447 | SW |  | Storm Sewer | 1984 | 3 | 38000 |  | KWPH | 450mm conc. storm sewer from drain chamber to maintenance hole. Approx. 23m in length to PL |  |  |  | 00006881 | [7 empty] | 2 | [8 empty] | 3 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the short term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0
5215 | SW | 00011144 | Swing Gate | 1984 | 2 | 4000 | IMG_20210510_095106 | KWPH |  |  |  |  | 00006881 | West Park Heights Reservoir | [6 empty] | 6 |  | Area 3 Water Treatment | W - Storage Reservoir | Siteworks |  |  |  | W-WW | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | Good