## Sheet1
seqNum | Description | Process | building | inspectorName | LocationTag | LocationORIGINAL | manufacturer | TransmitterModel | TransducerModel | TransducerSerial | InstMeva | installYear | installationDate | remainingESL | InstType | ServiceArea | FacilityType | LifeCycleCategory | SerialNo | Parent | RotatingItem | Status | Site | condition | assetName | CategoryCode | COF | facility | RehabRepairCost2 | RehabRepairYear2 | repCost | repProjectName | rehabProjectName | rehab2ProjectName | InspectionYear | photoName | assetTag | rehabComment1 | rehabCost1 | rehabComment2 | rehabCost2 | defect1Input | defect2Input | defect3Input | defect1 | defect2 | defect3 | RehabRepairYear | observations | RehabRepairCost
7041 | 1 single, 1 double |  |  |  | 00029225 | [6 empty] | 2009 |  | 9 | [9 empty] | 3 | Exterior Access Doors | AC | 1 | NSPS |  |  | 9000 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-1365 | [5 empty] | weathered exterior paint | minor corrosion at bottom of door frame |  | Weathered exterior paint was observed. | Minor corrosion was observed at bottom of door frame. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term.
7047 |  |  |  |  | 00029226 | [6 empty] | 2009 |  | 9 | [9 empty] | 3 | Lower Level Protective Floor Coating | AC | 1 | NSPS |  |  | 3000 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-1475 | [5 empty] | fair | localized wear |  |  | Localized wear was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term.
7043 |  |  |  |  | 00029227 | [6 empty] | 2009 |  | 9 | [9 empty] | 2 | Intermediate Level Interior Access Doors | AC | 1 | NSPS |  |  | 3500 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-1436 | [5 empty] | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
7044 |  |  |  |  | 00029226 | [6 empty] | 2009 |  | 9 | [9 empty] | 3 | Lower Level Interior Access Doors | AC | 1 | NSPS |  |  | 3500 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-1479 | [5 empty] | minor corrosion on hardware and bottom of door frame |  |  | Minor corrosion was observed on hardware and bottom of door frame. |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term.
7042 | 2 single doors |  |  |  | 00029228 | [6 empty] | 2009 |  | 9 | [9 empty] | 2 | Main Level Interior Access Doors | AC | 1 | NSPS |  |  | 7000 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-1404 | [5 empty] | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
7049 |  |  |  |  | 00029228 | [6 empty] | 2009 |  | 9 | [9 empty] | 3 | Main Level Wall Paint | AC | 1 | NSPS |  |  | 3000 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-1404 | [5 empty] | locazlied wear |  |  | Locazlied wear was observed. |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term.
7048 |  |  |  |  | 00029227 | [6 empty] | 2009 |  | 9 | [9 empty] | 3 | Intermediate Level Protective Floor Coating | AC | 1 | NSPS |  |  | 3000 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-1446 | [5 empty] | localized wear |  |  | Localized wear was observed. |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term.
7045 |  |  |  |  | 00029225 | [6 empty] | 2009 |  | 9 | [9 empty] | 2 | Roofing System | AC | 2 | NSPS |  |  | 15000 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-1329 | [5 empty] | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
7046 |  |  |  |  | 00029228 | [6 empty] | 2009 |  | 9 | [9 empty] | 3 | Main Level Protective Floor Coating | AC | 1 | NSPS |  |  | 4000 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-1391 | [5 empty] | localized wear |  |  | Localized wear was observed. |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term.
6498 | Brick, Exterior Finish, |  |  |  | 00029225 | Nobleton SPS Pumphouse | [5 empty] | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Architectural |  |  |  | OPERATING | W-WW | 3 | Exterior Brick Veneer | AC | 1 | NSPS |  |  | 40000 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-1327 | 00030046 |  |  |  |  | localized step cracking in mortar |  |  | Localized step cracking in mortar was observed. |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term.
6499 | Louvre Grilles, West Side, Exterior Finish, |  |  |  | 00029225 | Nobleton SPS Pumphouse | [5 empty] | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Architectural |  |  |  | OPERATING | W-WW | 3 | NOT USED (Move to Mech) | AC | 1 | NSPS |  |  | 0 | Nobleton SPS Capital Project 1 |  |  | 0 |  | 00030047 | [11 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the intermediate term.
6500 | Ceiling, Tectum Panel |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Architectural |  |  |  | OPERATING | W-WW | 2 | Acoustic Ceiling Panels | AC | 1 | NSPS |  |  | 8000 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-1420 | 00030058 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
7156 |  |  |  |  | 00029228 | [6 empty] | 2009 |  | 18 | [9 empty] | 3 | Toilet | BM | 1 | NSPS |  |  |  | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6784 | [5 empty] | Toilet bowl was stained. |  |  | Toilet bowl was stained was observed. |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term.
7167 |  |  |  |  | 00029228 | [6 empty] | 2023 |  | 32 | [9 empty] | 3 | *New Asset* Dehumidifier | BM | 2 | NSPS |  |  | 0 |  |  |  | 0 | [6 empty] | There was no dehumidifier installed at the station; however, significant condensation was observed on valves and piping with wet floors beneath. It is recommended to investigate the dehumidification needs and install a suitable unit if necessary. |  |  | There was no dehumidifier installed at the station; however, significant condensation was observed on valves and piping with wet floors beneath. it is recommended to investigate the dehumidification needs and install a suitable unit if necessary was observed. |  |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life.
7157 |  |  |  |  | 00029228 | [6 empty] | 2009 |  | 18 | [9 empty] | 3 | Washroom Sink | BM | 1 | NSPS |  |  | 0 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6786 | [12 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the long term.
6468 | DCW, Plumbing Fixture, Automatic Trap Primer |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical | 30212 |  |  | OPERATING | W-WW | 2 | Plumbing System | BM | 2 | NSPS |  |  | 25000 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6728 | 00022732 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6361 | EF 501, Motor, Induction |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00015 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 3 | Exhaust Fan 501 Motor | BM | 2 | NSPS |  |  | 0 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6707 | 00028900 | [11 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the long term.
6363 | Valve, Thermostatic Mixing |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00074 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical | 5307 |  |  | OPERATING | W-WW | 3 | Tempered Water Mixing Valve | BM | 1 | NSPS |  |  | 0 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6650 | 00029686 | [11 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the long term.
6367 | EF 503, Motor, Induction |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00015 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 3 | Exhaust Fan 503 Motor | BM | 2 | NSPS |  |  | 0 | Nobleton SPS Capital Project 2 |  |  | 0 |  | 00029691 | [11 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the long term.
6368 | EF 502, Motor, Induction |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00015 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 3 | Exhaust Fan 502 Motor | BM | 2 | NSPS |  |  | 0 | Nobleton SPS Capital Project 2 |  |  | 0 |  | 00029692 | [11 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the long term.
6364 | EF 504, Motor, Induction |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00021 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical | ILI3760 |  |  | OPERATING | W-WW | 3 | Exhaust Fan 504 Motor | BM | 2 | NSPS |  |  | 0 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6672 | 00029693 | [11 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the long term.
6494 | EF 504, Ventilation System, Exhaust Fan |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00327 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical | 401SC65306-00/0016501 |  |  | OPERATING | W-WW | 2 | Exhaust Fan 504 | BM | 2 | NSPS |  |  | 4500 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6672 | 00029694 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6474 | EF 503, Ventilation System, Exhaust Fan |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00327 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 2 | Exhaust Fan 503 | BM | 2 | NSPS |  |  | 3500 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6683 | 00029695 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6487 | EF 502, Ventilation System, Exhaust Fan |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00327 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 2 | Exhaust Fan 502 | BM | 2 | NSPS |  |  | 6000 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6677 | 00029696 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6477 | MD 510, Ventilation System, Damper |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00861 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 2 | Damper 510 | BM | 2 | NSPS |  |  | 1500 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6686 | 00029697 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6476 | MD 508, Ventilation System, Damper |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00861 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 2 | Damper 508 | BM | 2 | NSPS |  |  | 1500 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6680 | 00029698 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6492 | MD 513, Ventilation System, Damper |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00861 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 2 | Damper 513 | BM | 2 | NSPS |  |  | 2000 | Nobleton SPS Capital Project 2 |  |  | 0 |  | 00029699 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6491 | EF 501, Ventilation System, Exhaust Fan |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00327 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 3 | Exhaust Fan 501 | BM | 2 | NSPS |  |  | 5000 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6702 | 00029701 | [11 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the long term.
6471 | MD 507, Ventilation System, Damper |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00861 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 2 | Damper 507 | BM | 2 | NSPS |  |  | 1500 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6702 | 00029702 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6495 | MD 502, Ventilation System, Damper |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00861 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 2 | Damper | BM | 2 | NSPS |  |  | 3000 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6698 | 00029703 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6488 | MD 501, Ventilation System, Damper |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00861 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 2 | Damper 501 | BM | 2 | NSPS |  |  | 5000 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6697 | 00029704 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6486 | MD 509, Ventilation System, Damper |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00861 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 2 | Damper 509 | BM | 2 | NSPS |  |  | 3000 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6641 | 00029705 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6475 | MD 504, Ventilation System, Damper |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00861 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 2 | Damper 504 | BM | 2 | NSPS |  |  | 1500 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6642 | 00029706 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6493 | MD 509, Ventilation System, Damper |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00861 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 2 | Damper 509 | BM | 2 | NSPS |  |  | 2000 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6641 | 00029707 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6479 | MD 506, Ventilation System, Damper |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00861 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 2 | Damper 506 | BM | 2 | NSPS |  |  | 1500 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6640 | 00029708 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6482 | MD 511, Ventilation System, Damper |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00861 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 2 | Damper 511 | BM | 2 | NSPS |  |  | 1500 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6639 | 00029709 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6484 | MD 505, Ventilation System, Damper |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00861 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 2 | Damper 505 | BM | 2 | NSPS |  |  | 1500 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6637 | 00029710 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6469 | LV 502, Ventilation System, Louvre |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 2 | Louvre 502 | BM | 1 | NSPS |  |  | 4000 | Nobleton SPS Capital Project 2 |  |  | 0 |  | 00029711 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6473 | LV 501, Ventilation System, Louvre |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 3 | Louvre 501 | BM | 1 | NSPS |  |  | 6000 | Nobleton SPS Capital Project 2 |  |  | 0 |  | 00029712 | [11 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the long term.
6489 | LV 506, Ventilation System, Louvre |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 2 | Louvre 506 | BM | 1 | NSPS |  |  | 4000 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6609 | 00029713 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6478 | LV 505, Ventilation System, Louvre |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 2 | Louvre 505 | BM | 1 | NSPS |  |  | 4000 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6609 | 00029714 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6490 | LV 504, Ventilation System, Louvre |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 2 | Louvre 504 | BM | 1 | NSPS |  |  | 4000 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6609 | 00029715 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6485 | LV 503, Ventilation System, Louvre |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 2 | Louvre 503 | BM | 1 | NSPS |  |  | 3000 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6775 | 00029716 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6481 | SF 501, Ventilation System, Supply Fan |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 2 | Supply Fan 501 | BM | 2 | NSPS |  |  | 4500 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6647 | 00029717 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6366 | SF 501, Motor, Induction |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 3 | Supply Fan 501 Motor | BM | 2 | NSPS |  |  | 0 | Nobleton SPS Capital Project 2 |  |  | 0 |  | 00029718 | [11 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the long term.
6470 | EUH 502, Unit, Heater |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00366 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 2 | EUH 502 | BM | 2 | NSPS |  |  | 3500 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6692 | 00029720 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6472 | MD 503, Ventilation System, Damper |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00861 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 2 | Damper 503 | BM | 2 | NSPS |  |  | 3000 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6694 | 00029721 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6480 | Exhaust Silencer, Emergency Power, |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 2 | Exhaust Silencer | BM | 2 | NSPS |  |  | 6000 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6625 | 00029734 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6483 | Diesel, Emergency Power, Fuel Tank |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00309 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical | 6431-47 |  |  | OPERATING | W-WW | 3 | Diesel Fuel Tank | BM | 2 | NSPS |  |  | 4500 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6611 | 00029737 | Fuel system upgrades to meet TSSA requirements | 40000 |  |  | TSSA upgrades to the fuel system are required to bring system up to code CSA B139 | Tank was missing a WHMIS label. |  | Tssa upgrades to the fuel system are required to bring system up to code csa b139 was observed. | Tank was missing a whmis label was observed. |  |  | The asset was observed to be in fair condition.Fuel system upgrades to meet TSSA requirements Asset to be replaced in the long term. | 40000
6497 | EFF 501, Unit, Heater |  |  |  | 00029229 | Nobleton SPS PH Stairwell (404) | [5 empty] | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 2 | Unit Heater 501 | BM | 2 | NSPS |  |  | 2000 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6710 | 00029739 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6357 | Valve, Backflow Preventer |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00990 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 3 |  | BM | 1 | NSPS |  |  | 0 | Nobleton SPS Capital Project 2 |  |  | 0 |  | 00029747 | [11 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the long term.
7094 | BFP, Wilkins |  |  |  | 00029227 | [6 empty] | 2009 |  | 18 | [9 empty] | 2 | Backflow Preventer | BM | 1 | NSPS |  |  | 3000 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6742 | 00029747 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6347 | RP, Valve, Backflow Preventer |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00990 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical | 3106084 |  |  | OPERATING | W-WW | 3 |  | BM | 1 | NSPS |  |  | 0 | Nobleton SPS Capital Project 2 |  |  | 0 |  | 00029748 | [11 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the long term.
7095 | BFP, Wilkins |  |  |  | 00029227 | [6 empty] | 2009 |  | 18 | [9 empty] | 2 | Backflow Preventer | BM | 1 | NSPS |  |  | 3000 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6745 | 00029748 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6466 | HWT 501, Heating System, Water Heater Tank |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M10118 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical | FH12271405 |  |  | OPERATING | W-WW | 3 | Water Heater | BM | 2 | NSPS |  |  | 3000 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6718 | 00029757 | [11 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the long term.
6467 | EUH 503, Unit, Heater |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00366 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 2 | EUH 503 | BM | 2 | NSPS |  |  | 2000 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6730 | 00029758 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6460 | Diesel Exhaust Stack, Other Mechanical System, |  |  |  | 00029225 | Nobleton SPS Pumphouse | [5 empty] | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 2 | Diesel Stack | BM | 2 | NSPS |  |  | 20000 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6625 | 00029902 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6464 | Gas, Heating System, Unit Heater |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00366 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 2 |  | BM | 2 | NSPS |  |  | 7500 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6659 | 00029909 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6462 | Louvre Grille, East Side, Other Mechanical System, |  |  |  | 00029225 | Nobleton SPS Pumphouse | [5 empty] | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 3 | Louvre (East) | BM | 1 | NSPS |  |  | 0 | Nobleton SPS Capital Project 2 |  |  | 0 |  | 00030044 | [11 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the long term.
6461 | Louvre Grille, North Side, Other Mechanical System, |  |  |  | 00029225 | Nobleton SPS Pumphouse | [5 empty] | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 3 | Louvre (North) | BM | 1 | NSPS |  |  | 0 | Nobleton SPS Capital Project 2 |  |  | 0 |  | 00030045 | [11 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the long term.
6463 | Tank Filling Station and Monitor, Other Mechanical System, |  |  |  | 00029225 | Nobleton SPS Pumphouse | [5 empty] | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 3 | Diesel Tank Filling Station | BM | 2 | NSPS |  |  | 0 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-1338 | 00030240 | [11 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the long term.
6496 | MD 502, Ventilation System, Damper |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00861 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 2 | Damper | BM | 2 | NSPS |  |  | 2000 | Nobleton SPS Capital Project 2 |  |  | 0 |  | 00075849 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6465 | Unit Heater, Stelpro, SHU0563C |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00366 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 2 | EUH 502 | BM | 2 | NSPS |  |  | 4000 | Nobleton SPS Capital Project 2 |  |  | 0 | IMG_6757 | 00079982 |  |  |  |  | good | no asset tag |  |  | No asset tag was observed. |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term.
6506 | Lifting Device, 2 Tonne Chain Fall |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00091 |  |  |  |  | 2020 |  | 29 |  | Area 6 Wastewater Treatment |  | Building Mechanical | 001548 |  |  | OPERATING | W-WW | 3 | 2 Tonne Chain Fall (Main Level) | BM | 2 | NSPS |  |  | 0 |  |  |  | 0 | roy-nob-1424 | 00083515 | [11 empty] | The asset was assumed to be in fair condition. Asset to be replaced at the end of remaining service life.
6502 | Lifting Device, 2 Tonne Chain Fall |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00091 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Building Mechanical | 721311 |  |  | OPERATING | W-WW | 3 | 2 Tonne Chain Fall (Lower Level) | BM | 2 | NSPS |  |  | 0 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1485 | 00083516 | [11 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the long term.
6416 | Building Electrical, Lighting, Emergency Lighting Pack w/ Exit Sign, Battery, & Remote Heads, Lumacell, , , , 1 Unit |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Lower Level (401) | M00366 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 2 | Emergency Lighting Pack | ES | 2 | NSPS |  |  | 2500 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0863 |  | Replace all non-LED lighting fixtures with LED fixtures rated for Class 1, div 2 |  |  |  | Good | [6 empty] | The asset was observed to be in good condition.Replace all non-LED lighting fixtures with LED fixtures rated for Class 1, div 2 Asset to be replaced in the long term.
7069 | Process Electrical, Electrical Hydro Meter, Hyrdo One |  |  |  | 00029225 | [6 empty] | 2009 |  | 13 |  |  |  |  | Owned by Hydro One |  |  |  |  | 2 | Hydro Meter | ES | 2 | NSPS |  |  | 4000 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0522 | [5 empty] | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
7091 | Building Electrical, Lighting, Wet Well Wall Mounted HID Lighting Fixture, Appleton, CODE MASTER JR HID LIGHTING S35 Lamp, (120/20V, 50W, 60Hz, Class 1 DIV 1&2, 4x Enclosure), 6 Units |  |  |  | 00029231 | [6 empty] | 2009 |  | 13 | [9 empty] | 3 | Wet Well Lighting | ES | 1 | NSPS |  |  | 11400 | Nobleton SPS Capital Project 2 |  |  | 0 | NOB-ROY-1547 |  | Repalce all non-LED lighting fixtures with LED lighting fixtures rated for Class 1 Div 1. |  |  |  | Paint on light is beinging to errode. Minor rust formation on housing |  |  | Paint on light is beinging to errode. minor rust formation on housing was observed. |  |  |  | The asset was observed to be in fair condition.Repalce all non-LED lighting fixtures with LED lighting fixtures rated for Class 1 Div 1. Asset to be replaced in the long term.
7070 | Process Electrical, Primary Power, Utility Pad Mounted Transformer, ABB Power T&D Co., ,S/N:08J009047, Customer ID: 0000007240 , (300KVA, 3Ph, Primary: 27600/15935V, Secondary: 600/347V), 1 Unit |  |  |  | 00029225 | [6 empty] | 2009 |  | 13 |  |  |  |  | 08J009047; Owned by Hydro One |  |  |  |  | 3 | Utility Pad Mounted Transformer | ES | 3 | NSPS |  |  | 60000 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0527 | [5 empty] | Missing Region Asset Tag, (Unless utility owned) |  |  | Missing was observed region asset tag, (unless utility owned). |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term.
7072 | Process Electrical, Surge Protector Device, Eaton, 1 Unit |  |  |  | 00029228 | [6 empty] | 2009 |  | 13 | [9 empty] | 2 | Surge Protector Device (SPD) | ES | 2 | NSPS |  |  | 3000 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-1122 | [5 empty] | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6369 | Diesel, Standby Power Source, Engine |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00045 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical | 06R1022869 |  |  | OPERATING | W-WW | 3 | MOVE TO ELECTRICAL | ES | 2 | NSPS |  |  | 0 | Nobleton SPS Capital Project 2 |  |  | 0 |  | 00022846 | [11 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the long term.
6442 | Process Electrical, OC-1 Odour Control Fan Control Panel, ABB, , , ,600V 3Ph, 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00002 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 2 | OC-1 Odour Control Fan Control Panel | ES | 3 | NSPS |  |  | 7900 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0732 | 00022847 | Arc Flash Label to be placed on all 600V equipment |  |  |  | Good | Missing arc flash label. |  |  | Missing was observed arc flash label. |  |  | The asset was observed to be in good condition.Arc Flash Label to be placed on all 600V equipment Asset to be replaced in the long term.
6362 | LP PS Surge Suppressor, Surge Protection |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 3 | MOVE TO ELECTRICAL | ES | 2 | NSPS |  |  | 0 | Nobleton SPS Capital Project 2 |  |  | 0 |  | 00022848 | [11 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the long term.
6438 | Process Electrical, Main Service Circuit Breaker Switch, Eaton |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 2 | Main Service Circuit Breaker Switch | ES | 2 | NSPS |  |  | 20000 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0771 | 00022849 | Arc Flash Label to be placed on all 600V equipment |  |  |  | Good | Missing arc flash label. |  |  | Missing was observed arc flash label. |  |  | The asset was observed to be in good condition.Arc Flash Label to be placed on all 600V equipment Asset to be replaced in the long term.
6451 | Process Electrical, OC-1 Odour Control Unit MCC Circuit Breaker switch, |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 2 | OC-1 Odour Control Unit MCC Circuit Breaker Switch | ES | 2 | NSPS |  |  | 2700 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0611 | 00022850 | Arc Flash Label to be placed on all 600V equipment |  |  |  | Good | Missing arc flash label. |  |  | Missing was observed arc flash label. |  |  | The asset was observed to be in good condition.Arc Flash Label to be placed on all 600V equipment Asset to be replaced in the long term.
6450 | Electrical Equipment, Spare MCC Circuit Breaker Switch, EATON, 15A Breaker, (600V, 3Ph, 4W), 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 2 | Spare MCC Circuit Breaker Switch | ES | 2 | NSPS |  |  | 2700 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0585 | 00022851 | Arc Flash Label to be placed on all 600V equipment |  |  |  | Good | Missing arc flash label. |  |  | Missing was observed arc flash label. |  |  | The asset was observed to be in good condition.Arc Flash Label to be placed on all 600V equipment Asset to be replaced in the long term.
6457 | Process Electrical, T-PS Transformer MCC Circuit Breaker, EATON, 40A Breaker, (600V, 3Ph, 4W), 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 2 | T-PS MCC Circuit Breaker | ES | 2 | NSPS |  |  | 4000 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0588 | 00022852 | Arc Flash Label to be placed on all 600V equipment |  |  |  | Good | Missing arc flash label. |  |  | Missing was observed arc flash label. |  |  | The asset was observed to be in good condition.Arc Flash Label to be placed on all 600V equipment Asset to be replaced in the long term.
6434 | Process Electrical, EF-501 Exhuast Fan 1 MCC Circuit Breaker Switch, EATON, 15A Breaker, (600V, 3Ph, 4W), 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 2 | EF-501 MCC Circuit Breaker | ES | 2 | NSPS |  |  | 2700 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0580 | 00022853 | Arc Flash Label to be placed on all 600V equipment |  |  |  | Good | Missing arc flash label. |  |  | Missing was observed arc flash label. |  |  | The asset was observed to be in good condition.Arc Flash Label to be placed on all 600V equipment Asset to be replaced in the long term.
6437 | Process Electrical, EF-502 Exhuast Fan 2 MCC Circuit Breaker Switch, EATON, 15A Breaker, (600V, 3Ph, 4W), 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 2 | EF-502 MCC Circuit Breaker Switch | ES | 2 | NSPS |  |  | 2700 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0580 | 00022854 | Arc Flash Label to be placed on all 600V equipment |  |  |  | Good | Missing arc flash label. |  |  | Missing was observed arc flash label. |  |  | The asset was observed to be in good condition.Arc Flash Label to be placed on all 600V equipment Asset to be replaced in the long term.
6443 | Electrical Equipment, HWT-501 Hot Water Tank MCC Circuit Breaker Switch, EATON, 15A Breaker, (600V, 3Ph, 4W), 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 2 | HWT 501 MCC Circuit Breaker | ES | 2 | NSPS |  |  | 2700 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0581 | 00022855 | Arc Flash Label to be placed on all 600V equipment |  |  |  | Good | Missing arc flash label. |  |  | Missing was observed arc flash label. |  |  | The asset was observed to be in good condition.Arc Flash Label to be placed on all 600V equipment Asset to be replaced in the long term.
6447 | Electrical Equipment, SF 501 Supply Fan 1 MCC Circuit Breaker Switch, EATON, 15A Breaker, (600V, 3Ph, 4W), 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 2 | SF-501 MCC Circuit Breaker | ES | 2 | NSPS |  |  | 2700 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0581 | 00022856 | Arc Flash Label to be placed on all 600V equipment |  |  |  | Good | Missing arc flash label. |  |  | Missing was observed arc flash label. |  |  | The asset was observed to be in good condition.Arc Flash Label to be placed on all 600V equipment Asset to be replaced in the long term.
6430 | Process Electrical, MS-3 Monorail System MCC Circuit Breaker Switch, EATON, 15A Breaker, (600V, 3Ph, 4W), 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 2 | MS-3 MCC Circuit Breaker Switch | ES | 2 | NSPS |  |  | 2700 | Nobleton SPS Capital Project 2 |  |  | 0 | NOB-ROY-0582 | 00022857 | Arc Flash Label to be placed on all 600V equipment |  |  |  | Good | Missing arc flash label. |  |  | Missing was observed arc flash label. |  |  | The asset was observed to be in good condition.Arc Flash Label to be placed on all 600V equipment Asset to be replaced in the long term.
6429 | Process Electrical, EF-504 Exhaust Fan 4 MCC Circuit Breaker Switch, EATON, 15A Breaker, (600V, 3Ph, 4W), 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 2 | EF-504 MCC Circuit Breaker Switch | ES | 2 | NSPS |  |  | 2700 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0582 | 00022858 | Arc Flash Label to be placed on all 600V equipment |  |  |  | Good | Missing arc flash label. |  |  | Missing was observed arc flash label. |  |  | The asset was observed to be in good condition.Arc Flash Label to be placed on all 600V equipment Asset to be replaced in the long term.
6431 | Process Electrical, EFF-501 & EUH-501 MCC Circuit Breaker Switch, EATON, 20A Breaker, (600V, 3Ph, 4W), 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 2 | EFF 501 & EUH 501 MCC Circuit Breaker Switch, | ES | 2 | NSPS |  |  | 3000 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0583 | 00022859 | Arc Flash Label to be placed on all 600V equipment |  |  |  | Good | Missing arc flash label. |  |  | Missing was observed arc flash label. |  |  | The asset was observed to be in good condition.Arc Flash Label to be placed on all 600V equipment Asset to be replaced in the long term.
6436 | Process Electrical, EUH-501 MCC Controller, Eaton Cutler-Hammer |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 2 | EUH-501 MCC Controller | ES | 2 | NSPS |  |  | 7900 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0583 | 00022860 | Arc Flash Label to be placed on all 600V equipment |  |  |  | Good | Missing arc flash label. |  |  | Missing was observed arc flash label. |  |  | The asset was observed to be in good condition.Arc Flash Label to be placed on all 600V equipment Asset to be replaced in the long term.
6441 | Process Electrical, EUH-502 MCC Circuit Breaker Switch, EATON, 15A Breaker, (600V, 3Ph, 4W), 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 2 | EUH 502 MCC Circuit Breaker | ES | 2 | NSPS |  |  | 2700 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0584 | 00022861 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6454 | Process Electrical, EUH-503 MCC Circuit Breaker Switch, EATON, 15A Breaker, (600V, 3Ph, 4W), 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 2 | EUH-503 MCC Circuit Breaker | ES | 2 | NSPS |  |  | 2700 | Nobleton SPS Capital Project 2 |  |  | 0 | NOB-ROY-0584 | 00022862 | Arc Flash Label to be placed on all 600V equipment. |  |  |  | Good | Missing arc flash label. |  |  | Missing was observed arc flash label. |  |  | The asset was observed to be in good condition.Arc Flash Label to be placed on all 600V equipment. Asset to be replaced in the long term.
6448 | Process Electrical, Sump Pump Duplex Panel Disconnect Switch, EATON, 20A Breaker, (600V, 3Ph, 4W), 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 3 | Sump Pump Duplex Panel Disconnect Switch | ES | 2 | NSPS |  |  | 3000 | Nobleton SPS Capital Project 2 |  |  | 0 | NOB-ROY-0393 | 00022863 | [11 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the long term.
6446 | Spare, Switch, MCC Disconnect |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 2 | Spare Switch | ES | 1 | NSPS |  |  | 0 | Nobleton SPS Capital Project 2 |  |  | 0 | NOB-ROY-0585 | 00022864 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6432 | Process Electrical, RP-1 Rotary Phase Converter |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 3 | RP-1 Rotary Phase Converter | ES | 2 | NSPS |  |  | 7000 | Nobleton SPS Capital Project 2 |  |  | 0 |  | 00028925 |  |  |  |  | Asset no observed on site. |  |  | Asset no observed on site was observed. |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term.
6428 | Process Electrical, Starter, EF-501 Variable Frequency Drive (VFD), ABB, HVAC ACH550, ACH550-VCR-02A7-6+F267, Size 1, 2HP |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00002 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical | 2091100285 |  |  | OPERATING | W-WW | 2 | EF-501 VFD | ES | 3 | NSPS |  |  | 15000 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0652 | 00029687 | Arc Flash Label to be placed on all 600V equipment. |  |  |  | Good | Missing arc flash label. |  |  | Missing was observed arc flash label. |  |  | The asset was observed to be in good condition.Arc Flash Label to be placed on all 600V equipment. Asset to be replaced in the long term.
6444 | Process Electrical, Starter, EF-504 Variable Frequency Drive (VFD), ABB, HVAC ACH550, ACH550-VCR-02A7-6+F267, Size 1, 2HP |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00002 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical | 2091100820 |  |  | OPERATING | W-WW | 2 | EF-504 VFD | ES | 3 | NSPS |  |  | 15000 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0642 | 00029688 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6445 | Process Electrical, Starter, EF-502 Variable Frequency Drive (VFD), ABB ,HVAC ACH550, ACH550-VCR-02A7-6+F267, Size 1, 2HP |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00002 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical | 2091100670 |  |  | OPERATING | W-WW | 2 | EF 502 VFD | ES | 3 | NSPS |  |  | 15000 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0647 | 00029689 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6427 | Process Electrical, Starter, SF-501 Variable Frequency Drive (VFD), ABB, HVAC ACH550, ACH550-VCR-02A7-6+F267, Size 1, 2HP |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00002 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical | 2095100731 |  |  | OPERATING | W-WW | 2 | SF-501 VFD | ES | 3 | NSPS |  |  | 15000 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0652 | 00029690 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6440 | Building Electrical, EF-503 Local Disconnect Switch |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 2 | EF-503 Local Disconnect Switch | ES | 2 | NSPS |  |  | 0 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0637 | 00029700 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6453 | Building Electrical, Lighting Combination Unit w/ Exit Sign, Battery, & Remote Heads, Lumacell, 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00606 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 2 | Emergency Lighting Combination Unit | ES | 1 | NSPS |  |  | 2500 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0819 | 00029724 | Replace all non-LED lighting fixtures with LED fixtures. |  |  |  | Good | [6 empty] | The asset was observed to be in good condition.Replace all non-LED lighting fixtures with LED fixtures. Asset to be replaced in the long term.
6449 | Building Electrical, CP-03 Control Panel, MAAK TECHNOLOGIES GROUP INC, ,W178-002-3, (120VAC, 1A, 1Ph, 60Hz), CCT#15&#31, 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical | W178-002-3 |  |  | OPERATING | W-WW | 2 | CP-03 Control Panel | ES | 2 | NSPS |  |  | 100000 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0573 | 00029725 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6433 | Process Electrical, MCC-PS1 Main Breaker, Eaton, |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 2 | MCC-PS1 Main Disconnect Switch | ES | 3 | NSPS |  |  | 15800 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0316 | 00029726 | Arc Flash Label Required on all 600V Equipment |  |  |  | Good | Missing arc flash label. |  |  | Missing was observed arc flash label. |  |  | The asset was observed to be in good condition.Arc Flash Label Required on all 600V Equipment Asset to be replaced in the long term.
6439 | Process Electrical, Starter, PSP-1 Dry Pit Pump 1 Variable Frequency Drive (VFD), Eaton Cutler-Hammer, SVX9000, Size 4, 100HP |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 2 | PSP-1 Dry Pit Pump 1 VFD | ES | 3 | NSPS |  |  | 50000 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0606 | 00029727 | Arc Flash Label Required on all 600V Equipment |  |  |  | Good | Missing arc flash label. |  |  | Missing was observed arc flash label. |  |  | The asset was observed to be in good condition.Arc Flash Label Required on all 600V Equipment Asset to be replaced in the long term.
6455 | Process Electrical, Starter, PSP-2 Dry Pit Pump 2 Variable Frequency Drive (VFD), Eaton Cutler-Hammer, SVX9000, Size 4, 100HP |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 2 | PSP-2 Dry Pit Pump 2 VFD | ES | 3 | NSPS |  |  | 50000 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0600 | 00029728 | Arc Flash Label Required on all 600V Equipment |  |  |  | Good | Missing arc flash label. |  |  | Missing was observed arc flash label. |  |  | The asset was observed to be in good condition.Arc Flash Label Required on all 600V Equipment Asset to be replaced in the long term.
6426 | Process Electrical, Starter, PSP-3 Dry Pit Pump 3 Variable Frequency Drive (VFD), Eaton Cutler-Hammer, SVX9000, Size 4, 100HP, |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 2 | PSP-3 Dry Pit Pump 3 VFD | ES | 3 | NSPS |  |  | 50000 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0594 | 00029729 | Arc Flash Label Required on all 600V Equipment |  |  |  | Good | Missing arc flash label. |  |  | Missing was observed arc flash label. |  |  | The asset was observed to be in good condition.Arc Flash Label Required on all 600V Equipment Asset to be replaced in the long term.
6456 | Process Electrical, Standby Power , ATS-1 Local Disconnect Switch, Eaton |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 2 | ATS-1 Local Disconnect Switch | ES | 2 | NSPS |  |  | 8500 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0781 | 00029730 |  |  |  |  | Good | Missing arc flash label. |  |  | Missing was observed arc flash label. |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term.
6452 | Process Electricall, Standby Power, Battery Charger, Vulcan Electric, Model: DS-24 LV / HV, S/N: C159751, , (INPUT: 120V 4.5A 60Hz), (OUTPUT: 24V, 12A, 12Cell), 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00143 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical | C159751 |  |  | OPERATING | W-WW | 2 | Standby Battery Charger | ES | 2 | NSPS |  |  | 5900 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0618 | 00029731 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6360 | Surge Protection |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 3 | MOVE TO ELECTRICAL | ES | 2 | NSPS |  |  | 0 | Nobleton SPS Capital Project 2 |  |  | 0 |  | 00029732 | [11 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the long term.
6458 | Process Electrical, Standby Power , Generator Standby Power Source, MTU Onsite Energy, M/N: 350NXC6DT3, S/N: 305433-1-1-0209, Engine: 60 Series-Detroit,(347/600V, 421A, 3Ph, 4W, 0.8PF, 60Hz, 350kW, 438KVA) , 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M10085 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical | 305433-1-1-0209 |  |  | OPERATING | W-WW | 2 | Generator Standby Power Source | ES | 2 | NSPS |  |  | 170000 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-01619 | 00029733 | Arc Flash Label Required on all 600V Equipment |  |  |  | Good | Missing arc flash label. |  |  | Missing was observed arc flash label. |  |  | The asset was observed to be in good condition.Arc Flash Label Required on all 600V Equipment Asset to be replaced in the long term.
6459 | Lighting, Emergency, Exit Sign |  |  |  | 00029229 | Nobleton SPS PH Stairwell (404) | M00606 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 2 | Emergency Lighting Exit Sign | ES | 1 | NSPS |  |  | 300 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0827 | 00029742 | Replace all non-LED lighting fixtures with LED fixtures. |  |  |  | Good | [6 empty] | The asset was observed to be in good condition.Replace all non-LED lighting fixtures with LED fixtures. Asset to be replaced in the long term.
7035 | Building Electrical, Lighting, Emergency Double Remote Head, Lumacell, RS2012V9W, 1 Unit |  |  |  | 00029229 | [6 empty] | 2009 |  | 13 | [9 empty] | 2 | Emergency Lighting Double Remote Head | ES | 1 | NSPS |  |  | 350 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0843 | 00029742 | Replace all non-LED lighting fixtures with LED fixtures. |  |  |  | Good | [6 empty] | The asset was observed to be in good condition.Replace all non-LED lighting fixtures with LED fixtures. Asset to be replaced in the long term.
7037 | Building Electrical, Lighting, Emergency, Single Remote Head, Lumacell, 3 Units |  |  |  | 00029229 | [6 empty] | 2009 |  | 13 | [9 empty] | 2 | Emergency Lighting Single Remote Head | ES | 1 | NSPS |  |  | 510 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0930 | 00029742 | Replace all non-LED lighting fixtures with LED fixtures. |  |  |  | Good | [6 empty] | The asset was observed to be in good condition.Replace all non-LED lighting fixtures with LED fixtures. Asset to be replaced in the long term.
6422 | Process Electrical, PSP-3 Dry Pit Pump 3 Control Panel & MCC Circuit Breaker Switch, Eaton Cutler-Hammer, Breaker: 200A, 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00044 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 2 | PSP-3 Dry Pit Pump 3 Control Panel & Circuit Breaker | ES | 3 | NSPS |  |  | 26700 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0592 | 00029743 | ARC FLASH Label required on all 600V Equipment |  |  |  | Good | Missing arc flash label. |  |  | Missing was observed arc flash label. |  |  | The asset was observed to be in good condition.ARC FLASH Label required on all 600V Equipment Asset to be replaced in the long term.
6421 | Process Electrical, PSP-2 Dry Pit Pump Control Panel and MCC Circuit Breaker Switch, Eaton Cutler-Hammer, Breaker: 200A, 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00044 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 2 | PSP-2 Dry Pit Pump 2 Control Panel and Circuit Breaker Switch | ES | 3 | NSPS |  |  | 26700 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0597 | 00029744 | ARC FLASH Label required on all 600V Equipment |  |  |  | Good | Missing arc flash label. |  |  | Missing was observed arc flash label. |  |  | The asset was observed to be in good condition.ARC FLASH Label required on all 600V Equipment Asset to be replaced in the long term.
7088 | Process Electrical, PSP-1 Dry Pit Pump 1 Control Panel & MCC Circuit Breaker Switch, Eaton Cutler-Hammer, Breaker: 200A, 1 Unit |  |  |  | 00029228 | [6 empty] | 2009 |  | 13 | [9 empty] | 2 | PSP-1 Dry Pit Pump 1 Control Panel & Circuit Breaker | ES | 3 | NSPS |  |  | 26700 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0603 | 00029745 | ARC FLASH Label required on all 600V Equipment |  |  |  | Good | Missing arc flash label. |  |  | Missing was observed arc flash label. |  |  | The asset was observed to be in good condition.ARC FLASH Label required on all 600V Equipment Asset to be replaced in the long term.
6424 | SLP-1, Switch, Local Disconnect |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00044 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 3 | SLP-1 Local Disconnect Switch | ES | 2 | NSPS |  |  | 0 | Nobleton SPS Capital Project 2 |  |  | 0 |  | 00029745 | [11 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the long term.
6419 | Process Electrical, Motors, NBSSJA_RSP_PMP1_MTR RSP Pump 1 Motor, Hidrostal, TYP: HEVT4-YMKK + ND1B70-0, M. NR : 178684, , , 1 Unit |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00955 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical | 178684 |  |  | OPERATING | W-WW | 2 | NBSSJA_RSP_PMP1_MTR RSP Pump 1 Motor | ES | 4 | NSPS |  |  | 30000 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0980 | 00029766 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6418 | Process Electrical, Motors, NBSSJA_RSP_PMP2_MTR RSP Pump 2 Motor, Hidrostal, TYP: HEVT4-YMKK + ND1B70-0, M. NR : 178682, , , , 1 Unit |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00955 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical | 178682 |  |  | OPERATING | W-WW | 2 | NBSSJA_RSP_PMP2_MTR RSP Pump 2 Motor | ES | 4 | NSPS |  |  | 30000 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0991 | 00029767 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6415 | Process Electrical, Motors, NBSSJA_RSP_PMP3_MTR RSP Pump 3 Motor, Hidrostal, TYP: HEVT4-YMKK + ND1B70-0, M. NR : 178683 |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00955 |  |  |  |  | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical | 178683 |  |  | OPERATING | W-WW | 2 | NBSSJA_RSP_PMP3_MTR RSP Pump 3 Motor | ES | 4 | NSPS |  |  | 30000 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-1003 | 00029768 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6417 | Process Electrical, Control Panel, P-501 & P-502 Sump Pump 1 & 2 Control Panel, Unit |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | [5 empty] | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 2 | P-501 & P-502 Sump Pump Control Panel | ES | 2 | NSPS |  |  | 15000 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0972 | 00029779 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6414 | Building Electrical, Lighting, Exterior Wall Pack Light , Main Entrance, , , , , ,1 Unit |  |  |  | 00029225 | Nobleton SPS Pumphouse | [5 empty] | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical System |  |  |  | OPERATING | W-WW | 2 | Exterior Wall Pack Light | ES | 1 | NSPS |  |  | 1250 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0534 | 00029893 | Replace non-LED lighting fixtures with LED lighting fixtures rated for exterior use. |  |  |  | Good | [6 empty] | The asset was observed to be in good condition.Replace non-LED lighting fixtures with LED lighting fixtures rated for exterior use. Asset to be replaced in the long term.
7032 | Building Electrical, Lighting, Exterior Flood Lights, 2 Units |  |  |  | 00029225 | [6 empty] | 2009 |  | 13 | [9 empty] | 3 | Exterior Flood Light | ES | 1 | NSPS |  |  | 1500 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0481 | 00029893 | Replace all non-LED lighting fixtures with LED fixtures. |  |  |  | photosensor seems to be not working |  |  | Photosensor seems to be not working was observed. |  |  |  | The asset was observed to be in fair condition.Replace all non-LED lighting fixtures with LED fixtures. Asset to be replaced in the long term.
6423 | Building Electrical, Lighting, 2X48 Fluorescent Lighting Fixture, , , , , 9 Units |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | [5 empty] | 2009 |  | 13 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 2 | Intermediate Level Fluorescent Lighting Fixture | ES | 1 | NSPS |  |  | 7200 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0860 | 00029900 | Replace all non-LED lighting fixtures with LED fixtures. |  |  |  | Good | [6 empty] | The asset was observed to be in good condition.Replace all non-LED lighting fixtures with LED fixtures. Asset to be replaced in the long term.
7078 | Building Electrical, Lighting, 2X48 Fluorescent Lighting Fixture, , , , , 11 Units |  |  |  | 00029226 | [6 empty] | 2009 |  | 13 | [9 empty] | 2 | 2X48 Fluorescent Lighting Fixture | ES | 1 | NSPS |  |  | 8800 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-1069 | 00029900 | Replace all non-LED lighting fixtures with LED fixtures. |  |  |  | Good | [6 empty] | The asset was observed to be in good condition.Replace all non-LED lighting fixtures with LED fixtures. Asset to be replaced in the long term.
7034 | Building Electrical, Lighting, Emergency Lighting Pack w/ Exit Sign, Battery, & Remote Heads, Lumacell, 1 Unit |  |  |  | 00029226 | [6 empty] | 2009 |  | 13 | [9 empty] | 2 | Emergency Lighting Pack | ES | 1 | NSPS |  |  | 2500 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-1062 | 00029907 | Replace all non-LED lighting fixtures with LED fixtures rated for Class 1 Div 2. |  |  |  | Good | [6 empty] | The asset was observed to be in good condition.Replace all non-LED lighting fixtures with LED fixtures rated for Class 1 Div 2. Asset to be replaced in the long term.
7093 | Process Electrical, Sump Pump P-501 Motor | [10 empty] | 2009 |  | 13 | [9 empty] | 3 | Sump Pump P-501 Motor | ES | 1 | NSPS |  |  | 0 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-1170 | 00029913 | [11 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the long term.
7067 | Builidng Electrical, T-PS Transformer, Eaton Cutler-Hammer, (30kVA ,600-120/208VAC, 3Ph, 3W, 60Hz), 1 Unit |  |  |  | 00029228 | [6 empty] | 2009 |  | 13 | [9 empty] | 2 | T-PS Transformer | ES | 3 | NSPS |  |  | 15800 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0589 | 00087840 | Arc Flash Label to be placed on all 600V Equipment |  |  |  | Good | Missing arc flash label. |  |  | Missing was observed arc flash label. |  |  | The asset was observed to be in good condition.Arc Flash Label to be placed on all 600V Equipment Asset to be replaced in the long term.
7090 | Process Electrical, Motor Control Center (MCC), Eaton Cutler-Hammer, (347/600V, 400A, 3Ph, 4W), 12 Sections |  |  |  | 00029228 | [6 empty] | 2009 |  | 13 | [9 empty] | 2 | Motor Control Center MCC | ES | 4 | NSPS |  |  | 130000 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0577 | 00087842 | Arc Flash Label to be placed on all 600V equipment. |  |  |  | Good | Missing arc flash label. |  |  | Missing was observed arc flash label. |  |  | The asset was observed to be in good condition.Arc Flash Label to be placed on all 600V equipment. Asset to be replaced in the long term.
7081 | Process Electrical, Standby Power , ATS-1 Automatic Transfer Switch, Eaton Cutler-Hammer, ATC 300R |  |  |  | 00029228 | [6 empty] | 2009 |  | 13 | [9 empty] | 2 | ATS-1 Automatic Transfer Switch | ES | 2 | NSPS |  |  | 37500 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0772 | 00087842 | Arc Flash Label to be placed on all 600V equipment. |  |  |  | Good | Missing arc flash label. |  |  | Missing was observed arc flash label. |  |  | The asset was observed to be in good condition.Arc Flash Label to be placed on all 600V equipment. Asset to be replaced in the long term.
7068 | Building Electrical, LP-PS1 Lighting Distribution Panel/ Panelboard, ,PRL1a , ,(225A, 42CCT,120/208V,60Hz), 1 Unit |  |  |  | 00029228 | [6 empty] | 2009 |  | 13 | [9 empty] | 2 | LP-PS1 Lighting Distribution Panel/Panelboard | ES | 2 | NSPS |  |  | 11900 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0186 | 00087843 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
7089 | Process Electrical, EUH-504 MCC Circuit Breaker Switch, EATON, 15A Breaker, (600V, 3Ph, 4W), 1 Unit |  |  |  | 00029228 | [6 empty] | 2009 |  | 13 | [9 empty] | 2 | EUH-504 MCC Circuit Breaker | ES | 2 | NSPS |  |  | 3500 | Nobleton SPS Capital Project 2 |  |  | 0 | NOB-ROY-0611 |  | Arc Flash Label to be placed on all 600V equipment. Missing York Region Asset Tag. |  |  |  | Good | Missing arc flash label. |  |  | Missing was observed arc flash label. |  |  | The asset was observed to be in good condition.Arc Flash Label to be placed on all 600V equipment. Missing York Region Asset Tag. Asset to be replaced in the long term.
7086 | Building Electrical, Lighting, 2X48 Fluorescent Lighting Fixture, , , , , 9 Units |  |  |  | 00029228 | [6 empty] | 2009 |  | 13 | [9 empty] | 2 | Main Level Fluorescent Lighting Fixture | ES | 1 | NSPS |  |  | 7200 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0936 |  | Replace all non-LED lighting fixtures with LED fixtures. |  |  |  | Good | [6 empty] | The asset was observed to be in good condition.Replace all non-LED lighting fixtures with LED fixtures. Asset to be replaced in the long term.
7075 | Process Electrical, PSP-2 Disconnect Switch, Eaton Cutler-Hammer, (600V, 200A, 3Ph, Nema 3R) |  |  |  | 00029227 | [6 empty] | 2009 |  | 13 | [9 empty] | 2 | PSP-2 Disconnect Switch | ES | 1 | NSPS |  |  | 1800 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0867 |  | Arc Flash Label to be placed on all 600V Equipment Missing York Region Asset Tag. |  |  |  | Good | [6 empty] | The asset was observed to be in good condition.Arc Flash Label to be placed on all 600V Equipment Missing York Region Asset Tag. Asset to be replaced in the long term.
7077 | Building Electrical, Lighting, 2X48 Fluorescent Lighting Fixture, 5 Units |  |  |  | 00029229 | [6 empty] | 2009 |  | 13 | [9 empty] | 2 | 2X48 Fluorescent Lighting Fixture | ES | 1 | NSPS |  |  | 4000 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0936 |  | Replace all non LED fixtures with LED Fixtures |  |  |  | Good | [6 empty] | The asset was observed to be in good condition.Replace all non LED fixtures with LED Fixtures Asset to be replaced in the long term.
7076 | Process Electrical, PSP-1 Disconnect Switch, Eaton, (600V, 200A, 3Ph, Nema 3R), |  |  |  | 00029227 | [6 empty] | 2009 |  | 13 | [9 empty] | 2 | PSP-1 Disconnect Switch | ES | 1 | NSPS |  |  | 1800 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0868 |  | Arc Flash Label to be placed on all 600V Equipment Missing York Region Asset Tag |  |  |  | Good | Missing arc flash label. |  |  | Missing was observed arc flash label. |  |  | The asset was observed to be in good condition.Arc Flash Label to be placed on all 600V Equipment Missing York Region Asset Tag Asset to be replaced in the long term.
7073 | Process Electrical, Standby Power, EG-PS-1 Generator Breaker, GE, (600V,450A,3Ph) ,1 Unit |  |  |  | 00029228 | [6 empty] | 2009 |  | 13 | [9 empty] | 2 | EG-PS1 | ES | 2 | NSPS |  |  | 15000 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0802 |  | Arc Flash Label to be placed on all 600V Equipment Missing York Region Asset Tag |  |  |  | Good | Missing arc flash label. |  |  | Missing was observed arc flash label. |  |  | The asset was observed to be in good condition.Arc Flash Label to be placed on all 600V Equipment Missing York Region Asset Tag Asset to be replaced in the long term.
7074 | Process Electrical, PSP-3 Disconnect Switch, Eaton, (600V, 200A, 3Ph, Nema 3R) |  |  |  | 00029227 | [6 empty] | 2009 |  | 13 | [9 empty] | 2 | PSP-3 Disconnect Switch | ES | 1 | NSPS |  |  | 1800 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-0866 |  | Arc Flash Label to be placed on all 600V Equipment Missing York Region Asset Tag |  |  |  | Good | Missing arc flash label. |  |  | Missing was observed arc flash label. |  |  | The asset was observed to be in good condition.Arc Flash Label to be placed on all 600V Equipment Missing York Region Asset Tag Asset to be replaced in the long term.
7154 |  |  |  |  | 00029228 | [6 empty] | 2009 |  | 9 | [9 empty] | 3 | Eye Wash Station | HSS | 2 | NSPS |  |  | 500 | Nobleton SPS Capital Project 1 |  |  | 0 | IMG_6616 | [12 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the intermediate term.
7155 | HS_FE3 |  |  |  | 00029226 | [6 empty] | 2009 |  | 9 | [9 empty] | 3 | Fire Extinguisher | HSS | 1 | NSPS |  |  | 100 | Nobleton SPS Capital Project 1 |  |  | 0 | IMG_6756 | [12 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the intermediate term.
7165 | HS_FE2 |  |  |  | 00029227 | [6 empty] | 2009 |  | 9 | [9 empty] | 3 | Fire Extinguisher | HSS | 1 | NSPS |  |  | 100 | Nobleton SPS Capital Project 1 |  |  | 0 | IMG_6755 | [12 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the intermediate term.
7166 | HS_FE1 |  |  |  | 00029228 | [6 empty] | 2009 |  | 9 | [9 empty] | 3 | Fire Extinguisher | HSS | 1 | NSPS |  |  | 100 | Nobleton SPS Capital Project 1 |  |  | 0 | IMG_6656 | [12 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the intermediate term.
6412 | Unit 1, Fall Arrest System, Davit Arm Base |  |  |  | 00029233 | Nobleton SPS PH Site | [5 empty] | 2009 |  | 3 |  | Area 6 Wastewater Treatment |  | Health and Safety |  |  |  | OPERATING | W-WW | 3 | Davit Arm Base | HSS | 3 | NSPS |  |  | 0 | Nobleton SPS Capital Project 1 |  |  | 0 |  | 00022730 | [11 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the short term.
6413 | Unit 2, Fall Arrest System, Davit Arm Base |  |  |  | 00029233 | Nobleton SPS PH Site | [5 empty] | 2009 |  | 3 |  | Area 6 Wastewater Treatment |  | Health and Safety |  |  |  | OPERATING | W-WW | 3 | Davit Arm Base | HSS | 3 | NSPS |  |  | 0 | Nobleton SPS Capital Project 1 |  |  | 0 |  | 00022731 | [11 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the short term.
6410 | Entry / Exit Monitor, |  |  |  | 00029229 | Nobleton SPS PH Stairwell (404) | M00757 |  |  |  |  | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Health and Safety |  |  |  | OPERATING | W-WW | 3 |  | HSS | 2 | NSPS |  |  | 0 | Nobleton SPS Capital Project 1 |  |  | 0 |  | 00030052 | [11 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the intermediate term.
6409 | Process Instrumentation, Health and Safety Compliance Systems, Chemical Spill Kit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M10095 |  |  |  |  | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Health and Safety |  |  |  | OPERATING | W-WW | 3 | Chemical Spill Kit | HSS | 2 | NSPS |  |  | 500 | Nobleton SPS Capital Project 1 |  |  | 0 |  | 00079981 |  |  |  |  | Asset not observed on site. |  |  | Asset not observed on site was observed. |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term.
7161 | 200mm, SS |  |  |  | 00029226 | [6 empty] | 2009 |  | 18 | [9 empty] | 3 | Pump 3 Piping | PM | 3 | NSPS |  |  | 0 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1194 | [5 empty] | Condensation on pipe flanges |  |  | Condensation on pipe flanges was observed. |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term.
7162 | 250mm, SS |  |  |  | 00029227 | [6 empty] | 2009 |  | 18 | [9 empty] | 3 | Bypass Piping | PM | 3 | NSPS |  |  | 0 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1157 | [12 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the long term.
7160 | 200mm, SS |  |  |  | 00029226 | [6 empty] | 2009 |  | 18 | [9 empty] | 3 | Pump 2 Piping | PM | 3 | NSPS |  |  | 0 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1194 | [5 empty] | Condensation on pipe flanges |  |  | Condensation on pipe flanges was observed. |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term.
7164 | Purafil, S.O. No. 81509, Serial L08-0221, DS-300 |  |  |  | 00029231 | [6 empty] | 2009 |  | 18 | [9 empty] | 3 | Odour Control Unit | PM | 3 | NSPS |  |  | 0 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1551 | [5 empty] | The odour control unit is not in use. The Region did not report any odour complaints for the station. |  |  | The odour control unit is not in use. the region did not report any odour complaints for the station was observed. |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term.
7163 | 100mm, SS |  |  |  | 00029227 | [6 empty] | 2009 |  | 18 | [9 empty] | 3 | Surge Relief Piping | PM | 2 | NSPS |  |  | 0 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1138 | [12 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the long term.
7159 | 200mm, SS |  |  |  | 00029226 | [6 empty] | 2009 |  | 18 | [9 empty] | 3 | Pump 1 Piping | PM | 3 | NSPS |  |  | 0 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1183 | [5 empty] | Condensation on pipe flanges |  |  | Condensation on pipe flanges was observed. |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term.
7158 | 250mm, SS |  |  |  | 00029227 | [6 empty] | 2009 |  | 18 | [9 empty] | 3 | Discharge Header Piping | PM | 4 | NSPS |  |  | 0 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1139 | [5 empty] | Heavy condensation and a wet floor beneath the piping was observed. |  |  | Heavy condensation and a wet floor beneath the piping was observed was observed. |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term.
6503 | 50 mm Air, Relief, Valve |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00926 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 2 | Bypass Combined Air Relief Valve | PM | 1 | NSPS |  |  | 3000 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1161 | 00016583 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6330 | 100 mm Line 1 Drain, Valve, Gate |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00210 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 2 | Pump 1 Drain Gate Valve | PM | 1 | NSPS |  |  | 3000 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-1205 | 00022721 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6331 | 100 mm Line 2 Drain, Valve, Gate |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00210 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 2 | Pump 2 Drain Gate Valve | PM | 1 | NSPS |  |  | 3000 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-1198 | 00022722 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6336 | 100 mm Line 3 Drain, Valve, Gate |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00210 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 2 | Pump 3 Drain Gate Valve | PM | 1 | NSPS |  |  | 3000 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1206 | 00022723 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6353 | 75 mm Drain, Valve, Gate |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00210 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 3 | Discharge Header Drain Gate Valve | PM | 1 | NSPS |  |  | 2500 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1145 | 00022791 | replace cam lock and elbow | 1500 |  |  | drain pipe was severely corroded | cam lock corroded | very minor surface corrosion | Drain pipe was severely corroded was observed. | Cam lock corroded was observed. | Very minor surface corrosion was observed. |  | The asset was observed to be in fair condition.replace cam lock and elbow Asset to be replaced in the long term. | 1500
6352 | 100 mm Pressure Relief Line Feed, Valve, Plug |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00926 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical | M368280 |  |  | OPERATING | W-WW | 2 | Pressure Relief Line Plug Valve | PM | 1 | NSPS |  |  | 3000 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1133 | 00022792 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6354 | Piping, Pressure Regulator |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00145 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical | 0852W |  |  | OPERATING | W-WW | 3 | not found | PM | 1 | NSPS |  |  | 0 | Nobleton SPS Capital Project 2 |  |  | 0 |  | 00022793 | [11 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the long term.
6365 | 250 mm PGV 03B, Valve, Plug |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00926 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 2 | Bypass Plug Valve | PM | 1 | NSPS |  |  | 7000 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1211 | 00022865 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6350 | 250 mm PGV 03A, Valve, Plug |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00926 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical | M318740 |  |  | OPERATING | W-WW | 2 | Discharge Header Plug Valve | PM | 2 | NSPS |  |  | 7000 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1152 | 00029749 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6359 | PGV 02A, Valve, Plug |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00926 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical | M231210 |  |  | OPERATING | W-WW | 2 | Pump 1 Discharge Plug Valve | PM | 2 | NSPS |  |  | 5000 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1144 | 00029750 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6356 | 200 mm PGV 02B, Valve, Plug |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00926 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical | M518270 |  |  | OPERATING | W-WW | 2 | Pump 2 Discharge Plug Valve | PM | 2 | NSPS |  |  | 5000 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1143 | 00029751 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6349 | 200 mm PGV 02C, Valve, Plug |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00926 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical | M231210 |  |  | OPERATING | W-WW | 2 | Pump 3 Discharge Plug Valve | PM | 2 | NSPS |  |  | 5000 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1142 | 00029752 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6355 | 200 mm PGV 01C, Valve, Plug |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | [5 empty] | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 2 | Pump 3 Suction Plug Valve Stem and Handwheel | PM | 2 | NSPS |  |  | 5000 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1130 | 00029754 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6348 | 200 mm PGV 01B, Valve, Plug |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M10119 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 2 | Pump 2 Suction Plug Valve Stem and Handwheel | PM | 2 | NSPS |  |  | 5000 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-1135 | 00029755 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6358 | 200 mm PGV 01A, Valve, Plug |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | [5 empty] | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 2 | Pump 1 Suction Plug Valve Stem and Handwheel | PM | 2 | NSPS |  |  | 5000 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1136 | 00029756 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6351 | 100 mm Sewage, Valve, Pressure Relief |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00818 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical | 109-214 |  |  | OPERATING | W-WW | 2 | Pressure Relief Valve | PM | 2 | NSPS |  |  | 8000 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1131 | 00029761 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6342 | CV 01A, Valve, Check |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00926 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 2 | Pump 1 Discharge Check Valve | PM | 2 | NSPS |  |  | 5000 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1185 | 00029762 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6327 | 200 mm CV 01B, Valve, Check |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00926 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 2 | Pump 2 Discharge Check Valve | PM | 2 | NSPS |  |  | 5000 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1195 | 00029763 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6338 | 200 mm CV 01C, Valve, Check |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00926 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 2 | Pump 3 Discharge Check Valve | PM | 2 | NSPS |  |  | 5000 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1204 | 00029764 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6329 | RSP Pump 1, Inline Centrifugal, NBSSJA_RSP_PMP1, 53 L/s 54m TDH |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00955 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical | 241E-8492-2 |  |  | OPERATING | W-WW | 3 | Sewage Pump 1 | PM | 4 | NSPS |  |  | 100000 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-1180 | 00029769 | pump impeller and motor balance | 10000 |  |  | fair | excess vibration based on visual inspection |  |  | Excess vibration based on visual inspection was observed. |  |  | The asset was observed to be in fair condition.pump impeller and motor balance Asset to be replaced in the long term. | 10000
6335 | RSP Pump 2, Inline Centrifugal, NBSSJA_RSP_PMP2, 53 L/s 54 M TDH |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00955 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical | 241E-8492-1 |  |  | OPERATING | W-WW | 3 | Sewage Pump 2 | PM | 4 | NSPS |  |  | 100000 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1191 | 00029770 | pump balance | 15000 |  |  | Fair | excessive vibration based on visual inspection |  |  | Excessive vibration based on visual inspection was observed. |  |  | The asset was observed to be in fair condition.pump balance Asset to be replaced in the long term. | 15000
6345 | RSP Pump 3, Inline Centrifugal, NBSSJA_RSP_PMP3 53 L/S 54 M THD |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00955 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical | 241E-8492-3 |  |  | OPERATING | W-WW | 3 | Sewage Pump 3 | PM | 4 | NSPS |  |  | 100000 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1202 | 00029771 | pump balance | 15000 |  |  | fair | excessive vibration based on viusal inspection |  |  | Excessive vibration based on viusal inspection was observed. |  |  | The asset was observed to be in fair condition.pump balance Asset to be replaced in the long term. | 15000
6332 | 200 mm Suction 1, Valve, Plug |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00926 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 3 | Pump 1 Suction Plug Valve | PM | 2 | NSPS |  |  | 5000 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1175 | 00029772 |  |  |  |  | Minor localized paint peeling |  |  | Minor localized paint peeling was observed. |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term.
6328 | 200 mm plug valve PSP-2 |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00926 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 3 | Pump 2 Suction Plug Valve | PM | 2 | NSPS |  |  | 5000 | Nobleton SPS Capital Project 2 |  |  | 0 | ROY-NOB-1187 | 00029773 |  |  |  |  | Minor localized paint peeling |  |  | Minor localized paint peeling was observed. |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term.
6346 | 200 mm RSP PMP3 Line, Valve, Plug |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00926 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 3 | Pump 3 Suction Plug Valve | PM | 2 | NSPS |  |  | 5000 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1199 | 00029774 |  |  |  |  | Minor localized paint peeling |  |  | Minor localized paint peeling was observed. |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term.
6333 | 75 mm P 502, Valve, Check |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00926 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 2 | Sump Pump 2 Discharge Check Valve | PM | 2 | NSPS |  |  | 2500 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1174 | 00029775 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6337 | 75 mm P 501, Valve, Check |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00926 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 2 | Sump Pump 1 Discharge Check Valve | PM | 2 | NSPS |  |  | 2500 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1174 | 00029776 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6343 | 75 mm P 501, Valve, Plug |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00211 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 2 | Sump Pump 1 Discharge Plug Valve | PM | 2 | NSPS |  |  | 3000 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1168 | 00029777 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6340 | 75 mm P 502, Valve, Plug |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00211 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 2 | Sump Pump 2 Discharge Plug Valve | PM | 2 | NSPS |  |  | 3000 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1168 | 00029778 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6334 | P 502, Pump, Sump |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | [5 empty] | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 3 | Sump Pump 2 | PM | 2 | NSPS |  |  | 10000 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1171 | 00029910 |  |  |  |  | surface corrosion |  |  | Surface corrosion was observed. |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term.
6344 | P 501, Pump, Sump |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | [5 empty] | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 3 | Sump Pump 1 | PM | 2 | NSPS |  |  | 8000 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1170 | 00029912 |  |  |  |  | surface corrosion |  |  | Surface corrosion was observed. |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term.
6339 | P 501, Motor, Induction |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | [5 empty] | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 3 | Sump Pump 1 Motor | PM | 2 | NSPS |  |  | 2000 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1171 | 00029913 |  |  |  |  | fair | [6 empty] | The asset was observed to be in fair condition. Asset to be replaced in the long term.
6341 | P 502, Motor, Induction |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | [5 empty] | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 3 | Sump Pump 2 Motor | PM | 2 | NSPS |  |  | 2000 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1171 | 00029914 |  |  |  |  | fair | [6 empty] | The asset was observed to be in fair condition. Asset to be replaced in the long term.
6370 | 250 mm Flowmeter, Flow Meter, |  |  |  | 00029227 | Nobleton SPS PH Stairwell (404) | M00405 |  |  |  |  | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical | AB0027010E6 |  |  | OPERATING | W-WW | 2 | Discharge Header Magnetic Flow Meter | PM | 3 | NSPS |  |  | 20000 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1151 | 00030043 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6504 | 250 mm Station by-pass plug valve |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | [5 empty] | 2009 |  | 18 |  | Area 6 Wastewater Treatment |  | Process Mechanical | M238710 |  |  | OPERATING | W-WW | 2 | Bypass Plug Valve | PM | 2 | NSPS |  |  | 7000 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1147 | 00046890 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6373 | 600 mm x 600 mm Sluice Gate 3, Inlet, Valve |  |  |  | 00029232 | Nobleton SPS PH Wet Well Chamber - Lower Level (407) | [5 empty] | 2008 |  | 17 |  | Area 6 Wastewater Treatment |  | Process Mechanical | 550-1048496 |  |  | OPERATING | W-WW | 2 | Sluice Gate 3 | PM | 3 | NSPS |  |  | 10000 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1535 | 00079976 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6372 | 600 mm x 600 mm Sluice Gate 2, Inlet, Valve |  |  |  | 00029232 | Nobleton SPS PH Wet Well Chamber - Lower Level (407) | [5 empty] | 2008 |  | 17 |  | Area 6 Wastewater Treatment |  | Process Mechanical | 550-1048496 |  |  | OPERATING | W-WW | 2 | Sluice Gate 2 | PM | 3 | NSPS |  |  | 10000 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1534 | 00079977 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
6371 | 600 mm x 600 mm Sluice Gate 1, Inlet, Valve |  |  |  | 00029232 | Nobleton SPS PH Wet Well Chamber - Lower Level (407) | [5 empty] | 2008 |  | 17 |  | Area 6 Wastewater Treatment |  | Process Mechanical | 550-1048496 |  |  | OPERATING | W-WW | 2 | Sluice Gate 1 | PM | 3 | NSPS |  |  | 10000 | Nobleton SPS Capital Project 2 |  |  | 0 | roy-nob-1533 | 00079978 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the long term.
7065 |  |  |  |  | 00029233 | [6 empty] | 2009 |  | 48 | [9 empty] | 2 | Odour Control Access Ladder | SC | 3 | NSPS |  |  | 3000 |  |  |  | 0 | ROY-NOB-1562 | [5 empty] | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life.
7063 |  |  |  |  | 00029232 | [6 empty] | 2009 |  | 48 | [9 empty] | 4 | Wet Well Concrete Structure | SC | 5 | NSPS |  | 2038 | 500000 |  | Nobleton SPS Capital Project 1 | Nobleton SPS Capital Project 2 | 0 | ROY-NOB-1497 | [5 empty] | concrete spalling on underside of roof by access hatch |  |  | Concrete spalling was observed on underside of roof by access hatch. |  |  | 2023 | The asset was observed to be in poor condition. Provisions for structural repairs. Asset to be replaced at the end of remaining service life.
7056 |  |  |  |  | 00029231 | [6 empty] | 2009 |  | 48 | [9 empty] | 3 | Wet Well Access Ladder | SC | 2 | NSPS |  |  | 10000 |  |  |  | 0 | ROY-NOB-1510 | [5 empty] | minor pitting |  |  | Minor pitting was observed. |  |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life.
7059 | Into wet well 2 |  |  |  | 00029232 | [6 empty] | 2009 |  | 48 | [9 empty] | 3 | Wet Well Access Ladder (Chamber 2) | SC | 2 | NSPS |  |  | 5000 |  |  |  | 0 | ROY-NOB-1526 | [5 empty] | poor | pitting noted |  | Poor was observed. | Pitting was observed noted. |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life.
7057 |  |  |  |  | 00029231 | [6 empty] | 2009 |  | 48 | [9 empty] | 3 | Wet Well Access Ladder | SC | 2 | NSPS |  |  | 10000 |  |  |  | 0 | ROY-NOB-1509 | [5 empty] | minor pitting |  |  | Minor pitting was observed. |  |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life.
7066 |  |  |  |  | 00029233 | [6 empty] | 2009 |  | 48 | [9 empty] | 2 | Odour Control Access Hatch | SC | 2 | NSPS |  |  | 6000 |  |  |  | 0 | ROY-NOB-1561 | [5 empty] | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life.
7050 | Floor, Concrete |  |  |  | 00029227 | [6 empty] | 2009 |  | 48 | [9 empty] | 2 | Intermediate Level Concrete Floor Slab | SC | 4 | NSPS |  |  | 50000 |  | Nobleton SPS Capital Project 1 |  | 0 | ROY-NOB-1446 | [5 empty] | good | [5 empty] | 2031 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life.
7051 | Floor, Concrete |  |  |  | 00029226 | [6 empty] | 2009 |  | 48 | [9 empty] | 3 | Lower Level Concrete Floor Slab | SC | 4 | NSPS |  | 2038 | 260000 |  | Nobleton SPS Capital Project 1 | Nobleton SPS Capital Project 2 | 0 | ROY-NOB-1475 | [5 empty] | typical hairline cracking |  |  | Typical hairline cracking was observed. |  |  | 2023 | The asset was observed to be in fair condition. Provisions for structural repairs. Asset to be replaced at the end of remaining service life.
7053 |  |  |  |  | 00029227 | [6 empty] | 2009 |  | 48 | [9 empty] | 3 | Intermediate Level Concrete Walls | SC | 4 | NSPS |  | 2038 | 300000 |  | Nobleton SPS Capital Project 1 | Nobleton SPS Capital Project 2 | 0 | ROY-NOB-1435 | [5 empty] | fair | typical previous repairs | localized cracking observed |  | Typical previous repairs was observed. | Localized cracking observed was observed. | 2023 | The asset was observed to be in fair condition. Provisions for structural repairs. Asset to be replaced at the end of remaining service life.
7055 | Wet Well, Access, Hatch, Steel |  |  |  | 00029231 | [6 empty] | 2009 |  | 48 | [9 empty] | 3 | Wet Well Access Hatch | SC | 2 | NSPS |  |  | 6000 |  |  |  | 0 | ROY-NOB-1490 | [5 empty] | fair | [6 empty] | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life.
7058 | Into wet well 1 |  |  |  | 00029232 | [6 empty] | 2009 |  | 48 | [9 empty] | 3 | Wet Well Access Ladder (Chamber 1) | SC | 2 | NSPS |  |  | 5000 |  |  |  | 0 | ROY-NOB-1538 | [5 empty] | pitting noted |  |  | Pitting was observed noted. |  |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life.
7061 | Into inlet chamber |  |  |  | 00029232 | [6 empty] | 2009 |  | 48 | [9 empty] | 3 | Wet Well Access Ladder (Inlet Chamber) | SC | 2 | NSPS |  |  | 5000 |  |  |  | 0 | ROY-NOB-1511 | [5 empty] | poor | pitting noted |  | Poor was observed. | Pitting was observed noted. |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life.
7060 | Into wet well 3 |  |  |  | 00029232 | [6 empty] | 2009 |  | 48 | [9 empty] | 3 | Wet Well Access Ladder (Chamber 3) | SC | 2 | NSPS |  |  | 5000 |  |  |  | 0 | ROY-NOB-1513 | [5 empty] | pitting noted |  |  | Pitting was observed noted. |  |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life.
7064 |  |  |  |  | 00029233 | [6 empty] | 2009 |  | 48 | [9 empty] | 3 | Odour Control Precast Concrete Chamber | SC | 3 | NSPS |  | 2038 | 50000 |  | Nobleton SPS Capital Project 1 | Nobleton SPS Capital Project 2 | 0 | ROY-NOB-1562 | [5 empty] | water ingress from joint between roof and walls |  |  | Water ingress from joint between roof and walls was observed. |  |  | 2027 | The asset was observed to be in fair condition. Provisions for structural repairs. Asset to be replaced at the end of remaining service life.
7054 |  |  |  |  | 00029225 | [6 empty] | 2009 |  | 48 | [9 empty] | 2 | Wood Truss Roof | SC | 3 | NSPS |  |  | 12000 |  |  |  | 0 | ROY-NOB-1327 | [5 empty] | good | hidden under finishes |  |  | Hidden under finishes was observed. |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life.
7052 |  |  |  |  | 00029226 | [6 empty] | 2009 |  | 48 | [9 empty] | 3 | Lower Level Concrete Walls | SC | 3 | NSPS |  | 2038 | 600000 |  | Nobleton SPS Capital Project 1 | Nobleton SPS Capital Project 2 | 0 | ROY-NOB-1467 | [5 empty] | fair | typical previous repairs |  |  | Typical previous repairs was observed. |  | 2027 | The asset was observed to be in fair condition. Provisions for structural repairs. Asset to be replaced at the end of remaining service life.
7062 | 4 total |  |  |  | 00029232 | [6 empty] | 2009 |  | 48 | [9 empty] | 3 | Wet Well Aluminum Grating | SC | 2 | NSPS |  |  | 5000 |  |  |  | 0 | ROY-NOB-1507 | [5 empty] | minor pitting noted |  |  | Minor pitting was observed noted. |  |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life.
6319 | Monorail, Hoist Beam |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00366 |  |  |  |  | 2009 |  | 48 |  | Area 6 Wastewater Treatment |  | Structural |  |  |  | OPERATING | W-WW | 2 | Lower Level Monorail Hoist Beam | SC | 2 | NSPS |  |  | 8000 |  |  |  | 0 | ROY-NOB-1483 | 00029908 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life.
6320 | Basement Pump Removal, Hatch, Aluminum |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | [5 empty] | 2009 |  | 48 |  | Area 6 Wastewater Treatment |  | Structural |  |  |  | OPERATING | W-WW | 3 | Intermediate Level Pump Hatch | SC | 2 | NSPS |  |  | 5000 |  |  |  | 0 | ROY-NOB-1440 | 00029911 |  |  |  |  | fair | [6 empty] | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life.
6322 | Generator and MCC, Floor Slab, Concrete |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  | 48 |  | Area 6 Wastewater Treatment |  | Structural |  |  |  | OPERATING | W-WW | 3 | (NOT REQUIRED) | SC | 3 | NSPS |  |  | 0 |  |  |  | 0 |  | 00029936 | [11 empty] | The asset was assumed to be in fair condition. Asset to be replaced at the end of remaining service life.
6325 | Basement, Stair, Concrete |  |  |  | 00029229 | Nobleton SPS PH Stairwell (404) | [5 empty] | 2009 |  | 48 |  | Area 6 Wastewater Treatment |  | Structural |  |  |  | OPERATING | W-WW | 2 | Concrete Staircase | SC | 3 | NSPS |  |  | 60000 |  | Nobleton SPS Capital Project 1 |  | 0 | ROY-NOB-1428 | 00030051 |  |  |  |  | good | [5 empty] | 2031 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life.
6324 | Monorail, Hoist Beam |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00366 |  |  |  |  | 2009 |  | 48 |  | Area 6 Wastewater Treatment |  | Structural |  |  |  | OPERATING | W-WW | 2 | Main Level Monorail Hoist Beam | SC | 3 | NSPS |  |  | 7000 |  |  |  | 0 | ROY-NOB-1418 | 00030057 |  |  |  |  | good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life.
6321 | Wall, Concrete Block |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  | 48 |  | Area 6 Wastewater Treatment |  | Structural |  |  |  | OPERATING | W-WW | 3 | Main Level Masonry Blockwall | SC | 4 | NSPS |  |  | 50000 |  |  |  | 0 | ROY-NOB-1404 | 00030060 |  |  |  |  | localized step cracking |  |  | Localized step cracking was observed. |  |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life.
6323 | Basement Pump Removal, Hatch, Aluminum Floor |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  | 48 |  | Area 6 Wastewater Treatment |  | Structural |  |  |  | OPERATING | W-WW | 3 | Main Level Pump Hatch | SC | 2 | NSPS |  |  | 5000 |  |  |  | 0 | ROY-NOB-1389 | 00030061 |  |  |  |  | fair | [6 empty] | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life.
6501 | Floor, Concrete |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  | 48 |  | Area 6 Wastewater Treatment |  | Architectural |  |  |  | OPERATING | W-WW | 2 | Main Level Concrete Floor Slab | SC | 4 | NSPS |  |  | 80000 |  | Nobleton SPS Capital Project 1 |  | 0 | ROY-NOB-1391 | 00030062 |  |  |  |  | good | [5 empty] | 2031 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life.
6318 | Wet Well, Access, Hatch, Steel |  |  |  | 00029231 | Nobleton SPS Pumphouse | [5 empty] | 2009 |  | 48 |  | Area 6 Wastewater Treatment |  | Structural |  |  |  | OPERATING | W-WW | 3 | Wet Well Access Hatch | SC | 2 | NSPS |  |  | 6000 |  |  |  | 0 | ROY-NOB-1489 | 00030241 |  |  |  |  | fair | [6 empty] | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life.
7084 | Process Instrumentation, Communcation Antenna 2 |  |  |  | 00029225 | [6 empty] | 2009 |  | 9 | [9 empty] | 2 | Communication Antenna 2 | SIC | 1 | NSPS |  |  | 8000 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-0478 | [5 empty] | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
6395 | Process Instrumentation, BAS Panel Power Supply Aux/Control Transformer, Empire Controls Ltd., S/n :002-E, (120/24V, 15A, 1Ph), CCT No. 15 |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00183 |  |  |  |  | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | 002-E |  |  | OPERATING | W-WW | 2 | BAS Power Supply AUX/Control Transformer | SIC | 2 | NSPS |  |  | 1000 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-0693 | [5 empty] | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
7083 | Process Instrumentation, Communication Antenna 1 |  |  |  | 00029225 | [6 empty] | 2009 |  | 9 | [9 empty] | 3 | Communication Antenna 1 | SIC | 2 | NSPS |  |  | 8000 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-0496 | [5 empty] | Wire-Antenna connection is taped together. |  |  | Wire-antenna connection is taped together was observed. |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term.
7082 | Process Instrumentation, Monitor/Indicator, RFLM-1 Tank Fill Monitor, Clemmer |  |  |  | 00029225 | [6 empty] | 2009 |  | 9 | [9 empty] | 2 | RFLM-1 Tank Fill Monitor | SIC | 2 | NSPS |  |  | 2100 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-0494 | [5 empty] | Good | No Region Asset Tag. |  |  | No region asset tag was observed. |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
7040 | Process Instrumentation, Building Automation System (BAS) Remote Station Panel, Empire Controls Ltd., S/n : 001-E, (24V, 4A, 1Ph, CCT No. 15) |  |  |  | 00029228 | [6 empty] | 2009 |  | 9 |  |  |  |  | 001-E |  |  |  |  | 2 | Building Automation System (BAS) Remote Station Panel | SIC | 2 | NSPS |  |  | 11900 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-0696 | 00022712 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
6394 | Process Instrumentation, Network, Computer |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | 76487-OEM-0028092-70355 |  |  | OPERATING | W-WW | 3 | Computer | SIC | 1 | NSPS |  |  | 0 | Nobleton SPS Capital Project 1 |  |  | 0 |  | 00022713 |  |  |  |  | Asset not observed on site. |  |  | Asset not observed on site was observed. |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term.
6392 | Network, Monitor |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | MY20HVGS801165A |  |  | OPERATING | W-WW | 3 |  | SIC | 2 | NSPS |  |  | 0 | Nobleton SPS Capital Project 1 |  |  | 0 |  | 00022714 |  |  |  |  | Asset not observed on site. |  |  | Asset not observed on site was observed. |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term.
6396 | Process Instrumentation, Network, Printer |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M10115 |  |  |  |  | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | JNKA63216 |  |  | OPERATING | W-WW | 3 | Printer | SIC | 1 | NSPS |  |  | 0 | Nobleton SPS Capital Project 1 |  |  | 0 |  | 00022715 |  |  |  |  | Asset not observed on site. |  |  | Asset not observed on site was observed. |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term.
6378 | Process Instrumentation, Sump 1 Float Switch |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | [5 empty] | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control |  |  |  | OPERATING | W-WW | 2 | Sump 1 Float Switch | SIC | 1 | NSPS |  |  | 1900 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-0965 | 00022716 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
6379 | Process Instrumentation, Sump 2 Float Switch |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | [5 empty] | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control |  |  |  | OPERATING | W-WW | 2 | Sump 2 Float Switch | SIC | 1 | NSPS |  |  | 1900 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-0965 | 00022717 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
6377 | Process Instrumention, Sump 3 Float Switch |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | [5 empty] | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control |  |  |  | OPERATING | W-WW | 2 | Sump 3 Float Switch | SIC | 1 | NSPS |  |  | 1900 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-0965 | 00022718 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
6382 | Process Instrumentation, Sump 4 Float Switch |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | [5 empty] | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control |  |  |  | OPERATING | W-WW | 2 | Sump 4 Float Switch | SIC | 1 | NSPS |  |  | 1900 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-0965 | 00022719 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
6380 | Process Instrumentation, Flood Alarm & Float Switch |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | [5 empty] | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control |  |  |  | OPERATING | W-WW | 2 | Flood Alarm Float Switch | SIC | 2 | NSPS |  |  | 1900 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-1057 | 00022720 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
6384 | Process Instrumentation, Suction Line 1, Pressure Gauge |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00893 |  |  |  |  | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control |  |  |  | OPERATING | W-WW | 2 | Pump 1 Suction Pressure Gauge | SIC | 1 | NSPS |  |  | 630 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-1179 | 00022724 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
6383 | Process Instrumentation, Discharge Line 1 Pressure Gauge |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00893 |  |  |  |  | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control |  |  |  | OPERATING | W-WW | 2 | Pump 1 Discharge Pressure Gauge | SIC | 1 | NSPS |  |  | 630 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-1184 | 00022725 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
6376 | Process Instrumentation, Suction Line 2 Pressure Gauge, |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00893 |  |  |  |  | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control |  |  |  | OPERATING | W-WW | 2 | Pump 2 Suction Pressure Gauge | SIC | 1 | NSPS |  |  | 630 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-1189 | 00022726 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
6374 | Process Instrumentation, Discharge Line 2 Pressure Gauge, |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00893 |  |  |  |  | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control |  |  |  | OPERATING | W-WW | 2 | Pump 2 Discharge Pressure Gauge | SIC | 1 | NSPS |  |  | 630 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-1191 | 00022727 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
6375 | Process Instrumentation, Suction Line 3 Pressure Gauge |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00893 |  |  |  |  | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control |  |  |  | OPERATING | W-WW | 2 | Pump 3 Suction Pressure Gauge | SIC | 1 | NSPS |  |  | 630 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-1201 | 00022728 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
6381 | Process Instrumentation, Discharge Line 3 Pressure Gauge |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00893 |  |  |  |  | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control |  |  |  | OPERATING | W-WW | 2 | Pump 3 Discharge Pressure Gauge | SIC | 1 | NSPS |  |  | 630 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-1207 | 00022729 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
6390 | Process Instrumentation, Before Meter Upper DCW Pressure Gauge, TRERICE |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00893 |  |  |  |  | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control |  |  |  | OPERATING | W-WW | 2 | Before Meter Upper DCW Pressure Gauge | SIC | 1 | NSPS |  |  | 630 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-0873 | 00022794 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
6389 | Process Instrumentation, After Meter Lower DCW Pressure Gauge |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00893 |  |  |  |  | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control |  |  |  | OPERATING | W-WW | 3 | After Meter Lower DCW Pressure Gauge | SIC | 1 | NSPS |  |  | 630 | Nobleton SPS Capital Project 1 |  |  | 0 |  | 00022795 | [11 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the intermediate term.
6403 | Process Electrical, Netwrok, NBSSJA Ethernet Switch, Layer 3 Ethernet Switch, Interior PAC Panel, S/N: FOC1803Z3RU |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M01002 |  |  |  |  | 2015 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | FOC1803Z3RU |  |  | OPERATING | W-WW | 2 | NBSSJA Ethernet Switch | SIC | 2 | NSPS |  |  | 24800 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-0573 | 00025449 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
6398 | Process Instrumentation, Temperature Switch & Temeprature Low Alarm, Honeywell |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00076 | T631B |  |  | Temperature | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control |  |  |  | OPERATING | W-WW | 2 | Temperature Switch/Alarm | SIC | 1 | NSPS |  |  | 9000 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-0689 | 00029682 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
6505 | Automation, Controller, |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00547 |  |  |  |  | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control |  |  |  | OPERATING | W-WW | 3 |  | SIC | 1 | NSPS |  |  | 0 | Nobleton SPS Capital Project 1 |  |  | 0 |  | 00029683 | [11 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the intermediate term.
6435 | Process Instrumentation, ADP-2 ALARM DIALER PANEL, MAAK Technologies Group, S/N: W178-002-12 |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Electrical | W178-002-12 |  |  | OPERATING | W-WW | 2 | ADP-2 Alarm Dialer Panel | SIC | 2 | NSPS |  |  | 5900 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-0565 | 00029722 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
6393 | Process Instrumentation, Quad Gas II Gas Monitoring System for CH4, H2S, and O2, MSA, P/N: 215346, S/N: 145104-1, 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M10086 |  |  |  | CH4, H2S, O2 | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | 145104-1 |  |  | OPERATING | W-WW | 2 | Quad Gas II Gas Monitoring System | SIC | 3 | NSPS |  |  | 3750 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-0545 | 00029723 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
6397 | Process Instrumentation, DC RVLM 2 Tank Level Monitor & Indicator, Clemmer LS |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00309 |  |  |  |  | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control |  |  |  | OPERATING | W-WW | 2 | DC-RVLM-2 Tank Monitor | SIC | 2 | NSPS |  |  | 2100 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-0713 | 00029736 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
6411 | Process Instrumentation, Security System (including Card Readers, Panels, Networks, and Key Pads) |  |  |  | 00029229 | Nobleton SPS PH Stairwell (404) | M00757 |  |  |  |  | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Health and Safety |  |  |  | OPERATING | W-WW | 2 | Security System | SIC | 2 | NSPS |  |  | 50000 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-7987 | 00029741 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
6425 | Process Instrumentation, Temperature Switch & Temeprature Low Alarm, Honeywell, 1 Unit |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00076 |  |  |  |  | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 2 | Temperature Switch/Alarm | SIC | 1 | NSPS |  |  | 9000 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-0870 | 00029746 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
6420 | Process Instrumentation, Temperature Switch & Temeprature Low Alarm, Honeywell, 1 Unit |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00076 |  |  |  |  | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 2 | Temperature Switch/Alarm | SIC | 1 | NSPS |  |  | 9000 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-1018 | 00029765 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
6388 | Nobleton SPS, Sampler, Raw |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00526 |  |  |  |  | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | 208E02193 |  |  | OPERATING | W-WW | 3 | Sampler | SIC | 1 | NSPS |  |  | 0 | Nobleton SPS Capital Project 1 |  |  | 0 | roy-nob-1129 | 00031101 | [11 empty] | The asset was assumed to be in fair condition. Asset to be replaced in the intermediate term.
6385 | Process Instrumentation, Monitor/Sensor, NBSSJA_RSP_G021, A09-3014618-30-001 O2 Gas Monitor, MSA, Ultima XE, |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M10086 | ULTIMAX |  |  | O2 Gas | 2009 |  | 3 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | A09-3014616-30-001 |  |  | OPERATING | W-WW | 3 | O2 Gas Monitor | SIC | 3 | NSPS |  |  | 19800 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-1048 | 00042930 |  |  |  |  | Gas Monitor connections have sustained minor corrosion |  |  | Gas monitor connections have sustained minor corrosion was observed. |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term.
6386 | Process Instrumentation , Sensor/Monitor, NBSSJA_RSP_GH2S1, A09-3014618-20-001 H2S Gas Monitor, MSA, Ultima XE |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M10086 | ULTIMAX |  |  | H2S Gas | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | A09-3014616-20-001 |  |  | OPERATING | W-WW | 2 | H2S Gas Monitor | SIC | 3 | NSPS |  |  | 23700 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-1046 | 00042931 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
6387 | Process Instrumentation, Sensor/Monitor, NBSSJA_RSP_GLEL1, A09-3014616-10-001 CH4 & LEL Gas Monitorr, MSA, Ultima XE, |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M10086 | ULTIMAX |  |  | LEL Gas | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | A09-3014616-10-001 |  |  | OPERATING | W-WW | 2 | CH4 Gas Monitor | SIC | 3 | NSPS |  |  | 23700 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-1024 | 00042932 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
7085 | Process Instrumentation, Extreme Environment weather Monitoring System (HSPA System with Telemetry), Hoskin Scientific, Model: HSPALINK-E14, |  |  |  | 00029225 | [6 empty] | 2009 |  | 3 | [9 empty] | 3 | Extreme Environment Monitoring System | SIC | 3 | NSPS |  |  | 12600 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-0503 | 00075982 |  |  |  |  | Rust formation on base metal structure. |  |  | Rust formation on base metal structure was observed. |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term.
6407 | Process Instrumentation, Monitor/Indicator, Level, NBSSJA_GEN_TK1_LIT1 Diesel Tank Level Indicator & Capacitive Level Indicator |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M10252 |  | Echopod DL24-0 |  | Level | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | 111215-002559 |  |  | OPERATING | W-WW | 2 | Diesel Tank Level Indicator NBSSJA_GEN_TK1_LIT1 | SIC | 2 | NSPS |  |  | 2100 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-0715 | 00077601 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
6391 | Process Instrumentation, NBSSJA_RSP_FIT1 Station Discharge Magnetic Flowmeter, Endress+Hauser, ,S/N: K712f319000, 1 Unit |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00405 | Promag 400 (5X4CXX-1D93/156) | Promag W | C100A316000 | Flow | 2015 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | K712F319000 |  |  | OPERATING | W-WW | 2 | Discharge Header Flow Meter Transmitter | SIC | 2 | NSPS |  |  | 47500 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-0909 | 00078431 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
6401 | Process Instrumentation, NBSSJA PAC Panel OIT Computer, Advantech, S/N: ACF6003575 |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M10189 |  |  |  |  | 2015 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | ACF6003575 |  |  | OPERATING | W-WW | 2 | NBSSJA PAC Panel OIT Computer | SIC | 2 | NSPS |  |  | 7000 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-0573 | 00078432 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
6400 | Process Instrumentation, NBSSJA PAC Panel OIT Monitor, Advantech, S/N: KSA10698933 |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M10189 |  |  |  |  | 2015 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | KSA1068933 |  |  | OPERATING | W-WW | 2 | NBSSJA PAC Panel OIT Monitor | SIC | 2 | NSPS |  |  | 7000 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-0573 | 00078433 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
6402 | Process Instrumentation, NBSSJA Uninterruptible Power Supply (UPS) for PAC Tower/PAC Panel, APC, S/N: GJ255A0008 |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M10181 |  |  |  |  | 2015 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | GJ255A0008 |  |  | OPERATING | W-WW | 2 | NBSSJA UPS for PAC Tower/PAC Panel | SIC | 2 | NSPS |  |  | 8000 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-0573 | 00078434 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
6406 | Process Instrumentation, NBSSJA_WWEL_LIT2 Wet Well 1 Hydrostatic Level Indicator, Endress + Hauser, RIA 452, S/N: K1005904264 |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00405 | RIA452 | FMX21-97D7/0 | E600B215122 | Level | 2015 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | K1005904264 |  |  | OPERATING | W-WW | 2 | NBSSJA_WWEL_LIT2 Wet Well 1 Hydrostatic Level Indicator | SIC | 2 | NSPS |  |  | 2100 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-0671 | 00078443 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
6405 | Process Instrumentation, NBSSJA_WWEL_LIT1, Wet Well 1 Ultrasonic Level Transmitter, Endress+Hauser, FMU90, S/N: K1003E150E6, 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00405 | PROSONIC S FMU90 (N12EA161AA1A) | Prosonic FDU91 |  | Level | 2015 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | K1003E150E6 |  |  | OPERATING | W-WW | 2 | NBSSJA_WWEL_LIT1 Wet Well 1 Ultrasonic Level Transmitter | SIC | 2 | NSPS |  |  | 19900 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-0670 | 00078444 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
6399 | Process Instrumentation, NBSSJA Backup Control Panel, Summa Engineering Ltd, M/N: NBSSJA_BKUP, S/N: 14E-088/NBSSJA_BKUP, (120VAC 1Ph 60Hz) , 1 Unit, Enclosure Type 12 |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | 1002018 |  |  |  |  | 2015 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | 14E-088/NBSSJA_BKUP |  |  | OPERATING | W-WW | 2 | NBSSJA Backup Control Panel, | SIC | 3 | NSPS |  |  | 15000 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-0666 | 00078445 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
6404 | Process Electrical, Netwrok, NBSSJA Radio 1, 900MHZ Radio, Interior PAC Panel, S/N: 1808703 |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00455 |  |  |  |  | 2015 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | 1808703 |  |  | OPERATING | W-WW | 2 | NBSSJA Radio 1 | SIC | 2 | NSPS |  |  | 24800 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-0573 | 00078456 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
6408 | Process Instrumentation, NBSS_WWELL_LSOF Wet Well High High Level Switch |  |  |  | 00029231 | Nobleton SPS PH Wet Well Chamber - Upper Level (406) | M00061 | ENM-10 |  |  | High High Level | 2009 |  | 9 |  | Area 6 Wastewater Treatment |  | Instrumentation and Control |  |  |  | OPERATING | W-WW | 3 | NBSS_WWELL_LSOF Wet Well High High Level Switch | SIC | 2 | NSPS |  |  | 1900 | Nobleton SPS Capital Project 1 |  |  | 0 |  | 00080339 |  |  |  |  | Asset not observed on site. |  |  | Asset not observed on site was observed. |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term.
7092 | Process Instrumentation, BAS Panel Power Supply UPS , APC, |  |  |  | 00029228 | [6 empty] | 2009 |  | 9 | [9 empty] | 2 | BAS Power Supply AUX/Control Transformer | SIC | 2 | NSPS |  |  | 10000 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-0706 | [5 empty] | Good | No York Region Asset Tag |  |  | No york region asset tag was observed. |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
7029 |  |  |  |  | 00029225 | [6 empty] | 2009 |  | 8 | [9 empty] | 3 | Fire Hydrant fire hydrant | SW | 2 | NSPS |  |  | 4000 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-1247 | [5 empty] | Localized paint peeling and minor corrosion |  |  | Localized paint peeling and minor corrosion was observed. |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term.
7028 |  |  |  |  | 00029225 | [6 empty] | 2009 |  | 8 | [9 empty] | 3 | Driveway (Asphalt) | SW | 1 | NSPS |  |  | 41500 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-1287 | [5 empty] | some minor asphalt cracking | Minor cracking at gate | Moderate crack with vegetation along length of driveway and at area in front of station entrance | Some minor asphalt cracking was observed. | Minor cracking was observed at gate. | Moderate crack with vegetation along length of driveway and at area in front of station entrance was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term.
7031 |  |  |  |  | 00029225 | [6 empty] | 2009 |  | 8 | [9 empty] | 2 | Maintenance Hole Cover | SW | 1 | NSPS |  |  | 900 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-1225 | [5 empty] | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.
7030 | chainlink |  |  |  | 00029225 | [6 empty] | 2009 |  | 8 | [9 empty] | 3 | Fencing | SW | 1 | NSPS |  |  | 20000 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-1262 | [5 empty] | minor damage at the bottom of some part | very minor deformations throughout |  | Minor damage at the bottom of some part was observed. | Very minor deformations throughout was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term.
6326 | Wet Well Concrete Pad, Other Sitework, |  |  |  | 00029225 | Nobleton SPS Pumphouse | [5 empty] | 2009 |  | 8 |  | Area 6 Wastewater Treatment |  | Siteworks |  |  |  | OPERATING | W-WW | 2 | Wet Well Concrete Pad | SW | 2 | NSPS |  |  | 5100 | Nobleton SPS Capital Project 1 |  |  | 0 | ROY-NOB-1563 | 00030242 |  |  |  |  | Good | [6 empty] | The asset was observed to be in good condition. Asset to be replaced in the intermediate term.