## Sheet1
seqNum | facility | CategoryCode | assetName | LocationTag | Description | installYear | remainingESL | repCost | InspectionYear | CalcProcess | Process | building | inspectorName | assetTag | LocationORIGINAL | installationDate | condition | COF | defect1 | defect2 | defect3 | observations | RehabRepairCost | RehabRepairYear | RehabRepairCost2 | RehabRepairYear2 | photoName | repProjectName | rehabProjectName | rehab2ProjectName | LifeCycleCategory | TransmitterModel | TransducerModel | TransducerSerial | Status | rehabComment1 | rehabCost1 | rehabComment2 | rehabCost2 | defect1Input | defect2Input | defect3Input
4463 | SPS2 | PM | Wastewater Pump 2 | 00000005 | Submersible, centrifugal wastewater pump, 5.6 kW, 1740 rpm, 575/3/60; by Flygt model 3127-960; explosion proof enclosure (Class 1, Zone 1); | 1987 | 6 | 25000 | 0 | [7 empty] | 2 | 5 |  | Needs regular maintenance was observed. |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_7204 | SPS2 Capital Project 1 | [11 empty] | good | needs regular maintenance
4470 | SPS2 | SW | Catchbasin | 00000004 |  | 1978 | 6 | 8000 | 0 | [7 empty] | 3 | 2 | Debris was observed on the inlet of the catch basin. fair condition was observed. |  |  | The asset was observed to be in fair condition.Clear the debris from the catch basin inlet Asset to be replaced in the intermediate term. | 100 |  |  |  | IMG_2050 | SPS2 Capital Project 1 | [7 empty] | Clear the debris from the catch basin inlet | 100 |  |  | Debris was observed on the inlet of the catch basin. Fair condition.
4471 | SPS2 | SW | Maintenance Hole No.1 | 00000004 |  | 1981 | 6 | 30000 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_2051 | SPS2 Capital Project 1 | [11 empty] | good
4472 | SPS2 | SW | Maintenance Hole No.2 | 00000004 |  | 1984 | 6 | 30000 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_2055 | SPS2 Capital Project 1 | [11 empty] | good
4473 | SPS2 | SW | Swale | 00000004 | Approximately 60 m in length, 1 m in length, 0.5 m in depth | 1978 | 6 | 7200 | 0 | [7 empty] | 3 | 2 | Minor amount of debris was observed in the swale. good condition was observed. |  |  | The asset was observed to be in fair condition.Clear the debris from the swale. Asset to be replaced in the intermediate term. | 2500 |  |  |  | IMG_2048 | SPS2 Capital Project 1 | [7 empty] | Clear the debris from the swale. | 2500 |  |  | Minor amount of debris was observed in the swale. Good condition.
4474 | SPS2 | SW | Gravel road | 00000004 | Approximately 40m2 of gravel road | 1978 | 6 | 4800 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_2044 | SPS2 Capital Project 1 | [11 empty] | good
4491 | SPS2 | PM | Wastewater Pump 1 | 00000005 | Submersible, centrifugal wastewater pump #1, 5.6 kW, 1740 rpm, 575/3/60; by Flygt model 3127-960; explosion proof enclosure (Class 1, Zone 1); | 1978 | 6 | 25000 | 0 | [7 empty] | 2 | 5 |  | Need regular maintenance was observed. |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_7206 | SPS2 Capital Project 1 | [11 empty] | good | need regular maintenance
4492 | SPS2 | PM | Pump 1 Discharge Gate Valve | 00000005 | Gate valve, isolation of Pump #1 discharge line, 150 DIA, flanged, manual nut operator, valve box and extended stem. | 1978 | 2 | 3000 | 0 | [7 empty] | 3 | 4 | Severely corroded was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_0896 | SPS2 Capital Project 1 | [11 empty] | severely corroded
4493 | SPS2 | PM | Pump 2 Discharge Gate Valve | 00000005 | Gate valve, isolation of Pump #2 discharge line, 150 DIA, flanged, manual nut operator, valve box and extended stem. | 1978 | 2 | 3000 | 0 | [7 empty] | 3 | 4 | Severely corroded was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_0896 | SPS2 Capital Project 1 | [11 empty] | severely corroded
4494 | SPS2 | PM | Pump 1 Discharge Check Valve | 00000005 | Check valve, in Pump #1 discharge line, 150 DIA, flanged. | 1978 | 2 | 3500 | 0 | [7 empty] | 3 | 4 | Old style valve was observed. | Severely corroded was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_7190 | SPS2 Capital Project 1 | [11 empty] | Old style valve | Severely corroded
4495 | SPS2 | PM | Pump 2 Discharge Check Valve | 00000005 | Check valve, in Pump #2 discharge line, 150 DIA, flanged. | 1978 | 2 | 3500 | 0 | [7 empty] | 3 | 4 | Old style valve was observed. | Severely corroded was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_7190 | SPS2 Capital Project 1 | [11 empty] | Old style valve | severely corroded
4496 | SPS2 | PM | Overflow Pipe | 00000005 | 375 DIA Overflow pipe to Lake, with manual gate to open-close; overflow pipe c/w 15 DIA steel bars at outlet to lake. | 1978 | 2 | 10000 | 0 | [7 empty] | 3 | 3 | Fair condition; some corrosion at the outlet, at lake was observed. | No backflow preventing mechanism in place, replacement; a backflow preventing mechanism shall be installed at the wet well was observed. | Needs cleaning from deposits was observed. | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_0884 | SPS2 Capital Project 1 | [11 empty] | fair condition; some corrosion at the outlet, at lake | no backflow preventing mechanism in place, replacement; a backflow preventing mechanism shall be installed at the wet well. | needs cleaning from deposits
4497 | SPS2 | PM | Wet Well Piping | 00000005 | Pump discharge pipes of 150 DIA and common 200 DIA forcemain | 1978 | 2 | 10000 | 0 | [7 empty] | 3 | 4 | Severely corroded was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_0910 | SPS2 Capital Project 1 | [11 empty] | severely corroded
4498 | SPS2 | PM | Bypass Gate Valve | 00000004 | Pumping station bypass gate valve in MH, 100 DIA flanged c/w 100 DIA, 90 deg elbow (up) and blind flange. | 1978 | 2 | 3000 | 0 | [7 empty] | 3 | 3 | Mh was flooded to view the condition was observed. | Gravity drain c/w backflow preventing mechanism shall be installed to the wet well was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_0882 | SPS2 Capital Project 1 | [11 empty] | MH was flooded to view the condition | Gravity drain c/w backflow preventing mechanism shall be installed to the wet well.
4520 | SPS2 | PM | Gate Valve | 00000004 | Force main 150 DIA isolation gate valve; located in bypass valve MH. | 1978 | 2 | 3000 | 0 | [7 empty] | 3 | 4 | Not viewed, flooded mh was observed. | A gravity drain c/w backflow preventing mechanism shall be installed from the mh to the wet well was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_0882 | SPS2 Capital Project 1 | [11 empty] | Not viewed, Flooded MH | A gravity drain c/w backflow preventing mechanism shall be installed from the MH to the wet well
4578 | SPS2 | SIC | PLC RPU601 | 00000006 |  | 2014 | 8 | 60000 | 0 | [7 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_4962 | SPS2 Capital Project 1 | [11 empty] | good
4579 | SPS2 | SIC | Auto Dialer | 00000006 |  | 2014 | 8 | 6000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | PXL_20210518_132012403 | SPS2 Capital Project 1 | [11 empty] | good
4580 | SPS2 | SIC | level transmitter | 00000006 |  | 2014 | 8 | 12000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | PXL_20210518_131959660 | SPS2 Capital Project 1 | [11 empty] | good
4581 | SPS2 | ES | standby generator | 00000006 | 15kW diesel generator | 1979 | 6 | 40000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | PXL_20210518_133015975 | SPS2 Capital Project 1 | [11 empty] | good
4582 | SPS2 | ES | outdoor lights | 00000004 | wall pack | 1979 | 6 | 500 | 0 | [7 empty] | 3 | 2 | Black paint was observed over the fixture was observed. | To be replaced with leds in next upgrade was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5019 | SPS2 Capital Project 1 | [11 empty] | black paint was observed over the fixture | to be replaced with LEDs in next upgrade
4583 | SPS2 | ES | Exit sign | 00000006 |  | 2014 | 18 | 500 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. |  |  |  |  | IMG_5023 | SPS2 Capital Project 2 | [11 empty] | good
4585 | SPS2 | ES | Hydro Meter |  |  | 1979 | 2 | 5000 | 0 | [7 empty] | 3 | 3 |  | To be cleaned from spider webs and debris was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_5018 | SPS2 Capital Project 1 | [11 empty] | fair | to be cleaned from spider webs and debris
4586 | SPS2 | ES | Automatic Transfer Switch Panel | 00000006 |  | 1979 | 6 | 30000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5027 | SPS2 Capital Project 1 | [11 empty] | good
4587 | SPS2 | ES | Main Breaker | 00000006 |  | 1979 | 6 | 10000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | PXL_20210518_132005693 | SPS2 Capital Project 1 | [11 empty] | good
4588 | SPS2 | ES | Lighting Transformer | 00000006 |  | 1979 | 6 | 8000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5028 | SPS2 Capital Project 1 | [11 empty] | good
4589 | SPS2 | ES | Generator Room Lighting | 00000006 | 3 linear fixtures | 1979 | 6 | 1200 | 0 | [7 empty] | 2 | 2 |  | To be replaced with leds in next upgrade was observed. |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5021 | SPS2 Capital Project 1 | [11 empty] | good | to be replaced with LEDs in next upgrade
4590 | SPS2 | ES | 600V distribution panel | 00000006 |  | 1979 | 6 | 14000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | PXL_20210518_131731363 | SPS2 Capital Project 1 | [11 empty] | good
4591 | SPS2 | ES | Pump Control Panel | 00000006 |  | 1979 | 6 | 21000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | PXL_20210518_132059476 | SPS2 Capital Project 1 | [11 empty] | good
4592 | SPS2 | ES | Lighting Panel | 00000006 |  | 1979 | 6 | 5000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | PXL_20210518_132017083 | SPS2 Capital Project 1 | [11 empty] | good
4593 | SPS2 | SIC | temperature switch | 00000006 |  | 2010 | 10 | 1500 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5025 | SPS2 Capital Project 1 | [11 empty] | good
4594 | SPS2 | SIC | Anthenna | 00000004 |  | 2014 | 8 | 8000 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | [5 empty] | SPS2 Capital Project 1 | [11 empty] | good
4629 | SPS2 | BM | Intake damper | 00000003 | damper | 1984 | 2 | 2000 | 0 | [7 empty] | 3 | 3 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_6110 | SPS2 Capital Project 1
4630 | SPS2 | BM | Unit Heater | 00000006 | unit heater, chromalox, BUH-05, , 5kw | 1984 | 6 | 3000 | 0 | [7 empty] | 3 | 2 | Unit appears to be orignial with building was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_6112 | SPS2 Capital Project 1 | [11 empty] | unit appears to be orignial with building.
4631 | SPS2 | BM | Diesel fuel system | 00000006 | fuel tank and piping | 2007 | 16 | 20000 | 0 | [7 empty] | 3 | 3 | It was noted on site that the diesel fuel system is not up to current tssa regulations and will need to be upgraded in the future. ab inspection report provided detailed deficiency list was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term. |  |  |  |  | IMG_6119 | SPS2 Capital Project 2 | [11 empty] | It was noted on site that the diesel fuel system is not up to current TSSA regulations and will need to be upgraded in the future. AB inspection report provided detailed deficiency list.
4632 | SPS2 | BM | Exhaust fan | 00000006 | exhaust fan, greenheck, SDE-12-24-D, 1/20HP | 1984 | 6 | 2000 | 0 | [7 empty] | 3 | 2 | Fan was in fair condition but has neared its end of life was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_6129 | SPS2 Capital Project 1 | [11 empty] | Fan was in fair condition but has neared its end of life.
4633 | SPS2 | BM | Generator Exhaust | 00000006 | ductwork and dampers | 1984 | 2 | 7500 | 0 | [7 empty] | 3 | 4 | Exhaust system to be replaced with generator replacement was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_6128 | SPS2 Capital Project 1 | [11 empty] | Exhaust system to be replaced with generator replacement.
4635 | SPS2 | BM | Eyewash combo | 00000006 |  | 2000 | 9 | 1000 | 0 | [7 empty] | 3 | 2 | Emergency eyewashes are required to provide tepid water. no water heater was installed. no instantaneous heater would be required was observed. |  | Eyewash sink combo looked to be in good condition was observed. | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 3000 |  |  |  | IMG_6139 | SPS2 Capital Project 1 | [8 empty] | 3000 |  |  | Emergency eyewashes are required to provide tepid water. No water heater was installed. No instantaneous heater would be required. |  | Eyewash sink combo looked to be in good condition.
4636 | SPS2 | BM | Backflow preventer | 00000006 | backflow, conbraco, , 1" | 2010 | 19 | 2500 | 0 | [7 empty] | 3 | 2 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the long term. |  |  |  |  | IMG_6141 | SPS2 Capital Project 2
4677 | SPS2 | AC | Generator Room Exterior Brick Veneer | 00000006 |  | 1987 | 6 | 10000 | 0 | [7 empty] | 3 | 1 | Step cracking in mortar typical was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_7163 | SPS2 Capital Project 1 | [11 empty] | step cracking in mortar typical
4678 | SPS2 | AC | Generator Room Access Door | 00000006 |  | 1987 | 6 | 3500 | 0 | [7 empty] | 3 | 1 | Weathered paint was observed on exterior. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_7163 | SPS2 Capital Project 1 | [11 empty] | weathered paint on exterior
4679 | SPS2 | AC | Generator Room Roofing System | 00000006 |  | 1987 | 6 | 5000 | 0 | [7 empty] | 3 | 2 | Vegetation on roof was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_7164 | SPS2 Capital Project 1 | [11 empty] | vegetation on roof
4680 | SPS2 | AC | Generator Room Wall and Ceiling Paint | 00000006 |  | 1987 | 6 | 3000 | 0 | [7 empty] | 3 | 1 |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_7215 | SPS2 Capital Project 1 | [11 empty] | fair
4681 | SPS2 | SC | Wet Well Precast Concrete Structure | 00000005 |  | 1987 | 26 | 130000 | 0 | [7 empty] | 3 | 4 | Efflorescence/leakage around ladder bolt was observed. |  |  | The asset was observed to be in fair condition. Provisions for structural repairs. Asset to be replaced at the end of remaining service life. |  | 2023 |  | 2038 | IMG_7181 |  | SPS2 Capital Project 1 | SPS2 Capital Project 2 | [9 empty] | efflorescence/leakage around ladder bolt
4682 | SPS2 | SC | Wet Well Aluminum Platform | 00000005 |  | 1987 | 26 | 6000 | 0 | [7 empty] | 3 | 3 |  |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7181 | [12 empty] | fair
4683 | SPS2 | SC | Wet Well Access Ladder | 00000005 | Exterior to platform | 1987 | 26 | 5000 | 0 | [7 empty] | 3 | 3 |  |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7194 | [12 empty] | fair
4684 | SPS2 | SC | Wet Well Access Ladder | 00000005 | Platform to base | 1987 | 26 | 5000 | 0 | [7 empty] | 3 | 3 |  |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7191 | [12 empty] | fair
4685 | SPS2 | SC | Wet Well Access Hatch | 00000005 |  | 1987 | 26 | 5000 | 0 | [7 empty] | 3 | 3 |  |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7168 | [12 empty] | fair
4686 | SPS2 | SC | Wet Well Pump Hatch | 00000005 |  | 1987 | 26 | 5000 | 0 | [7 empty] | 3 | 3 |  |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7168 | [12 empty] | fair
4687 | SPS2 | SC | Wet Well Pump Hatch | 00000005 |  | 1987 | 26 | 5000 | 0 | [7 empty] | 3 | 3 |  |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7168 | [12 empty] | fair
4688 | SPS2 | SC | Generator Building Concrete Foundation | 00000006 |  | 1987 | 26 | 30000 | 0 | [7 empty] | 3 | 4 |  |  |  | The asset was observed to be in fair condition. Provisions for structural repairs. Asset to be replaced at the end of remaining service life. |  | 2023 |  | 2038 |  |  | SPS2 Capital Project 1 | SPS2 Capital Project 2 | [9 empty] | fair
4689 | SPS2 | SC | Generator Building Concrete Floor Slab | 00000006 |  | 1987 | 26 | 8000 | 0 | [7 empty] | 3 | 4 |  |  |  | The asset was observed to be in fair condition. Provisions for structural repairs. Asset to be replaced at the end of remaining service life. |  | 2023 |  | 2038 | IMG_7216 |  | SPS2 Capital Project 1 | SPS2 Capital Project 2 | [9 empty] | fair
4690 | SPS2 | SC | Generator Building Masonry Blockwall | 00000006 |  | 1987 | 26 | 15000 | 0 | [7 empty] | 3 | 4 | Minor step cracking in mortar was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7214 | [12 empty] | minor step cracking in mortar
4691 | SPS2 | SC | Generator Building Concrete Roof | 00000006 |  | 1987 | 26 | 10000 | 0 | [7 empty] | 3 | 4 |  |  |  | The asset was observed to be in fair condition. Provisions for structural repairs. Asset to be replaced at the end of remaining service life. |  | 2023 |  | 2038 | IMG_7215 |  | SPS2 Capital Project 1 | SPS2 Capital Project 2 | [9 empty] | fair
4736 | SPS2 | SC | Wet Well Davit Base Socket | 00000005 |  | 1987 | 26 | 5000 | 0 | [7 empty] | 3 | 3 |  |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7168 | [12 empty] | fair