## Sheet1
seqNum | facility | CategoryCode | assetName | LocationTag | Description | installYear | remainingESL | repCost | InspectionYear | CalcProcess | Process | building | inspectorName | assetTag | LocationORIGINAL | installationDate | condition | COF | defect1 | defect2 | defect3 | observations | RehabRepairCost | RehabRepairYear | RehabRepairCost2 | RehabRepairYear2 | photoName | repProjectName | rehabProjectName | rehab2ProjectName | LifeCycleCategory | TransmitterModel | TransducerModel | TransducerSerial | Status | rehabComment1 | rehabCost1 | rehabComment2 | rehabCost2 | defect1Input | defect2Input | defect3Input | InstType | InstMeva | ServiceArea | FacilityType | SerialNo | Parent | RotatingItem | Site | manufacturer
4475 | SPS7 | SW | Maintenance Hole No.1 | 7 |  | 1999 | 6 | 30000 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_2068 | SPS7 Capital Project 1 | [11 empty] | good
4476 | SPS7 | SW | Maintenance Hole No.2 | 7 |  | 1979 | 6 | 30000 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_2078 | SPS7 Capital Project 1 | [11 empty] | good
4477 | SPS7 | SW | Pavement | 7 | Approximately 75 m2 of pavement for access road | 1979 | 6 | 9750 | 0 | [7 empty] | 3 | 2 | Minor cracks observed on the pavement. good condition was observed. |  |  | The asset was observed to be in fair condition.Asphalt resurfacing Asset to be replaced in the intermediate term. | 6375 |  | 4900 |  | IMG_2074 | SPS7 Capital Project 1 | [7 empty] | Asphalt resurfacing | 6375 | Minor crack repair/filling | 4900 | Minor cracks observed on the pavement. Good condition.
4478 | SPS7 | SW | Swale No.1 | 7 | Approximately 4 m in length, 1 m in width and 0.5 m in depth | 1979 | 6 | 500 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition.Clearing debris from the swale Asset to be replaced in the intermediate term. | 150 |  |  |  | IMG_2067 | SPS7 Capital Project 1 | [7 empty] | Clearing debris from the swale | 150 |  |  | good
4479 | SPS7 | SW | Swale No.2 | 7 | Approximately 7.5 m in length, 1 m in width and 0.5 m in depth | 1979 | 6 | 900 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition.Clearing debris from the swale Asset to be replaced in the intermediate term. | 320 |  |  |  | IMG_2065 | SPS7 Capital Project 1 | [7 empty] | Clearing debris from the swale | 320 |  |  | good
4480 | SPS7 | SW | Stormwater Culvert | 7 | Approximately 6.5 m in length and 400 mm in diameter | 1979 | 6 | 5400 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_2066 | SPS7 Capital Project 1 | [11 empty] | good
4506 | SPS7 | PM | Wastewater Pump 1 | 10 | Submersible, dry pit, centrifugal wastewater pump, 22 kW, 1750 rpm, 600/3/60; by Flygt model 3170.180; explosion proof enclosure (Class 1, Zone 1); | 1979 | 6 | 35000 | 0 | [7 empty] | 2 | 4 |  | Needs regular maintenance was observed. |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_0969 | SPS7 Capital Project 1 | [11 empty] | good | needs regular maintenance
4507 | SPS7 | PM | Wastewater Pump 2 | 10 | Submersible, dry pit, centrifugal wastewater pump, 22 kW, 1750 rpm, 600/3/60; by Flygt model 3170.180; explosion proof enclosure (Class 1, Zone 1); | 1979 | 6 | 35000 | 0 | [7 empty] | 2 | 4 |  | Needs regular maintenance was observed. |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_0957 | SPS7 Capital Project 1 | [11 empty] | good | needs regular maintenance
4508 | SPS7 | PM | Pump 1 Suction Gate Valve | 10 | Isolation gate valve, 200 DIA, Flanged, NRS, Pump #1 suction line, by Seguro | 1979 | 2 | 3000 | 0 | [7 empty] | 3 | 4 | Fair condition was observed. | Maintenance was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_0994 | SPS7 Capital Project 1 | [11 empty] | Fair Condition | maintenance
4509 | SPS7 | PM | Pump 1 Discharge Gate Valve | 10 | Isolation gate valve, Pump #1 discharge line, 200 DIA, flanged, NRS, by Seguro | 1979 | 2 | 3000 | 0 | [7 empty] | 3 | 4 | Fair condition was observed. | Maintenance was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_0996 | SPS7 Capital Project 1 | [11 empty] | Fair Condition | maintenance
4510 | SPS7 | PM | Pump 1 Discharge Swing Check Valve | 10 | AWWA Swing Check Valve, with lever and spring, Pump #1 discharge line, 200 DIA, flanged, by Kennedy | 1985 | 2 | 5000 | 0 | [7 empty] | 3 | 4 | Fair condition was observed. | Maintenance was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_0997 | SPS7 Capital Project 1 | [11 empty] | Fair Condition | maintenance
4511 | SPS7 | PM | Pump 2 Discharge Swing Check Valve | 10 | AWWA Swing Check Valve, with lever and spring, Pump #2 discharge line, 200 DIA, flanged, by Kennedy | 1985 | 2 | 5000 | 0 | [7 empty] | 3 | 4 | Fair condition was observed. | Maintenance was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_0955 | SPS7 Capital Project 1 | [11 empty] | Fair Condition | maintenance
4512 | SPS7 | PM | Pump 2 Suction Gate Valve | 10 | Isolation gate valve, 200 DIA, Flanged, NRS, Pump #2 suction line, by Seguro | 1979 | 2 | 3000 | 0 | [7 empty] | 3 | 4 | Fair condition was observed. | Maintenance was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_0965 | SPS7 Capital Project 1 | [11 empty] | Fair condition | maintenance
4513 | SPS7 | PM | Pump 2 Discharge Gate Valve | 10 | Isolation gate valve, Pump #2 discharge line, 200 DIA, flanged, NRS, by Clow | 1979 | 2 | 3000 | 0 | [7 empty] | 3 | 4 | Fair condition was observed. | Maintenance was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_0983 | SPS7 Capital Project 1 | [11 empty] | Fair condition | maintenance
4514 | SPS7 | PM | Discharge piping | 10 | 200 DIA suction and discharge piping, DI, Victaulic couplings | 1979 | 2 | 10000 | 0 | [7 empty] | 3 | 4 | Fair condition was observed. | Maintenance was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_1005 | SPS7 Capital Project 1 | [11 empty] | Fair condition | maintenance
4515 | SPS7 | PM | Bypass Gate Valve | 7 | Bypass gate valve in bypass MH, 100 DIA flanged c/w 100 DIA, 90 deg elbow (up) and blind flange. | 1979 | 2 | 3000 | 0 | [7 empty] | 3 | 3 | Fair condition was observed. | Backflow preventing mechanism shall be installed in the drain to the wet well was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_0933 | SPS7 Capital Project 1 | [11 empty] | Fair condition | backflow preventing mechanism shall be installed in the drain to the wet well.
4516 | SPS7 | PM | Overflow | 8 | 400 DIA overflow pipe with manual gate to open-close; CPM pipe c/w 15 DIA steel bars at outlet, | 1979 | 2 | 10000 | 0 | [7 empty] | 3 | 3 | Fair condition was observed. | Maintenance; a backflow preventing mechanism shall be installed in the wet well overflow was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_7253 | SPS7 Capital Project 1 | [11 empty] | Fair condition | maintenance; a backflow preventing mechanism shall be installed in the wet well overflow.
4517 | SPS7 | PM | Bar screen and trash basket | 8 | Bar screen and trash basket. | 1979 | 2 | 8000 | 0 | [7 empty] | 3 | 3 | Fair condition was observed. | Maintenance was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_7252 | SPS7 Capital Project 1 | [11 empty] | fair condition | maintenance
4518 | SPS7 | PM | Gate valve | 7 | Force main 200 DIA isolation gate valve; NRS, by Seguro, located in pass valve MH. | 1979 | 2 | 3000 | 0 | [7 empty] | 3 | 4 | Goodcondition was observed. | Maintenance was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_0933 | SPS7 Capital Project 1 | [11 empty] | goodcondition | maintenance
4549 | SPS7 | ES | outdoor lighting | 7 | 3 wall pack fixtures | 1987 | 6 | 1500 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5034 | SPS7 Capital Project 1 | [11 empty] | good
4550 | SPS7 | ES | hydro meter | 7 | hydro meter | 2014 | 18 | 5000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. |  |  |  |  | IMG_5037 | SPS7 Capital Project 2 | [11 empty] | good
4551 | SPS7 | ES | exit sign | 7 | exit sign | 2014 | 18 | 500 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. |  |  |  |  | IMG_5038 | SPS7 Capital Project 2 | [11 empty] | good
4552 | SPS7 | ES | main level lighting | 9 | 4 linear fluroscent | 2014 | 18 | 1600 | 0 | [7 empty] | 4 | 2 | Fixture above mcc did not turn on was observed. | To be replaced with leds in next upgrade was observed. |  | The asset was observed to be in poor condition. Asset to be replaced in the long term. |  |  |  |  | IMG_5041 | SPS7 Capital Project 2 | [11 empty] | fixture above MCC did not turn on | to be replaced with LEDs in next upgrade
4553 | SPS7 | ES | automatic transfer switch | 9 | automatic transfer switch | 1987 | 6 | 30000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5043 | SPS7 Capital Project 1 | [11 empty] | good
4554 | SPS7 | ES | MCC | 9 | MCC, 4 columns | 1987 | 6 | 35000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5045 | SPS7 Capital Project 1 | [11 empty] | good
4555 | SPS7 | ES | Main Breaker | 9 | Main Breaker;; ; ; 600V, 200A | 1987 | 6 | 12000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5050 | SPS7 Capital Project 1 | [11 empty] | good
4556 | SPS7 | ES | Capacitors | 9 | Capacitors | 1987 | 6 | 2500 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5056 | SPS7 Capital Project 1 | [11 empty] | good
4557 | SPS7 | ES | Pump Control Panel | 9 | Pump Control Panel | 1987 | 6 | 15000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5058 | SPS7 Capital Project 1 | [11 empty] | good
4558 | SPS7 | ES | Pump #1 Starter | 9 | Pump #1 Starter | 1987 | 6 | 6000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5059 | SPS7 Capital Project 1 | [11 empty] | good
4559 | SPS7 | ES | Pump #2 Starter | 9 | Pump #2 Starter | 1987 | 6 | 6000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5061 | SPS7 Capital Project 1 | [11 empty] | good
4560 | SPS7 | ES | supply fan Starter | 9 | supply fan Starter | 1987 | 6 | 6000 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5063 | SPS7 Capital Project 1 | [11 empty] | good
4561 | SPS7 | ES | lighting panel | 9 | lighting panel | 1987 | 6 | 5000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5066 | SPS7 Capital Project 1 | [11 empty] | good
4562 | SPS7 | ES | lighting transformer | 9 | lighting transformer, 7.5kVA | 1987 | 6 | 9000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5070 | SPS7 Capital Project 1 | [11 empty] | good
4563 | SPS7 | ES | standby generator | 9 | standby generator, 75kW | 1987 | 6 | 140000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5077 | SPS7 Capital Project 1 | [11 empty] | good
4564 | SPS7 | ES | Pump Ds and control keyboard | 10 | 2 Pump Ds and control keyboard | 1987 | 6 | 10000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_0953 | SPS7 Capital Project 1 | [11 empty] | good
4565 | SPS7 | ES | supply fan DS | 10 | supply fan DS | 1987 | 6 | 2000 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_0982 | SPS7 Capital Project 1 | [11 empty] | good
4566 | SPS7 | ES | drywell lighting | 10 | 4 wall-pack fixtures | 1987 | 6 | 2400 | 0 | [7 empty] | 2 | 2 |  | To be replaced with class 1, div 2 leds in next upgrade was observed. |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_1006 | SPS7 Capital Project 1 | [11 empty] | good | to be replaced with class 1, div 2 LEDs in next upgrade
4567 | SPS7 | ES | wet well lighting | 8 | 3 fixtures | 1987 | 6 | 2400 | 0 | [7 empty] | 2 | 2 |  | To be replaced with leds in next upgrade was observed. |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_7225 | SPS7 Capital Project 1 | [11 empty] | good | to be replaced with LEDs in next upgrade
4569 | SPS7 | SIC | PLC RPU607 | 9 | PLC | 2014 | 8 | 60000 | 0 | [7 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5059 | SPS7 Capital Project 1 | [11 empty] | good
4570 | SPS7 | SIC | Autodialer | 9 | Autodialer | 2014 | 8 | 6000 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5079 | SPS7 Capital Project 1 | [11 empty] | good
4571 | SPS7 | SIC | level transmitter | 9 | level transmitter | 2014 | 8 | 12000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5046 | SPS7 Capital Project 1 | [11 empty] | good
4572 | SPS7 | SIC | wet well floats | 8 | 3 floats | 2014 | 8 | 1500 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_7242 | SPS7 Capital Project 1 | [11 empty] | good
4573 | SPS7 | SIC | dry well floats | 10 | 2 floats | 2014 | 8 | 1000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_7273 | SPS7 Capital Project 1 | [11 empty] | good
4574 | SPS7 | SIC | temperature switch | 10 | 2 temperature switches | 2014 | 8 | 3000 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_0981 | SPS7 Capital Project 1 | [11 empty] | good
4575 | SPS7 | SIC | pressure gauge | 10 | 2 pressure gauges | 2014 | 8 | 2000 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_0956 | SPS7 Capital Project 1 | [11 empty] | good
4576 | SPS7 | SIC | Anthenna | 7 | Anthenna | 2014 | 8 | 8000 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_6173 | SPS7 Capital Project 1 | [11 empty] | good
4637 | SPS7 | BM | Intake damper | 10 | damper and actuator | 1985 | 2 | 4000 | 0 | [7 empty] | 3 | 3 | To be upgrade with generator replacement was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_6177 | SPS7 Capital Project 1 | [11 empty] | To be upgrade with generator replacement.
4638 | SPS7 | BM | Eyewash combo | 9 | eyewash | 2000 | 9 | 1000 | 0 | [7 empty] | 3 | 3 | Emergency eyewashes are required to provide tepid water. no water heater was installed. no instantaneous heater would be required was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 3000 |  |  |  | IMG_6179 | SPS7 Capital Project 1 | [8 empty] | 3000 |  |  | Emergency eyewashes are required to provide tepid water. No water heater was installed. No instantaneous heater would be required.
4639 | SPS7 | BM | Backflow preventer | 9 | backflow, conbraco, , 1" | 2010 | 19 | 2500 | 0 | [7 empty] | 3 | 2 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the long term. |  |  |  |  | IMG_6184 | SPS7 Capital Project 2
4640 | SPS7 | BM | Generator Exhaust | 10 | ductwork and dampers | 1985 | 2 | 5000 | 0 | [7 empty] | 3 | 3 | Exhaust system to be replaced with generator replacement was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_6187 | SPS7 Capital Project 1 | [11 empty] | Exhaust system to be replaced with generator replacement.
4641 | SPS7 | BM | Diesel Fuel system | 10 | fuel tank and piping | 2008 | 17 | 20000 | 0 | [7 empty] | 3 | 2 | It was noted on site that the diesel fuel system is not up to current tssa regulations and will need to be upgraded in the future. ab inspection report provided detailed deficiency list was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term. |  |  |  |  | IMG_6198 | SPS7 Capital Project 2 | [11 empty] | It was noted on site that the diesel fuel system is not up to current TSSA regulations and will need to be upgraded in the future. AB inspection report provided detailed deficiency list.
4642 | SPS7 | BM | Dry well supply fan | 9 | Supply fan with duct heater | 1985 | 2 | 4500 | 0 | [7 empty] | 3 | 3 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_6203 | SPS7 Capital Project 1
4643 | SPS7 | BM | Generator Exhaust | 10 | ductwork and dampers | 1985 | 2 | 5000 | 0 | [7 empty] | 3 | 3 | Exhaust system to be replaced with generator replacement was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_6211 | SPS7 Capital Project 1 | [11 empty] | Exhaust system to be replaced with generator replacement.
4644 | SPS7 | BM | Wet Well Intake | 8 | Intake Louver | 1985 | 6 | 1500 | 0 | [7 empty] | 3 | 2 | Intake louver does not meet the code requirement for clearances to an unclassified space. adjacent door is 450mm. nfpa 820 points out that 0.9m from an opening is a classified area. wet well intake should be sealed closed. new intake vent from roof to be was observed. | Louver has some physical damage was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 3000 |  |  |  | IMG_6165 | SPS7 Capital Project 1 | [8 empty] | 3000 |  |  | Intake louver does not meet the code requirement for clearances to an unclassified space. Adjacent door is 450mm. NFPA 820 points out that 0.9m from an opening is a classified area. Wet well intake should be sealed closed. New Intake vent from roof to be | Louver has some physical damage.
4645 | SPS7 | BM | Wet well Exhaust fan | 8 | exhaust fan and ductwork | 1985 | 6 | 7500 | 0 | [7 empty] | 3 | 2 | Fan enclosure has severe corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_6217 | SPS7 Capital Project 1 | [11 empty] | Fan enclosure has severe corrosion
4646 | SPS7 | BM | Sump Pump | 10 | sump pump | 2010 | 19 | 1500 | 0 | [7 empty] | 3 | 3 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the long term. |  |  |  |  | IMG_0964 | SPS7 Capital Project 2
4647 | SPS7 | BM | Unit Heater | 10 | unit heater, chromalox, , 5kw | 1984 | 6 | 2500 | 0 | [7 empty] | 3 | 2 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_0982 | SPS7 Capital Project 1
4648 | SPS7 | BM | Dehumidifier | 10 | Dehumidifier | 1984 | 2 | 3000 | 0 | [7 empty] | 3 | 3 | Wall mounted unit did not appear to be working was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_0999 | SPS7 Capital Project 1 | [11 empty] | wall mounted unit did not appear to be working.
4692 | SPS7 | SC | Dry Well Concrete Structure | 10 |  | 1987 | 26 | 135000 | 0 | [7 empty] | 3 | 4 |  |  |  | The asset was observed to be in fair condition. Provisions for structural repairs. Asset to be replaced at the end of remaining service life. |  | 2023 |  | 2038 | IMG_7235 |  | SPS7 Capital Project 1 | SPS7 Capital Project 2 | [9 empty] | fair
4693 | SPS7 | SC | Dry Well Masonry Blockwall | 10 |  | 1987 | 26 | 15000 | 0 | [7 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7299 | [12 empty] | good
4694 | SPS7 | SC | Dry Well Precast Concrete Roof | 10 |  | 1987 | 26 | 15000 | 0 | [7 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. |  | 2031 |  |  | IMG_7299 |  | SPS7 Capital Project 1 | [10 empty] | good
4695 | SPS7 | SC | Dry Well Monorail Crane Beam | 10 |  | 1987 | 26 | 5000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7299 | [12 empty] | good
4696 | SPS7 | SC | Dry Well Access Ladder | 10 | Upper | 1987 | 26 | 5000 | 0 | [7 empty] | 3 | 3 |  |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7289 | [12 empty] | Fair
4697 | SPS7 | SC | Dry Well Guardrail | 10 |  | 1987 | 26 | 4000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7306 | [12 empty] | good
4698 | SPS7 | SC | Dry Well Aluminum Grating | 10 |  | 1987 | 26 | 1500 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7306 | [12 empty] | good
4699 | SPS7 | SC | Wet Well Concrete Structure | 8 |  | 1987 | 26 | 130000 | 0 | [7 empty] | 3 | 4 |  | Previous coating on walls has failed was observed. | Active leaking was observed and abandoned previous anchors at ladder. | The asset was observed to be in fair condition. Provisions for structural repairs. Asset to be replaced at the end of remaining service life. |  | 2023 |  | 2038 | IMG_7270 |  | SPS7 Capital Project 1 | SPS7 Capital Project 2 | [9 empty] | fair | previous coating on walls has failed | active leaking and abandoned previous anchors at ladder
4700 | SPS7 | SC | Wet Well Aluminum Platform | 8 |  | 1987 | 26 | 10000 | 0 | [7 empty] | 3 | 3 |  | Minor pitting was observed and calcium deposits. |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7270 | [12 empty] | fair | minor pitting and calcium deposits
4701 | SPS7 | SC | Wet Well Access Ladder | 8 | Exterior to platform | 1987 | 26 | 5000 | 0 | [7 empty] | 3 | 3 |  | Minor pitting was observed and calcium deposits. |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7270 | [12 empty] | fair | minor pitting and calcium deposits
4702 | SPS7 | SC | Wet Well Access Ladder | 8 | Platform to base | 1987 | 26 | 5000 | 0 | [7 empty] | 3 | 3 |  | Minor pitting was observed and calcium deposits. |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7246 | [12 empty] | fair | minor pitting and calcium deposits
4703 | SPS7 | SC | Wet Well Masonry Blockwall | 8 |  | 1987 | 26 | 6000 | 0 | [7 empty] | 3 | 4 |  |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7225 | [12 empty] | fair
4704 | SPS7 | SC | Wet Well Monorail Crane Beam | 8 |  | 1987 | 26 | 2000 | 0 | [7 empty] | 3 | 2 |  | Minor corrosion was observed noted. |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7225 | [12 empty] | fair | minor corrosion noted
4705 | SPS7 | AC | Exterior Brick Veneer | 9 |  | 1987 | 6 | 12000 | 0 | [7 empty] | 3 | 1 | Minor cracking in mortar was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_7223 | SPS7 Capital Project 1 | [11 empty] | minor cracking in mortar
4706 | SPS7 | AC | Roofing System | 9 |  | 1987 | 6 | 10000 | 0 | [7 empty] | 3 | 2 |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_7233 | SPS7 Capital Project 1 | [11 empty] | fair
4707 | SPS7 | AC | Wet Well Wall and Ceiling Paint | 8 |  | 1987 | 6 | 1000 | 0 | [7 empty] | 3 | 1 |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_7225 | SPS7 Capital Project 1 | [11 empty] | fair
4708 | SPS7 | AC | Wet Well Access Door | 8 |  | 1987 | 6 | 3500 | 0 | [7 empty] | 3 | 1 | Local missing paint was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_7227 | SPS7 Capital Project 1 | [11 empty] | local missing paint
4709 | SPS7 | AC | Dry Well Access Door | 10 |  | 1987 | 6 | 5500 | 0 | [7 empty] | 3 | 1 |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_7231 | SPS7 Capital Project 1 | [11 empty] | fair
4710 | SPS7 | AC | Dry Well Wall and Ceiling Paint | 10 |  | 1987 | 6 | 15000 | 0 | [7 empty] | 3 | 1 | Localized missing paint was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_7277 | SPS7 Capital Project 1 | [11 empty] | localized missing paint
4711 | SPS7 | SC | Dry Well Access Ladder | 10 | Lower | 1987 | 26 | 5000 | 0 | [7 empty] | 3 | 3 |  |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7289 | [12 empty] | Fair
4712 | SPS7 | SC | Dry Well Access Platform | 10 |  | 1987 | 26 | 5000 | 0 | [7 empty] | 3 | 3 |  |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7289 | [12 empty] | Fair
4713 | SPS7 | SC | Wet Well Precast Concrete Roof | 8 |  | 1987 | 26 | 1500 | 0 | [7 empty] | 3 | 4 |  |  |  | The asset was observed to be in fair condition. Provisions for structural repairs. Asset to be replaced at the end of remaining service life. |  | 2023 |  | 2038 | IMG_7225 |  | SPS7 Capital Project 1 | SPS7 Capital Project 2 | [9 empty] | fair