## Sheet1
CategoryCode | assetTag | assetName | installYear | COF | repCost | photoName | seqNum | facility | Description | Process | building | inspectorName | LocationTag | LocationORIGINAL | manufacturer | TransmitterModel | TransducerModel | TransducerSerial | InstMeva | installationDate | remainingESL | InstType | ServiceArea | FacilityType | LifeCycleCategory | SerialNo | Parent | RotatingItem | Site | condition | defect1 | defect2 | defect3 | observations | RehabRepairCost | RehabRepairYear | RehabRepairCost2 | RehabRepairYear2 | repProjectName | rehabProjectName | rehab2ProjectName | Status | InspectionYear | rehabComment1 | rehabCost1 | rehabComment2 | rehabCost2 | defect1Input | defect2Input | defect3Input
AC |  | Chemical Entry Access Door (Single) | 1984 | 1 | 3500 | IMG_7060 | 5551 | KWPH |  |  |  |  | 00016088 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | corrosion at bottom of door frame
AC |  | Chemical Entry Room Ceiling Paint | 1984 | 1 | 500 | IMG_7062 | 5562 | KWPH |  |  |  |  | 00016088 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
AC |  | Chemical Entry Room Protective Floor Coating | 1984 | 1 | 1000 | IMG_7062 | 5549 | KWPH |  |  |  |  | 00016088 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | failed
AC |  | Chemical Room Access Door (Single) | 1984 | 1 | 3500 | IMG_7062 | 5552 | KWPH |  |  |  |  | 00016089 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | worn paint at bottom
AC |  | Chemical Room Protective Floor Coating | 1984 | 1 | 2000 | IMG_7064 | 5561 | KWPH |  |  |  |  | 00016089 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | failed
AC |  | Chemical Storage Ceiling Paint | 1984 | 1 | 700 | IMG_7065 | 5550 | KWPH |  |  |  |  | 00016089 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
AC |  | Chlorination Building Exterior Brick Veneer | 1984 | 1 | 10000 | IMG_7052 | 5564 | KWPH |  |  |  |  | 00006881 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | localized spalling/erosion at bottom
AC | 00011176 | Chlorination Building Louvre Grilles | 1984 | 1 | 1500 | IMG_1321 | 5513 | KWPH | two (2) in total |  |  |  | 00006881 | West Park Heights Reservoir | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
AC | 00011174 | Chlorination Building Roofing System | 2014 | 2 | 8000 | IMG_7046 | 5512 | KWPH |  |  |  |  | 00016086 | West Park Heights Reservoir | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
AC |  | Electrical Room Access Door (Single) | 1984 | 1 | 3500 | IMG_7053 | 5565 | KWPH |  |  |  |  | 00016090 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | corrosion on kick plate at bottom
AC |  | Electrical Room Ceiling Paint | 1984 | 1 | 500 | IMG_7055 | 5563 | KWPH |  |  |  |  | 00016090 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
AC |  | Electrical Room Protective Floor Coating | 1984 | 1 | 1000 | IMG_7056 | 5548 | KWPH |  |  |  |  | 00016090 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | failed
BM | 00004238 | Chemical Entry Room Electric Heater | 2014 | 2 | 1000 | IMG_0477 | 5176 | KWPH | wall mount convection Heater, by Stelpro, 1 kW, 120/1/60 |  |  |  | 00016088 | West Park Heights Res Chemical Entry Room | M00037 | [5 empty] | 0 |  | Area 3 Water Treatment |  | Building Mechanical |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
BM | 00004239 | Chemical Entry Room Exhaust Fan | 1984 | 2 | 5000 | IMG_0469 | 5177 | KWPH | Greenheck Model DSQ-100-B-QD; 1/6hp. 115VAC/1/60, 1140 rpm |  |  |  | 00016088 | West Park Heights Res Chemical Storage Room | M00069 | [5 empty] | 0 |  | Area 3 Water Treatment |  | Building Mechanical | 85F04708 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
BM | 00004240 | Chemical Entry Room Motorized Damper | 1984 | 2 | 2000 | IMG_0470 | 5178 | KWPH | Damper, c/w Honeywell actuator; 120/1/60; |  |  |  | 00016088 | West Park Heights Res Chemical Storage Room | M00076 | [5 empty] | 0 |  | Area 3 Water Treatment |  | Building Mechanical |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
BM | 00004227 | Chemical Room Exhaust Fan | 1984 | 2 | 5000 | IMG_0532 | 5166 | KWPH | Greenheck Model DSQ-80-DGF-QD; 1550rpm. |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room | M00069 | [5 empty] | 0 |  | Area 3 Water Treatment |  | Building Mechanical | 85E01526 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | Minor surface corrosion
BM | 00004228 | Chemical Room Motorized Damper | 1984 | 2 | 3000 | IMG_0524 | 5167 | KWPH | Damper, c/w Honeywell actuator; 120/1/60; |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room | [6 empty] | 0 |  | Area 3 Water Treatment |  | Building Mechanical |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
BM | 00004226 | Chemical Room Unit Heater | 2014 | 2 | 3000 | IMG_0519 | 5165 | KWPH | wall mount Unit Heater, 3.6 kW, 208/1/60; Ouellet Model OCC4800AM-MO-TB6/CCG4800AM-MO-TB6, the heater appear to be new |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room | M00037 | [5 empty] | 0 |  | Area 3 Water Treatment |  | Building Mechanical |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | very good
BM | 00055015 | Valve Chamber Air Supply ductwork | 2014 | 2 | 1500 | IMG_0554 | 5247 | KWPH | ducting system: 150DIA PVC c/w thermal insulation in jacket |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | [6 empty] | 0 |  | Area 3 Water Treatment | [5 empty] | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
BM | 00055016 | Valve Chamber Air Supply Fan | 2014 | 2 | 3500 | IMG_0642 | 5248 | KWPH | Twin City Model DSI-120AAL; 115/1/60; 1/8hp, ODP enclosure |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | [6 empty] | 0 |  | Area 3 Water Treatment |  |  | K12-000000078996 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
BM | 00055017 | Valve Chamber Dehumidifier | 2014 | 2 | 5000 | IMG_0602 | 5190 | KWPH | Manufacturer: Ebac Inductrial Products Ltd. model 10264CS-US, capacity 17 PPD; 120/1/60; 350 W; built-in controls |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | [6 empty] | 0 |  | Area 3 Water Treatment |  | Building Mechanical | 251000341 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | Moderate corrosion
BM |  | Valve Chamber Gooseneck Vent | 1984 | 1 | 1000 | IMG_1312 | 5612 | KWPH |  |  |  |  | 00016091 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | minor surface corrosion
BM | 00004251 | Valve Chamber Sump Pump | 1984 | 2 | 3000 | IMG_0606 | 5189 | KWPH | Submersible Centrifugal Pump with associated piping, 120/1/60 |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | [6 empty] | 0 |  | Area 3 Water Treatment |  | Process Mechanical |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | Severe corrosion
BM | 00004254 | Valve Chamber Unit heater | 2014 | 2 | 1000 | IMG_0594 | 5192 | KWPH | Heating System, Convection Heater, wall mount, by Ouellet |  |  |  | 00016091 | West Park Heights Res Control Room | M00037 | [5 empty] | 0 |  | Area 3 Water Treatment |  | Building Mechanical |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | Minor corrosion
ES | 00006900 | Chlorination Building Emergency Lights | 2002 | 2 | 5000 | IMG_4724 | 5200 | KWPH | 2 units with battery packs. |  |  |  | 00016086 | West Park Heights Reservoir | M00606 | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Reservoir | Electrical System |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
ES |  | Chlorination Building Indoor Lighting Fixtures | 2002 | 2 | 9000 | IMG_4717 | 5609 | KWPH | 6 fluroscent fixtures |  |  |  | 00016086 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
ES |  | Chlorination Building Outdoor Light Fixture | 2002 | 2 | 1000 | IMG_4698 | 5608 | KWPH | One (1) in total. Installation year assumed to be 2010. |  |  |  | 00016086 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
ES | 00006894 | Chlorine Booster Pump 1 Disconnect Switch | 2002 | 2 | 5000 | img_1302 | 5196 | KWPH |  |  |  |  | 00016090 | West Park Heights Res Control Room | M00571 | [5 empty] | 0 |  | Area 3 Water Treatment |  | Electrical System |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
ES | 00006895 | Chlorine Booster Pump 2 Disconnect Switch | 2002 | 2 | 5000 | IMG_1304 | 5197 | KWPH |  |  |  |  | 00016090 | West Park Heights Res Control Room | M00311 | [5 empty] | 0 |  | Area 3 Water Treatment |  | Electrical System |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
ES | 00006892 | Enclosed Switch | 2002 | 3 | 6000 | IMG_1300 | 5194 | KWPH | 125/250V, 100A |  |  |  | 00016090 | West Park Heights Res Control Room | M00129 | [5 empty] | 0 |  | Area 3 Water Treatment |  | Electrical System | T3 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
ES | 00006891 | Generator Panel | 2002 | 3 | 12000 | img_1295 | 5193 | KWPH | 24 Circuits |  |  |  | 00016090 | West Park Heights Res Control Room | M00059 | [5 empty] | 0 |  | Area 3 Water Treatment |  | Electrical System | GP3P60-20 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
ES | 00006893 | Panel Board LP A | 2002 | 3 | 20000 | img_1301 | 5195 | KWPH |  |  |  |  | 00016090 | West Park Heights Res Control Room | M00129 | [5 empty] | 0 |  | Area 3 Water Treatment |  | Electrical System | T2 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
ES | 00055029 | Panel Board LP B | 2014 | 3 | 15000 | IMG_4759 | 5261 | KWPH | LP B, Panel Board, Lighting Panel |  |  |  | 00016090 | West Park Heights Res Control Room | [6 empty] | 0 |  | Area 3 Water Treatment | [5 empty] | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
ES |  | Valve Chamber Indoor Lighting Fixtures | 2002 | 2 | 6000 | IMG_7076 | 5613 | KWPH | 4 fluroscent fixtures |  |  |  | 00016091 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
HSS | 00044422 | Battery Acid Spill Containment | 2020 | 2 | 100 | img_1297 | 5245 | KWPH |  |  |  |  | 00006881 | West Park Heights Reservoir | M10266 | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Reservoir | Health and Safety |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
HSS |  | Chlorine Room Smoke Detector | 2014 | 1 | 0 | IMG_1271 | 5618 | KWPH |  |  |  |  | 00016089 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
HSS | 00024557 | Eyewash Station | 2014 | 3 | 600 | IMG_4725 | 5242 | KWPH |  |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room | M00191 | [5 empty] | 0 |  | Area 3 Water Treatment |  | Health and Safety |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
HSS |  | Fire Extinguisher | 2020 | 1 | 300 | img_1234 | 5623 | KWPH | Total of 1 |  |  |  | 00016086 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
HSS |  | First Aid Kit | 2020 | 1 | 500 | IMG_1280 | 5621 | KWPH |  |  |  |  | 00016089 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
PM |  | Chamber No.1 Watermain Air Release Valve | 2008 | 2 | 3500 | IMG_0744 | 5475 | KWPH | 50 DIA Combination Air Relief/ Vacuum Valve c/w isolation ball valve, by ARI model D-040-C2 |  |  |  | 00016092 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | Good
PM |  | Chamber No.1 Watermain Butterfly Valve | 2008 | 3 | 20000 | IMG_0686 | 5472 | KWPH | Diameter: 750mm, with AWWA square operator nut and extension stem |  |  |  | 00016092 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | Minor surface corrosion
PM |  | Chamber No.2 Watermain Air Release Valve | 2008 | 3 | 3500 | IMG_0730 | 5469 | KWPH | 50 DIA Combination Air Relief/ Vacuum Valve c/w isolation ball valve, by ARI model D-040-C2 | [11 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
PM |  | Chamber No.2 Watermain Butterfly Valve 1 | 2008 | 3 | 20000 | IMG_0726 | 5617 | KWPH | Diameter: 750mm, with AWWA square operator nut and extension stem |  |  |  | 00016092 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | Minor surface corrosion
PM |  | Chamber No.2 Watermain Butterfly Valve 2 | 2008 | 3 | 20000 | IMG_0725 | 5471 | KWPH | Diameter: 750mm, with AWWA square operator nut and extension stem | [11 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | Minor surface corrosion
PM |  | Chamber No.2 Watermain Butterfly Valve 3 | 2008 | 3 | 20000 | IMG_0724 | 5470 | KWPH | Diameter: 750mm, with AWWA square operator nut and extension stem | [11 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | minor surface corrosion
PM |  | Chamber No.2 Watermain Drain Gate Valve 1 | 2008 | 2 | 1500 | IMG_0725 | 5474 | KWPH | Diameter: 150mm, with 50 mm square operating nut and extension stem |  |  |  | 00016092 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | Minor surface corrosion
PM |  | Chamber No.2 Watermain Drain Gate Valve 2 | 2008 | 2 | 1500 | IMG_0724 | 5473 | KWPH | Diameter: 150mm, with 50 mm square operating nut and extension stem |  |  |  | 00016092 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | minor surface corrosion
PM | 00017994 | Chlorination System 2 | 2002 | 4 | 45000 | IMG_0503 | 5170 | KWPH | US Filter -Wallce & Tiernan, model V10k |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room | M00899 | [5 empty] | 0 |  | Area 3 Water Treatment |  | Process Mechanical | 234300009501-001887 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
PM | 00017993 | Chlorination System 1 | 2002 | 4 | 45000 | IMG_0493 | 5168 | KWPH | US Filter -Wallce & Tiernan, model V10k |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room | M00899 | [5 empty] | 0 |  | Area 3 Water Treatment |  | Process Mechanical | 234300009501-001891 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
PM | 00004246 | Chlorine Booster Pump 1 | 2002 | 3 | 7500 | IMG_0653 | 5184 | KWPH | Grundfos Model A96083903P117420003, 15.41 gpm at 90.6 ft, 0.75hp, 3439 rpm; 240VAC/1/60 |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | M00951 | [5 empty] | 0 |  | Area 3 Water Treatment |  | Process Mechanical | 0002 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
PM | 00004247 | Chlorine Booster Pump 2 | 2002 | 3 | 7500 | IMG_0658 | 5185 | KWPH | Grundfos Model A96083903P117420002, 15.41 gpm at 90.6 ft, 0.75hp, 3439 rpm |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | M00951 | [5 empty] | 0 |  | Area 3 Water Treatment |  | Process Mechanical | 0003 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
PM | 00004246 | Chlorine Booster Pump Piping System | 2002 | 3 | 3000 | IMG_0653 | 5616 | KWPH |  |  |  |  | 00016091 | [7 empty] | 0 |  |  |  |  | 0002 |  |  |  | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
PM | 00017056 | Chlorine Injection System Tubing System | 2002 | 3 | 3000 | IMG_0618 | 5223 | KWPH | Chlorine system tubing system from valve chamber to chlorine room. |  |  |  | 00016086 | West Park Heights Res Tank | [6 empty] | 0 |  | Area 3 Water Treatment |  | Process Mechanical |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
PM |  | Drain Chamber Drain Line Butterfly Valve | 1984 | 2 | 8000 | IMG_0417 | 5466 | KWPH | Diameter: 300mm |  |  |  | 00016086 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | surface corrosion
PM |  | Drain Chamber Overflow Line Flap Gate | 1984 | 2 | 6000 | IMG_0417 | 5467 | KWPH | Diameter: 450mm |  |  |  | 00016092 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | surface corrosion
PM | 00055036 | Reserovir Overflow Piping | 1984 | 4 | 12000 | IMG_4697 | 5268 | KWPH | Diameter: 350mm, above ground,approximately 12 meters. |  |  |  | 00016086 | West Park Heights Res Tank | [6 empty] | 0 |  | Area 3 Water Treatment | [5 empty] | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | Good
PM | 00055035 | Reservoir Inlet/Outlet Line Piping | 2014 | 5 | 54000 | IMG_0405 | 5267 | KWPH | Diameter: 450mm, approximately 33 meters. |  |  |  | 00016086 | West Park Heights Res Tank | [6 empty] | 0 |  | Area 3 Water Treatment | [5 empty] | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | Good
PM | 00055035 | Reservoir Mixing System | 2014 | 3 | 35000 | IMG_0405 | 5614 | KWPH |  |  |  |  | 00016086 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | Good
PM | 00055018 | Valve Chamber Blind Flange | 2014 | 2 | 4000 | IMG_0630 | 5250 | KWPH | Blind flange for an adandonded pipe line. |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | [6 empty] | 0 |  | Area 3 Water Treatment | [5 empty] | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
PM | 00055027 | Valve Chamber Inlet/Outlet Line Butterfly Valve 1 | 2014 | 3 | 15000 | IMG_0572 | 5259 | KWPH | Diameter: 450mm, Val-Matic Model 2018XF, electric actuator by Rotork Type IQS-12FA10-B4, 120/1/60 |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | M00926 | [5 empty] | 0 |  | Area 3 Water Treatment | [5 empty] | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | Surface corrosion
PM | 00055026 | Valve Chamber Inlet/Outlet Line Butterfly Valve 1 Electric Actuator | 2014 | 3 | 11000 | IMG_0682 | 5258 | KWPH | Rotork Type IQS-12FA10-B4, 120/1/60 |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | M00120 | [5 empty] | 0 |  | Area 3 Water Treatment |  |  | 0122960102 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | minor paint peeling
PM | 00055021 | Valve Chamber Inlet/Outlet Line Butterfly Valve 2 | 1984 | 3 | 15000 | IMG_0588 | 5181 | KWPH | Main Line, Valve, Butterfly, 450 DIA flanged, Val-Matic Model 2018XF, electric actuator by Rotork Type IQS-12FA10-B4, 120/1/60 |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | [6 empty] | 0 |  | Area 3 Water Treatment |  | Process Mechanical |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | Minor surface corrosion
PM | 00055020 | Valve Chamber Inlet/Outlet Line Butterfly Valve 2 Electric Actuator | 2014 | 3 | 11000 | IMG_1398 | 5252 | KWPH | Diameter: 450mm |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | M00120 | [5 empty] | 0 |  | Area 3 Water Treatment |  |  | 0122960101 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
PM | 00055022 | Valve Chamber Inlet/Outlet Line Flexible Coupling | 2014 | 3 | 5000 | IMG_1396 | 5254 | KWPH | diameter: 250mm |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | [6 empty] | 0 |  | Area 3 Water Treatment | [5 empty] | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
PM | 00055025 | Valve Chamber Inlet/Outlet Line Piping | 2014 | 3 | 5000 | IMG_0619 | 5257 | KWPH | Diameter: 250mm, length: 8 meters |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | [6 empty] | 0 |  | Area 3 Water Treatment | [5 empty] | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | Good
PM |  | Valve Chamber Sampling Line | 2002 | 3 | 2000 | IMG_1450 | 5607 | KWPH |  |  |  |  | 00016091 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
SC |  | Chemical Entry Concrete Roof | 1984 | 4 | 6000 | IMG_7062 | 5578 | KWPH |  |  |  |  | 00016088 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
SC | 00011171 | Chemical Entry Room Concrete Blockwall | 1984 | 4 | 9000 | IMG_7062 | 5511 | KWPH |  |  |  |  | 00016088 | West Park Heights Reservoir | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | step cracking in mortar
SC | 00011171 | Chemical Room Concrete Blockwall | 1984 | 4 | 12000 | IMG_7068 | 5553 | KWPH |  |  |  |  | 00016089 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | step cracking in mortar
SC |  | Chemical Room Concrete Roof | 1984 | 4 | 8000 | IMG_7065 | 5572 | KWPH |  |  |  |  | 00016089 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
SC |  | Drain Chamber Access Hatch | 1984 | 3 | 3000 | IMG_7057 | 5580 | KWPH |  |  |  |  | 00016092 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
SC |  | Drain Chamber Access Ladder | 1984 | 3 | 2000 | IMG_7058 | 5574 | KWPH |  |  |  |  | 00016092 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
SC |  | Drain Chamber Concrete Structure | 1984 | 3 | 10000 | IMG_7058 | 5579 | KWPH |  |  |  |  | 00016092 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
SC | 00011171 | Electrical Room Concrete Blockwall | 1984 | 4 | 10000 | IMG_7055 | 5566 | KWPH |  |  |  |  | 00016090 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | mortar step cracking
SC |  | Electrical Room Concrete Roof | 1984 | 4 | 6000 | IMG_7055 | 5573 | KWPH |  |  |  |  | 00016090 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
SC | 00011170 | Reservoir Access Ladder | 2014 | 3 | 10000 | IMG_7011 | 5510 | KWPH | Metal ladder to the top of Reservoir |  |  |  | 00006881 | West Park Heights Reservoir | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | Fall arrest system is not compliant to current CSA standards
SC |  | Reservoir Exterior Coating | 1984 | 3 | 575000 | IMG_7011 | 5555 | KWPH |  |  |  |  | 00006881 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
SC |  | Reservoir Interior Coating | 1984 | 4 | 750000 | IMG_7014 | 5567 | KWPH |  |  |  |  | 00006881 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
SC |  | Reservoir Roof Guardrail | 2014 | 3 | 10000 | IMG_7037 | 5586 | KWPH |  |  |  |  | 00006881 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | localized cracked pipe sleeve
SC |  | Reservoir Roof Hatch 1 | 1984 | 3 | 5000 | IMG_7038 | 5556 | KWPH |  |  |  |  | 00006881 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | covered in roofing material
SC |  | Reservoir Roof Hatch 2 | 1984 | 3 | 5000 | IMG_7045 | 5568 | KWPH |  |  |  |  | 00006881 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | covered in roofing material
SC |  | Reservoir Side Access Hatch 1 | 1984 | 3 | 10000 | IMG_7019 | 5588 | KWPH |  |  |  |  | 00006881 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | minor surface corrosion
SC |  | Reservoir Side Access Hatch 2 | 1984 | 3 | 14000 | IMG_7012 | 5587 | KWPH |  |  |  |  | 00006881 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | Minor surface corrosion
SC |  | Reservoir Steel Tank | 1984 | 5 | 1500000 | IMG_7031 | 5554 | KWPH |  |  |  |  | 00006881 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | leakage staining noted on interior of tank at top of wall
SC |  | Valve Chamber Access Hatch 1 | 1984 | 3 | 5000 | IMG_7069 | 5571 | KWPH |  |  |  |  | 00016091 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
SC |  | Valve Chamber Access Hatch 2 | 1984 | 3 | 3000 | IMG_7056 | 5577 | KWPH |  |  |  |  | 00016091 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
SC |  | Valve Chamber Access Ladder 1 | 1984 | 3 | 5000 | IMG_7077 | 5570 | KWPH |  |  |  |  | 00016091 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
SC |  | Valve Chamber Access Ladder 2 | 1984 | 3 | 5000 | IMG_7080 | 5576 | KWPH |  |  |  |  | 00016091 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
SC |  | Valve Chamber Concrete Structure | 1984 | 4 | 100000 | IMG_7077 | 5569 | KWPH |  |  |  |  | 00016091 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | localized rust spots
SIC | 00083304 | Chemical Entry Room Chlorine Gas Detector | 2014 | 2 | 2000 | IMG_4719 | 5273 | KWPH | KSTKWP_CL2D_GCL21 |  |  |  | 00016088 | West Park Heights Res Chemical Entry Room | M10086 | A-ULTIMAX-PL-18 |  |  | Gas |  | 0 |  | Area 3 Water Treatment |  | Instrumentation and Control | A17-400747637 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SIC | 00018060 | Chemical Entry Room Temperature Switch | 1984 | 1 | 1000 | IMG_4702 | 5239 | KWPH | Installtion year assumed to be 1984 |  |  |  | 00016088 | West Park Heights Res Control Room | M00076 | T631A1063 |  |  | Temperature |  | 0 |  | Area 3 Water Treatment |  | Instrumentation and Control | NOT AVAILABLE |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SIC | 00017992 | Chemical Room Chlorine Gas Detector | 2014 | 0 | 2000 | IMG_1262 | 5229 | KWPH | KST1CLD101 |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room | M00937 | 50-125 |  |  | Chlorine Gas |  | 0 |  | Area 3 Water Treatment |  | Instrumentation and Control | A17-0023409 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SIC | 00006896 | Chlorination Building Entry Security System | 2014 | 3 | 10000 | IMG_4701 | 5198 | KWPH | Security System includind card readerS and password enter panel. |  |  |  | 00016086 | West Park Heights Res Control Room | M00026 | [5 empty] | 0 |  | Area 3 Water Treatment |  | Health and Safety | RANGER 8980 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SIC | 00006896 | Chlorination Building Security Panels | 2014 | 3 | 20000 | IMG_4753 | 5610 | KWPH | Three (3) honeywell panels in total |  |  |  | 00016086 | [7 empty] | 0 |  |  |  |  | RANGER 8980 |  |  |  | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
SIC | 00004235 | Chlorine Injection Line 1 Eductor | 2002 | 3 | 3500 | IMG_0510 | 5173 | KWPH |  |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room | M00899 | [5 empty] | 0 |  | Area 3 Water Treatment |  | Process Mechanical |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SIC | 00004236 | Chlorine Injection Line 1 Electric Actuator | 2002 | 3 | 3500 | IMG_0510 | 5174 | KWPH | True Blue Model EBV-65 |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room | M00894 | [5 empty] | 0 |  | Area 3 Water Treatment |  | Process Mechanical | 9373-083 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | Good
SIC | 00004234 | Chlorine Injection Line 2 Eductor | 2002 | 3 | 3500 | IMG_0510 | 5172 | KWPH |  |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room | M00899 | [5 empty] | 0 |  | Area 3 Water Treatment |  | Process Mechanical |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SIC | 00004237 | Chlorine Injection Line 2 Electric Actuator | 2002 | 3 | 3500 | IMG_0510 | 5175 | KWPH | True Blue Model EBV-65 |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room | M00894 | [5 empty] | 0 |  | Area 3 Water Treatment |  | Process Mechanical | 9373-083 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SIC | 00006918 | Chlorine System Pressure Gauges | 2002 | 2 | 1000 | IMG_1258 | 5213 | KWPH | Two (2) in total. |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room | M00924 | [5 empty] | 0 |  | Area 3 Water Treatment |  | Instrumentation and Control |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | minor surface corrosion
SIC | 00004230 | Chlorine Weight Scale | 2002 | 3 | 20000 | IMG_0494 | 5465 | KWPH | Avery Weigh-Tronix |  |  |  | 00016089 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | minor surface corrosion
SIC |  | Electrical Room Temperature Switch | 2014 | 1 | 1000 | IMG_4771 | 5611 | KWPH |  |  |  |  | 00016090 | [7 empty] | 0 |  |  |  |  | NOT AVAILABLE |  |  |  | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
SIC | 00083300 | Facility PAC Control Panel | 2014 | 4 | 60000 | img_1313 | 5206 | KWPH |  |  |  |  | 00016092 | West Park Heights Res Chemical Storage Room | M00899 | [5 empty] | 0 |  | Area 3 Water Treatment |  | Electrical System | 03-01-D |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SIC | 00080207 | Facility PAC Control Panel 3 Layer Ethernet Switch | 2014 | 2 | 3000 |  | 5269 | KWPH | KSETWP Ethernet Switch, Inside PAC control Panel |  |  |  | 00006881 | West Park Heights Reservoir | M01002 | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Reservoir | Instrumentation and Control | FOC1834Z4H1 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SIC | 00028277 | Facility PAC Control Panel Network Radio Modem | 2014 | 2 | 3000 |  | 5244 | KWPH | KST1RAD101,Inside PAC control Panel |  |  |  | 00016090 | West Park Heights Res Control Room | M01018 | [5 empty] | 0 |  | Area 3 Water Treatment |  | SCADA | 831028 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SIC | 00083302 | Facility PAC Control Panel OIT Computer | 2014 | 2 | 2000 | IMG_4767 | 5272 | KWPH |  |  |  |  | 00006881 | West Park Heights Reservoir | M10189 | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Reservoir | Instrumentation and Control | 14E-088/KSTKWP_PAC |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SIC | 00083301 | Facility PAC Control Panel OIT Display and Panel | 2014 | 2 | 10000 | IMG_4767 | 5271 | KWPH |  |  |  |  | 00016090 | West Park Heights Reservoir | M10189 | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Reservoir | Instrumentation and Control | KSA1450204 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SIC | 00028276 | Facility PAC Control Panel RPU | 2014 | 2 | 3000 |  | 5243 | KWPH | Inside PAC control Panel |  |  |  | 00016090 | West Park Heights Res Control Room | M00020 | [5 empty] | 0 |  | Area 3 Water Treatment |  | SCADA | 32520A39 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SIC | 00083387 | Facility PAC Control Panel UPS | 2014 | 2 | 3000 |  | 5275 | KWPH | Inside PAC control Panel |  |  |  | 00006881 | West Park Heights Reservoir | M10181 | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Reservoir | Instrumentation and Control | GK053A0118 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SIC | 00017995 | Free Chlorine Residual Analyzer | 2002 | 0 | 10000 | IMG_4713 | 5232 | KWPH |  |  |  |  | 00016088 | West Park Heights Res Chemical Entry Room | M00482 | CL17 |  |  | Chlorine |  | 0 |  | Area 3 Water Treatment |  | Instrumentation and Control | 030800008011 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | outdated.
SIC | 00018001 | Network Antenna | 2014 | 1 | 10000 | img_7047 | 5238 | KWPH | Installation year assumed to be 2010 |  |  |  | 00016090 | West Park Heights Res Control Room | [6 empty] | 0 |  | Area 3 Water Treatment |  | SCADA |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SIC | 00048031 | OMNI Antenna & Cable | 2014 | 1 | 10000 | img_7044 | 5619 | KWPH |  |  |  |  | 00006881 | Nobleton North ET Tank Roof | [6 empty] | 8 |  | Area 4 Water Treatment |  | SCADA/ Instrumentation/ Control | SC488-SF3SNF |  |  | W-WW | 2 |  |  |  | The omni antenna & cable was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | Nobleton North ET Capital Project 1 |  |  | OPERATING | 2019 |  |  |  |  | Good
SIC | 00055023 | Reservoir Inlet/Outlet Line Bidirectional Flowmeter | 2014 | 3 | 12000 | IMG_0578 | 5464 | KWPH | KSTKWP_TWR_LIT1, Endress+Hauser, Promag, diameter: 250mm |  |  |  | 00016091 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | Good
SIC | 00055030 | Reservoir Inlet/Outlet Line Flowmeter Transmitter | 2014 | 3 | 4000 | img_4706 | 5262 | KWPH | FIT Display |  |  |  | 00016088 | West Park Heights Res Chemical Entry Room | M00405 | [5 empty] | 0 |  | Area 3 Water Treatment |  |  | FA02E916000 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SIC | 00006919 | Reservoir Pressure-type Level Transmitter | 2014 | 3 | 9000 | IMG_1392 | 5214 | KWPH | KSTKWP_TWR_LIT1 |  |  |  | 00016090 | West Park Heights Res Control Room | M00020 | [5 empty] | 0 |  | Area 3 Water Treatment |  | Instrumentation and Control | 94A-11316 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SIC | 00017996 | Total Chlorine Residual Analyzer | 2002 | 3 | 10000 | IMG_4710 | 5233 | KWPH | Assume to be original |  |  |  | 00016088 | West Park Heights Res Chemical Entry Room | M00482 | CL17 |  |  | Total Chlorine |  | 0 |  | Area 3 Water Treatment |  | Instrumentation and Control | 030800008013 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | outdated.
SIC | 00004234 | Vacuum Regulator 1 | 2002 | 3 | 4000 | IMG_4744 | 5463 | KWPH | Manufacturer: US Filter -Wallce & Tiernan |  |  |  | 00016089 | [7 empty] | 0 |  |  |  |  | BK17251 |  |  |  | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
SIC | 00004235 | Vacuum Regulator 2 | 2002 | 3 | 4000 | IMG_4744 | 5171 | KWPH | Manufacturer: US Filter -Wallce & Tiernan |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room | M00899 | [5 empty] | 0 |  | Area 3 Water Treatment |  | Process Mechanical | BK17251 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SIC | 00017988 | Valve Chamber Float Switch | 2002 | 2 | 1000 | IMG_1403 | 5227 | KWPH |  |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | M00061 | Not available |  |  | Level |  | 0 |  | Area 3 Water Treatment |  | Instrumentation and Control | NOT AVAILABLE |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0
SIC | 00017988 | Valve Chamber Sump Pit Float Switch | 2002 | 2 | 1000 | IMG_0609 | 5622 | KWPH |  |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | M00061 | Not available |  |  | Level |  | 0 |  | Area 3 Water Treatment |  | Instrumentation and Control | NOT AVAILABLE |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SIC | 00048032 | YAGI Antenna & Cable | 2014 | 1 | 10000 | IMG_7043 | 5620 | KWPH |  |  |  |  | 00006881 | Nobleton North ET Tank Roof | [6 empty] | 8 |  | Area 4 Water Treatment |  | SCADA/ Instrumentation/ Control | RY-9008 |  |  | W-WW | 2 |  |  |  | The yagi antenna & cable was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | Nobleton North ET Capital Project 1 |  |  | OPERATING | 2019 |  |  |  |  | Good
SW |  | 600mm Watermain | 1984 | 5 | 60000 |  | 5451 | KWPH | 600mm ductile iron watermain on site. Approx. 20m in length |  |  |  | 00006881 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0
SW |  | 750mm Watermain | 2008 | 5 | 100000 |  | 5452 | KWPH | 750mm CPP watermain on site. Approx. 30m in length |  |  |  | 00006881 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0
SW |  | Asphalt Driveway | 1984 | 2 | 65000 | IMG_20210510_095755 | 5443 | KWPH | Asphalt driveway, including parking spots andasphalt around tank. |  |  |  | 00006881 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 2023 | 0 | 2023 |  |  |  |  | 0 | Reconstruct or repave asphalt surfaces on site. | 60000 | Remove and replace full depth asphalt at location that is damaged (along the edge). Raise gravel shoulder between tank and asphalt to ensure positive drainage away from tank and across pavement | 15000 | Large amount of cracking observed at driveway and parking spots. | Edge of asphalt along asphalt around tank is damaged and breaking off.
SW |  | Chainlink Fence | 1984 | 2 | 25000 | IMG_20210510_095527 | 5442 | KWPH | Chainlink fence around site, approximately 205m. |  |  |  | 00006881 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | Signs of corrosion at various locations of the fence.
SW |  | Chamber No.1 Access Hatch | 2008 | 3 | 5000 | IMG_7083 | 5590 | KWPH |  |  |  |  | 00016092 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
SW |  | Chamber No.1 Access Ladder | 2008 | 3 | 5000 | IMG_7084 | 5585 | KWPH |  |  |  |  | 00016092 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
SW |  | Chamber No.1 Concrete Structure | 2008 | 3 | 40000 | IMG_7086 | 5589 | KWPH |  |  |  |  | 00016092 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
SW |  | Chamber No.2 Access Hatch 1 | 2008 | 3 | 5000 | IMG_7072 | 5581 | KWPH |  |  |  |  | 00016092 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
SW |  | Chamber No.2 Access Hatch 2 | 2008 | 3 | 5000 | IMG_7072 | 5582 | KWPH |  |  |  |  | 00016092 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
SW |  | Chamber No.2 Access Ladder 1 | 2008 | 3 | 5000 | IMG_7091 | 5583 | KWPH |  |  |  |  | 00016092 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
SW |  | Chamber No.2 Access Ladder 2 | 2008 | 3 | 5000 | IMG_0722 | 5584 | KWPH |  |  |  |  | 00016092 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
SW |  | Chamber No.2 Concrete Structure | 2008 | 3 | 100000 | IMG_7091 | 5575 | KWPH |  |  |  |  | 00006881 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | good
SW |  | Reservoir Drain Piping | 1984 | 4 | 10000 |  | 5448 | KWPH | 300mm reservoir drain from reservoir to drain chamber, length: 8 meters |  |  |  | 00006881 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0
SW |  | Reservoir Overflow Pipe | 1984 | 4 | 17500 |  | 5449 | KWPH | 450mm ductile iron overflow pipe from reservoir to drain chamber. Approx. 8.0m in length |  |  |  | 00006881 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0
SW | 00011149 | Site Drainage (soft surfaces) | 1984 | 1 | 20000 | IMG_20210510_100127 | 5216 | KWPH | Site drainage on soft surfaces |  |  |  | 00006881 | West Park Heights Reservoir | [6 empty] | 0 |  | Area 3 Water Treatment | W - Storage Reservoir | Siteworks |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | Various locations damaged by tires or animals.
SW |  | Storm Sewer | 1984 | 3 | 38000 |  | 5447 | KWPH | 450mm conc. storm sewer from drain chamber to maintenance hole. Approx. 23m in length to PL |  |  |  | 00006881 | [7 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0
SW | 00011144 | Swing Gate | 1984 | 2 | 4000 | IMG_20210510_095106 | 5215 | KWPH |  |  |  |  | 00006881 | West Park Heights Reservoir | [6 empty] | 0 |  | Area 3 Water Treatment | W - Storage Reservoir | Siteworks |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | Good