## Sheet1
Discipline | OverallConditionrating1_5 | InspectorsComments | Keyword
Process Electrical | 2 | Fixtures were in good condition, however they did not have mechanical protection. | An electrical connection for a portable generator was not provided
Building and Process Structural | 3 | The concrete foundation could not be inspected as it is buried. The foundation was assumed to be in fair condition based on its age and the condition of other visible structural components.
Building and Process Structural | 3 | The steel tank was observed to be in fair condition. Corrosion was noted primarily at the bottom of the tank. | Corrosion
Building Services | 5 | Exhaust Fan 1 was missing. | missing
Process Mechanical Equipment | 3 | Sewage Lift Pump 1 was in fair condition with moderate surface corrosion and paint wear observed. However, the pump was original to the facility and was approaching the end of its estimated remaining service life. Pump testing was not undertaken as part o | moderate surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 1 was in fair condition with moderate surface corrosion and paint wear observed. However, the pump was original to the facility and was approaching the end of its estimated remaining service life. Pump testing was not undertaken as part o | paint wear
Process Mechanical Equipment | 3 | Sewage Lift Pump 1 Motor was in fair condition and was approaching the end of its remaining service life.
Process Mechanical Equipment | 3 | Sewage Lift Pump 1 Discharge Check Valve was in fair condition with moderate surface corrosion and paint wear observed. The valve was original to the facility and was approaching the end of its estimated remaining service life. An internal assessment of t | moderate surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 2 Discharge Gate Valve was in fair condition with moderate surface corrosion and paint wear observed. The valve was original to the facility and was approaching the end of its estimated remaining service life. Based on its age, replacemen | moderate surface corrosion
Process Piping | 5 | The Forcemain was in poor condition. The Region's operations staff reported that the forcemain failed 2 years prior to this assessment and is scheduled to be replaced up to Lakeshore Blvd. | failed
Process Mechanical Equipment | 3 | Sewage Lift Pump 2 Discharge Check Valve was in fair condition with moderate surface corrosion and paint wear observed. The valve was original to the facility and was approaching the end of its estimated remaining service life. An internal assessment of t | moderate surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 2 was in fair condition with moderate surface corrosion and paint wear observed. However, the pump was original to the facility and was approaching the end of its estimated remaining service life. Pump testing was not undertaken as part o | moderate surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 2 Motor was in fair condition and was approaching the end of its remaining service life. Minor surface corrosion was observed. | minor surface corrosion
Building Services | 3 | The Sump Pump was in fair condition. Moderate surface corrosion was observed. | moderate surface corrosion
Process Instrumentation SCADA | 5 | The Dry Well Transmitter Level was not operational at the time of the assessment. | not operational
Building and Process Structural | 3 | The ladder was in fair condition with minor corrosion and paint wear observed. | minor corrosion
Process Electrical | 2
Building and Process Structural | 3 | The manhole cover and frame was observed to be in fair condition with minor corrosion on the frame. | minor corrosion
Building and Process Structural | 3 | The base slab could not be inspected as it was submersed at the time of the assessment. The slab was assumed to be in fair condition based on its age and the condition of other visible structural components.
Building and Process Structural | 3 | The walls were observed to be in fair condition. Existing bitumous coating appears to be in fair condition.
Building and Process Structural | 3 | The ladder rungs were in fair condition with minor corrosion observed. | minor corrosion
Building and Process Structural | 3 | The platform was observed to be in fair condition. Corrosion was noted on all components. | Corrosion
Building and Process Structural | 3 | The steel hatch was in fair condition with moderate corrosion observed. | moderate corrosion
Building and Process Structural | 3 | The roof was observed to be in fair condition with minor bug holes. | minor bug holes
Process Electrical | 2
Process Electrical | 2
Process Electrical | 2 |  | minor corrosion
Process Electrical | 2
Process Electrical | 2
Process Piping | 3 | The Overflow piping was observed to be in fair condition. Corrosion on the visible portion of the piping as well as stone build-up in the piping at the wet well was observed. | Corrosion
Process Piping |  | As per the Region’s Water and Wastewater Facilities Design Manual (Halton Region, January 2012) an emergency overflow shall be provided for all wastewater pumping stations.
Building Services | 3 | The Baseboard Heater was in fair condition. Minor surface corrosion was observed. | minor surface corrosion
Process Piping | 3 | Pump 1 Discharge Piping was in fair condition. Moderate surface corrosion was observed throughout. | moderate surface corrosion
Process Piping | 3 | Pump 2 Discharge Piping was in fair condition. Moderate surface corrosion was observed throughout. | moderate surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 1 was in fair condition. Corrosion was observed on the visible parts of the pump. No performance issues were reported, however the pump was approaching the end of its remaining service life. | Corrosion
Building and Process Structural | 3 | Aluminum guardrail was observed to be in fair condition. Deposits were noted throughout. | deposits
Building and Process Structural | 3 | The concrete walls were observed to be in fair condition. Spalling was typically noted at form tie locations. | spalling
Building and Process Structural | 3 | Aluminum ladder was observed to be in fair condition. Anchor bolts, washers and nuts were noted to be corroded. Deposits were noted throughout. | Corrosion
Process Mechanical Equipment | 3 | Discharge Header Gate Valve was in fair condition. Moderate surface corrosion was observed. | moderate surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 1 Discharge Gate Valve was in fair condition. Severe surface corrosion was observed. | severe surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 1 Discharge Check Valve was in fair condition. Paint wear and moderate corrosion was observed. | paint wear
Process Mechanical Equipment | 3 | Sewage Lift Pump 2 Discharge Gate Valve was in fair condition. Severe surface corrosion was observed with a small loss of the valve flange. | severe surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 2 Discharge Check Valve was in fair condition. Severe surface corrosion was observed. | severe surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 2 was in fair condition. Corrosion was observed on the visible parts of the pump. No performance issues were reported , however the pump was approaching the end of its remaining service life. | Corrosion
Building and Process Structural | 3 | The concrete roof was observed to be in fair condition. Minor wear with exposed aggregates was noted on the underside. | minor wear
Building and Process Structural | 3 | Aluminum ladder was observed to be in fair condition. Anchor bolts, washers and nuts were noted to be corroded. Deposits were noted throughout. | Corrosion
Process Electrical | 2 | Main Breaker was in good condition. | minor discoloration
Process Electrical | 2 | Meter Socket was in good condition. | minor corrosion
Process Electrical | 2 | The Cathodic Protection was assumed to be in good condition. The installation of the cathodic protection system was assumed to coincide with the installation of the above grade panel.
Process Electrical | 2 | The enclosure was in good condition.
Process Electrical | 2 | The Transfer Switch was in good condition. | minor corrosion
Process Piping |  | As per the Region’s Water and Wastewater Facilities Design Manual (Halton Region, January 2012) an emergency overflow shall be provided for all wastewater pumping stations. It is therefore recommended to install overflow piping.
Building and Process Structural | 3 | Aluminum guardrail was observed to be in fair condition. Deposits were noted throughout. | deposits
Building and Process Structural | 3 | The service platform was observed to be in fair condition. Grating was not installed over opening to the bottom ladder. | not installed
Building and Process Structural | 3 | Aluminum ladder was observed to be in fair condition. Anchor bolts, washers and nuts were noted to be corroded. Deposits were noted throughout. | Corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 1 Discharge Gate Valve was in fair condition. Moderate surface corrosion and paint wear was observed. | moderate surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 2 Discharge Gate Valve was in fair condition. Moderate surface corrosion and paint wear was observed. | moderate surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 1 Discharge Check Valve was in fair condition. Moderate surface corrosion of the bolts and flanges was observed. | moderate surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 2 Discharge Check Valve was in fair condition. Moderate surface corrosion of the bolts and flanges was observed. | moderate surface corrosion
Process Piping | 3 | The Pump 1 Discharge Piping was in fair condition as moderate surface corrosion was observed throughout. | moderate surface corrosion
Process Piping | 3 | The Pump 2 Discharge Piping was in fair condition as moderate surface corrosion was observed throughout. | moderate surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 1 was submersed at the time of the inspection, but was assumed to be in fair condition based on its age. No performance issues were reported, however the pump was approaching the end of its remaining service life.
Process Mechanical Equipment | 3 | Sewage Lift Pump 2 was submersed at the time of the inspection, but was assumed to be in fair condition based on its age. No performance issues were reported, however the pump was approaching the end of its remaining service life.
Process Electrical | 2 | The Hydro Meter Socket was in good condition. | deposits
Building and Process Structural | 3 | Aluminum ladder was observed to be in fair condition. Anchor bolts, washers and nuts were noted to be corroded. Deposits were noted throughout. | Corrosion
Process Electrical | 2 | The equipment was in good condition. | moderate corrosion
Process Electrical | 2 | The Lighting Fixtures were in good condition, however they had surpassed their expected service life.
Process Electrical | 2 | Lighting fixtures were in good condition. | very minor corrosion
Building and Process Structural | 3 | The concrete foundation could not be inspected as it is buried. The foundation was assumed to be in fair condition based on its age and the condition of other visible structural components.
Building Services | 5 | Exhaust Fan 1 was not found at the time of the inspection. | not found
Building and Process Structural | 3 | The manhole cover and frame was observed to be in fair condition.
Building and Process Structural | 3 | The steel hatch was observed to be in fair condition. Gasket was missing between hatch and shaft. Minor corrosion and paint wear was also observed. | missing
Building and Process Structural | 3 | The steel tank was observed to be in fair condition. Corrosion was noted primarily at the bottom of the tank. | Corrosion
Building and Process Structural | 3 | The steel ladder was in fair condition with some minor paint wear also observed. | minor paint wear
Process Mechanical Equipment | 3 | Sewage Lift Pump 1 was in fair condition with moderate surface corrosion and paint wear observed. However, the pump was original to the facility and was approaching the end of its estimated remaining service life. Pump testing was not undertaken as part o | moderate surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 1 Motor was in fair condition. Minor surface corrosion and paint wear was observed. The motor was original to the facility and had surpassed its useful service life. Testing of the motor was not undertaken as part of this assessment. Base | minor surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 1 Discharge Check Valve was in fair condition. Minor surface corrosion, as well as corrosion of the bolts was observed. | minor surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 2 Discharge Check Valve was in fair condition. Minor surface corrosion, as well as corrosion of the bolts was observed. | minor surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 2 was in fair condition with moderate surface corrosion and paint wear observed. However, the pump was original to the facility and was approaching the end of its estimated remaining service life. Pump testing was not undertaken as part o | moderate surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 2 Motor was in fair condition. Minor surface corrosion and paint wear was observed. The motor was original to the facility and had surpassed its useful service life. Testing of the motor was not undertaken as part of this assessment. Base | paint wear
Building Services | 3 | The Sump Pump was in fair condition. Moderate surface corrosion was observed. | moderate surface corrosion
Building and Process Structural | 3 | The walls were observed to be in fair condition. Minor rust spots were noted. | minor rust spots
Building and Process Structural | 3 | The concrete roof was observed to be in fair condition. Bugholes were noted throughout along with minor rust spots. | minor rust spots
Process Electrical | 2 | Disconnect Switch was in good condition.
Process Electrical | 2 | Pump Control Panel was in good condition.
Process Electrical | 2 | Pump Control Panel was in good condition. | minor mechanical damage
Building and Process Structural | 3 | The concrete foundation could not be inspected as it is buried. The foundation was assumed to be in fair condition based on its age and the condition of other visible structural components.
Building and Process Structural | 3 | The steel tank was observed to be in fair condition. Corrosion was noted primarily at the bottom of the tank. | Corrosion
Building and Process Structural | 3 | The ladder was in fair condition. Minor corrosion and paint wear on the rungs was noted. | minor corrosion
Building and Process Structural | 3 | The steel hatch was observed to be in fair condition. Gasket was missing between hatch and shaft. | missing
Building Services | 3 | The Sump Pump was in fair condition. Moderate corrosion was observed. | moderate corrosion
Building and Process Structural | 3 | The base slab could not be inspected as it was submersed at the time of the assessment. The slab was assumed to be in fair condition based on its age and the condition of other visible structural components.
Building and Process Structural | 3 | The platform was observed to be in fair condition.
Building and Process Structural | 3 | The walls were observed to be in fair condition due to age.
Building and Process Structural | 3 | The guardrail was observed to be in fair condition. Deposits were noted. | deposits
Building and Process Structural | 4 | The roof was observed to be in poor condition. Corroded exposed rebar and concrete spalling was noted at hatch openings. | Corrosion
Process Instrumentation SCADA | 5 | The floats in the wet well were found missing, with the exception of one float. | missing
Building and Process Structural | 3 | The ladder was observed to be in fair condition. Deposits were noted. | deposits
Process Electrical | 2 | Lighting panel was in good condition. | oxidation
Building and Process Structural | 3 | The ladder rungs were observed to be in fair condition. Corrosion and deposits were observed throughout. | deposits
Process Electrical | 2 | Circuit Breaker was in good condition. | minor corrosion
Process Electrical | 2 | Distribution Panel was in good condition. | minor corrosion
Building and Process Structural | 3 | The concrete foundation could not be inspected as it is buried. The foundation was assumed to be in fair condition based on its age and the condition of other visible structural components.
Building Services | 3 | Sump Pump 1 assumed to be in fair condition based on its age.
Building and Process Structural | 3 | The steel ladder was observed to be in fair condition. Paint wear on the rungs was noted. | paint wear
Building and Process Structural | 3 | The steel tank was observed to be in fair condition. Corrosion was noted primarily at the bottom of the tank. | Corrosion
Process Electrical | 2 | Pump Control Panel was in good condition.
Process Mechanical Equipment | 3 | Sewage Lift Pump 1 was in fair condition. Moderate corrosion over the pump casing was observed. The pump was assumed to be original to the station and was approaching the end of its remaining service life. Based on the age of the pump, replacement is reco | moderate corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 2 was in fair condition. Moderate corrosion over the pump casing was observed. The pump was assumed to be original to the station and was approaching the end of its remaining service life. Based on the age of the pump, replacement is reco | moderate corrosion
Building Services | 3 | Ventilation Fan 1 was observed to be in fair condition with minor corrosion throughout. | minor corrosion
Building and Process Structural | 3 | The steel hatch was observed to be in fair condition with minor corrosion. Gasket was missing between hatch and shaft. | minor corrosion
Building and Process Structural | 3 | The walls were observed to be in fair condition. Minor rust spots were noted throughout. | minor rust spots
Building and Process Structural | 3 | The base slab could not be inspected as it was submersed at the time of the assessment. The slab was assumed to be in fair condition based on its age and the condition of other visible structural components.
Process Instrumentation SCADA | 3 | The Wet Well Float System was in fair condition in accordance with its age.
Building and Process Structural | 4 | The platform was observed to be in poor condition. Corrosion was noted on all components. | Corrosion
Building and Process Structural | 4 | The concrete roof was observed to be in poor condition. Exposed corroded reinforcement was noted. | Corrosion
Process Electrical | 2 | Fixtures were in good condition. | minor corrosion
Process Instrumentation SCADA | 3 | Wet Well Level Transmitter 1 was in fair condition. Screws were found loose from the cover and should be tightened during regular maintenance. | screws loose
Process Electrical | 2 | Power Converter was in good condition. The Region's operation staff reported that the voltage rating for the station is not compatible with a portable generator, therefore the station cannot be operational during a power failure.
Process Electrical | 2 | Equipment was in good condition.
Building and Process Structural | 3 | The concrete foundation could not be inspected as it is buried. The foundation was assumed to be in fair condition based on its age and the condition of other visible structural components.
Building Services | 5 | Exhaust Fan 1 was missing during the assessment. | missing
Process Piping | 3 | The Forcemain was assumed to be in fair condition based on its age. However, internal inspection of the piping was not undertaken.
Process Electrical | 2 | Lighting Fixture was in good condition.
Building and Process Structural | 3 | The steel hatch was observed to be in fair condition with minor corrosion. | minor corrosion
Building and Process Structural | 3 | The ladder was observed to be in fair condition with minor corrosion and paint wear on the rungs. | minor corrosion
Building and Process Structural | 3 | The steel tank was observed to be in fair condition. Corrosion was noted primarily at the bottom of the tank. | Corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 1 Inlet Gate Valve was in fair condition. Minor surface corrosion and paint wear was observed. | minor surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 1 Motor was in fair condition. Minor surface corrosion and paint wear was observed. The motor was original to the facility and was approaching the end of its useful service life. Testing of the motor was not undertaken as part of this ass | minor surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 1 was in fair condition with minor surface corrosion and paint wear observed. The pump base was in poor condition with moderate corrosion throughout. The pump was original to the facility and was approaching the end of its estimated remai | minor surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 1 Discharge Check Valve was in fair condition. Minor surface corrosion and paint wear was observed. | minor surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 2 Inlet Gate Valve was in fair condition. Minor surface corrosion and paint wear was observed. | minor surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 2 Motor was in fair condition. Minor surface corrosion and paint wear was observed. The motor was original to the facility and was approaching the end of its useful service life. Testing of the motor was not undertaken as part of this ass | minor surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 2 was in fair condition with minor surface corrosion and paint wear observed. The pump base was in poor condition with moderate corrosion throughout. The pump was original to the facility and was approaching the end of its estimated remai | minor surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 2 Discharge Check Valve was in fair condition. Minor surface corrosion and paint wear was observed. | paint wear
Building Services | 3 | The Sump Pump was in fair condition. Surface corrosion was observed throughout. | surface corrosion
Building and Process Structural | 3 | The roof was observed to be in fair condition due to age.
Building and Process Structural | 3 | The ladder was observed to be in fair condition. Deposits were noted. | deposits
Building and Process Structural | 3 | The manhole cover and frame was observed to be in fair condition. Moderate corrosion of the frame was observed. | moderate corrosion
Building and Process Structural | 3 | The base slab could not be inspected as it was submersed at the time of the assessment. The slab was assumed to be in fair condition based on its age and the condition of other visible structural components.
Building and Process Structural | 3 | The platform was observed to be in fair condition. A large opening for the float system was located at the bottom of the ladder, posing a slip and fall hazard. | large opening
Building and Process Structural | 3 | The walls were observed to be in fair condition due to age.
Process Electrical | 2 | Enclosure was in good condition.
Process Electrical | 2 | Panel was in good condition. | minor discoloration
Process Electrical | 2 | Panel was in good condition.
Building and Process Structural | 3 | The concrete foundation could not be inspected as it is buried. The foundation was assumed to be in fair condition based on its age and the condition of other visible structural components.
Building and Process Structural | 3 | The steel tank was observed to be in fair condition. Corrosion was noted throughout. | Corrosion
Process Piping | 3 | The Pump 1 Discharge Piping was observed to be in fair condition. Moderate surface corrosion was observed throughout. | moderate surface corrosion
Process Piping | 3 | The Pump 2 Discharge Piping was observed to be in fair condition. Moderate surface corrosion was observed throughout. | moderate surface corrosion
Process Mechanical Equipment | 4 | Sewage Lift Pump 2 Discharge Knife Gate Valve was in poor condition. Severe corrosion of the hand wheel and flanges was observed. | severe corrosion
Building and Process Structural | 4 | The ladder was observed to be in poor condition. Deposits were noted on the ladder. Brackets for attachment to tank were noted to be bent. | deposits
Process Electrical | 2 | Panel was in fair condition. | minor corrosion
Process Mechanical Equipment | 4 | Sewage Lift Pump 1 Discharge Knife Gate Valve was in poor condition. Severe surface corrosion of the handwheel and flanges was observed. | severe surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 1 Discharge Check valve was in fair condition. Moderate surface corrosion was observed throughout. | moderate surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 1 was submersed at the time of the inspection, but was assumed to be in fair condition based on its age.
Process Mechanical Equipment | 3 | Sewage Lift Pump 2 Discharge Check valve was in fair condition. Moderate surface corrosion was observed throughout. | moderate surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 2 was submersed at the time of the inspection, but was assumed to be in fair condition based on its age.
Building and Process Structural | 3 | The guardrails were observed to be in fair condition. Deposits were noted. | deposits
Building and Process Structural | 3 | The aluminum platform was observed to be in fair condition. Deposits were noted. | deposits
Building Services |  | The Region's operation staff reported that the electrical components in the panel overheats.
Building and Process Structural | 3 | The concrete foundation could not be inspected as it is buried. The foundation was assumed to be in fair condition based on its age and the condition of other visible structural components.
Building Services |  | Exhaust Fan 1 was missing.
Building and Process Structural | 4 | The platform was observed to be in poor condition. Corrosion was noted on all components. Grating was missing and not clipped to framing. | Corrosion
Building and Process Structural | 3 | The walls were observed to be in fair condition due to age.
Building and Process Structural | 3 | The ladder rungs were observed to generally be in fair condition. Corrosion was noted on rungs below platform level. | Corrosion
Building and Process Structural | 3 | The concrete roof was observed to be in fair condition due to age.
Building and Process Structural | 3 | The manhole cover and frame was observed to be in fair condition. Moderate surface corrosion was noted. | moderate surface corrosion
Process Piping | 3 | The visible section of the In-line Storage Pipe from the wet well platform was observed to be in fair condition.
Building and Process Structural | 3 | The base slab could not be inspected as it was submersed at the time of the assessment. The slab was assumed to be in fair condition based on its age and the condition of other visible structural components.
Building and Process Structural | 3 | The steel tank was observed to be in fair condition. Corrosion was noted primarily at the bottom of the tank. | Corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 2 was in fair condition. Minor surface corrosion and paint wear was observed. The pump was original to the facility and was approaching the end of its useful service life. Pump testing was not undertaken as part of this assessment. Based | minor surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 2 Motor was in fair condition. Minor surface corrosion and paint wear was observed. The motor was original to the facility and was approaching the end of its useful service life. | minor surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 1 was in fair condition. Minor surface corrosion and paint wear was observed. The pump was original to the facility and was approaching the end of its useful service life. Pump testing was not undertaken as part of this assessment. Based | minor surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 1 Motor was in fair condition. Minor surface corrosion and paint wear was observed. The motor was original to the facility and was approaching the end of its useful service life. | paint wear
Building Services | 3 | The Sump Pump was in fair condition. Moderate corrosion was observed. | moderate corrosion
Process Electrical | 2 | Panel was in good condition. | minor corrosion
Process Electrical | 2 | Panel was in good condition. | minor corrosion
Process Electrical | 2 | Main Breaker was in good condition. | minor surface corrosion
Building Services | 3 | The Air Supply Fan 1 was observed to be in fair condition. Moderate surface corrosion and paint wear was observed. | moderate surface corrosion
Process Electrical | 2 | Transformer was in good condition. | minor corrosion
Process Mechanical Equipment | 3 | By-pass Isolation Gate Valve 1 was observed to be in fair condition. Moderate surface corrosion of the handwheel and flanges was observed. | moderate surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 2 Discharge Gate Valve was observed to be in fair condition. Moderate surface corrosion of the handwheel and flanges was observed. | moderate surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 1 Discharge Gate Valve was observed to be in fair condition. Moderate surface corrosion of the handwheel and flanges was observed. | moderate surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 2 Discharge Check Valve was observed to be in fair condition. Moderate surface corrosion was observed. | moderate surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 1 Discharge Check Valve was observed to be in fair condition. Moderate surface corrosion was observed. | moderate surface corrosion
Process Piping | 3 | The Forcemain was assumed to be in fair condition based on its age. However internal inspection of the piping was not undertaken.
Process Piping | 3 | The Forcemain By-Pass Piping observed to be in fair condition. Moderate surface corrosion was observed throughout. | moderate surface corrosion
Process Mechanical Equipment | 3 | Forcemain By-Pass Knife Gate Valve was in fair condition. Moderate surface corrosion of the hand wheel and flanges was observed. | moderate surface corrosion
Building Services | 5 | Exhaust Fan 1 was not operational at the time of inspection and should be repaired or replaced. | not operational
Process Electrical | 2 | The Cathodic Protection system was assumed to be in good condition based on its age. | moderate corrosion
Process Mechanical Equipment | 3 | Forcemain Isolation Knife Gate Valve 1 was in fair condition. Moderate surface corrosion of the hand wheel and flanges was observed. | moderate surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 1 Discharge Knife Gate Valve was in fair condition. Moderate surface corrosion of the hand wheel and flanges was observed. | moderate surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 1 Discharge Check Valve was in fair condition. Moderate surface corrosion was observed. | moderate surface corrosion
Process Piping | 3 | The Pump 1 Discharge Piping was in fair condition. Moderate surface corrosion was observed throughout. | moderate surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 2 Discharge Knife Gate Valve was in fair condition. Moderate surface corrosion of the hand wheel and flanges was observed. | moderate surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 2 Discharge Check Valve was in fair condition. Moderate surface corrosion was observed. | moderate surface corrosion
Process Piping | 3 | The Pump 2 Discharge Piping was in fair condition. Moderate surface corrosion was observed throughout. | moderate surface corrosion
Process Instrumentation SCADA | 3 | Combustible Gas Monitor 1 was in fair condition and was approaching the end of its useful service life.
Building Services | 3 | The Diesel Fuel Storage Tank was observed to be in fair condition. The Region's operations reported that the fuel tank could not be filled and therefore, the station could not be operated during a power failure. There was no WHMIS pictograms for the diese | fuel tank could not be filled
Building Services | 3 | The Baseboard Unit Heater was in fair condition. Minor surface corrosion was observed. | minor surface corrosion
Building Architectural | 3 | The metal roof was observed to be in fair condition. Sections of roof were found to be damaged. | damaged
Building Architectural | 3 | The drywall was observed to be in fair condition. A few spots were noted to be damaged by moisture. | damaged by moisture
Building and Process Structural | 3 | The guardrail was observed to be in fair condition. A heavy amount of deposits were noted. Kickplate at bottom was missing. | heavy amount of deposits
Process Instrumentation SCADA | 3 | Wet Well Float System was observed to be in fair condition. Only one of the four floats shown on the record drawings was installed. | installed
Process Electrical | 2 | Lighting fixtures were in good condition but were approaching the end of their useful service life. | moderate corrosion
Process Mechanical Equipment | 3 | Pump 1 Discharge Ball Check Valve was in fair condition. Moderate corrosion throughout the valve surface was observed. | moderate corrosion
Process Mechanical Equipment | 3 | Pump 1 Discharge Knife Gate Valve was in fair condition. Moderate corrosion of the hand wheel and flanges was observed. | moderate corrosion
Process Mechanical Equipment | 3 | Pump 2 Discharge Knife Gate Valve was in fair condition. Moderate corrosion of the hand wheel and flanges was observed. | moderate corrosion
Process Mechanical Equipment | 3 | Pump 2 Discharge Ball Check Valve was in fair condition. Moderate corrosion throughout the valve surface was observed. | moderate corrosion
Process Piping | 3 | The Pump 1 Discharge Piping was in fair condition. Moderate surface corrosion throughout the piping was observed. | moderate surface corrosion
Process Piping | 3 | The Pump 2 Discharge Piping was in fair condition. Moderate surface corrosion throughout the piping was observed. | moderate surface corrosion
Process Electrical | 2 | Enclosure was in good condition with minor corrosion observed on panel interior. | missing
Process Electrical | 2 | Control Panel Enclosure was in good condition.
Process Electrical | 2 | Meter Socket was in good condition.
Building and Process Structural | 3 | The concrete foundation could not be inspected as it is buried. The foundation was assumed to be in fair condition based on its age and the condition of other visible structural components.
Building Services |  | Exhaust Fan 1 was missing during the assessment.
Process Piping | 3 | The Forcemain was assumed to be in fair condition based on its age. However, internal inspection of the piping was not undertaken.
Building and Process Structural | 3 | The hatch was in fair condition with corrosion and paint wear observed throughout. | Corrosion
Building and Process Structural | 3 | The steel tank was observed to be in fair condition. Corrosion was noted primarily at the bottom of the tank. | Corrosion
Process Piping | 3 | Pump 2 Suction Piping was in fair condition. Minor surface corrosion was observed. | minor surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 2 was in fair condition. Moderate surface corrosion and paint wear was observed. The pump was original to the facility and was approaching the end of its useful service life. Pump testing was not undertaken as part of this assessment. Ba | moderate surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 2 Motor was in fair condition. The motor was original to the facility and was approaching the end of its useful service life.
Process Piping | 3 | Pump 1 Suction Piping was in fair condition. Minor surface corrosion was observed. | minor surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 1 was in fair condition. Moderate surface corrosion and paint wear was observed. The pump was original to the facility and was approaching the end of its useful service life. Pump testing was not undertaken as part of this assessment. Ba | moderate surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 1 Motor was in fair condition. Minor surface corrosion and paint wear was observed. The motor was original to the facility and was approaching the end of its useful service life. | minor surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 1 Inlet Gate Valve was in fair condition. Minor surface corrosion and paint wear was observed. The valve was original to the facility and was approaching the end of its useful service life. | minor surface corrosion
Building and Process Structural | 3 | The steel ladder was observed to be in fair condition. A gap in a joint in the ladder was noted. | gap in joint
Building and Process Structural | 3 | The manhole cover and frame was observed to be in fair condition. Corrosion of the frame was noted. | Corrosion
Building and Process Structural | 3 | The ladder rungs were observed to be in fair condition with minor corrosion at the bottom. | minor corrosion
Building and Process Structural | 3 | The base slab could not be inspected as it was submersed at the time of the assessment. The slab was assumed to be in fair condition based on its age and the condition of other visible structural components.
Building and Process Structural | 3 | The platform was observed to be in fair condition. Corrosion was noted on all components. | Corrosion
Building and Process Structural | 3 | The roof was observed to be in fair condition.
Building and Process Structural | 3 | The precast walls were observed to be in fair condition due to age and working/atmospheric conditions.
Process Electrical | 2 | Equipment was in good condition.
Process Electrical | 2 | Splitter was in good condition. | moderate corrosion
Process Electrical | 2 | Circuit Breaker was in good condition. | minor corrosion
Building and Process Structural | 3 | The walls of Cell 1 were in fair to good condition. Previously repaired cracking was noted on the dividing common wall between the Cell 1 and Cell 2 walls. The lower 0.6m in height at the base of the common dividing wall showed signs of loss of cement/ex | loss of cement
Building and Process Structural | 3 | — The Cell 1 concrete platform, concrete stairs and aluminum guardrails was in good to fair condition. Calcium deposits were noted on the aluminum guardrails. The existing submarine access door was noted to be in good condition. | calcium deposits
Building and Process Structural | 3 | The Cell 1 concrete platform, concrete stairs and aluminum guardrails was in good to fair condition. Calcium deposits were noted on the aluminum guardrails. The existing submarine access door was noted to be in good condition. | calcium deposits
Building Architectural | 3 | The roofing system can't be inspected even if the cell is drained. It is buried. The roofing system was assumed to be in fair condition.
Building and Process Structural | 3 | The Cell 1 concrete platform, concrete stairs and aluminum guardrails was in good to fair condition. Calcium deposits were noted on the aluminum guardrails. The existing submarine access door was noted to be in good condition. | calcium deposits
Building and Process Structural | 3 | The Cell 1 concrete platform, concrete stairs and aluminum guardrails was in good to fair condition. Calcium deposits were noted on the aluminum guardrails. The existing submarine access door was noted to be in good condition. | calcium deposits
Building and Process Structural | 3 | The walls of Cell 2 were in fair to good condition. The majority of deficiencies were noted on the west dividing wall and at the north end of the east well. 30.6m of cracking was noted to be previously repaired with a cementitious waterproofing. Around 4 | cracking
Building and Process Structural | 3 | The Cell 2 concrete platform, concrete stairs and aluminum guardrails was in good to fair condition. Calcium deposits were noted on the guardrails. The existing submarine access door was noted to be in good condition. | calcium deposits
Building and Process Structural | 3 | The Cell 2 concrete platform, concrete stairs and aluminum guardrails was in good to fair condition. Calcium deposits were noted on the guardrails. The existing submarine access door was noted to be in good condition. | calcium deposits
Building and Process Structural | 3 | — The ladder located on the northwest corner of Cell 2 was found to have corrosion staining. The ladder was securely affixed to the wall. However, corrosion was noted on a few anchors. | corrosion staining
Building Architectural | 3 | The roofing system could not be inspected as it was covered at the time of the assessment. The roofing system was assumed to be in fair condition based on its age and the condition of other visible structural components.
Building and Process Structural | 3 | The Cell 2 concrete platform, concrete stairs and aluminum guardrails was in good to fair condition. Calcium deposits were noted on the guardrails. The existing submarine access door was noted to be in good condition. | calcium deposits
Building and Process Structural | 3 | The Cell 2 concrete platform, concrete stairs and aluminum guardrails was in good to fair condition. Calcium deposits were noted on the guardrails. The existing submarine access door was noted to be in good condition. | calcium deposits
Process Instrumentation SCADA | 4 | The Sodium Hypochlorite Tank and transmitter were being replaced as part of the contract for the construction of the Appleby Booster Station.
Building Services | 3 | Unit Heater EH-1 appeared to be in fair condition, however it had surpassed its typical service life.
Building Services | 3 | Motorized Damper was observed to be in fair condition. Minor surface corrosion was observed. | minor surface corrosion
Building Services | 3 | Unit Heater EH-2 was observed to be in fair condition. Minor corrosion of the blades was noted. | minor corrosion
Building Services | 3 | Dehumidifier was observed to be in fair condition. It was not in service at the time of the inspection. | not in service
Process Instrumentation SCADA | 3 | Sodium Hypochlorite Pump 2 Speed Indicator was observed to be in fair condition. The Region's staff reported that a new marshalling panel was installed and system was connected to the new booster station PLC.
Building Architectural | 3 | The submarine door was observed to be in fair condition. Minor surface corrosion was noted. | minor surface corrosion
Building Architectural | 3 | The submarine door was observed to be in fair condition. Minor corrosion was noted. | minor corrosion
Building Services | 3 | Exhaust Fan EF1 was observed to be in fair condition, however, it was approaching the end of its service life.
Process Instrumentation SCADA | 4 | Flow Switch was observed to be in poor condition with moderate corrosion throughout. The Region's staff reported that the flow siwtch had been replaced with a new flow meter in November 2018. | moderate corrosion
Process Piping | 3 | Cell 2 Inlet/Outlet Piping was observed to be in fair condition. Minor corrosion and paint wear was observed on the exposed sections of pipe. Previous repairs to the concrete insulation were noted. However, spalled concrete was observed. | minor corrosion
Process Mechanical Equipment | 3 | Reservoir Outlet Butterfly Valve (Cell 1 Header) was observed to be in fair condition. Minor corrosion was noted on the valve surface. The valve was approaching the end of its service life. | minor corrosion
Process Mechanical Equipment | 3 | Reservoir Outlet Check Valve (Cell 1 Header) was observed to be in fair condition. Minor corrosion was noted on the valve surface. | minor corrosion
Process Mechanical Equipment | 3 | Reservoir Outlet Butterfly Valve 2 (Cell 1 Header) was observed to be in fair condition. Minor corrosion was noted on the valve surface. The valve was approaching the end of its service life. | minor corrosion
Process Mechanical Equipment | 3 | Reservoir Outlet Motorized Butterfly Valve (Cell 1 Header) was observed to be in fair condition. Minor corrosion was observed on the valve surface. The valve was approaching the end of its service life. | minor corrosion
Process Mechanical Equipment | 3 | Reservoir Outlet Motorized Butterfly Valve Actuator (Cell 1 Header) was observed to be in fair condition. Handwheel was chained at the time of the inspection.
Building Services | 3 | Unit Heater EH-4 was observed to be in fair condition, however it was approaching the end of its service life.
Process Piping | 3 | Reservoir Overflow Piping was observed to be in fair condition. Staining of the concrete insulation was noted. | staining of the concrete insulation
Process Mechanical Equipment | 3 | Cell 1 & Cell 2 Isolation Butterfly Valve was observed to be in fair condition. Minor corrosion was noted. | minor corrosion
Process Instrumentation SCADA | 3 | Reservoir Cell 1 Level Switch was observed to be in fair condition. Bolts and screws were corroded. | corrosion
Process Instrumentation SCADA | 3 | Reservoir Cell 2 Level Switch was observed to be in fair condition. Bolts and screws were corroded. | corrosion
Building Services | 3 | Unit Heater EH-3 was observed to be in fair condition. Minor corrosion of blades was noted. | minor corrosion
Building Architectural | 3 | The exterior door was observed to be in fair condition. Door was noted to be very tight and hard to open/close. This is likely due to an improper door frame installation or improperly sized doors. Minor corrosion was noted on the door closers. | improper door frame installation
Building Architectural | 3 | The brick veneer was observed to be in fair condition. Mortar was noted to be missing in some areas. Brick damage was also noted. | missing
Building and Process Structural | 3 | The concrete floor was observed to be in fair condition. Previous crack injection repairs were noted on the underside of the floor. | crack injection repairs
Building and Process Structural | 3 | The concrete walls were observed to be in fair condition. Previous crack injection repairs were noted in the basement on walls adjacent to the reservoir cells. Minor hairline cracking was noted. | crack injection repairs
Building Architectural | 3 | The roofing system was observed to be in fair condition due to age.
Building Architectural | 3 | The wall and ceiling paint was observed to be in fair condition with heavy staining in the basement at previous crack injection areas. | heavy staining
Building Architectural | 3 | The protective curb coating was observed to be in fair condition on curbs. Coating was noted to be missing on floor. The Region’s staff reported that the Epoxy coating was being completed in November 2018. | missing
Process Electrical | 2 | Circuit Breaker was in good condition. | minor corrosion
Process Electrical | 2 | Disconnect Switch was in good condition. | minor corrosion
Process Electrical | 2 | Transformer was in good condition. | minor corrosion
Process Electrical | 2 | Lighting Panel was in good condition. | minor corrosion
Process Electrical | 2 | Control Panel was in good condition.
Process Electrical | 2 | Fixture was in good condition.
Process Electrical | 2 | Surge Protector was in good condition.
Process Mechanical Equipment | 3 | Washdown Pump was observed to be in fair condition. The Region's operators reported that the pump is not performing well when the wash down the reservoir. | not performing well
Process Mechanical Equipment | 3 | Washdown Pump Motor Drive was observed to be in fair condition.
Process Mechanical Equipment | 3 | Reservoir Outlet Check Valve 2 (Cell 1 Header) was observed to be in fair condition. Minor corrosion was seen on the valve surface. The valve was approaching the end of its service life. | minor corrosion
Process Piping | 3 | The visible section of Cell 1 Inlet/Outlet Piping was observed to be in fair condition. Minor corrosion and paint wear was observed.
Building and Process Structural | 3 | As per the Region’s Water and Wastewater Facilities Design Manual (Halton Region, January 2012) a minimum of 1 hour emergency storage is required. However, it was projected that the current conditions will only provide 10.65 minutes of emergency storage a
Building and Process Structural | 3 | Stairs observed to be in good condition and securely anchored. | securely anchored
Building and Process Structural | 3 | Frame and hatch were observed to be in good condition.
Building and Process Structural | 3 | Frame and hatch were observed to be in good condition.
Building and Process Structural | 3 | Grating and support structure was observed to be in good serviceable condition.
Building and Process Structural | 3 | The base slab could not be inspected as it was submersed at the time of the assessment. The slab was assumed to be in good condition based on its age and the condition of other visible structural components.
Building and Process Structural | 3 | Corroded previous anchors and supports were noted. Minor delamination of concrete was noted on north wall. Previous patching was also observed. Walls were observed to be in good condition. | minor delamination
Process Mechanical Equipment | 4 | Pump 2 Discharge Gate Valve was observed to be in fair condition. Moderate surface corrosion was observed. The valve had surpassed its service life. | moderate surface corrosion
Process Mechanical Equipment | 4 | Pump 1 Discharge Gate Valve was observed to be in fair condition. Moderate surface corrosion was observed. The valve had surpassed its service life. | moderate surface corrosion
Process Electrical | 2 | Disconnect Switch was in good condition.
Process Mechanical Equipment | 3 | Sewage Lift Pump 1 was submersed at the time of the inspection, but was assumed to be in good condition based on its age. However, as per the feasibility study carried out under this project, it is recommended to upsize Pump 1 to 14.1L/s at 15.8m TDH to m
Process Mechanical Equipment | 3 | Sewage Lift Pump 2 was submersed at the time of the inspection, but was assumed to be in good condition based on its age. However, as per the feasibility study carried out under this project, it is recommended to upsize Pump 2 to 14.1L/s at 15.8m TDH to m
Building and Process Structural | 3 | Underside of roof was observed with exposed aggregates. Top surface of roof slab could not be inspected as it is covered by interlocking pavers. Roof was observed to be in good condition. | exposed aggregates
Building and Process Structural | 3 | Exposed aggregates was noted at both chimney locations. Chimney was observed to be in good condition. | exposed aggregates
Building and Process Structural | 3 | Ladder was observed to be in good condition.
Building and Process Structural | 3 | Paint was observed to be weathered and missing in some areas. Minor corrosion was noted at missing paint locations. | weathered
Building and Process Structural | 4 | Paint was observed to be weathered and missing in some areas. Minor corrosion was noted at missing paint locations. Screen at opening was observed to be broken. | weathered
Process Piping | 4 | Pump Discharge Piping was observed to be in fair condition. Moderate surface corrosion was observed throughout the piping. | moderate surface corrosion
Process Piping | 3 | The Overflow Piping was assumed to be in good condition based on its age. Minor surface corrosion at the discharge was observed. | minor surface corrosion
Building and Process Structural | 3 | The columns were observed to be in fair condition. Minor honeycombing was noted at base pedestal. Cracking with efflorescence was noted on struts at a few areas. | minor honeycombing
Building and Process Structural | 3 | The roof was observed to be in fair condition. Cracking with efflorescence deposits were noted in a few areas. | cracking
Building and Process Structural | 3 | The roof was observed to be in fair condition. Hairline cracking with efflorescence deposits and rust spots were noted. | hairline cracking
Process Instrumentation SCADA | 3 | Cell 1 Level Transmitter was observed to be in fair condition and was approaching the end of its useful service life.
Process Mechanical Equipment | 3 | Washwater to Cell 2 Butterfly Isolation Valve was observed to be in fair condition. Moderate corrosion was observed on the valve surface. | moderate corrosion
Process Mechanical Equipment | 3 | Butterfly Isolation Valve #1 was observed to be in fair condition. Minor corrosion was observed on the valve surface. | minor corrosion
Process Mechanical Equipment | 3 | Washwater to Waste (Overflow) Butterfly Isolation Valve was observed to be in fair condition. Minor corrosion was observed on the valve surface. | minor corrosion
Process Mechanical Equipment | 3 | Washwater Butterfly Isolation Valve 2 was observed to be in fair condition. Minor corrosion was observed on the valve surface. | minor corrosion
Process Mechanical Equipment | 3 | Washwater to Cell 1 Butterfly Isolation Valve was observed to be in fair condition. Minor corrosion was observed on the valve surface. | minor corrosion
Building and Process Structural | 3 | The platform was observed to be in fair condition. A portion of grating was noted to be spanning in the wrong direction. | spanning in wrong direction
Building Architectural | 3 | The concrete veneer was observed to be in fair condition. Previous patching was noted. | previous patching
Building Architectural | 3 | The louvre was observed to be in fair condition. Minor corrosion from the exterior screen (chain-link) was noted. | minor corrosion
Building and Process Structural | 3 | The roof was observed to be in fair condition. Staining was noted around openings and between joints. | staining
Building and Process Structural | 3 | The grating was observed to be generally in fair condition. Damage was noted on portions of the grating likely due to items being dropped. | damage
Building Architectural | 3 | The door was observed to be in fair condition. Corrosion was noted at the bottom of the door frame. | corrosion
Building and Process Structural | 3 | The base slab could not be inspected as it was submersed at the time of the assessment. The slab was assumed to be in fair condition based on its age and the condition of other visible structural components.
Building Architectural | 3 | The door was observed to be in fair condition. Minor corrosion was noted on the door frame. | minor corrosion
Building and Process Structural | 3 | The floor was observed to be in good condition.
Building and Process Structural | 3 | The concrete walls were observed to be in fair condition. Previous crack injection repairs were noted in the basement.
Building Architectural | 3 | The roofing system was observed to be in fair condition and was approaching the end of its useful service life.
Building Services | 3 | Exhaust Fan 2 was observed to be in fair condition and was approaching the end of its useful service life.
Process Instrumentation SCADA | 3 | Inlet Flow Switch was assumed to be in fair condition. Minor surface corrosion was observed. | minor surface corrosion
Process Electrical | 2 | Pump Control Panel was in good condition. | moderate corrosion
Building Services | 3 | Water Booster Pump (for eyewash station) was observed to be in fair condition. Minor surface corrosion was observed. | minor surface corrosion
Process Mechanical Equipment | 4 | Washdown Pump 1 Motor Drive was in poor condition as moderate to severe corrosion was observed. | moderate corrosion
Process Mechanical Equipment | 4 | Reservoir Inlet Header Check Valve was observed to be in poor condition. Moderate corrosion was observed throughout. An internal inspection was not undertaken. | moderate corrosion
Process Mechanical Equipment | 4 | Reservoir Bypass Butterfly Isolation Valve was observed to be in poor condition. Moderate corrosion was observed on the valve surface. | moderate corrosion
Process Mechanical Equipment | 3 | Reservoir Outlet Header Check Valve was observed to be in fair condition. Minor corrosion was observed on the valve surface. An internal inspection was not undertaken. | minor corrosion
Process Mechanical Equipment | 3 | Cell 2 Outlet Air Release Valve was observed to be in fair condition. Minor corrosion was observed on the valve surface. | minor corrosion
Process Mechanical Equipment | 4 | Cell 2 Outlet Isolation Butterfly Valve was observed to be in poor condition. Moderate corrosion was observed on the valve surface. | moderate corrosion
Process Mechanical Equipment | 3 | Washdown Drain Piping Gate Valve 2 was observed to be in good condition. Minor corrosion was observed on the valve surface. | minor corrosion
Process Mechanical Equipment | 3 | Washdown Drain Piping Gate Valve 1 was observed to be in fair condition. Minor corrosion was observed on the valve surface. | minor corrosion
Process Mechanical Equipment | 4 | Washdown Pump 1 was in poor condition as severe corrosion was observed on the pump surface. The Region's Operators reported that the pump does not run under consistent speed while washing down the reservoir. | severe corrosion
Process Mechanical Equipment | 4 | Cell 1 Inlet Isolation Butterfly Valve was observed to be in poor condition. Moderate corrosion was observed throughout. | moderate corrosion
Process Mechanical Equipment | 4 | Washwater Pump 1 Suction Isolation Butterfly Valve 1 was observed to be in poor condition. Moderate to severe corrosion was observed on the valve surface. | moderate corrosion
Process Mechanical Equipment | 3 | Reservoir Washdown Pump Check Valve was observed to be in fair condition. Minor to moderate corrosion was observed on the valve surface. | minor corrosion
Process Piping | 3 | Washwater Piping was observed to be in fair condition. Minor corrosion was noted on piping surface. | minor corrosion
Process Mechanical Equipment | 3 | Washwater Pump 1 Suction Isolation Valve was observed to be in fair condition. Minor corrosion was observed on the valve surface. | minor corrosion
Process Mechanical Equipment | 4 | Washwater Pump 1 Suction Isolation Butterfly Valve 2 (from Cell 1) was observed to be in poor condition. Moderate corrosion was observed on the valve surface. | moderate corrosion
Process Mechanical Equipment | 3 | Cell 1 Inlet Air Release Valve was observed to be in fair condition. Minor corrosion was observed on the valve surface. | minor corrosion
Process Piping | 3 | 150mm Watermain Piping was assumed to be fair condition based on its age.
Process Piping | 3 | 750mm Watermain Piping was assumed to be fair condition based on its age.
Process Piping | 3 | Cell 1 Inlet/Outlet Piping was assumed to be in fair condition based on its age.
Building and Process Structural | 3 | The columns could not be inspected as they were submersed at the time of the assessment. The columns were assumed to be in fair condition based on their age and the condition of other visible structural components.
Building and Process Structural | 3 | The base slab could not be inspected as it was submersed at the time of the assessment. The slab was assumed to be in fair condition based on its age and the condition of other visible structural components.
Building and Process Structural | 3 | The roof could not be inspected as it was submersed at the time of the assessment. The roof was assumed to be in fair condition based on its age and the condition of other visible structural components.
Building and Process Structural | 3 | The walls could not be inspected as they were submersed at the time of the assessment. The walls were assumed to be in fair condition based on their age and the condition of other visible structural components.
Building and Process Structural | 3 | The ladder could not be inspected as it was submersed at the time of the assessment. The ladder was assumed to be in fair condition based on its age and the condition of other visible structural components.
Process Piping | 3 | 150mm Watermain Piping was assumed to be fair condition based on its age.
Building and Process Structural | 3 | The columns could not be inspected as they were submersed at the time of the assessment. The columns were assumed to be in fair condition based on their age and the condition of other visible structural components.
Building and Process Structural | 3 | The base slab could not be inspected as it was submersed at the time of the assessment. The slab was assumed to be in fair condition based on its age and the condition of other visible structural components.
Building and Process Structural | 3 | The roof could not be inspected as it was submersed at the time of the assessment. The roof was assumed to be in fair condition based on its age and the condition of other visible structural components.
Building and Process Structural | 3 | The walls could not be inspected as they were submersed at the time of the assessment. The walls were assumed to be in fair condition based on their age and the condition of other visible structural components.
Building and Process Structural | 3 | The ladder could not be inspected as it was submersed at the time of the assessment. The ladder was assumed to be in fair condition based on its age and the condition of other visible structural components.
Building and Process Structural | 3 | The wall could not be inspected as it was submersed at the time of the assessment. The wall was assumed to be in fair condition based on its age and the condition of other visible structural components.
Process Piping | 3 | Cell 3 Inlet/Outlet Piping was assumed to be in fair condition based on its age.
Building and Process Structural | 3 | The columns could not be inspected as they were submersed at the time of the assessment. The columns were assumed to be in fair condition based on their age and the condition of other visible structural components.
Building and Process Structural | 3 | The base slab could not be inspected as it was submersed at the time of the assessment. The slab was assumed to be in fair condition based on its age and the condition of other visible structural components.
Building and Process Structural | 3 | The roof could not be inspected as it was submersed at the time of the assessment. The roof was assumed to be in fair condition based on its age and the condition of other visible structural components.
Building and Process Structural | 3 | The walls could not be inspected as they were submersed at the time of the assessment. The walls were assumed to be in fair condition based on their age and the condition of other visible structural components.
Building and Process Structural | 3 | The ladder could not be inspected as it was submersed at the time of the assessment. The ladder was assumed to be in fair condition based on its age and the condition of other visible structural components.
Building and Process Structural | 3 | The wall could not be inspected as it was submersed at the time of the assessment. The wall was assumed to be in fair condition based on its age and the condition of other visible structural components.
Process Piping | 3 | Reservoir Drain Piping was assumed to be in fair condition based on its age.
Process Mechanical Equipment | 4 | Cell 3 Isolation Butterfly Valve appeared to be in fair condition and had surpassed its service life. Moderate corrosion was observed on the valve surface. No issues were reported for the valve. Based on its age, replacement is recommended in next 10 year | moderate corrosion
Process Mechanical Equipment | 4 | Cell 3 Mud Valve was observed to be in poor condition and had surpassed its service life. Moderate corrosion was observed. No issues were reported for the valve. Based on its age, replacement is recommended in the next 10 years. | moderate corrosion
Process Mechanical Equipment | 3 | Sample Sink was observed to be in fair condition. Minor to moderate corrosion was observed. | minor corrosion
Process Electrical | 2 | Pump Control Panel was in good condition. | minor corrosion
Process Instrumentation SCADA | 3 | Cell 2 Level Indicator was observed to be in fair condition. Minor corrosion was observed on the sealing bolts. One bolt was missing at the time of inspection. | minor corrosion
Process Instrumentation SCADA | 3 | Level Cell 3 Indicator was observed to be in fair condition. Minor corrosion was observed on the sealing bolts. One bolt was missing at the time of inspection. | minor corrosion
Process Mechanical Equipment | 4 | Cell 2 Isolation Butterfly Valve appeared to be in poor condition and had surpassed its service life. Moderate corrosion and paint wear was observed on the valve surface. No issues were reported for this valve. Based on its age, replacement is recommended | moderate corrosion
Process Mechanical Equipment | 4 | Valve Chamber Check Valve was observed to be in poor condition. Moderate to severe corrosion was observed on the valve surface. | moderate corrosion
Building and Process Structural | 3 | The concrete structure was observed to be in fair condition. According to drawing 669-S6F, a new floor slab and floor slab support wall and beams were constructed in 1966.
Building Architectural | 3 | The infill panels were observed to be in fair condition. Corrosion was noted on the frames of all panels within the access house and metal bars on the exterior. The Region's Operators reported ventilation and condensation issues at the three access houses | corrosion
Building Architectural | 3 | The roofing system was observed to be in fair condition. Wood soffit was deteriorating. | deteriorating
Building Architectural | 3 | The wall and ceiling paint was observed to be in fair condition. Ceiling paint was peeling throughout. | paint peeling
Building and Process Structural | 3 | The access hatches were observed to be in fair condition due to age. Minor corrosion was observed on the surface. | minor corrosion
Building and Process Structural | 3 | The valve chamber was not entered as it is a confined space. The concrete floor was observed to be in fair condition from above. The valve chamber was in atmpspheric conditions. Damp was noted at the bottom of the valve chamber. | damp
Building and Process Structural | 3 | The valve chamber was not entered as it is a confined space. The concrete walls were observed to be in fair condition from above. The valve chamber was in atmpspheric conditions.
Process Mechanical Equipment | 3 | Cell 1 Isolation Butterfly Valve was observed to be in fair condition. Minor corrosion was observed on the valve surface. | minor corrosion
Building Architectural | 3 | The infill panels were observed to be in fair condition. Corrosion was noted on the frames of all panels within the access house and metal bars on the exterior. The Region's Operators reported ventilation and condensation issues at the three access houses | corrosion
Building Architectural | 3 | The roofing system was observed to be in fair condition due to age.
Building and Process Structural | 3 | The access hatch was observed to be in fair condition with minor paint wear. | minor paint wear
Building Architectural | 3 | The wall and ceiling paint was observed to be in fair condition. Paint was noted to be peeling on the ceiling. | paint peeling
Building and Process Structural | 3 | The access hatches were observed to be in fair condition due to age. Minor corrosion was observed on the surface. | minor corrosion
Building and Process Structural | 3 | The valve chamber was not entered as it is a confined space. The concrete floor was observed to be in fair condition from above. The valve chamber was in atmpspheric conditions. Damp was noted at the bottom of the valve chamber. | damp
Building and Process Structural | 3 | The valve chamber was not entered as it is a confined space. The concrete walls were observed to be in fair condition from afar and based on the condition of other visible structural components. The valve chamber was in atmpspheric conditions damp was not | damp
Building and Process Structural | 3 | The ladder was observed to be in fair condition due to age. The valve chamber was in atmospheric conditions and damp was noted, which may increase the deterioration rate of the ladder. | deterioration
Building Architectural | 3 | The infill panels were observed to be in fair condition. Corrosion was noted on all panels from within the access house and metal bars on the exterior. The Region's Operators reported ventilation and condensation issues at the three access houses as was e | corrosion
Building Architectural | 3 | The wall and ceiling paint was observed to be in fair condition. Staining from miscellaneous metals was observed on the walls. | staining
Building and Process Structural | 3 | The grating was observed to be in fair condition with minor corrosion and deposits. | minor corrosion
Building and Process Structural | 3 | The access hatch was observed to be in fair condition due to age. Minor corrosion was observed on the surface. | minor corrosion
Building and Process Structural | 3 | The valve chamber was not entered as it is a confined space. The concrete floor was observed to be in fair condition from above. The valve chamber was in atmpspheric conditions. Damp was noted at the bottom of the valve chamber. | damp
Building and Process Structural | 3 | The valve chamber was not entered as it is a confined space. The concrete walls were observed to be in fair condition from above. The valve chamber was in atmpspheric conditions Damp was noted on the walls of the valve chamber. | damp
Building and Process Structural | 3 | The ladder was observed to be in fair condition due to age. The valve chamber was in atmospheric conditions and damp was noted, which may increase the deterioration rate of the ladder. | damp
Process Electrical | 2 | Lighting Panel was in good condition. | moderate corrosion
Process Electrical | 2 | Meter Socket was in good condition. | minor surface corrosion
Process Electrical | 2 | Meter Socket was in good condition. | outdated
Process Mechanical Equipment | 4 | Valve Chamber Air Release Valve was observed to be in poor condition and had surpassed its service life. Moderate to severe corrosion was observed on the valve surface. No issue were reported for the valve. Based on its age, replacement is recommended in | moderate corrosion
Process Mechanical Equipment | 4 | Valve Chamber Drain Valve was observed to be in poor condition and had surpassed its service life. Moderate to severe corrosion was observed on the valve surface. No issues were reported for the valve. Based on its age, replacement is recommended in the n | moderate corrosion
Process Piping | 3 | Reservoir Cell 1 400mm Inlet Piping was assumed to be in fair condition.
Process Piping | 3 | Reservoir Cell 1 400mm Overflow Piping was assumed to be in fair condition.
Process Piping | 3 | Reservoir Cell 1 Inlet/Discharge Piping was assumed to be in fair condition.
Building Services | 3 | Reservoir Sample Pump was in fair condition based on its age. Sample Pump was installed beneath a hatch that was not able to be opened during the assessment.
Building Services | 3 | Building Louvre was observed to be in fair condition. Minor corrosion was observed on the surface. | minor corrosion
Process Electrical | 2 | Transfer Switch was in good condition. | minor corrosion
Building Services | 3 | Reservoir Cell 2 Vent was observed to be in fair condition. Minor corrosion and paint wear was observed. | minor corrosion
Process Mechanical Equipment | 4 | Valve Chamber #2 Gate Valve #2 was assumed to be in poor condition as the valve had surpassed its expected service life.
Process Mechanical Equipment | 3 | Valve Chamber #1 Inlet/Outlet Gate Valve #1 was observed to be in fair condition and had surpassed its expected service life. Moderate corrosion was observed on the valve surface. The valve was not regularly used/exercised as part of the Region's preventa | moderate corrosion
Process Mechanical Equipment | 3 | Valve Chamber #1 Discharge Non-rising Stem Gate Valve #2 was observed to be in fair condition as the valve had surpassed its expected service life and moderate corrosion was observed on the valve surface. The valve was not regularly used/exercised as part | moderate corrosion
Building Architectural | 3 | The door was observed to be in fair condition. Moderate corrosion was observed on the surface of the door frame. | moderate corrosion
Building and Process Structural | 3 | The walls were covered in insulation on the interior. Exterior portion of blockwall was observed to be in fair condition.
Building and Process Structural | 3 | The roof could not be inspected as it was covered in insulation. The roof was assumed to be in fair condition based on its age and the condition of other visible structural components.
Building Architectural | 3 | The roofing system was observed to be in fair condition. Downspouts on side of building were noted to be slightly bent. | slightly bent
Building and Process Structural | 3 | The ladder was observed to be in fair condition. Rung spacing was observed to be greater than code requirements. | greater than code requirements
Building and Process Structural | 3 | The concrete columns were observed to be in fair condition. Minor bugholes were noted at the bottom of the column. | minor bugholes
Building and Process Structural | 3 | The concrete floor was observed to be in fair condition.
Building and Process Structural | 3 | The concrete roof was observed to be in fair condition. Previous crack injection repairs were noted. New hairline cracking, rust spots, concrete spalling and embedded wood was also noted. | hairline cracking
Building and Process Structural | 3 | The concrete walls were observed to be in fair condition. Cracking with efflorescence deposits and deteriorated joint sealants at previous infilled openings were noted. Signs of potential leaks were noted at the top of the wall. | cracking
Process Piping | 3 | Reservoir Cell 1 400mm Inlet Piping was observed to be in fair condition. Minor corrosion was observed on the pipe surface. | minor corrosion
Process Mechanical Equipment | 4 | Cell 1 Inlet Check Valve was observed to be in poor condition and had surpassed its expected service life. The valve may have been corroded pior covered in a build-up of iron, as is common in groundwater. | corroded
Process Mechanical Equipment | 4 | Cell 1 Discharge Gate Valve was observed to be in poor condition and had surpassed its expected service life. The valve may have been corroded or covered in a build-up of iron, as is common in groundwater. | corroded
Process Mechanical Equipment | 4 | Cell 1 Inlet/Outlet Gate Valve was observed to be in poor condition and it had surpassed its expected service life. The valve may have been corroded or covered in a build-up of iron, as is common in groundwater. | corroded
Building Services | 3 | Reservoir Cell 1 Vent was observed to be in fair condition. Minor corrosion and painted wear was observed. | minor corrosion
Building Services | 4 | Reservoir Cell 2 Ventilator was observed to be in poor condition. Minor corrosion was observed on the surface. | minor corrosion
Building and Process Structural | 3 | The concrete floor was observed to be in fair condition.
Building and Process Structural | 3 | The concrete walls were generally observed to be in fair condition. Cracking with efflorescence deposits was noted on walls adjacent to reservoir. Active leaking crack was noted on the east wall. | cracking
Process Piping | 3 | Reservoir Cell 2 Discharge Piping was assumed to be in fair condition based on visible section of pipe in the Valve Pit. Minor corrosion was observed throughout the piping in the valve pit. | minor corrosion
Process Piping | 3 | Reservoir Cell 2 Drain Piping was assumed to be in fair condition based on the visible section of pipe in the valve pit. Minor corrosion was observed throughout the piping in the valve pit. | minor corrosion
Process Piping | 3 | Reservoir Cell 2 Overflow Piping was assumed to be in fair condition based on the visible section of the pipe in the valve pit. Minor corrosion was observed throughout the piping in the valve house. | minor corrosion
Building and Process Structural | 3 | The ladder was observed to be in fair condition. Anchor bolts, washers and nuts were observed to be missing at a few locations. | missing
Process Mechanical Equipment | 3 | Cell 2 Discharge Butterfly Valve was observed to be in fair condition and had surpassed its expected service life. Minor corrosion was observed on the valve surface. | minor corrosion
Process Mechanical Equipment | 3 | Cell 2 Discharge Check Valve was observed to be in fair condition and had surpassed its expected service life. However, an internal inspection of the valve was not undertaken. Minor corrosion was observed on the valve surface. | minor corrosion
Process Mechanical Equipment | 3 | Cell 2 Inlet Check Valve was observed to be in fair condition and had surpassed its expected service life. However, an internal inspection of the valve was not undertaken. Minor corrosion was observed on the valve surface. | minor corrosion
Process Mechanical Equipment | 3 | Reservoir Connection Pipe Butterfly Valve was observed to be in fair condition and had surpassed its expected service life. Minor corrosion was observed on the valve surface. | minor corrosion
Process Piping | 3 | Reservoir Cell 1 & Cell 2 400mm Connection Piping was assumed to be in fair condition based on visible section of pipe in the valve pit. Minor corrosion was observed throughout the piping in the valve pit. | minor corrosion
Process Mechanical Equipment | 3 | Reservoir Connecting Pipe Butterfly Valve was observed to be in fair condition as the valve had surpassed its expected service life. Minor corrosion was observed on the valve surface. | minor corrosion
Process Mechanical Equipment | 3 | Cell 2 Drain Pipe Butterfly Valve was observed to be in fair condition and had surpassed its expected service life. Minor corrosion was observed on the valve surface. | minor corrosion
Building Services | 3 | Sump Pump was observed to be in fair condition and had surpassed its expected service life.
Process Mechanical Equipment | 5 | Valve Chamber #3 Air Release Valve was observed to be in very poor condition as the valve had surpassed its expected service life and moderate corrosion was observed throughout the surface of the valve. The valve was most likely not operational given its | moderate corrosion
Process Mechanical Equipment | 3 | Valve Chamber #3 Gate Valve was observed to be in fair condition and had surpassed its expected service life. Moderate corrosion was observed on the valve surface. | moderate corrosion
Process Mechanical Equipment | 3 | Valve Chamber #4 Gate Valve was observed to be in fair condition and had surpassed its expected service life. Moderate corrosion was observed on the surface of the valve. A leak was observed at the pipe penetration in the manhole. The water in the manhole | moderate corrosion
Process Mechanical Equipment | 3 | Valve Chamber #2 Gate Valve #1 was observed to be in fair condition as the valve had surpassed its expected service life. Moderate corrosion was observed on the valve surface. | moderate corrosion
Building and Process Structural | 3 | The ladder was observed to be in fair condition. Bottom rung was observed to be too high off the floor. Anchor bolts were noted to be corroded. | too high off the floor
Building and Process Structural | 3 | The columns were generally noted to be in fair condition. Rust spots and heavy corrosion deposits were noted on a few columns | rust spots
Building and Process Structural | 3 | The concrete floor was observed to be in fair condition. Joint sealants were observed to be in fair condition but not NSF 61 certified. | not certified
Building and Process Structural | 3 | The concrete roof was observed to be in fair condition. Minor cracking with efflorescence was noted. Corroded form ties were noted throughout. | minor cracking
Building and Process Structural | 3 | The concrete walls were observed to be in fair condition. Minor cracking with efflorescence and rust spots were noted. Efflorescence deposits were noted on joints. Joint sealants were noted to be in fair condition but not NSF 61 certified. | minor cracking
Process Piping | 3 | Reservoir Cell 2 Inlet Piping was observed to be in fair condition.
Building and Process Structural | 3 | The guardrails were observed to be in fair condition. Deposits were noted. | deposits
Building and Process Structural | 3 | The overflow trough was not inspected as it was inaccessible. The overflow trough were assumed to be in fair condition based on its age and other visible structural components.
Building Services | 3 | The Sink was observed to be in fair condition.
Building Services | 3 | Sump Pump 1 was observed to be in fair condition. Moderate surface corrosion was observed. | moderate surface corrosion
Building Services | 3 | City Water Regulating Check Valve 1 was observed to be in fair condition. Moderate surface corrosion was observed. Dripping condensation was noted on the service water line. However, no performance issues were identified during the assessment. | moderate surface corrosion
Building and Process Structural | 3 | The ladder was observed to be in fair condition.
Building and Process Structural | 3 | The concrete tank was observed to be in fair condition.
Building and Process Structural | 3 | The access hatch was observed to be in fair condition. Lifting handles were noted to be damaged or missing due to snow plow. | damaged
Building and Process Structural | 3 | The hatch was observed to be in fair condition.
Building and Process Structural | 3 | The hatch was observed to be in fair condition.
Building and Process Structural | 3 | The precast roof was observed to be in fair condition.
Building Architectural | 3 | The ceramic tiles were observed to be in fair condition. A few tiles on the wall by the double door was noted to be cracked. | cracked
Building and Process Structural | 3 | The crane beam was observed to be in fair condition.
Building and Process Structural | 3 | The roof was covered and could not be inspected. The roof was assumed to be in fair condition based on its age and other visible structural components.
Building and Process Structural | 3 | The concrete floor was observed to be in fair condition.
Building and Process Structural | 3 | The concrete blockwalls were covered by tiles and brick. The concrete blockwalls were assumed to be in fair condition based on their age and other visible structural components.
Process Mechanical Equipment | 3 | Valve Chamber 1 Priming Valve was observed to be in fair condition. Moderate corrosion was observed. | moderate corrosion
Building and Process Structural | 3 | The staircase was observed to be in fair condition.
Building and Process Structural | 3 | The concrete beams were observed to be in fair condition. Corrosion and spalled concrete was noted. | corrosion
Building and Process Structural | 3 | The aluminum platform was observed to be in fair condition.
Building and Process Structural | 3 | The floor was submerged and could not be inspected. The floor was assumed to be in fair condition based on its age and other visible structural components.
Building and Process Structural | 3 | The concrete walls were observed to be in fair condition. Spalled concrete was noted at south end at base of wall. | spalled concrete
Building and Process Structural | 3 | The concrete floor was observed to be in fair condition. Spalling was noted on the underside. | spalling
Building Architectural | 3 | The ceramic tiles were observed to be in fair condition due to environmental factors.
Building and Process Structural | 3 | The concrete blockwalls were covered by tiles and brick. The concrete blockwalls were assumed to be in fair condition based on their age and other visible structural components.
Building and Process Structural | 3 | The roof was observed to be in fair condition. Corroded exposed rebar was observed. | corroded
Building and Process Structural | 3 | The checker plate cover was observed to be in fair condition.
Building and Process Structural | 3 | The checker plate cover was observed to be in fair condition.
Process Mechanical Equipment | 3 | Valve Chamber 2 Gate Valve 2 was in fair condition. Moderate corrosion of the flanges was observed. | moderate corrosion
Process Mechanical Equipment | 3 | Valve Chamber 2 Gate Valve 1 was in fair condition. Moderate corrosion of the flanges was observed. | moderate corrosion
Building Architectural | 3 | The wall and ceiling paint was observed to be in fair condition. Peeling paint was noted in a few areas. | peeling paint
Building and Process Structural | 3 | The concrete walls were observed to be in fair condition. Concrete spalling was on the north wall. Signs of leakage were noted at crane beam mount on north wall. | concrete spalling
Building and Process Structural | 3 | The concrete floor was observed to be in fair condition.
Building and Process Structural | 3 | The checker plate cover was observed to be in fair condition.
Building and Process Structural | 3 | The concrete staircase was observed to be in fair condition.
Building and Process Structural | 3 | The handrail was observed to be in fair condition.
Process Electrical | 2 | Lighting Panel was in good condition.
Process Electrical | 2 | Lighting Panel was in good condition. | operation issues
Process Electrical | 2 | Transformer was in good condition. | operation issues
Process Electrical | 2 | Generator was approaching the end of its theoretical service life, however it appeared to be in good condition. | operation issues
Process Electrical | 2 | Fixtures were in good condition. | minor corrosion
Process Electrical | 2 | Fixtures were in good condition. | minor corrosion
Process Electrical | 2 | Cathodic Protection was assumed to be in good condition. The installation of the cathodic protection system was assumed to coincide with the installation of the above grade panel.
Process Mechanical Equipment | 3 | Sewage Lift Pump 3 Discharge Check Valve was in fair condition. Moderate surface corrosion was observed. However, no performance issues were identified during the assessment. | moderate surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 2 Discharge Check Valve was in fair condition. Moderate surface corrosion was observed. However, no performance issues were identified during the assessment. | moderate surface corrosion
Process Mechanical Equipment | 3 | Sewage Lift Pump 1 Discharge Check Valve was in fair condition. Moderate surface corrosion was observed. However, no performance issues were identified during the assessment. | moderate surface corrosion
Process Instrumentation SCADA | 3 | The Flow Meter was observed to be in fair condition. Minor corrosion of the flanges was observed. | minor corrosion
Building and Process Structural | 3 | The ladder could not be inspected as it was submersed at the time of the assessment.Cole Engineeirng Group Limited and Region's staff reproted that a new ladder/ safety staris and rails to need to be installed to access Cell 1.
Building and Process Structural | 3 | The ladder could not be inspected as it was submersed at the time of the assessment. Cole Engineeirng Group Limited and Region's staff reproted that a new ladder/ safety staris and rails to need to be installed to access Cell 1.
Building and Process Structural | 3 | The columns could not be inspected as they were submersed at the time of the assessment. The columns were assumed to be in fair condition based on its age and the condition of other visible structural components. Cole Engineering completed an internal ins
Building and Process Structural | 3 | The base slab could not be inspected as it was submersed at the time of the assessment. The slab was assumed to be in fair condition based on its age and the condition of other visible structural components.
Building and Process Structural | 3 | The foundation could not be inspected as it is buried. The foundation was assumed to be in fair condition based on its age and the condition of other visible structural components.
Building and Process Structural | 3 | The roof could not be inspected as it was submersed at the time of the assessment. The roof was assumed to be in fair condition based on its age and the condition of other visible structural components. Cole Engineering completed an internal inspection of
Building Architectural | 3 | The door was observed to be in fair condition. Door sweep was loose at bottom of door. Gap between bottom of door frame and top of floor was observed. Corrosion on edge of door was also noted. | loose
Building and Process Structural | 3 | The concrete platform was observed to be in fair condition. Additional topping and drainage channels were added to try to resolve ponding water issue. The Region's operators reported that ponding water/ice on surface of the loading area creates a slip/tri | ponding water issue
Building and Process Structural | 3 | The guardrails were observed to be in fair condition. Due to additional topping on floor, guardrails are less than 1070mm in height as mandated by code. This should be rectified when grinding and resurfacing of the loading area is completed. | less than 1070mm in height as mandated by code
Building and Process Structural | 3 | The staircase and handrails were observed to be in fair condition. A large gap between the top of stair tread and bottom of base plate was noted. | large gap
Building Architectural | 3 | The exterior stone cladding and precast coping was observed to be in good to fair condition. A few areas where the precast coping joins together was not fully caulked. Efflorescence deposits were noted and step cracking was noted in the mortar. Wet spots | not fully caulked
Building Architectural | 3 | The door was observed to be in fair condition. Minor corrosion was noted on the door closer arm. | minor corrosion
Building and Process Structural | 3 | The walls were observed to be in fair condition. Cracking with signs of leakage was noted on walls adjacent to the clearwells. | cracking
Building and Process Structural | 3 | The concrete floor was observed to be in fair condition. Previous crack injections were noted. A rough surface was noted in a few areas which may pose a trip hazard. | rough surface
Building and Process Structural | 3 | The walls were observed to be in fair condition. Previous crack injections were noted.
Building and Process Structural | 3 | The concrete columns were generally observed to be in fair condition. A wide crack was observed on the south side of the pipe gallery. | wide crack
Building and Process Structural | 3 | The beams were observed to be in fair to poor condition. Exposed steel was noted to be corroded. | exposed steel
Building and Process Structural | 3 | The grating was observed to be in fair condition. Parts of grating has been cut for previous decommissioned equipment. | parts of grating has been cut
Building and Process Structural | 4 | The concrete walls were observed to be in fair to poor condition based on the visible areas from the pipe gallery, transformer room and fuel storage room. Expansion joints were noted to be previously repaired by crack injection. Cole Engineering completed
Building Architectural | 3 | The wall and ceiling paint was observed to be in fair condition. Minor corrosion was noted on the steel beams. | minor corrosion
Building and Process Structural | 3 | The steel columns were observed to be in fair condition based on age.
Building and Process Structural | 3 | The concrete blockwalls were observed to be in fair condition. Hairline cracking was noted. | hairline cracking
Building and Process Structural | 3 | The grating was observed to be in fair condition. Span of grating at surge tanks is too large and has bent the grating. | span of grating at surge tanks is too large
Building and Process Structural | 3 | The roof was observed to be in fair condition. Minor corrosion was noted. | minor corrosion
Building and Process Structural | 3 | The steel beams were observed to be in fair condition. Corrosion was noted at weld locations. | corrosion
Building and Process Structural | 3 | The steel beams were observed to be in fair condition with minor corrosion noted. | minor corrosion
Building Architectural | 3 | The skylight was observed to be in fair condition. Corrosion was noted at the bottom of the skylight curb and may be due to moisture penetration. | corrosion
Building Architectural | 3 | The exterior brick veneer and precast coping was observed to be in good to fair condition. A few areas where the precast coping joins together was not fully caulked. Wet spots and efflorescence deposits due to insufficient overhang of precast coping. | not fully caulked
Building and Process Structural | 3 | The staircase and handrails were observed to be in fair condition. A large gap between top of stair tread and bottom of base plate was noted. | large gap
Building and Process Structural | 3 | The steel framing was observed to be in fair condition. Corrosion was noted on the framing and on the precast clip angles. | corrosion
Building Architectural | 3 | The door was observed to be in fair condition. Staining due to leaking water was noted at the bottom. Corrosion of door frame is accelerated due to this. | staining
Building and Process Structural | 3 | The access hatch was observed to be in fair condition. Staining and discolouration was noted. | staining
Building and Process Structural | 3 | The ladder was observed to be in fair condition. Staining and discolouration was noted. | staining
Building and Process Structural | 3 | The access stairs and handrails were observed to be in fair condition. Staining and discolouration was noted. Although the stairs were installed in recent years, the environment of the access house had accelerated the corrosion. Stairs can be replaced wit | staining
Building and Process Structural | 3 | The concrete walls were observed to be in fair condition. Bottom edge of wall against clearwells has been previously crack injected. Wide vertical crack was observed next to cell #2 submarine door. | wide vertical crack
Building Architectural | 3 | The exterior stone cladding and precast coping was observed to be in good to fair condition. A few areas where the precast coping joins together was not fully caulked. | not fully caulked
Building and Process Structural | 3 | The ladder was observed to be in fair condition. Minor corrosion of the rungs was noted. | minor corrosion
Building and Process Structural | 3 | The access hatch was observed to be in fair condition. Minor corrosion and paint wear was noted. | minor corrosion
Building and Process Structural | 3 | The access hatch was observed to be in fair condition in accordance with its age.
Building and Process Structural | 3 | The staircase and handrails were observed to be in fair condition. A large gap between top of stair tread and bottom of base plate was noted. | large gap
Process Electrical | 2 | Interior Lighting Fixtures were observed to be in good condition, however they were approaching the end of their typical useful life. | minor corrosion
Process Mechanical Equipment | 3 | Zone 2 Surge Tank Manual Butterfly Valve V0011 was in fair condition. Minor corrosion was observed on valve surface. | minor corrosion
Process Mechanical Equipment | 3 | Zone 2 Bypass Manual Butterfly Valve V0028 was in good condition. Corrosion of the pipe flange was observed. | corrosion
Process Mechanical Equipment | 3 | Highlift Booster Pump 8 Discharge Check Valve was in fair condition. Minor corrosion of the bolts was observed. | minor corrosion
Building Mechanical | 3 | Moderate surface corrosion was observed. | moderate surface corrosion
Structural | 3 | Minor corrosion was noted. | minor corrosion
Building Mechanical | 3 | Moderate surface corrosion was observed. | moderate surface corrosion
Building Mechanical | 3 | Moderate surface corrosion was observed. | moderate surface corrosion
Building Mechanical | 3 | Moderate corrosion was observed. | moderate corrosion
Building Mechanical | 3 | Major surface corrosion was observed. | major surface corrosion
AC | 2 | Minor corrosion on the door frame was observed. | missing
Building Mechanical | 3 | Minor surface corrosion was observed. | minor surface corrosion
Process Mechanical | 3 | Minor surface corrosion was observed. | minor surface corrosion
Structural | 3 | Minor corrosion was noted. | minor corrosion
Process Mechanical | 3 | Moderate surface corrosion and paint wear was observed. | moderate surface corrosion
Process Mechanical | 3 | Minor surface corrosion was observed. | minor surface corrosion
Process Mechanical | 3 | Minor surface corrosion and paint wear was observed. | minor surface corrosion
Process Mechanical | 3 | Minor corrosion and paint wear was observed. | minor corrosion
Process Mechanical | 3 | Minor corrosion and paint wear was observed. | minor corrosion
Process Mechanical | 3 | Minor surface corrosion and paint wear was observed. | minor surface corrosion
Process Mechanical | 3 | Moderate surface corrosion and paint wear was observed. | moderate surface corrosion
Process Mechanical | 3 | Moderate surface corrosion and paint wear was observed. | moderate surface corrosion
Process Mechanical | 3 | Moderate surface corrosion was observed. | moderate surface corrosion
Process Mechanical | 3 | Minor corrosion and paint wear was observed. | minor corrosion
Process Mechanical | 3 | Minor corrosion and paint wear was observed. | minor corrosion
Process Mechanical | 3 | Minor surface corrosion and paint wear of the bolts and flanges was observed. | minor surface corrosion
Process Mechanical | 3 | Moderate surface corrosion and paint wear was observed. | moderate surface corrosion
Process Mechanical | 3 | Moderate surface corrosion and paint wear was observed. | paint wear
Building Mechanical | 3 | Moderate surface corrosion was observed. | moderate surface corrosion
Building Mechanical | 3 | Moderate surface corrosion was observed. | moderate surface corrosion
Process Mechanical | 3 | Minor paint wear of the handwheel was observed. | minor paint wear
Process Mechanical | 3 | Minor paint wear was observed. | minor paint wear
Process Mechanical | 3 | Minor surface corrosion and paint wear was observed. | minor surface corrosion
Process Mechanical | 3 | Minor surface corrosion and paint wear was observed. | minor surface corrosion
AC | 2 | Missing/fallen block above the louvre was observed. | weathered
AC | 2 | Minor corrosion at the base of the door frame was observed. | deteriorated brick
AC | 2 | Door was observed to not latch automatically which is a potential hazard in the event of a fire. | weathered
AC | 2 | Some screws were observed to be missing from the dome. | weathered
AC | 2 | Minor corrosion at bottom of door and frame was observed. | damaged
AC | 2 | Minor hairline cracking in mortar joints was observed. | weathered
AC | 2 | Objects can fall through the treads in the staircases to the floor below. | missing
Process Mechanical | 3 | Moderate corrosion of the pump casing and base was observed. | moderate surface corrosion
Process Mechanical | 3 | Moderate corrosion of the pump casing and base was observed. | moderate surface corrosion
Process Mechanical | 3 | Moderate corrosion of the pump casing and base was observed. | moderate surface corrosion
Structural | 3 | Spalling and exposed corroded reinforcement on underside | spalling
Structural | 3 | Spalling and exposed corroded reinforcement on underside | spalling
Structural | 3 | Concrete spalling was observed. | conceret spalling
Structural | 3 | Corrosion of steel in screen room | corrosion
Process Mechanical | 3 | Moderate corrosion of the pump casing and base was observed. | moderate corrosion
Process Mechanical | 3 | Moderate corrosion of the pump casing and base was observed. | moderate corrosion
Structural | 3 | Bugholes and exposed reinforcement on underside | bugholes
Structural | 3 | Corrosion of steel in screen room | corrosion
Structural | 3 | Minor hairline cracking | minor hairline cracking
Structural | 3 | Cracking with efflorescence deposits | cracking
Process Mechanical | 3 | Leakage was observed. | leakage
AC | 2 | There was no inspect screen installed on the louvre. | cracking
AC | 2 | There were no insect screens installed on the louvres. | cracking
AC | 2 | Minor corrosion was noted at the bottom of the door and frame. | cracking
AC | 2 | Areas of ponding water noted on roof surface. | cracking
Structural | 3 | Concrete spalling on top of floor | concrete spalling
Structural | 3 | Concrete spalling at overhead door and by heater | concrete spalling
Structural | 3 | Minor hairline cracking on underside | minor hairline cracking
Structural | 3 | Exposed reinforcement and delaminated concrete | exposed reinforcement
Building Mechanical | 3 | Minor corrosion was observed at the bottom of the heater. | minor corrosion
Building Mechanical | 3 | Minor to moderate corrosion was observed on the surface. | minor corrosion
Building Mechanical | 3 | Minor to moderate corrosion was observed on the surface. | minor corrosion
Building Mechanical | 3 | Minor to moderate corrosion was observed on the surface. | minor corrosion
Building Mechanical | 3 | Minor to moderate corrosion was observed on the surface. | minor corrosion
Process Electrical | 2 | Exterior Lighting Fixtures were observed to be in good condition. | minor local corrosion
Building Mechanical | 3 | Minor corrosion was observed on the surface. | minor corrosion
Process Mechanical | 3 | Minor surface corrosion was observed throughout. | minor surface corrosion
Process Mechanical | 3 | Minor surface corrosion was observed throughout. | minor surface corrosion
Process Mechanical | 3 | Minor surface corrosion was noted. | minor surface corrosion
Process Mechanical | 3 | Minor surface corrosion was noted on the valve hand wheel. | minor surface corrosion
Process Mechanical | 3 | Local corrosion and paint peeling was observed on the bolts. | local corrosion
Process Mechanical | 3 | Minor surface corrosion was noted. | minor surface corrosion
Process Mechanical | 3 | Minor surface corrosion was observed. | minor surface corrosion
Process Mechanical | 3 | Minor corrosion was observed throughout. | minor corrosion
Building Mechanical | 3 | Minor corrosion was observed on the surface. | minor corrosion
Building Mechanical | 3 | Minor corrosion was observed throughout. | minor corrosion
Building Mechanical | 3 | Minor surface corrosion was observed. | minor surface corrosion
Building Mechanical | 3 | Minor corrosion was observed throughout. | minor corrosion
Process Mechanical | 3 | Minor to moderate surface corrosion and paint pealing were observed. | minor surface corrosion
Process Mechanical | 3 | Local corrosion and paint peeling were observed on the valve surface. | local corrosion
Process Mechanical | 3 | Minor corrosion was observed on the bolts. Paint peeling was also noted. | minor corrosion
Process Mechanical | 3 | Minor corrosion was observed. | minor corrosion
Instrumentation and Control | 4 | The gauge was labeled "broken". | broken
Process Mechanical | 3 | Minor surface corrosion was noted. | minor surface corrosion
Building Mechanical | 3 | Minor corrosion of the bolts was observed. | minor corrosion
Structural | 3 | Calcium deposits and pitting | calcium deposits
Structural | 3 | Missing grating | missing
Structural | 3 | Calcium deposits and pitting | calcium deposits
AC | 2 | Minor physical damage to block units was observed. | weathered
AC | 2 | Minor localized defects in lower level due to moisture transmission through wall. | debonded
AC | 2 | Minor localized defects caused by substrate defects were observed. | cracked
AC | 2 | Missing screws in hinge. | weathered
AC | 2 | Minor cracks in mortar joints were observed. | weathered
AC | 2 | Paint finish was faded. | weathered
AC | 2 | Paint finish was faded. | weathered
AC | 2 | Minor cracks in mortar joints were observed. | weathered
AC | 2 | Door jamb gaskets were damaged. | corrosion
AC | 2 | Corrosion of door hinges was observed. | corrosion
AC | 2 | Door was propped open at the time of the assessment, creating a potential hazard in the event of a fire. | missing
AC | 2 | Gasket appeared to be damaged and hanging loose. | weathered
Architectural | 3 | Floor tiles were noted to be missing by the north wall of the main floor and on the walls of the stairwell. | weathered
Architectural | 3 | Paint was noted to be weathered. | weathered
Architectural | 3 | Deteriorated brick was noted at the bottom of the wall by the screen room door. | weathered
Architectural | 3 | Paint was noted to be weathered. | ponding
Structural | 3 | Surface corrosion on all components | surface corrosion
Architectural | 3 | Paint was noted to be weathered. | missing
Building Mechanical | 3 | Minor corrosion was observed on the surface. | corrosion
Building Mechanical | 3 | Minor corrosion was observed on the surface. | minor corrosion
Building Mechanical | 3 | Minor corrosion was observed on the surface. | minor corrosion
Process Electrical | 2 | Panel Board No.1 was observed to be in good condition. | shattered
Process Mechanical | 3 | Minor surface corrosion was observed. | minor surface corrosion
Process Mechanical | 3 | Minor corrosion were observed at the bolts and pump base. | minor corrosion
Process Mechanical | 3 | Minor to moderate corrosion was observed on the surface of the pump. | minor corrosion
Process Mechanical | 3 | Minor to moderate surface corrosion was observed throughout. | minor corrosion
Building Mechanical | 3 | Minor to moderate corrosion was observed throughout. | moderate corrosion
Building Mechanical | 3 | Minor corrosion was observed on surface. | minor corrosion
Building Mechanical | 3 | Minor corrosion was observed on surface. | minor corrosion
Building Mechanical | 3 | Minor corrosion was observed throughout. | minor corrosion
Building Mechanical | 3 | Minor corrosion was observed around bolts. | minor corrosion
Structural | 3 | Tile embedded in treads was noted to be loose and pose a trip hazard. | loose
Structural | 3 | Corroded form ties | corroded
Structural | 3 | Hairline cracking and concrete spalling was noted by the overhead door and at opening locations. | hairline cracking
Structural | 3 | Minor cracking with efflorescence was noted by a roof drain. | minor cracking
Structural | 3 | Corrosion in embedded metals and on form ties. | corrosion
Structural | 3 | Spalling on web of precast tee above screen | spaling
Structural | 3 | Step cracking in the mortar joints was noted on the east wall | step cracking
Structural | 3 | Cracking and spalling was noted around 2 generator piping penetrations. | cracking
Process Mechanical | 3 | Minor to moderate corrosion was observed on the valve surface. | minor corrosion
Process Mechanical | 3 | Minor to moderate corrosion was observed. | minor corrosion
Process Mechanical | 3 | Minor to moderate corrosion was observed. | minor corrosion
Process Mechanical | 3 | Minor to moderate corrosion was observed on the valve surface. | minor corrosion
Process Mechanical | 3 | Minor to moderate corrosion was observed on the valve surface. | minor corrosion
Process Mechanical | 3 | Minor to moderate corrosion was observed on the valve surface. | minor corrosion
Process Mechanical | 3 | Minor to moderate corrosion was observed on the valve surface. | minor corrosion
Process Mechanical | 3 | Minor to moderate corrosion was observed on the valve surface. | minor corrosion
Process Mechanical | 3 | Minor to moderate corrosion was observed on the valve surface. | minor corrosion
Process Mechanical | 3 | Minor to moderate corrosion was observed on the valve surface. | minor corrosion
Process Mechanical | 3 | Minor corrosion and paint peeling were observed. | minor corrosion
Process Mechanical | 3 | Minor corrosion and paint peeling were observed. | minor corrosion
Process Mechanical | 3 | Minor corrosion and paint peeling were observed. | minor corrosion
Process Mechanical | 3 | Minor corrosion and paint peeling were observed. | minor corrosion
Process Mechanical | 3 | Minor corrosion and paint peeling were observed. | minor corrosion
Process Mechanical | 3 | Minor corrosion and paint peeling were observed. | minor corrosion
Process Mechanical | 3 | Minor corrosion and paint peeling were observed. | minor corrosion
Process Mechanical | 3 | Minor corrosion and paint peeling were observed. | minor corrosion
Process Mechanical | 3 | Minor corrosion and paint peeling were observed. | minor corrosion
Process Mechanical | 3 | Minor corrosion and paint peeling were observed. | minor corrosion
Process Mechanical | 3 | Minor to moderate corrosion and paint peeling were observed. | minor corrosion
Process Mechanical | 3 | Minor to moderate corrosion and paint peeling were observed throughout. | paint peeling
Structural | 3 | Missing kickplate | missing
Structural | 3 | Impact damage on guardrail | damage
Structural | 3 | Missing kickplates | missing
Architectural | 3 | Flashing was noted to be damaged/missing at the northwest corner. | cracking
Architectural | 3 | Paint was noted to be weathered. | corrosion
Architectural | 3 | Insulation was noted to be missing on a few areas. | corrosion
Architectural | 3 | Sealants around louvre was noted to be cracking and debonded from the brick. | corrosion
Architectural | 3 | Sealants around louvre was noted to be cracking and debonded from the brick. | corrosion
Architectural | 3 | Sealants around louvre was noted to be cracking and debonded from the brick. | corrosion
Architectural | 3 | Sealants around louvre was noted to be cracking and debonded from the brick. | minor corrosion
Architectural | 3 | Paint was noted to be weathered. | corrosion
Architectural | 3 | Joint sealants debonded from the precast in a few areas | ponding
Process Electrical | 2 | Wash Down Pump Disconnect Switch was observed to be in good condition. However it should be replaced when the pump is replaced. | minor corrosion
Process Electrical | 2 | Emergency Lighting Fixtures were observed to be in good condition, however the fixtures on the ground level and upper level were approaching the end of their service life. | minor corrosion
BM | 3 | Moderate corrosion of the pump was observed. | moderate corrosion
BM | 3 | Toilet paper and cleaning fluids were being stored on top of the heater which is a potential fire hazard. | fire hazard
BM | 5 | The drinking fountain was not operational at the time of the assessment. | not operational
BM | 3 | The actuator for the cold water line control valve had been removed, and there was no temperature control. | removed
Process Electrical | 2 | Transformer was observed to be in good condition. | exceed guideline
BM | 3 | Minor surface corrosion of the valve was observed. | minor surface corrosion
PM | 3 | Localized corrosion and paint peeling were observed at the bolts and pump base. | localized corrosion
PM | 3 | Minor surface corrosion of the pump was observed, as well as moderate corrosion and paint peeling of the pump base. | minor surface corrosion
PM | 3 | Localized corrosion and paint peeling were observed at the bolts and pump base. | localized corrosion
PM | 3 | Minor corrosion and paint peeling on the motor was observed. | minor corrosion
PM | 3 | Minor corrosion and paint peeling on the motor was observed. | paint peeling
PM | 3 | Minor surface corrosion of the pump was observed. | minor surface corrosion
Process Electrical | 2 | Exterior Lighting Fixture was observed to be in good condition. | not operating
Process Electrical | 2 | Lighting Panel LP 1 was observed to be in good condition. | minor corrosion
Process Electrical | 2 | Circuit Breaker was observed to be in good condition. | minor corrosion
Process Electrical | 2 | Water Booster Pump Starter was observed to be in good condition. | minor corrosion
Process Electrical | 2 | Washdown Pump Starter was observed to be in good condition. | moderate corrosion
Process Electrical | 2 | Interior Light Fixtures were observed to be in good condition. | should be sealed with a fire stop product
SW | 3 | Minor localized damage and deformation was observed throughout the fence. | minor localized damage
SW | 3 | Minor localized damage and deformation was observed throughout the fence. | deformation
SW | 3 | Minor corrosion of the gate and locks was observed. | minor corrosion
Architectural | 3 | A few panels were noted to be cracked. | moderate corrosion
Architectural | 3 | Door paint was noted to be weathered. | minor corrosion
Architectural | 3 | Door paint was noted to be weathered and missing in some areas. | localized flaking of floor coating
Architectural | 3 | Door paint was noted to be weathered. | significant wear
SW | 3 | Moderate vegetation throughout the interlock entrance was observed. | moderate vegetation
SW | 3 | Transverse and longitudinal cracks were observed in the asphalt driveway. | transverse cracks
SW | 3 | Transverse and longitudinal cracks were observed in the asphalt driveway. | longitudinal cracks
SW | 3 | Localized rot and decay of the timbers was observed. | localized rot
SW | 3 | Localized rot and decay of the timbers was observed. | decay
SW | 4 | Some of the signage was weathered and illegible. | illegible
SW | 4 | Some of the signage was weathered and illegible. | weathered
PM | 3 | Paint peeling and surface corrosion of the discharge piping was observed. | paint peeling
PM | 3 | Paint peeling and surface corrosion of the discharge piping was observed. | surface corrosion
PM | 3 | Paint peeling and surface corrosion of the discharge piping was observed. | paint peeling
PM | 3 | Paint peeling and surface corrosion of the discharge piping was observed. | surface corrosion
PM | 3 | Paint peeling and surface corrosion of the suction piping was observed. | paint peeling
PM | 3 | Paint peeling and surface corrosion of the suction piping was observed. | surface corrosion
BM | 3 | There was no spill containment on the fill line. | no spill containment
BM | 3 | The return line showed signs of leakage. | leakage
Process Electrical | 2 | Light fixtures were observed to be in good condition. | missing
PM | 3 | The manual backflow actuator at the bottom of the valve was leaking. Water was pooled on the concrete floor. | leaking
SC | 3 | Concrete spalling and exposed reinforcement at the top edge of foundation wall was observed. | exposed reinforcement
SC | 3 | Concrete spalling and exposed reinforcement at the top edge of foundation wall was observed. | concrete spalling
SC | 3 | Hairline cracking measuring approximately 1m was noted above the north door. | hairline cracking
SC | 3 | Local cracking/ drying out of joints between panels was observed. | drying out of joints
SC | 3 | Local cracking/ drying out of joints between panels was observed. | local cracking
SC | 3 | The floor drain in the valve chamber was clogged. Approximately 1 ft of standing water was noted at the time of the assessment. | clogged
SC | 3 | Concrete spalling was noted around the pipe penetration at the north end of the valve chamber. | concrete spalling
SC | 3 | Corrosion spots were noted on the beams and underside of the roof surface. | corrosion spots
SC | 3 | Corrosion spots were noted at the wall to slab interface. | corrosion spots
SC | 3 | Evidence of age/standing water was noted. | evidence of age
SC | 3 | Evidence of age/standing water was noted. | standing water
SC | 3 | Minor corrosion at the sleeve penetration for the valve shaft was observed. | minor corrosion
SC | 3 | Minor corrosion of the ladder was observed. | minor corrosion
SC | 3 | A layer of slime was noted at the bottom of the ladder due to standing water. | slime
BM | 3 | Minor surface corrosion of the piping was observed. | minor surface corrosion
BM | 3 | Minor surface corrosion of the gate valve was observed. | minor surface corrosion
PM | 4 | Moderate corrosion covering the surface of the valve was observed. | moderate corrosion
Architectural | 3 | Door paint was noted to be weathered. | missing
SC | 3 | Corroded exposed reinforcement was observed by the vents. | corroded
SC | 3 | Corroded exposed reinforcement was observed by the vents. | exposed reinforcement
SW | 4 | Some of the posts were leaning or had fallen over. | leaning
SW | 4 | Some of the posts were leaning or had fallen over. | fallen over
PM | 4 | Moderate corrosion covering the valve surface was observed. | moderate corrosion
PM | 4 | Moderate corrosion covering the valve surface was observed. | moderate corrosion
Architectural | 3 | Door paint was noted to be weathered. | significant tree growth
PM | 3 | Very minor surface corrosion was observed. | very minor surface corrosion
SC | 3 | Cracking with efflorescence deposits was noted throughout the walls. | cracking
SC | 3 | Cracking with efflorescence deposits was noted throughout the walls. | efflorescence deposits
SC | 3 | Calcium deposits were noted on the ladders. | calcium deposits
SW | 5 | The barrier chain behind the roof of the Valve House was not installed at the time of the assessment. | not installed
SIC | 3 | Wear and tear on the equipment exterior was observed. | wear and tear
PM | 3 | Minor to moderate corrosion at the top of the valve was observed. | minor corrosion
PM | 3 | Minor to moderate corrosion at the top of the valve was observed. | moderate corrosion
PM | 3 | Paint peeling and minor to moderate corrosion was observed throughout the station piping. | paint peeling
PM | 3 | Paint peeling and minor to moderate corrosion was observed throughout the station piping. | minor corrosion
PM | 3 | Paint peeling and minor to moderate corrosion was observed throughout the station piping. | moderate corrosion
PM | 3 | Minor corrosion and discolouration of the pump was observed. | minor corrosion
PM | 3 | Minor corrosion and discolouration of the pump was observed. | discolouration
HSS | 3 | Minor surface corrosion of the eye wash station was observed. | minor surface corrosion
BM | 3 | The louver for the exhaust fan was missing a blade. | missing
SW | 5 | The chainlink fence was collapsed at the south side of the driveway. | collapsed
SW | 3 | The fence was detached from its posts at the south side of the site. | detached
PM | 4 | Moderate surface corrosion of the valve was observed. | moderate surface corrosion
PM | 3 | Guarding on the pump was missing at the time of the inspection. | missing
PM | 3 | Paint peeling and moderate corrosion was observed on the piping throughout the station. | paint peeing
PM | 3 | Paint peeling and moderate corrosion was observed on the piping throughout the station. | moderate corrosion
PM | 3 | Minor surface corrosion of the valve was observed. | minor surface corrosion
PM | 3 | Minor surface corrosion of the valve was observed. | minor surface corrosion
PM | 3 | Minor surface corrosion of the valve was observed. | minor surface corrosion
PM | 3 | Minor surface corrosion of the valve was observed. | minor surface corrosion
BM | 3 | Moderate corrosion was observed at the bottom of the tank. | moderate corrosion
PM | 3 | Minor surface corrosion of the valve was observed. | minor surface corrosion
HSS | 4 | Minor surface corrosion and staining was observed on the eye wash station. | minor surface corrosion
HSS | 4 | Minor surface corrosion and staining was observed on the eye wash station. | staining
BM | 3 | A portable unit heater was found in the chemical room.
BM | 3 | A portable unit heater was found in the chemical room. Operation of the forced fan heater should be confirmed.
BM | 3 | The fan was dirty at the time of the inspection and in need of cleaning. | dirty
BM | 3 | The exhaust fan vents to the building exterior by the doorway to the pump room. In an emergency situation (gas leak), this could allow operators to come into contact with chlorine gas as there is no chlorine scrubber at the facility. | leak
PM | 3 | Very minor corrosion of the valve was observed. | very minor corrosion
Process Electrical | 2 | Interior Light Fixtures were observed to be in good condition. | minor corrosion
Process Electrical | 2 | Lighting Panel 2 was observed to be in fair condition. Minor surface corrosion was observed. | non-functional
PM | 3 | The chemical line for the metering pump was not installed. | not installed
Process Electrical | 2 | Emergency Lighting System was observed to be in good condition. | minor corrosion
Process Electrical | 2 | Battery Charger was observed to be in good condition. Operations reported that it was no longer used after the standby power was installed. | minor corrosion
Process Electrical | 2 | Standby Engine Transfer Switch was observed to be in good condition. | moderate corrosion
Process Electrical | 2 | Standby Engine Transfer Switch was observed to be in good condition. | moderate corrosion
Process Electrical | 2 | Lighting Panel was observed to be in good condition. | minor corrosion
SC | 3 | Cracking was noted in a straight line between the pump room and door lintel. | cracking
Architectural | 3 | Corrosion was noted on the door frame. | moderate corrosion
Architectural | 3 | Corrosion was noted on the door frame | moderate corrosion
Architectural | 3 | Door paint was noted to be missing at the bottom of the door. | moderate corrosion
Architectural | 3 | Door paint was noted to be weathered. | moderate corrosion
SC | 5 | Access hatch above pump room was missing and the opening was covered with a piece of plywood. | missing
SC | 3 | Minor corrosion was observed on the steel components of the superstructure in the chemical room. | minor corrosion
Architectural | 3 | Door paint was noted to be weathered. | minor corrosion
Architectural | 3 | Door paint was noted to be weathered. | minor corrosion
Architectural | 3 | Door paint was noted to be weathered. | minor corrosion
SW | 3 | Minor localized damage and deformation was observed throughout the fence. | minor localized damage
SW | 3 | Minor surface corrosion was observed on the hydrant. | minor surface corrosion
PM | 3 | Discolouration of the sampling trough was observed. | discolouration
PM | 3 | Surface corrosion of the valve was observed. | surface corrosion
PM | 3 | Surface corrosion of the valve was observed. | surface corrosion
PM | 3 | Surface corrosion of the valve was observed. | surface corrosion
PM | 3 | Corrosion and paint peeling were observed throughout the piping within the Valve House. The performance of the dehumidifier for the valve room should be confirmed. | corrosion
PM | 3 | Corrosion and paint peeling were observed throughout the piping within the Valve House. The performance of the dehumidifier for the valve room should be confirmed. | paint peeling
BM | 3 | Moderate paint wear on exhaust fan duct system was observed. | moderate paint wear
SIC | 5 | The pressure level gauge was not in service. | not in service
SC | 3 | Hairline cracking with efflorescence deposits noted on majority of columns. | hairline cracking
SC | 3 | Hairline cracking with efflorescence deposits noted on majority of columns. | efflorescence deposits
SC | 3 | Hairline cracking with efflorescence deposits noted on majority of columns. | hairline cracking
SC | 3 | Hairline cracking with efflorescence deposits noted on majority of columns. | efflorescence deposits
SW | 4 | Minor localized damage and deformation was observed throughout the fence. | minor localized damage
SW | 4 | Minor localized damage and deformation was observed throughout the fence. | deformation
SW | 3 | Minor corrosion of the gate and locks was observed. | minor corrosion
PM | 3 | Minor surface corrosion was observed. | minor surface corrosion
PM | 3 | Minor surface corrosion was observed. | minor surface corrosion
PM | 3 | Very minor surface corrosion was noted. | very minor surface corrosion
PM | 3 | Minor surface corrosion was noted. | minor surface corrosion
PM | 3 | Minor surface corrosion was observed. | minor surface corrosion
PM | 3 | Minor surface corrosion was observed. | minor surface corrosion
PM | 3 | Minor surface corrosion was observed. | minor surface corrosion
Process Electrical | 2 | Interior Lighting was observed to be in good condition. However, it was approaching the end of its service life. | minor surface corrosion
Process Electrical | 2 | Standby Power Generator was observed to be in good condition. | moderate surface corrosion
SC | 3 | Previous repairs had been completed using a material that is not NSF certified. | not certified
SC | 3 | Previous repairs had been completed using a material that is not NSF certified. | not certified
SW | 3 | Minor corrosion on roof drain piping was observed. | minor corrosion
SW | 3 | Moderate corrosion of the gate as well as paint peeling was observed. | moderate surface corrosion
SW | 3 | Moderate corrosion of the gate as well as paint peeling was observed. | paint peeling
PM | 3 | Minor surface corrosion was observed. | minor surface corrosion
PM | 3 | Minor surface corrosion was observed. | minor surface corrosion
Process Electrical | 2 | Exterior Lighting was observed to be in good condition. However, it was approaching the end of its service life. | not in service
SC | 3 | Previous repairs had been completed using a material that is not NSF certified. | not certified
SC | 3 | Previous repairs had been completed using a material that is not NSF certified. | not certified
Architectural | 3 | Ponding was noted on the southern edge of the high roof. | peeling paint
SC | 3 | Hairline cracking was observed on underside of slab. | hairline cracking
Architectural | 3 | Paint was noted to be missing in a few areas due to wear and tear. | missing
Architectural | 3 | Sealants around louvre was noted to be cracking and debonded from the brick. | displaced
Architectural | 3 | Corrosion was noted at the bottom of the door frame. | corrosion
Architectural | 3 | Corrosion was noted at the bottom of the door frame. | faded
Architectural | 3 | Corrosion was noted at the bottom of the door frame. | minor corrosion
SW | 3 | Moderate surface corrosion was observed. | moderate surface corrosion
BM | 3 | Minor surface corrosion was observed throughout the interior of the silencer. | minor surface corrosion
BM | 3 | Minor surface corrosion of the exhaust piping exiting the building was observed. | minor surface corrosion
SC | 3 | Minor corrosion on frame | minor corrosion
SC | 3 | Minor corrosion on frame | minor corrosion
BM | 3 | Moderate surface corrosion was observed. | moderate surface corrosion
SC | 3 | Moderate surface corrosion of the cover and frame was observed. | moderate surface corrosion
PM | 3 | Very minor surface corrosion of the valve was observed, | very minor surface corrosion
PM | 3 | Moderate surface corrosion of the flanges and handwheel was observed. | moderate surface corrosion
BM | 3 | The fan belt was broken in a number of areas and in need of replacement. | broken
Architectural | 3 | Corrosion was noted at the bottom of the door frame. | minor weathering
Architectural | 3 | Corrosion was noted at the bottom of the door frame. | corrosion
SW | 4 | The signage surrounding the reservoir site was typically leaning (not in an upright position). | leaning
BM | 3 | The ULC Labels had been painted over. | painted over
BM | 3 | The ULC Labels had been painted over. | painted over
PM | 3 | Duct tape was observed on the bottom of the valve at the concrete support. It was assumed that the duct tape was applied in the absence of a proper bond break between the equipment and concrete support. | absence of propoer bond break
SC | 3 | Bug holes/voids were noted at grade on the north side of the building. | bug holes
SC | 3 | Bug holes/voids were noted at grade on the north side of the building. | voids
SC | 3 | Cracking was noted on the south side, east of the overhead door (1.5m long) and on the north side, east of the access door (0.6m long). | cracking
SC | 3 | Bug holes were noted in the concrete surface. | bug holes
SW | 4 | The fence wire was disconnected at several posts. | disconnected
SC | 3 | Hairline cracking was noted throughout the walls. | hairline cracking
SC | 3 | Pitting was observed. | pitting
SW | 5 | Sections of the chainlink fence at the north side of the driveway had been removed. | removed
BM | 3 | Very minor corrosion and discolouration of the heater was observed. | very minor corrosion
BM | 3 | Very minor corrosion and discolouration of the heater was observed. | discolouration
BM | 3 | Very minor corrosion of the heater was observed. | very minor corrosion
Process Electrical | 2 | Building Emergency Lights were observed to be in good condition. | lack of spare circuits on the MCC
SC | 3 | Cracking in the mortar was also noted in corners of the pump room. | cracking
Architectural | 3 | Minor corrosion was also noted in a few spots. | minor weathering
Architectural | 3 | Corrosion was noted at the bottom of the door frame. | minor weathering
Architectural | 3 | Ponding was also noted at the northeast corner of the lower roof. | minor weathering
AC | 3 | Moderate corrosion at the base of the hollow metal door frame was observed. | minor impact damage
PM | 3 | Minor corrosion of the Cell 1 and 2 sampling lines was observed. The other three sampling lines (for the Valve House) had been replaced. | minor corrosion
PM | 3 | Moderate efflorescence was observed on the CPP inlet/outlet header. | moderate efflorescence
SC | 3 | Rust spots and worn surfaces with exposed aggregates were observed. | rust spots
SC | 3 | Rust spots and worn surfaces with exposed aggregates were observed. | rust spots
SW | 4 | Fence was missing at the south boundary of the site. | missing
SC | 3 | Hairline cracking was observed. | hairline cracking
SC | 3 | Hairline cracking was observed. | hairline cracking
SC | 3 | Cracking with efflorescence deposits was observed. | cracking
SC | 3 | Cracking with efflorescence deposits was observed. | cracking
AC | 3 | Minor corrosion on the hollow metal door frame was observed. | minor corrosion
AC | 3 | Significant tree growth was observed on the roof. | faded
AC | 3 | Moderate corrosion at the base of the hollow metal door frame was observed. | corrosion
AC | 3 | Moderate corrosion at the base of the hollow metal door frame was observed. | wear
AC | 3 | Moderate corrosion at the base of the hollow metal door frame was observed. | faded
Process Piping | 2
Process Piping | 2
Process Mechanical Equipment | 2
Process Piping | 2 |  | Minor surface corrosion
Process Piping | 2
Process Mechanical Equipment | 2
Process Piping | 2
Process Mechanical Equipment | 2
Building Services | 2
Process Instrumentation SCADA | 2
Process Instrumentation SCADA | 2
Process Instrumentation SCADA | 2
Process Instrumentation SCADA | 2
Process Electrical | 2 | MCC was in good condition. | No mechanical protection
Process Instrumentation SCADA | 2
Process Piping | 2
Process Mechanical Equipment | 2
Process Instrumentation SCADA | 2
Building and Process Structural | 2 |  | not inspected
Building and Process Structural | 2
Process Mechanical Equipment | 2
Process Mechanical Equipment | 2
Process Piping | 2
Building and Process Structural | 2
Building and Process Structural | 2
Process Electrical | 2 | Generator was in good condition. | minor corrosion
Process Electrical | 2 | Lighting Panel was in good condition.
Process Instrumentation SCADA | 2
Process Electrical | 2 | Transformer was in good condition.
Process Electrical | 2 | Control Panel was in good condition. | Deteriorating panel-sealant
Process Piping | 2
Process Instrumentation SCADA | 2
Process Instrumentation SCADA | 2
Building Services | 2
Building and Process Structural | 2
Building and Process Structural | 2 |  | Missing grating-clips
Process Instrumentation SCADA | 2
Process Electrical | 2 | Fixtures were in good condition.
Building and Process Structural | 2
Building and Process Structural | 2
Building and Process Structural | 2
Process Electrical | 2 | Control Panel was in good condition.
Building Services | 2
Process Instrumentation SCADA | 2 |  | Loose screws
Process Instrumentation SCADA | 2
Building and Process Structural | 2 | The base slab could not be inspected as it was submersed at the time of the assessment. The slab was assumed to be in good condition based on its age and the condition of other visible structural components.
Process Instrumentation SCADA | 2 | The Wet Well Float System was observed to in good condition.
Building and Process Structural | 2 | The concrete walls were observed to be in good condition.
Building and Process Structural | 2 | The concrete roof was observed to be in good condition. Half of the roof underside was covered in insulation. Minor bugholes were noted around vent pipe penetration. | minor bugholes
Process Piping | 2 | The Forcemain was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken. Corrosion was noted on the visible section within the wet well.
Building and Process Structural | 2 | The hatch was observed to be in good condition.
Building and Process Structural | 2 | The hatch was observed to be in good condition.
Building and Process Structural | 2 | The hatch was observed to be in good condition.
Building Services | 2 | The Wet Well Vent Piping was in good condition.
Process Electrical | 2 | Fixtures were in good condition.
Process Electrical | 2 | Control Panel was in good condition.
Process Piping | 2 | The Overflow Piping was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken.
Process Electrical | 2 | Fixtures were in good condition.
Process Piping | 2 | Pump 1 Piping was in good condition. Minor surface corrosion was observed. | Minor surface corrosion
Process Mechanical Equipment | 2 | Sewage Lift Pump 1 Inlet Gate Valve was in good condition. Minor surface corrosion was observed. | Minor surface corrosion
Process Mechanical Equipment | 2 | Sewage Lift Pump 1 Discharge Gate Valve was in good condition
Process Mechanical Equipment | 2 | Sewage Lift Pump 2 Discharge Gate Valve was in good condition. Minor surface corrosion was observed. | Minor surface corrosion
Process Piping | 2 | Pump 1 Piping was in good condition. Minor surface corrosion was observed.
Process Mechanical Equipment | 2 | Sewage Lift Pump 2 Inlet Gate Valve was in good condition. Minor surface corrosion was observed. | Minor surface corrosion
Process Instrumentation SCADA | 2 | Wet Well Level Transmitter 1 was observed to be in good condition.
Process Piping | 2 | The Forcemain was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken.
Process Instrumentation SCADA | 2 | The Dry Well Float System was observed to be in good condition.
Building and Process Structural | 2 | The ladder rungs were observed to be in good condition.
Building and Process Structural | 2 | The base slab could not be inspected as it was submersed at the time of the assessment. The slab was assumed to be in good condition based on its age and the condition of other visible structural components.
Process Instrumentation SCADA | 2 | The Wet Well Float System was observed to be in good condition.
Building and Process Structural | 2 | The platform was observed to be in good condition.
Process Electrical | 2 | Control Panel was in good condition.
Process Electrical | 2 | TX-1 Primary Transformer was observed to be in good condition. Minor corrosion was observed on exterior bolts.
Process Electrical | 2 | TX-2 Primary Transformer was observed to be in good condition. Minor corrosion was observed on exterior bolts.
Process Electrical | 2 | DP-C Panel Distribution C Disconnect Switch was observed to be in good condition.
Process Electrical | 2 | DP-C Distribution Panel C was observed to be in good condition.
Process Instrumentation SCADA | 2 | The Remote Communication Equipment was observed to be in good condition.
Building Services | 2 | The dehumidifier was observed to be in good condition.
Building Services | 2 | The Portable Unit Heater was observed to be in good condition.
Process Piping | 2 | The Overflow Piping was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken.
Process Instrumentation SCADA | 2 | Control Panel, CP-01 was observed to be in good condition.
Process Instrumentation SCADA | 2 | Back-up System Level Transmitter 1 was observed to be in good condition.
Process Instrumentation SCADA | 2 | Back-up System Level Transmitter 2 was observed to be in good condition.
Process Instrumentation SCADA | 2 | The Flow Transmitter was observed to be in good condition.
Process Instrumentation SCADA | 2 | Communication System UPS 1 was observed to be in good condition. However, the communications cable was found loosely strung along the perimeter of the fence and through a tree.
Building Services | 2 | Exhaust Fan 2 was in good condition.
Building Services | 2 | The Filter Fan was in good condition.
Building Services | 2 | Unit Heater 2 was observed to be in good condition.
Building Services | 2 | The Vent Piping was observed to be in good condition.
Building Services | 2 | The Filter Fan was in good condition.
Building Services | 2 | Unit Heater 1, HTR -1 was observed to be in good condition.
Building Services | 2 | The Exhaust Fan was in good condition. Minor corrosion of the screen was observed.
Process Mechanical Equipment | 2 | Valve Chamber 1 Isolation Valve 2 was observed to be in good condition.
Process Mechanical Equipment | 2 | Valve Chamber 1 Forcemain Bypass Knife Gate Valve was observed to be in good condition.
Process Mechanical Equipment | 2 | Valve Chamber 1 Isolation Valve 1 was observed to be in good condition.
Building and Process Structural | 2 | The ladder was observed to be in good condition.
Building and Process Structural | 2 | The manhole cover and frame was observed to be in good condition.
Process Instrumentation SCADA | 2 | The Dry Well Float System was in good condition.
Process Mechanical Equipment | 2 | Sewage Lift Pump 3 Discharge Check Valve was observed to be in good condition.
Process Mechanical Equipment | 2 | Sewage Lift Pump 2 was observed to be in good condition. Minor surface corrosion was observed. The pump was mid-way through its typical service life. Based on the age of the pump, rehabilitation is recommended.
Process Mechanical Equipment | 2 | Sewage Lift Pump 2 Motor was in good condition. Minor surface corrosion was observed. | Minor surface-corrosion
Process Piping | 2 | The Pump 2 Suction Piping was in good condition overall, however minor corrosion and paint wear was observed.
Process Mechanical Equipment | 2 | Sewage Lift Pump 2 Inlet Knife Gate Valve was observed to be in good condition.
Process Mechanical Equipment | 2 | Sewage Lift Pump 2 Discharge Check Valve was observed to be in good condition. However, an internal inspection was not undertaken. Minor surface corrosion was observed.
Process Mechanical Equipment | 2 | Sewage Lift Pump 2 Discharge Knife Gate Valve was observed to be in good condition.
Process Piping | 2 | The Pump 3 Suction Piping was in good condition overall, however minor corrosion and paint wear was observed.
Process Mechanical Equipment | 2 | Sewage Lift Pump 3 Inlet Knife Gate Valve was observed to be in good condition.
Process Mechanical Equipment | 2 | Sewage Lift Pump 3 was observed to be in good condition. Minor surface corrosion was observed.
Process Mechanical Equipment | 2 | Sewage Lift Pump 3 Motor was in good condition.
Process Mechanical Equipment | 2 | Sewage Lift Pump 1 Inlet Knife Gate Valve was observed to be in good condition.
Process Mechanical Equipment | 2 | Sewage Lift Pump 1 was observed to be in good condition. Minor surface corrosion was observed. The pump was mid-way through its typical service life. Based on the age of the pump, rehabilitation is recommended.
Process Mechanical Equipment | 2 | Sewage Lift Pump 1 Motor was in good condition. Minor surface corrosion was observed.
Process Mechanical Equipment | 2 | Sewage Lift Pump 1 Discharge Check Valve was observed to be in good condition. However, an internal inspection was not undertaken.
Process Mechanical Equipment | 2 | Sewage Lift Pump 1 Discharge Knife Gate Valve was observed to be in good condition.
Building Services | 2 | The Dehumidifier was observed to be in good condition.
Building Services | 2 | Unit Heater 1 was observed to be in good condition.
Building Services | 2 | Exhaust Fan 1 was in good condition. Minor surface corrosion was observed.
Building Services | 2 | Supply Fan 1 was in good condition. Minor surface corrosion was observed.
Building Services | 2 | The Explosion Proof Unit Heater was in good condition.
Process Electrical | 2 | LP-C Panel Lighting C was observed to be in good condition.
Process Electrical | 2 | Dist TX-2 Transformer 2 Distribution was observed to be in good condition.
Process Piping | 2 | The Pump 1 Suction Piping was in good condition overall, however minor corrosion and paint wear was observed.
Process Mechanical Equipment | 2 | Sewage Lift Pump 3 Discharge Knife Gate Valve is observed to be in good condition.
Building and Process Structural | 2 | The access hatch was observed to be in good condition.
Building and Process Structural | 2 | The access hatch was observed to be in good condition.
Building and Process Structural | 2 | The access hatch was observed to be in good condition.
Process Instrumentation SCADA | 2 | The Magnetic Flow Meter was observed to be in good condition.
Process Piping | 2 | The Forcemain was assumed to be in very good condition based on its age and the visible section of the piping. However, internal inspection of the piping was not undertaken.
Process Mechanical Equipment | 2 | The Valve Chamber 2 was observed to be in good condition.
Process Mechanical Equipment | 2 | Valve Chamber 2 Forcemain Bypass Knife Gate Valve was observed to be in good condition.
Process Mechanical Equipment | 2 | Valve Chamber 2 Isolation Knife Gate Valve was observed to be in good condition.
Process Electrical | 2 | TX-2 Disconnect Switch was observed to be in good condition.
Process Electrical | 2 | LP-B Panel Lighting B was observed to be in good condition.
Process Electrical | 2 | EUH-03 Disconnect Switch was observed to be in good condition.
Process Instrumentation SCADA | 2 | The Remote Communication Equipment was observed to be in good condition.
Process Electrical | 2 | Dehumidifier-1 Disconnect Switch was observed to be in good condition.
Process Electrical | 2 | Clearwell Cell 2 Feed Valve Disconnect Switch was observed to be in good condition.
Process Electrical | 2 | MCC 1 was observed to be in good condition.
Process Electrical | 2 | MCC 2 was observed to be in very good condition.
Process Piping | 2 | The Forcemain was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken.
Process Piping | 2 | The Overflow Piping was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken.
Process Piping | 2 | The Pump 1 Piping was assumed to be in good condition based on its age. However, internal inspection of the piping is required to assess its condition.
Process Mechanical Equipment | 2 | Sewage Lift Pump 1 Inlet Gate Valve was in good condition. Minor corrosion was observed.
Process Mechanical Equipment | 2 | Sewage Lift Pump 1 Motor was in good condition. The motor was assumed to be original to the station and was approaching the end of its remaining service life. Based on its age the motor replacement is recommended in next 10 years.
Process Mechanical Equipment | 2 | Sewage Lift Pump 1 Discharge Check Valve was in good condition. Minor corrosion was observed.
Process Mechanical Equipment | 2 | Sewage Lift Pump 1 Discharge Gate Valve was in good condition. Minor corrosion was observed.
Process Mechanical Equipment | 2 | Sewage Lift Pump 2 Discharge Gate Valve was in good condition. Minor corrosion was observed.
Process Mechanical Equipment | 2 | Sewage Lift Pump 2 Discharge Check Valve was in good condition. Minor corrosion was observed.
Process Mechanical Equipment | 2 | Sewage Lift Pump 2 Motor was in good condition. The motor was assumed to be original to the station and was approaching the end of its remaining service life. Based on the age of the motor, replacement is recommended in the next 10 years.
Process Piping | 2 | The Pump 2 Piping was assumed to be in good condition based on its age. However, internal inspection of the piping is required to assess its condition.
Process Mechanical Equipment | 2 | Sewage Lift Pump 2 Inlet Gate Valve was in good condition. Minor surface corrosion was observed.
Process Instrumentation SCADA | 2 | The Dry Well Float System was in good condition.
Building and Process Structural | 2 | The manhole cover and frame was observed to be in good condition.
Building and Process Structural | 2 | The ladder rungs were observed to be in good condition.
Process Electrical | 2 | Emergency Fixtures were observed to be in good condition.
Building Services | 2 | The Portable Dehumidifier was observed to be in good condition.
Process Instrumentation SCADA | 2 | The Remote Communication Equipment was observed to be in good condition.
Building Services | 2 | The Portable Unit Heater was observed to be in good condition.
Process Piping | 2 | The in-system overflow was not visually inspected, but was assumed to be in good condition based on its age.
Process Piping | 2 | The Pump 1 Piping was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken.
Process Mechanical Equipment | 2 | Sewage Lift Pump 1 Discharge Gate Valve was in good condition.
Process Piping | 2 | The Pump 2 Piping was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken.
Process Mechanical Equipment | 2 | Sewage Lift Pump 2 Discharge Gate Valve was in good condition.
Process Instrumentation SCADA | 2 | Wet Well Level Transmitter 1 was observed to be in good condition.
Process Instrumentation SCADA | 2 | The Dry Well Float System was observed to be in good condition.
Process Instrumentation SCADA | 2 | The Wet Well Float System was observed to be in good condition.
Process Electrical | 2 | MCC 1A was observed to be in good condition.
Process Electrical | 2 | MCC 2A was observed to be in good condition.
Building Services | 2 | Dehumidifier was observed to be in good condition.
Building Services | 2 | The Portable Unit Heater was observed to be in good condition.
Process Piping | 2 | The Overflow Piping was assumed to be in good condition based on its age.
Building Services | 2 | Air Supply Fan 1 was observed to be in good condition, however it was approaching the end of its useful service life.
Process Instrumentation SCADA | 2 | The PLC Control Panel was observed to be in good condition.
Process Instrumentation SCADA | 2 | The Wet Well Level Transmitter was observed to be in good condition.
Process Instrumentation SCADA | 2 | The Remote Communication System was observed to be in good condition.
Process Instrumentation SCADA | 2 | The Flowmeter was observed to be in good condition.
Process Piping | 2 | The Forcemain was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken.
Building Services | 2 | The Air Supply Piping was in good condition. However, moderate corrosion at the junction was observed.
Process Instrumentation SCADA | 2 | The Wet Well Float System was observed to be in good condition.
Building and Process Structural | 2 | The roof was observed to be in good condition.
Building Services | 2 | The Wet Well Vent Piping was observed to be in good condition.
Process Electrical | 2 | Dist TX-1 Transformer 2 Distribution was observed to be in good condition.
Process Electrical | 2 | LP-A Panel Lighting A was observed to be in good condition.
Process Electrical | 2 | Capacitor was observed to be in good condition.
Process Electrical | 2 | Reactor 1 was observed to be in good condition.
Process Electrical | 2 | Capacitor was observed to be in good condition.
Process Electrical | 2 | Reactor 2 was in good condition.
Process Electrical | 2 | Capacitor was observed to be in good condition.
Process Electrical | 2 | Reactor 3 was observed to be in good condition.
Building Services | 2 | The Heater was observed to be in good condition, however it was approaching the end of its useful service life.
Process Piping | 2 | The Forcemain was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken.
Process Electrical | 2 | Capacitor was observed to be in good condition.
Building and Process Structural | 2 | The hatch was observed to be in good condition with some minor discoloration. | minor discoloration
Process Instrumentation SCADA | 2 | The Wet Well Float System was observed to be in good condition.
Building and Process Structural | 2 | The steel ladder was observed to be in good condition.
Process Piping | 2 | Pump 2 Suction Piping was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken.
Process Mechanical Equipment | 2 | Sewage Lift Pump 2 Inlet Gate Valve was in good condition. Minor surface corrosion and paint wear was observed.
Process Mechanical Equipment | 2 | Sewage Lift Pump 2 Discharge Check Valve was in good condition. Minor surface corrosion and paint wear was observed.
Process Mechanical Equipment | 2 | Sewage Lift Pump 2 Discharge Gate Valve was in good condition. Minor surface corrosion and paint wear was observed.
Process Mechanical Equipment | 2 | Sewage Lift Pump 1 Discharge Valve Gate was in good condition. Minor surface corrosion and paint wear was observed.
Process Mechanical Equipment | 2 | Sewage Lift Pump 1 Discharge Check Valve was in good condition. Minor surface corrosion and paint wear was observed.
Process Piping | 2 | Pump 1 Suction Piping was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken.
Process Mechanical Equipment | 2 | Sewage Lift Pump 1 Inlet Gate Valve was in good condition. Minor surface corrosion and paint wear was observed.
Process Instrumentation SCADA | 2 | The Wet Well Level Transmitter was observed to be in good condition.
Building Services | 2 | The Dehumidifier was observed to be in good condition.
Process Piping | 2 | The Pump Discharge Piping was observed to be in good condition.
Building Services | 2 | The Portable Unit Heater was observed to be in good condition.
Process Electrical | 2 | Reactor 4 was observed to be in good condition.
Process Electrical | 2 | Pump 1 Discharge Valve Disconnect Switch was observed to be in good condition.
Process Piping | 2 | The Forcemain was assumed to be in good condition based on its age. However, internal inspection of the piping is was not undertaken.
Process Instrumentation SCADA | 2 | The PLC 1 was observed to be in good condition, however it was approaching the end of its remaining service life.
Process Instrumentation SCADA | 2 | The Wet Well Level Transmitter was observed to be in good condition.
Process Instrumentation SCADA | 2 | The UPS 2 was observed to be in good condition, however it was approaching the end of its remaining service life.
Process Instrumentation SCADA | 2 | The Remote Communication Equipment was observed to be in good condition, however it was approaching the end of its remaining service life.
Building Services | 2 | The Baseboard Heater was observed to be in good condition.
Building Services | 2 | The Vent Piping was observed to be in good condition.
Building and Process Structural | 2 | The aluminum platform was observed to be in good condition.
Building and Process Structural | 2 | The stainless steel ladder was observed to be in good condition. The retractable safety handle was noted to be stuck. | Stuck handle
Building and Process Structural | 2 | The base slab could not be inspected as it was submersed at the time of the assessment. The slab was assumed to be in good condition based on its age and the condition of other visible structural components.
Building and Process Structural | 2 | The walls were observed to be in good condition.
Building and Process Structural | 2 | The roof was observed to be in good condition.
Building Services | 2 | The External Blower Blow Down Piping was observed to be in good condition.
Process Instrumentation SCADA | 2 | The Wet Well Float System was observed to be in good condition.
Process Instrumentation SCADA | 2 | The Pressure Gauges were observed to be in good condition.
Process Piping | 2 | The Pump 1 Discharge Piping was in good condition. Minor surface corrosion was observed.
Process Piping | 2 | Pump 2 Discharge Piping was in fair condition. Minor surface corrosion was observed.
Process Piping | 2 | The Emergency Overflow Piping was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken.
Building and Process Structural | 2 | The stainless steel ladder was observed to be in good condition.
Building and Process Structural | 2 | The aluminum guardrail was observed to be in good condition.
Process Mechanical Equipment | 2 | Sewage Lift Pump 1 was submersed at the time of the inspection, but was assumed to be in good condition based on its age.
Process Mechanical Equipment | 2 | Sewage Lift Pump 2 was submersed at the time of the inspection, but was assumed to be in good condition based on its age.
Building and Process Structural | 2 | The hatch was observed to be in good condition.
Building and Process Structural | 2 | The hatch was observed to be in good condition.
Process Electrical | 2 | Pump 3 Discharge Valve Disconnect Switch was observed to be in good condition.
Process Electrical | 2 | Pump 5 Discharge Valve Disconnect Switch was observed to be in good condition.
Process Electrical | 2 | Pump 7 Discharge Valve Disconnect Switch was observed to be in good condition.
Process Electrical | 2 | EUH-04 Disconnect Switch was observed to be in good condition.
Process Electrical | 2 | Sump Pump Disconnect Switch was observed to be in good condition.
Process Electrical | 2 | Dehumidifier-2 Disconnect Switch was observed to be in good condition.
Process Electrical | 2 | Pump 8 Discharge Valve Disconnect Switch was observed to be in good condition.
Process Electrical | 2 | Disconnect Switch was observed to be in good condition.
Process Electrical | 2 | Disconnect Switch was observed to be in good condition.
Process Electrical | 2 | Disconnect Switch was observed to be in good condition.
Process Piping | 2 | The Forcemain was assumed to be in good condition based on its age. However internal inspection of the piping was not undertaken.
Process Piping | 2 | The Overflow Piping was assumed to be in good condition based on its age. However internal inspection of the piping was not undertaken.
Building Services | 2 | The Vent Piping was observed to be in good condition.
Process Instrumentation SCADA | 2 | PLC 1 was observed to be in good condition.
Process Instrumentation SCADA | 2 | The Wet Well Level Transmitter was observed to be in good condition.
Process Instrumentation SCADA | 2 | The UPS 1 was observed to be in good condition.
Building and Process Structural | 2 | The base slab could not be inspected as it was submersed at the time of the assessment. The slab was assumed to be in good condition based on its age and the condition of other visible structural components.
Building and Process Structural | 2 | The aluminum service platform was observed to be in good condition.
Process Instrumentation SCADA | 2 | The Wet Well Float System was observed to be in good condition.
Building and Process Structural | 2 | The aluminum guardrail was observed to be in good condition. Minor deposit buildup was noted. | Minor deposit-buildup
Building and Process Structural | 2 | The concrete walls were observed to be in good condition. Minor rust spots and efflorescence deposits were noted. | Minor rust-spots
Building and Process Structural | 2 | The precast concrete roof was observed to be in good condition. Minor rust spots were noted. | Efflorescence deposits
Building and Process Structural | 2 | The stainless steel ladder was observed to be in good condition.
Building and Process Structural | 2 | The stainless steel ladder was observed to be in good condition. The safety extension rail could not be extended and should be repaired/replaced. | not extended
Process Mechanical Equipment | 2 | Sewage Lift Pump 1 was submersed at the time of the inspection, but was assumed to be in good condition based on its age.
Process Mechanical Equipment | 2 | Sewage Lift Pump 2 was submersed at the time of the inspection, but was assumed to be in good condition based on its age.
Building and Process Structural | 2 | The aluminum hatch was observed to be in good condition. Vegetation in hatch frame should be cleaned out periodically. | Vegetation
Building and Process Structural | 2 | The aluminum hatch was observed to be in good condition. Vegetation in hatch frame should be cleaned out periodically.
Building and Process Structural | 2 | The aluminum hatch was observed to be in good condition. Vegetation in hatch frame should be cleaned out periodically.
Building and Process Structural | 2 | The foundation could not be inspected as it is hidden. The foundation was assumed to be in good condition based on its age and the condition of other visible structural components.
Building and Process Structural | 2 | The electrical panel structure was observed to be in good condition.
Process Electrical | 2 | Disconnect Switch was observed to be in good condition.
Process Electrical | 2 | Disconnect Switch was observed to be in good condition.
Process Electrical | 2 | Disconnect Switch was observed to be in good condition.
Process Electrical | 2 | EUH-05 Disconnect Switch was observed to be in good condition.
Process Electrical | 2 | Fixtures were observed to be in good condition. The light fixtures in the Pump Gallery were installed directly below skylights.
Process Electrical | 2 | Disconnect Switch was observed to be in good condition.
Process Electrical | 2 | Disconnect Switch was observed to be in good condition.
Process Piping | 2 | The Forcemain was assumed to be in good condition based on its age. However, internal inspection of the piping was not undertaken.
Building and Process Structural | 2 | The concrete foundation could not be inspected as it is buried. The foundation was assumed to be in good condition based on its age and the condition of other visible structural components.
Process Instrumentation SCADA | 2 | Level Transmitter 1 was observed to be in good condition.
Building Services | 2 | Heater Unit 1 was observed to be in good condition.
Building Services | 2 | The Temperature Controller 1 was observed to be in good condition, but was approaching the end of its useful service life.
Building Services | 2 | The Smoke Detector/ Carbon Monoxide Alarm Unit was observed to be in good condition.
Building Services | 2 | The Eyewash Station was observed to be in good condition, however a 15 minute flush eyewash unit should be installed.
Building Services | 2 | The Fire Extinguisher was observed to be in good condition.
Building Services | 2 | Motorized Damper 4 was observed to be in good condition.
Building Services | 2 | Motorized Damper 3 was observed to be in good condition.
Building Services | 2 | Fan Exhaust 1 was observed to be in good condition.
Building Services | 2 | Motorized Damper 2 was observed to be in good condition.
Process Instrumentation SCADA | 2 | Remote Communication System was observed to be in good condition.
Process Instrumentation SCADA | 2 | PLC 1 was observed to be in good condition, however it was approaching the end of its estimated remaining service life.
Process Instrumentation SCADA | 2 | UPS 1 was observed to be in good condition.
Process Instrumentation SCADA | 2 | Diesel Fuel Tank Level Transmitter was observed to be in good condition.
Building and Process Structural | 2 | The concrete floor was observed to be in good condition.
Building Services | 2 | The Generator Exhaust System was observed to be in good condition.
Building Services | 2 | The Smoke Detector Alarm Unit was observed to be in good condition.
Building Services | 2 | Motorized Damper 1 was observed to be in good condition.
Building Services | 2 | Wet Well Air Supply Fan 1 was in good condition, however minor corrosion on metal wire mesh was observed.
Process Mechanical Equipment | 2 | The Forcemain Bypass Isolation Gate Valve was in good condition.
Process Piping | 2 | The Forcemain By-pass Piping was observed to be in good condition.
Process Mechanical Equipment | 2 | The Forcemain Gate Valve was in good condition.
Process Piping | 2 | The Overflow Piping was assumed to be in good condition based on its age. The Region is planning to partially remove the existing overflow and construct a new overflow extension across Tannery Park with a new headwall at the lakeshore in accordance with E
Building Services | 2 | The Vent Piping was in good condition.
Building and Process Structural | 2 | The access hatch was observed to be in good condition.
Building and Process Structural | 2 | The access hatch was observed to be in good condition.
Building Architectural | 2 | The generator building aluminum louvre was observed to be in good condition.
Building Architectural | 2 | The stone veneer was observed to be in good condition.
Building Architectural | 2 | The exterior door was observed to be in fair condition. Paint was noted to be missing in a few areas. | Missing paint
Building Architectural | 2 | The generator building aluminum louvre was observed to be in good condition.
Building Architectural | 2 | The louvre was observed to be in good condition.
Building Architectural | 2 | The louvre was observed to be in good condition.
Building and Process Structural | 2 | The concrete block walls were observed to be in good condition. Minor step cracking was noted in the mortar joints. | Minor step-cracking
Building and Process Structural | 2 | The roof framing could not be inspected as it was covered by drywall. The roof framing was assumed to be in good condition based on its age and the condition of other visible structural components.
Building and Process Structural | 2 | The base slab could not be inspected as it was submersed at the time of the assessment. The slab was assumed to be in good condition based on its age and the condition of other visible structural components.
Building and Process Structural | 2 | The walls were observed to be in good condition. Minor rust spots were noted.
Building and Process Structural | 2 | The aluminum ladder was observed to be in good condition. Minor deposit buildup was noted. | Minor deposit buildup
Building and Process Structural | 2 | The aluminum service platform was observed to be in good condition.
Building and Process Structural | 2 | The roof was observed to be in good condition.
Process Mechanical Equipment | 2 | Sewage Lift Pump 1 was submersed at the time of the inspection, but was assumed to be in good condition based on its age.
Process Mechanical Equipment | 2 | Sewage Lift Pump 2 was submersed at the time of the inspection, but was assumed to be in good condition based on its age.
Process Electrical | 2 | Disconnect Switch was observed to be in good condition.
Process Electrical | 2 | Disconnect Switch was observed to be in good condition.
Process Electrical | 2 | Lighting Panel was observed to be in good condition.
Process Electrical | 2 | Transformer was observed to be in good condition.
Process Instrumentation SCADA | 2 | Wet Well Pressure Transmitter 1 was observed to be in good condition, however it was approaching the end of its estimated remaining service life.
Process Electrical | 2 | Disconnect Switch was observed to be in good condition.
Process Electrical | 2 | Disconnect Switch was observed to be in good condition.
Process Electrical | 2 | Panel was observed to be in good condition.
Electrical | 2 | Minor corrosion on the panel was observed.
Electrical | 2 | Minor corrosion was observed on the surface.
Process Piping | 2 | The visible section of the Overflow Piping was observed to be in good condition.
Process Piping | 2 | Pump 2 Discharge Piping was in good condition. Minor surface corrosion was observed.
Process Mechanical Equipment | 2 | Sewage Lift Pump 2 Inlet Gate Valve was observed to be in good condition.
Process Mechanical Equipment | 2 | Sewage Lift Pump 2 Discharge Check Valve was in good condition. Minor surface corrosion was observed.
Process Mechanical Equipment | 2 | Sewage Lift Pump 2 Discharge Gate Valve was in good condition. Minor surface corrosion was observed.
Process Mechanical Equipment | 2 | Sewage Lift Pump 1 Discharge Valve was in good condition. Minor surface corrosion was observed.
Process Mechanical Equipment | 2 | Sewage Lift Pump 1 Discharge Check Valve was in good condition. Minor surface corrosion was observed.
Process Piping | 2 | Pump 1 Discharge Piping was in good condition. Minor surface corrosion was observed.
Process Instrumentation SCADA | 2 | Wet Well Level Transmitter 1 was observed to be in good condition.
Process Instrumentation SCADA | 2 | The Remote Communication System was observed to be in good condition.
Building Services | 2 | The Sump Pump was in good condition. Minor surface corrosion was observed.
Process Instrumentation SCADA | 2 | Wet Well Float System was observed to be in good condition.
Building Services | 2 | The Dehumidifier was observed to be in good condition.
Building Services | 2 | The Portable Unit Heater was observed to be in good condition.
Process Piping | 2 | 400mm Watermain Piping was assumed to be in good condition.
Process Piping | 2 | 900mm Watermain Piping was assumed to be in good condition.
Building and Process Structural | 2 | The Cell 1 columns were in good condition. Rust spots were noted at anchor locations for the washdown pipe. Previous repair were also noted on a few columns. | Rust spots
Building and Process Structural | 2 | The Cell 1 floor slab was in good condition. Previous cracking repaired with the same material as expansion joint repairs on the floor and walls were noted. The existing coating of the expansion joint was noted to be cracking. The existing joint sealant
Building and Process Structural | 2 | The Cell 1 Roof Slab was in good condition. Corroded metal disk were noted typically throughout the underside of the underside of the roof slab. Embedded wood was also noted throughout the underside of the roof slab. The existing joint filler in expansio | Corroded metal disk
Building and Process Structural | 2 | The ladder located on the northeast corner of Cell 1 was in good condition and securely affixed to the wall.
Building and Process Structural | 2 | The ladder located on the northeast corner of Cell 1 was in good condition and securely affixed to the wall.
Building and Process Structural | 2 | The Cell 2 columns were in good condition. Rust spots at anchor locations for the washdown pipe were noted on three (3) columns.
Building and Process Structural | 2 | The Cell 2 floor slab was in good condition. Previously repaired cracking was noted around the perimeter of Cell 2. In addition, hairline cracking with efflorescence totalling 39.05m was also noted around the Cell 2 perimeter. The existing coating of the | hairline cracking
Building and Process Structural | 2 | The underside of the Cell 2 roof slab was in good condition. Corroded form ties were noted typically throughout the underside of the roof slab. Existing joint filler in the expansion joint was also noted to be loose. However, no active leaking was noted. | Loose joint filler
Building and Process Structural | 2 | — The ladder located on the northwest corner of Cell 2 was found to have corrosion staining. The ladder was securely affixed to the wall. However, corrosion was noted on a few anchors. | corrosion staining
Building Services | 2 | Building Security System was observed to be in good condition.
Building Services | 2 | Fire Extinguisher was observed to be in good condition.
Process Instrumentation SCADA | 2 | UPS 1 was observed to be in good condition but was approaching the end of its service life.
Process Instrumentation SCADA | 2 | UPS 2 was observed to be in good condition but was approaching the end of its service life.
Process Instrumentation SCADA | 2 | UPS 3 was observed to be in good condition.
Process Instrumentation SCADA | 2 | PLC Panel was observed to be in good condition. The Region's staff reported that a new marshalling panel was installed and system was connected to the new booster station PLC.
Process Instrumentation SCADA | 2 | Cell 1 Isolation Valve Position Indicator was observed to be in good condition. The Region's staff reported that a new marshalling panel was installed and system was connected to the new booster station PLC.
Process Instrumentation SCADA | 2 | Sodium Hypochlorite Pump 1 Speed Indicator was observed to be in good condition. The Region's staff reported that a new marshalling panel was installed and system was connected to the new booster station PLC.
Process Instrumentation SCADA | 2 | Sodium Hypochlorite Pump 1 Set Point Indicator 1 was observed to be in good condition. The Region's staff reported that a new marshalling panel was installed and system was connected to the new booster station PLC.
Process Instrumentation SCADA | 2 | Sodium Hypochlorite Pump 1 Speed Indicator was observed to be in good condition. The Region's staff reported that a new marshalling panel was installed and system was connected to the new booster station PLC.
Process Instrumentation SCADA | 2 | Chlorine Residual Set Point Indicator was observed to be in good condition. The Region's staff reported that a new marshalling panel was installed and system was connected to the new booster station PLC.
Process Instrumentation SCADA | 2 | Chlorine Residual Set Point Indicator was observed to be in good condition. The Region's staff reported that a new marshalling panel was installed and system was connected to the new booster station PLC.
Process Instrumentation SCADA | 2 | Sodium Hypochlorite Pump 2 Set Point Indicator was observed to be in good condition. The Region's staff reported that a new marshalling panel was installed and system was connected to the new booster station PLC.
Process Instrumentation SCADA | 2 | Temperature Switch was observed to be in good condition.
Process Instrumentation SCADA | 2 | Reservoir Work Station was observed to be in good condition.
Process Piping | 2 | Washdown Piping was observed to be in good condition.
Process Mechanical Equipment | 2 | Sample Station was observed to be in good condition. Minor corrosion was observed on the sink.
Process Instrumentation SCADA | 2 | Chlorine Outlet Analyzer was observed to be in good condition.
Process Instrumentation SCADA | 2 | Chlorine Inlet Analyzer was observed to be in good condition.
Process Mechanical Equipment | 2 | Cell 1 Drain Gate Valve was observed to be in good condition.
Process Piping | 2 | The visible section of the cell 1 Drain Piping was observed to be in good condition.
Process Mechanical Equipment | 2 | Cell 2 Drain Gate Valve was observed to be in good condition.
Process Piping | 2 | The visible section of the Cell 2 Drain Piping was observed to be in good condition.
Electrical | 2 | Minor corrosion was observed on transformer exterior
Process Instrumentation SCADA | 2 | Cell 1 Level Transmitter was observed to be in good condition.
Building Services | 2 | Smoke Detector 1 was observed to be in good condition.
Building Services | 2 | Smoke Detector 2 was observed to be in good condition.
Process Instrumentation SCADA | 2 | Cell 2 Level Transmitter was observed to be in good condition.
Building Services | 2 | Eyewash Station was observed to be in good condition.
Building and Process Structural | 2 | The monorail beam was observed to be in good condition. However its annual certification information was not accessible to determine if it was valid at the time of the assessment.
Building and Process Structural | 2 | The handrail was observed to be in good condition. However, kickplate was noted to be missing at intermediate landing. The Region's Operations mentioned that the kickplate was installed after the inspection. | missing kickplate
Building and Process Structural | 2 | The concrete staircase was observed to be in good condition.
Building and Process Structural | 2 | The concrete floor was observed to be in good condition.
Building and Process Structural | 2 | The concrete beams were observed to be in good condition.
Building and Process Structural | 2 | The equipment hatch was observed to be in good condition.
Building and Process Structural | 2 | The roof was observed to be in good condition.
Building and Process Structural | 2 | The checker plate hatch was observed to be in good condition.
Building and Process Structural | 2 | The access hatch was observed to be in good condition.
Building and Process Structural | 2 | The access hatch was observed to be in good condition.
Building Architectural | 2 | The exterior door was observed to be in good condition. Minor corrosion was noted on the door closer.
Building Architectural | 2 | The louvre was observed to be in good condition.
Building Architectural | 2 | The louvre was observed to be in good condition.
Building and Process Structural | 2 | The access hatch was observed to be in good condition.
Building and Process Structural | 2 | The access hatch was observed to be in good condition.
Building and Process Structural | 2 | The access hatch was observed to be in good condition.
Building and Process Structural | 2 | The access hatch was observed to be in good condition.
Building and Process Structural | 2 | The containment curbs were observed to be in good condition.
Building Architectural | 2 | The louvre was observed to be in good condition.
ES | 2 | Minor surface corrosion was observed.
ES | 2 | Minor surface corrosion was observed.
ES | 2 | Conduits and supports below the junction box was observed with moderate corrosion, replace conduits and supports.
ES | 2 | Conduits and supports below the junction box were observed with moderate corrosion.
Building Services | 2 | Sump Pump Assembly was assumed to be in good condition. However, minor corrosion on exterior casing was noted. The region's staff reported that the sump pit had been sealed and water was pumped into sanitary system.
Process Instrumentation SCADA | 2 | Wet Well Float System was in very good condition.
Process Mechanical Equipment | 2 | Pump 2 Discharge Swing Check Valve was observed to be in very good condition.
Process Mechanical Equipment | 2 | Pump 1 Discharge Swing Check Valve was observed to be in very good condition.
Process Piping | 2 | Reservoir Inlet/Outlet Piping was assumed to be in good condition based on its age.
Process Piping | 2 | Watermain Piping was assumed to be in good condition based on its age.
Building and Process Structural | 2 | The ladder was observed to be in good condition. Safety extension at top of ladder is loose and could fall. | loose safety extension
Process Piping | 2 | Cell 1 Inlet Piping was observed to be in good condition. Moderate corrosion was noted on pipe flanges.
Building and Process Structural | 2 | The floor was observed to be in good condition. Joint sealant was found to either be missing or debonded from the concrete. Insufficient sloping was noted within the drainage trough. Guardrail was noted to be missing by drainage trench. | missing joint sealant
Building and Process Structural | 2 | The walls were observed to be in good condition. Minor cracking with efflorescence, honeycombing and rust spots were noted throughout. | Minor cracking
Building and Process Structural | 2 | The platform was observed to be in good condition. A nut and washer was noted to be corroded and missing at the tread to stringer connection.
Building and Process Structural | 2 | The ladder was observed to be in good condition.
Building and Process Structural | 2 | The columns were observed to be in good condition. Minor cracking with efflorescence deposits were noted. | Minor cracking with efflorescence deposits
Building and Process Structural | 2 | The floor was observed to be in good condition. Cracking with efflorescence deposits were noted. An active leak was noted at the expansion joint adjacent to the valve chamber at the northwest corner. Guardrail was noted to be missing at ladder landing. | Cracking with efflorescence deposits
Building and Process Structural | 2 | The walls were observed to be in good condition. Cracking with efflorescence deposits, rust spots and honeycombing were noted. Joint sealants were found to be deteriorated. | Cracking with rust spots
Building and Process Structural | 2 | The ladder was observed to be in good condition. Safety extension at top of ladder was loose and could fall. | Loose safety extension
Process Piping | 2 | Cell 2 Outlet Piping was observed to be in good condition. Moderate corrosion was observed on the pipe flanges
Building Services | 2 | Unit Heater 1 was observed to be in good condition.
Building Services | 2 | Eye Wash Station was observed to be in good condition.
Building Services | 2 | Electric Water Heater was observed to be in good condition.
Building Services | 2 | Unit Heater 2 was observed to be in good condition.
Building Services | 2 | Smoke Detector was appeared to be in good condition, however it was approaching the end of its useful life.
Building Services | 2 | Unit Heater #4 was observed to be in good condition.
Building Services | 2 | Exhaust Fan 1 was observed to be in good condition. However, moderate to severe corrosion was observed on the ducting in the basement.
Process Instrumentation SCADA | 2 | Reservoir Outlet Chlorine Analyzer was observed to be in good condition, however it was approaching
Process Instrumentation SCADA | 2 | Reservoir Inlet Chlorine Analyzer was observed to be in good condition, however, it was approaching the end of its service life.
Building Services | 2 | Unit Heater #3 was observed to be in good condition.
Building Services | 2 | Dehumidifier Unit was observed to be in good condition. The dehumidifier is installed to reduce condensation in the Valve House and corrosion of the process piping and equipment. However, minor to moderate corrosion throughout the process piping and equip
Process Instrumentation SCADA | 2 | Cell 2 Level Transmitter was observed to be in good condition, however, it was approaching the end of its service life.
Process Instrumentation SCADA | 2 | Sodium Hypo Tank 2 Level Transmitter was observed to be in good condition, however it was approaching the end of its service life.
Process Instrumentation SCADA | 2 | Sodium Hypo Tank 1 Level Transmitter was observed to be in good condition.
Process Mechanical Equipment | 2 | Sodium Hypochlorite Storage Tank 1 was observed to be in good condition.
Process Mechanical Equipment | 2 | Sodium Hypochlorite Storage Tank 2 was observed to be in good condition.
Process Mechanical Equipment | 2 | Sodium Hypochlorite Metering Pump 2 was observed to be in good condition.
Process Mechanical Equipment | 2 | Sodium Hypochlorite Metering Pump 1 was observed to be in good condition.
Process Instrumentation SCADA | 2 | Reservoir Inlet Isolation Valve Indicator was observed to be in good condition.
Process Instrumentation SCADA | 2 | Reservoir Outlet Isolation Valve Indicator was observed to be in good condition.
Process Instrumentation SCADA | 2 | PLC Panel was observed to be in good condition.
Building Services | 2 | Facility Security System was observed to be in good condition.
Building Services | 2 | Fire Extinguisher was observed to be in good condition.
Process Instrumentation SCADA | 2 | Reservoir Work Station was observed to be in good condition.
Building Architectural | 2 | The door was observed to be in good condition. Minor corrosion was noted at the bottom of the door.
Building Architectural | 2 | The louvre was observed to be in good condition.
Building Architectural | 2 | The louvre was observed to be in good condition.
Building Architectural | 2 | The door was observed to be in GOOD condition. Minor corrosion was noted at the bottom of the door. | Minor corrosion
Building and Process Structural | 2 | The access hatch was observed to be in good condition.
Building Architectural | 2 | The roofing system was observed to be in good condition.
Building Architectural | 2 | The roofing system was observed to be in good condition.
Building and Process Structural | 2 | The access hatch was observed to be in good condition.
Building and Process Structural | 2 | The access hatch was observed to be in good condition.
Building and Process Structural | 2 | The access hatch was observed to be in good condition.
Building and Process Structural | 2 | The concrete floor was observed to be in good condition.
Building and Process Structural | 2 | The guardrail was observed to be in good condition.
Building and Process Structural | 2 | The platform was observed to be in good condition.
Building Architectural | 2 | The door was observed to be in good condition.
Building Architectural | 2 | The door was observed to be in good condition.
Building and Process Structural | 2 | The staircase was observed to be in good condition.
Building and Process Structural | 2 | The overflow chamber was not entered, however the concrete walls were observed to be in good condition from above.
Building and Process Structural | 2 | The ladder was observed to be in good condition.
Building and Process Structural | 2 | The platform was observed to be in good condition.
Building and Process Structural | 2 | The floor was observed to be in good condition.
Building and Process Structural | 2 | The checker plate was observed to be in good condition.
Building and Process Structural | 2 | The checker plate was observed to be in good condition.
Building and Process Structural | 2 | The roof was observed to be in good condition.
Building and Process Structural | 2 | The walls were generally observed to be in good condition. Previous crack injection was noted at the hatch location. | Previous crack injection
Building and Process Structural | 2 | The ladder was observed to be in good condition.
Building and Process Structural | 2 | The walls were observed to be in good condition.
Building Architectural | 2 | The door was observed to be in good condition. Minor corrosion was noted on the door frame.
Building and Process Structural | 2 | The floor was observed to be in good condition.
Building and Process Structural | 2 | The concrete beams were observed to be in good condition.
Building and Process Structural | 2 | The ladder was observed to be in good condition.
ES | 2 | The Control Panel was installed at a location in violation of OESC 2015, 26-402. 1 (stairways) and OBC 2012, 3.4.4.4.(1) and 3.4.4.4.(6).
Process Electrical | 3 | An electrical connection for a portable generator was not provided. According to Section 9.11 of the Region’s Water & Wastewater Facilities Design Manual (Jan. 20112), standby power shall be provided for sewage pumping stations.
Process Electrical | 3 | The Pump Control/ Wet Well Level Panel was observed to be in good condition.
Process Electrical | 3 | The MCC was in fair condition, however due to equipment age, the availability of replacement parts and increased maintenance costs will be an issue.
Process Electrical | 3 | Equipment was in fair condition with respect to equipment age, however due to equipment age, the availability of replacement parts and increased maintenance costs will be an issue.
Process Electrical | 3 | The Transformer was in fair condition. Minor corrosion was observed on equipment.
Process Electrical | 3 | Equipment was in fair condition.
Process Electrical | 3 | Lighting Fixture was in fair condition with minor discoloration.
Process Mechanical Equipment | 2 | Cell 2 Outlet Isolation Butterfly Valve Actuator was observed to be in good condition.
Process Mechanical Equipment | 2 | Cell 1 Inlet Isolation Butterfly Valve Actuator was observed to be in good condition.
Process Mechanical Equipment | 2 | Sample Sink was observed to be in good condition.
Process Mechanical Equipment | 2 | Cell Interconnection Butterfly Valve 1 was observed to be in good condition.
Process Mechanical Equipment | 2 | Cell Interconnection Butterfly Valve 2 was observed to be in good condition.
Process Piping | 2 | Reservoir Interconnection Piping was observed to be in good condition.
Building Services | 2 | Cell 1 Wall Heater was observed to be in good condition with very minor surface corrosion.
Process Instrumentation SCADA | 2 | Cell 3 Level Transmitter was observed to be in good condition.
Building Services | 2 | Fire Extinguishers were observed to be in good condition.
Building Services | 2 | Cell 2 Access House Wall Heater was observed to be in good condition with very minor surface corrosion.
Process Instrumentation SCADA | 2 | Cell 2 Level Transmitter was observed to be in good condition.
Building Services | 2 | Cell 3 Wall Heater was observed to be in good condition with very minor surface corrosion.
Process Instrumentation SCADA | 2 | Cell 1 Level Transmitter and Indicator was observed to be in good condition.
Building Services | 2 | The High Temperature Alarm was observed to be in good condition.
Building Services | 2 | The Low Temperature Alarm was observed to be in good condition.
Building Services | 2 | Portable Air Conditioners and Dehumidifiers were observed to be in good condition. The Region's Operators reported ventilation and condensation issues at the three access houses as was evident from the corrosion observed and peeling ceiling paint. The por | Peeling ceiling paint
Building Services | 2 | Security System was observed to be in good condition.
Building Architectural | 2 | The access door was observed to be in good condition. Door sweeps and caulking around doors were in serviceable condition.
Building and Process Structural | 2 | The access hatch was observed to be in good condition.
Building and Process Structural | 2 | The ladder was observed to be in good condition.
Building and Process Structural | 2 | The concrete structure was observed to be in good condition due to age.
Building Architectural | 2 | The access door was observed to be in good condition. Door sweeps and caulking around doors were in serviceable condition.
Building and Process Structural | 2 | The grating was observed to be in good condition.
Building and Process Structural | 2 | The concrete structure was observed to be in good condition due to age.
Building Architectural | 2 | The access door was observed to be in good condition. Door sweeps and caulking around doors were in serviceable condition.
Building Architectural | 2 | The roofing system was observed to be in good condition.
Building and Process Structural | 2 | The access hatch was observed to be in good condition.
Process Electrical | 3 | Enclosure was in fair condition. Minor corrosion was observed throughout.
Process Electrical | 3 | Transfer Switch was in fair condition and had surpassed its expected service life.
Process Electrical | 3 | Pump Control Panel was in fair condition and had surpassed its expected service life.
Process Instrumentation SCADA | 2 | PLC Panel & PLC Uninterruptible Power Supply (UPS) was observed to be in good condition.
Process Instrumentation SCADA | 2 | Reservoir Outlet Chlorine Analyzer was observed to be in good condition.
Process Instrumentation SCADA | 2 | Chlorine Analyzer was observed to be in good condition.
Process Electrical | 3 | Main Breaker was in fair condition. Minor corrosion was observed.
Process Electrical | 3 | Enclosure was in fair condition. Moderate corrosion and paint wear was observed.
Process Electrical | 3 | Pump Control Panel was in fair condition and was approaching the end of its useful service life.
Process Electrical | 3 | Transfer Switch was in fair condition with very minor corrosion.
Building Services | 2 | Dehumidifier was observed to be in good condition.
Process Instrumentation SCADA | 2 | PLC Control Panel was observed to be in fair condition.
Process Instrumentation SCADA | 2 | Cell 1 Level Transmitter was observed to be in good condition. The level meters are required to be calibrated. During the draining of the Cell 1, the Region determined that the level meters were switched (meter for Cell 1 was reading for Cell 2, and vise
Building Services | 2 | High Temperature Alarm was observed to be in good condition.
Building Services | 2 | Low Temperature Alarm was observed to be in good condition.
Process Instrumentation SCADA | 2 | PLC Uninterruptible Power Supply (UPS) was observed to be in good condition.
Building Services | 2 | Unit Heater was observed to be in good condition.
Process Electrical | 3 | The MCC was in fair condition, however the availability of replacement parts and increased maintenance costs will be an issue in the next few years.
Building Services | 2 | Smoke Detector Alarm Unit was in good condition.
Building Services | 2 | Fire Extinguisher was observed to be in good condition.
Building Services | 2 | Security System was observed to be in good condition.
Process Electrical | 3 | The panel was in fair condition, however the availability of replacement parts and increased maintenance costs will be an issue in the next few years.
Building Services | 2 | Secondary Containment Generator Base Tank was observed to be in good condition.
Process Instrumentation SCADA | 2 | Cell 2 Level Transmitter was observed to be in good condition. The level meters are required to be calibrated. During the draining of the Cell 1, the Region determined that the level meters were switched (meter for Cell 1 was reading for Cell 2, and vise
Process Electrical | 3 | Minor mechanical damage was observed on transformer exterior. The transformer has surpassed its expected service life.
Building and Process Structural | 2 | The hatch was observed to be in good condition.
Building and Process Structural | 2 | The access hatch was observed to be in good condition.
Building and Process Structural | 2 | The hatch was observed to be in good condition.
Building and Process Structural | 2 | The manhole cover and frame was observed to be in good condition.
Building and Process Structural | 2 | The hatch was observed to be in good condition.
Process Electrical | 3 | Fixtures were in fair condition. Oxidation and corrosion was observed on fixtures.
Process Piping | 2 | The Drain Piping was assumed to be in good condition based on its age.
Process Piping | 2 | The Forcemain Air Release Valve was assumed to be in good condition based on its age. The Region's Operations reported the air release valves may plug, allowing air to accumulate at high points.
Process Piping | 2 | The Forcemain Air Release Valve was assumed to be in good condition based on its age. The Region's Operations reported the air release valves may plug, allowing air to accumulate at high points.
Process Piping | 2 | The Forcemain Air Release Valve was assumed to be in good condition based on its age. The Region's Operations reported the air release valves may plug, allowing air to accumulate at high points.
Process Piping | 2 | The Forcemain Air Release Valve was assumed to be in good condition based on its age. The Region's Operations reported the air release valves may plug, allowing air to accumulate at high points.
Building Services | 2 | The Motorized Damper was observed to be in good condition.
Process Instrumentation SCADA | 2 | PLC 1 was observed to be in good condition, however, it was approaching the end of its useful service life. Availability of parts and increased maintenance costs will be an issue. It is recommended to replace the equipment in next 5 years.
Building Services | 2 | The Motorized Damper was observed to be in good condition.
Process Instrumentation SCADA | 2 | Communication System UPS 1 was observed to be in good condition, but was approaching the end of its useful service life.
Process Instrumentation SCADA | 2 | Remote Communication System was observed to be in good condition.
Process Instrumentation SCADA | 2 | Combustible Gas Monitor 1 was observed to be in good condition, but is approaching the end of its useful service life.
Process Instrumentation SCADA | 2 | Wet Well Level Transmitter 1 was observed to be in good condition, however it is approaching the end of its useful service.
Process Instrumentation SCADA | 2 | Wet Well Level Transmitter 2 was observed to be in good condition, however it is approaching the end of its useful service.
Process Instrumentation SCADA | 2 | Flow Transmitter 1 was observed to be in good condition, however it was approaching the end of its useful service.
Building Services | 2 | The Temperature Alarm Unit was observed to be in good condition, however it was approaching the end of its useful service life.
Building Services | 2 | The Generator Cooling Water Heat Exchanger was observed to be in good condition.
Building Services | 2 | The Fire Extinguisher was observed to be in good condition.
Building Services | 2 | The Motorized Damper was observed to be in good condition.
Building Services | 2 | Air Supply Fan 3 was observed to be in good condition.
Building Services | 2 | Unit Heater 2 was observed to be in good condition.
Building Services | 2 | Smoke Detector Alarm Unit 1 was observed to be in good condition, however it was approaching the end of its useful service life.
Process Instrumentation SCADA | 2 | Generator Fuel Supply UPS was observed to be in good condition.
Building Services | 2 | Air Conditioner Unit 1 was observed to be in good condition.
Building Services | 2 | The Generator Exhaust was observed to be in good condition.
Building Services | 2 | Glycol Tank 1 was observed to be in good condition.
Building Services | 2 | Unit Heater 1 was observed to be in good condition.
Building Services | 2 | Glycol Cooler 1 was observed to be in good condition.
Building Services | 2 | Dehumidifier was observed to be in good condition.
Building Services | 2 | Backflow Preventer 1 Outlet Isolation Gate Valve 2 was observed to be in good condition.
Building Services | 2 | Backflow Preventer 1 was observed to be in good condition.
Building Services | 2 | Backflow Preventer 1 Inlet Isolation Gate Valve 1 was observed to be in good condition.
Building Services | 2 | Backflow Preventer 2 Outlet Isolation Gate Valve 4 was observed to be in good condition. The hand wheel was found missing.
Building Services | 2 | Backflow Preventer 2 was observed to be in good condition.
Building Services | 2 | Backflow Preventer 2 Inlet Isolation Gate Valve 3 was observed to be in good condition. The hand wheel was found missing.
Building Services | 2 | Water Meter was observed to be in good condition.
Building Services | 2 | The Temperature Control Valve was observed to be in good condition. The Region's Operations reported issues with cooling. The heat sensor to open the coolant is on the incorrect cooling jacket as it is on "after cooler return (glycol)" and should be on "j
Building Services | 2 | The Dry Well Temperature Alarm Unit was observed to be in good condition, however it is approaching the end of its useful service life.
Building Services | 2 | Dry Well Air Supply Fan 2 was observed to be in good condition.
Building Services | 2 | The Motorized Damper was observed to be in good condition.
Process Piping | 2 | The Overflow Piping was observed to be in good condition.
Process Mechanical Equipment | 2 | The Flap Gate was observed to be in good condition. Minor surface corrosion and paint wear was observed.
Process Instrumentation SCADA | 2 | The Manhole 1 Float System was observed to be in good condition, but is approaching the end of its useful service life.
Building Architectural | 2 | The exterior brick cladding was observed to be in good condition.
Building Architectural | 2 | The door was observed to be in good condition. Weatherstripping on bottom of door was noted to be loose. | loose weatherstripping
Building Architectural | 2 | The knockout panels were observed to be in good condition overall. Caulking was noted to be dry and detached.
Building Architectural | 2 | The door was observed to be in good condition.
Building Architectural | 2 | The door was observed to be in good condition.
Building Architectural | 2 | The louvre was observed to be in good condition.
Building and Process Structural | 2 | The access hatch was observed to be in good condition.
Building Architectural | 2 | The wall and ceiling paint was observed to be in good condition.
Building Architectural | 2 | The roofing system was observed to be in good condition.
Building Services | 2 | Wet Well Exhaust Fan 1 was observed to be in good condition.
Building Services | 2 | Wet Well Exhaust Fan 1 Motor was observed to be in good condition. Minor corrosion on motor casing was observed.
Process Mechanical Equipment | 2 | Valve Chamber 1 Gate Valve 1 was observed to be in good condition, however, minor corrosion of the flanges was observed.
Process Mechanical Equipment | 2 | Valve Chamber 1 Gate Valve 2 was observed to be in good condition, however, minor corrosion of the flanges was observed.
Building and Process Structural | 2 | The valve chamber was observed to be in good condition.
Building Services | 2 | Dry Well Exhaust Fan 1 was observed to be in good condition.
Building Services | 2 | Dry Well Exhaust Fan 1 Motor was observed to be in good condition. Minor corrosion and paint wear was observed.
Building Services | 2 | Dry Well Air Supply Fan 2 Motor was observed to be in good condition.
Building Services | 2 | Air Supply Fan 3 Motor was observed to be in good condition. Minor corrosion of the casing was observed.
Building Services | 2 | Wet Well Air Supply Fan 1 Motor was observed to be in good condition.
Process Mechanical Equipment | 2 | Wet Well 2 Gate was assumed to be in good condition based on its age. The pedestal and gate operator was observed to be in good condition.
Process Mechanical Equipment | 2 | The Influent Chamber Stop Gate was assumed to be in good condition based on its age. The mount and crank was in fair condition as moderate corrosion and paint wear was observed.
Process Mechanical Equipment | 2 | The Wet Well 1 Stop Gate was assumed to be in good condition based on its age. The mount and crank was in fair condition as moderate corrosion and paint wear was observed.
Process Instrumentation SCADA | 2 | The Wet Well Float System was observed to be in good condition, but is approaching the end of its useful service life.
Process Piping | 2 | The visible portion of the Forcemain was in fair condition as moderate surface corrosion was observed. The buried portion was assumed to be in good condition based on its age.
Process Piping | 2 | The visible portion of the Forcemain was in fair condition as moderate surface corrosion was observed. The buried portion was assumed to be in good condition based on its age.
Building and Process Structural | 2 | The concrete chamber was observed to be in good condition.
Building and Process Structural | 2 | The ladder was observed to be in good condition.
Building and Process Structural | 2 | The aluminum platform was observed to be in good condition.
Building and Process Structural | 2 | The concrete pipe supports were observed to be in good condition.
Building and Process Structural | 2 | The crane beams was observed to be in good condition. Signs of leakage were noted at mount on north wall. | Signs of leakage
Building and Process Structural | 2 | The hatch was observed to be in good condition.
Process Piping | 2 | The Off line Storage Piping was assumed to be in good condition based on its age.
Building and Process Structural | 2 | The tank was observed to be in good condition.
Building and Process Structural | 2 | The ladder was observed to be in good condition.
Process Electrical | 3 | Minor corrosion was observed on enclosure.
Process Electrical | 3 | Transformer was in fair condition. Minor corrosion was observed on transformer base.
Process Electrical | 3 | Lighting fixture was in fair condition.
Process Electrical | 3 | Minor corrosion was observed on Disconnect Switch.
Process Electrical | 3 | Control Panel was in fair condition. The equipment had surpassed its service life. The availability of replacement parts and increased maintenance costs will be an issue.
Process Electrical | 3 | Control Panel was in fair condition. The equipment had surpassed its service life. The availability of replacement parts and increased maintenance costs will be an issue.
Process Electrical | 3 | Catholic Protection was assumed to be in fair condition.
Process Electrical | 3 | Equipment was in fair condition.
Process Electrical | 3 | Equipment was in fair condition with minor discoloration observed.
Process Electrical | 3 | Equipment was in fair condition according to equipment age. The availability of parts and increased costs will be an issue.
Process Electrical | 3 | Fixtures were in fair condition. Minor corrosion was observed.
Building and Process Structural | 2 | The manhole cover was observed to be in good condition.
Building Services | 2 | The Motorized Damper was observed to be in good condition.
Building Services | 2 | Wet Well Air Supply Fan 1 was observed to be in good condition. Minor corrosion on the screen and fan casing was observed. | Minor corrosion
Process Mechanical Equipment | 2 | Sewage Lift Pump 3 was observed to be in good condition. Minor corrosion of the pump casing and pump base was observed. Pump testing was also undertaken as a part of this assessment. No performance issues were identified during the pump inspection. Pump t
Process Piping | 2 | Pump 3 Piping was observed to be in good condition.
Process Mechanical Equipment | 2 | Sewage Lift Pump 3 Motor was observed to be in good condition. Minor surface corrosion was observed. No performance issues were identified during the testing.
Process Mechanical Equipment | 2 | Sewage Lift Pump 3 Inlet Knife Gate Valve was observed to be in good condition.
Building Services | 2 | Water Service Piping was observed to be in good condition.
Building Services | 2 | Cooling Coil Piping was covered in insulated jacket, but was assumed to be in good condition base on its age.
Process Mechanical Equipment | 2 | Sewage Lift Pump 3 Discharge Knife Gate Valve was in good condition. Very minor corrosion of the flanges was observed.
Process Mechanical Equipment | 2 | Sewage Lift Pump 3 Air Release Valve was observed to be in good condition.
Process Mechanical Equipment | 2 | Sewage Lift Pump 2 Motor was observed to be in good condition. Minor surface corrosion was observed. No performance issues were identified during the inspection.
Process Mechanical Equipment | 2 | Sewage Lift Pump 2 Inlet Knife Gate Valve was observed to be in good condition.
Process Piping | 2 | Pump 2 Piping was observed to be in good condition.
Process Mechanical Equipment | 2 | Sewage Lift Pump 2 Discharge Knife Gate Valve was observed to be in good condition.
Process Mechanical Equipment | 2 | Sewage Lift Pump 2 was observed to be in good condition. Minor corrosion of the pump casing and pump base was observed. Pump testing was also undertaken as a part of this assessment. No performance issues were identified during the pump testing. Pump test
Process Mechanical Equipment | 2 | Sewage Lift Pump 1 Motor was observed to be in good condition. Minor surface corrosion was observed. No performance issues were identified during the inspection.
Process Mechanical Equipment | 2 | Sewage Lift Pump 1 Air Release Valve was in good condition. Minor corrosion was observed.
Process Mechanical Equipment | 2 | Sewage Lift Pump 1 Discharge Knife Gate Valve was observed to be in good condition.
Process Piping | 2 | Pump 1 Piping was observed to be in good condition.
Process Mechanical Equipment | 2 | Sewage Lift Pump 1 was observed to be in good condition. Minor corrosion of the pump casing and pump base was observed. Pump testing was also undertaken as a part of this assessment. Pump test results indicated reduced performance of the pumps as compared | Minor corrosion
Process Mechanical Equipment | 2 | Sewage Lift Pump 1 Inlet Knife Gate Valve was observed to be in good condition. Minor paint wear of the flanges was observed.
Process Mechanical Equipment | 2 | Electric Actuated Ball Valve 1 was observed to be in good condition.
Process Mechanical Equipment | 2 | Electric Actuated Ball Valve 2 was observed to be in good condition.
Process Instrumentation SCADA | 2 | The Dry Well Float System was observed to be in good condition, but was approaching the end of its useful service life.
Process Instrumentation SCADA | 2 | The Sump Pump Float System was observed to be in good condition, but is approaching the end of its useful service life.
Building and Process Structural | 2 | The checker plate cover could not be inspected as it was covered at time of inspection. The checker plate cover was assumed to be in good condition based on its age and the condition of other visible structural components.
Building and Process Structural | 2 | The beams could not be inspected as they were submersed at the time of the assessment. The beams were assumed to be in good condition based on its age and the condition of other visible structural components.
Building and Process Structural | 2 | The columns could not be inspected as they were submersed at the time of the assessment. The columns were assumed to be in good condition based on its age and the condition of other visible structural components.
Building and Process Structural | 2 | The base slab could not be inspected as it was submersed at the time of the assessment. The slab was assumed to be in good condition based on its age and the condition of other visible structural components.
Building and Process Structural | 2 | The walls could not be inspected as they were submersed at the time of the assessment. The walls were assumed to be in good condition based on their age and the condition of other visible structural components. The vertical joint of access house has alway
Building and Process Structural | 2 | The ladder could not be inspected as it was submersed at the time of the assessment.
Building and Process Structural | 2 | The floor could not be inspected as it was submersed at the time of the assessment. The floor was assumed to be in good condition based on its age and the condition of other visible structural components.
Building and Process Structural | 2 | The concrete platform could not be inspected as it was submersed at the time of the assessment. The concrete platform was assumed to be in good condition based on its age and the condition of other visible structural components.
Building and Process Structural | 2 | The walls could not be inspected as they were submersed at the time of the assessment. The walls were assumed to be in good condition based on its age and the condition of other visible structural components.
Building and Process Structural | 2 | The guardrail could not be inspected as it was submersed at the time of the assessment. The guardrail was assumed to be in good condition based on its age and the condition of other visible structural components.
Building and Process Structural | 2 | The ladder could not be inspected as it was submersed at the time of the assessment. The ladder was assumed to be in good condition based on its age and the condition of other visible structural components.
Building and Process Structural | 2 | The floor could not be inspected as it was submersed at the time of the assessment. The floor was assumed to be in good condition based on its age and the condition of other visible structural components.
Building and Process Structural | 2 | The concrete platform could not be inspected as it was submersed at the time of the assessment. The concrete platform was assumed to be in good condition based on its age and the condition of other visible structural components.
Building and Process Structural | 2 | The walls could not be inspected as they were submersed at the time of the assessment. The walls were assumed to be in good condition based on its age and the condition of other visible structural components.
Building and Process Structural | 2 | The guardrail could not be inspected as it was submersed at the time of the assessment. The guardrail was assumed to be in good condition based on its age and the condition of other visible structural components.
Building and Process Structural | 2 | The ladder could not be inspected as it was submersed at the time of the assessment. The ladder was assumed to be in good condition based on its age and the condition of other visible structural components.
Process Mechanical Equipment | 2 | Clearwell Overflow Pipe Duckbill Check Valve V0042 was assumed to be in good condition.
Building Services | 2 | Exhaust Fan-04 was assumed to be in good condition.
Building Services | 2 | Exhaust Fan-05 was assumed to be in good condition.
Building Services | 2 | Exhaust Fan-07 was assumed to be in good condition.
Building and Process Structural | 2 | The foundation could not be inspected as it was covered. The foundation was assumed to be in good condition based on its age and the condition of other visible structural components.
Building and Process Structural | 2 | The ladder could not be inspected as it was submersed at the time of the assessment. The ladder was assumed to be in good condition based on its age and the condition of other visible structural components.
Building Architectural | 2 | The roofing system could not be inspected as it was inaccessible. Roof access ladder was recommended to be installed. The roofing system was assumed to be in good condition based on its age and the condition of other visible components.
Building and Process Structural | 2 | The concrete beams could not be inspected as they were in a confined space. The beams were assumed to be in good condition based on their age and the condition of other visible structural components.
Building and Process Structural | 2 | The base slab could not be inspected as it was submersed at the time of the assessment. The slab was assumed to be in good condition based on its age and the condition of other visible structural components.
Building and Process Structural | 2 | The roof slab could not be inspected as it was in a confined space. The roof was assumed to be in good condition based on its age and the condition of other visible structural components.
Building and Process Structural | 2 | The guardrail could not be inspected as it was in a confined space. The guardrail was assumed to be in good condition based on its age and the condition of other visible structural components.
Building and Process Structural | 2 | The ladder could not be inspected as it was in a confined space. The ladder was assumed to be in good condition based on its age and the condition of other visible structural components.
Building and Process Structural | 2 | The ladder could not be inspected as it was in a confined space. The ladder was assumed to be in good condition based on its age and the condition of other visible structural components.
Building and Process Structural | 2 | The precast roof panels could not be inspected as they were in a confined space. The precast panels were assumed to be in good condition based on its age and the condition of other visible structural components.
Process Mechanical Equipment | 2 | Submersible Pump 1 was assumed to be in good condition.
Process Mechanical Equipment | 2 | Overflow Retention Chamber Submersible Pump 1 Check Valve was assumed to be in good condition.
Process Mechanical Equipment | 2 | Overflow Retention Chamber Submersible Pump 1 Gate Valve was assumed to be in good condition.
Process Mechanical Equipment | 2 | Overflow Retention Chamber Submersible Pump 2 was assumed to be in good condition.
Process Instrumentation SCADA | 2 | Pump 1 High and Low Pressure Switches were observed to be in good condition.
Process Instrumentation SCADA | 2 | Pump 2 High and Low Pressure Switches were observed to be in good condition.
Process Instrumentation SCADA | 2 | Pump 3 High and Low Pressure Switches were observed to be in good condition.
Process Instrumentation SCADA | 2 | Pump 7 High and Low Pressure Switches were observed to be in good condition.
Building Architectural | 2 | The roofing system could not be inspected as it was inaccessible. Roof access ladder was recommended to be installed. The roofing system was assumed to be in good condition based on its age and the condition of other visible components.
Building Architectural | 2 | The roofing system could not be inspected as it was inaccessible. Roof access ladder was recommended to be installed. The roofing system was assumed to be in good condition based on its age and the condition of other visible components.
Process Piping | 2 | Reservoir Cell 1 & Cell 2 Interconnection Piping was assumed to be in good condition.
Process Mechanical Equipment | 2 | Reservoir Cell 1 & Cell 2 Water Supply Inlet Butterfly Valve (Valve Chamber 1) was assumed to be in good condition. The valve is not included in the construction drawing. However it is included in the facility asset inventory list.
Process Piping | 2 | Reservoir Cell 1 Drain Piping was assumed to be in good condition.
Process Mechanical Equipment | 2 | Reservoir Cell 1 Inlet Butterfly Valve V0006 (Valve Chamber 1) was assumed to be in good condition.
Process Mechanical Equipment | 2 | Reservoir Cell 2 Connection Pipe Butterfly Valve V0005 (Valve Chamber 1) was assumed to be in good condition.
Process Mechanical Equipment | 2 | Reservoir Cell 2 Drain Gate Valve V0063 was assumed in good condition.
Process Piping | 2 | Reservoir Cell 2 Drain Piping was assumed to be in good condition.
Process Mechanical Equipment | 2 | Reservoir Cell 2 Inlet Butterfly Valve V0004 (Valve Chamber 1) was assumed to be in good condition.
Process Piping | 2 | Reservoir Cell 2 Overflow Piping was assumed to be in good condition.
Process Mechanical Equipment | 2 | Reservoir Overflow Pipe Duckbill Check Valve V0054 was assumed to be in good condition.
Building Architectural | 2 | The roofing system could not be inspected as it was inaccessible. Roof access ladder was recommended to be installed. The roofing system was assumed to be in good condition based on its age and the condition of other visible components.
Building Services | 2 | Sump Pump P-01 was assumed to be in good condition.
Building Services | 2 | Sump Pump P-02 was assumed to be in good condition.
Building Services | 2 | Supply Fan-04 was assumed to be in good condition.
Building Services | 2 | Supply Fan-05 was assumed to be in good condition.
Building and Process Structural | 2 | The foundation could not be inspected as it is buried. The foundation was assumed to be in good condition based on its age and the condition of other visible structural components. No settlement was noted.
Process Mechanical Equipment | 2 | Valve Chamber 2 Butterfly Valve V0003 (to Cell 1) was assumed to be in good condition.
Process Mechanical Equipment | 2 | Valve Chamber 2 Gate Valve V0053 (to Cell 1) was assumed to be in good condition.
Process Piping | 2 | Water Supply Piping for Reservoir Cell 1 and Cell 2 was assumed to be in good condition.
Process Mechanical Equipment | 2 | Zone 3 Discharge Header Butterfly Valve 1 (Valve Chamber 4) was assumed to be in good condition.
Process Mechanical Equipment | 2 | Zone 3 Discharge Header Butterfly Valve 2 (Valve Chamber 4) was assumed to be in good condition.
Process Instrumentation SCADA | 2 | Chlorine Gas Sensor and Monitor including sensor, monitor, strobe lights were observed to be in good condition but were approaching the end of their service life.
Process Instrumentation SCADA | 2 | Chlorine Gas Weigh Scale was observed to be in good condition.
Process Instrumentation SCADA | 2 | Clearwell 2 Level Sensor and Transmitter was observed to be in good condition.
Process Instrumentation SCADA | 2 | Clearwell 2 High and Low Level Switches were observed to be in good condition.
Process Instrumentation SCADA | 2 | Pump 4 High and Low Pressure Switches were observed to be in good condition.
Process Instrumentation SCADA | 2 | Pump 5 High and Low Pressure Switches were observed to be in good condition.
Process Instrumentation SCADA | 2 | Pump 6 High and Low Pressure Switches.
Process Instrumentation SCADA | 2 | Pump 8 High and Low Pressure Switches were observed to be in good condition.
Process Instrumentation SCADA | 2 | Network Distribution Panel was observed to be in good condition.
Process Instrumentation SCADA | 2 | Zone 1 Inlet Free Chlorine Sensor and Analyzer was observed to be in good condition. The sensor will likely need to be replaced with in 5 years due to its age.
Process Instrumentation SCADA | 2 | Zone 2 Discharge Free Chlorine Sensor and Analyzer was observed to be in good condition. The sensor will likely need to be replaced with in 5 years due to its age.
Process Instrumentation SCADA | 2 | Zone 3 Discharge Free Chlorine Sensor and Analyzer was observed to be in good condition. The sensor will likely need to be replaced with in 5 years due to its age.
Process Instrumentation SCADA | 2 | Zone 2 Discharge Magnetic Flowmeter was observed to be in good condition.
Process Instrumentation SCADA | 2 | Zone 2 Discharge Pressure Transmitters was observed to be in good condition. However, valve manifold assemblies showed signs of minor corrosion on their surface.
Process Instrumentation SCADA | 2 | Zone 2 Discharge High and Low Pressure Switches were observed to be in good condition.
Process Instrumentation SCADA | 2 | Zone 3 Discharge Magnetic Flowmeter was observed to be in good condition.
Process Instrumentation SCADA | 2 | Differential Level Transmitters (4 Transmitters) were observed to be in good condition and were expected to reach their life expectancy. However, two valve manifold assemblies as well as flanges showed signs of minor corrosion on the surface.
Process Instrumentation SCADA | 2 | Zone 3 Discharge Header Pressure Transmitters was observed to be in good condition. However, valve manifold assemblies showed signs of minor corrosion on their surface.
Process Instrumentation SCADA | 2 | Zone 3 Discharge High and Low Pressure Switches were observed to be in good condition.
Process Instrumentation SCADA | 2 | Reservoir Cell 2 High and Low Level Switches were recently replaced and were observed to be in good condition. However, stainless steel bolts on flanges showed signs of corrosion.
Process Instrumentation SCADA | 2 | Reservoir Cell 2 Level Sensor and Transmitter were recently replaced and were observed to be in good condition. However, stainless steel bolts on flanges showed signs of corrosion.
Building Services | 2 | Reservoir Cell 1 Gooseneck Vent was observed to be in good condition. The vent was very short with snow accumulation in the winter, the vent may become blocked.
Building and Process Structural | 2 | The checker plate cover was observed to be in good condition.
Building and Process Structural | 2 | The checker plate cover was in good condition however the second cover below that provides access to the chamber could not be inspected as it was covered at the time of inspection. The second cover was assumed to be in good condition based on its age and
Building and Process Structural | 2 | The visible section of platform was observed to be in good condition.
Building and Process Structural | 2 | The visible sections of the walls were observed to be in good condition. However, the chamber was not inspected as it was confined space.
Process Mechanical Equipment | 2 | Overflow Retention Chamber Submersible Pump 2 Check Valve was assumed to be in good condition.
Process Mechanical Equipment | 2 | Overflow Retention Chamber Submersible Pump 2 Gate Valve was assumed to be in good condition.
Building Architectural | 2 | The door was observed to be in good condition. However, the door rubs on door frame at top of door.
Building Architectural | 2 | The door was observed to be in good condition.
Building Architectural | 2 | The door was observed to be in good condition.
Building and Process Structural | 2 | The staircase was observed to be in good condition.
Building Architectural | 2 | The aluminum louvre was observed to be in good condition.
Building Architectural | 2 | The overhead door was observed to be in good condition.
Building Architectural | 2 | The door was observed to be in good condition. Door seal was found to not be continuous.
Building Architectural | 2 | The door was observed to be in good condition. Signage was noted to be missing.
Building Architectural | 2 | The door was observed to be in good condition. Door seal was noted to be torn and minor corrosion was noted by door strike plate.
Building and Process Structural | 2 | The concrete blockwalls were observed to be in good condition.
Building and Process Structural | 2 | The concrete floor was observed to be in good condition. However, the Region's operators reported that the floor drain in the chlorine area is not located at the lowest point, which causes drainage issues each time the emergency eye wash & shower is used/
Building Architectural | 2 | The wall and ceiling paint was observed to be in good condition.
Building Architectural | 2 | The door was observed to be in good condition.
Building Architectural | 2 | The window was observed to be in good condition.
Building Architectural | 2 | The floor tiles were observed to be in good condition.
Building Architectural | 2 | The wall and ceiling paint was observed to be in good condition.
Building Architectural | 2 | The door was observed to be in good condition.
Building Architectural | 2 | The floor tiles were observed to be in good condition.
Building Architectural | 2 | The wall and ceiling paint was observed to be in good condition.
Building Architectural | 2 | The door was observed to be in good condition.
Building Architectural | 2 | The protective floor coating was observed to be in good condition.
Building Architectural | 2 | The wall and ceiling paint was observed to be in good condition.
Building Architectural | 2 | The door was observed to be in good condition.
Building Architectural | 2 | The window was observed to be in good condition.
Building Architectural | 2 | The window was observed to be in good condition.
Building Architectural | 2 | The wall and ceiling paint was observed to be in good condition.
Building Architectural | 2 | The door was observed to be in good condition.
Building Architectural | 2 | The wall and ceiling paint was observed to be in good condition.
Building Architectural | 2 | The door was observed to be in good condition.
Building and Process Structural | 2 | The handrail was observed to be in good condition.
Building and Process Structural | 2 | The staircase was observed to be in good condition.
Building Architectural | 2 | The wall and ceiling paint was observed to be in good condition.
Building Architectural | 2 | The door was observed to be in good condition.
Building and Process Structural | 2 | The concrete blockwalls were observed to be in good condition.
Building and Process Structural | 2 | The concrete floor was observed to be in good condition.
Building Architectural | 2 | The wall and ceiling paint was observed to be in very good condition.
Building and Process Structural | 2 | The platform was observed to be in good condition. Washers were noted to be missing on one side of all bolts. Top of ladder ends with sharp corners may pose a hazard.
Building and Process Structural | 2 | The steel beams were observed to be in good condition.
Building and Process Structural | 2 | The platform was observed to be in good condition. Washers were noted to be missing on one side of all bolts. Top of ladder ends with sharp corners may pose a hazard. | sharp corners
Building and Process Structural | 2 | The platform was observed to be in good condition. Washers were noted to be missing on one side of all bolts. Top of ladder ends with sharp corners may pose a hazard.
Building and Process Structural | 2 | The platform was observed to be in good condition. Washers were noted to be missing on one side of all bolts. | Missing washers
Building Architectural | 2 | The door was observed to be in good condition.
Building and Process Structural | 2 | The concrete floor was observed to be in good condition. Minor cracking was noted by edge of grating. | Minor cracking
Building and Process Structural | 2 | The staircase was observed to be in good condition. Washers were noted to be missing on one side of all bolts for framing and treads.
Building Architectural | 2 | The protective floor coating was observed to be in good condition.
Building and Process Structural | 2 | The guardrails were observed to be in good condition.
Building and Process Structural | 2 | The ladder was observed to be in good condition.
Building and Process Structural | 2 | The platform was observed to be in good condition.
Process Mechanical Equipment | 2 | Surge Tank 2 was observed to be in good condition.
Process Mechanical Equipment | 2 | Surge Tank 4 was observed to be in good condition.
Building Architectural | 2 | The door was observed to be in good condition.
Building Architectural | 2 | The door was observed to be in good condition.
Building and Process Structural | 2 | The top surface of the concrete floor was observed to be in good condition. Underside of the floor could not be inspected as it is in a confined space.
Building and Process Structural | 2 | The concrete blockwalls were observed to be in good condition.
Building and Process Structural | 2 | The hatch was observed to be in good condition.
Building and Process Structural | 2 | The steel beams and trusses were observed to be in good condition.
Building and Process Structural | 2 | The grating was observed to be in good condition.
Building and Process Structural | 2 | The hatch was observed to be in good condition.
Building and Process Structural | 2 | The hatch was observed to be in good condition.
Building and Process Structural | 2 | The hatch was observed to be in good condition.
Building and Process Structural | 2 | The hatch was observed to be in good condition.
Building and Process Structural | 2 | The hatch was observed to be in good condition.
Building and Process Structural | 2 | The concrete platform was observed to be in good condition.
Building and Process Structural | 2 | The guardrails were observed to be in good condition.
Building and Process Structural | 2 | The underside of the roof was observed to be in good condition with no visible leaks. | no visible leaks
Building Architectural | 2 | The skylight was inspected from the underside and was observed to be in good condition with no visible signs of leakage. | no visible signs of leakage
Building Architectural | 2 | The skylight was inspected from the underside and was observed to be in good condition with no visible signs of leakage.
Building Architectural | 2 | The skylight was inspected from the underside and was observed to be in good condition with no visible signs of leakage.
Building Architectural | 2 | The skylight was inspected from the underside and was observed to be in good condition with no visible signs of leakage.
Building Architectural | 2 | The skylight was inspected from the underside and was observed to be in good condition with no visible signs of leakage.
Building Architectural | 2 | The skylight was inspected from the underside and was observed to be in good condition with no visible signs of leakage.
Building Architectural | 2 | The skylight was inspected from the underside and was observed to be in good condition with no visible signs of leakage.
Building Architectural | 2 | The skylight was inspected from the underside and was observed to be in good condition with no visible signs of leakage.
Building and Process Structural | 2 | The monorail crane beam was observed to be in good condition. The Region's operators reported that they need a ladder to be installed for access to the crane.
Building and Process Structural | 2 | The guardrail was observed to be in good condition.
Building and Process Structural | 2 | The ladder was observed to be in good condition.
Building Architectural | 2 | The door was observed to be in good condition.
Building and Process Structural | 2 | The steel columns were observed to be in good condition.
Building Architectural | 2 | The wall, ceiling and floor paint was observed to be in good condition.
Building and Process Structural | 2 | The roof was observed to be in good condition. The region's staff reported that roof drain leaking to floor.
Building and Process Structural | 2 | The steel framing was observed to be in good condition.
Building Architectural | 2 | The wall and ceiling paint was observed to be in good condition.
Building and Process Structural | 2 | The monorail beam was observed to be in good condition.
Building and Process Structural | 2 | The precast roof was observed to be in good condition.
Building Architectural | 2 | The door was observed to be in good condition. However, paint was noted to be missing on the due to wear and tear.
Building and Process Structural | 2 | The concrete blockwalls were observed to be in good condition.
Building and Process Structural | 2 | The concrete floor was observed to be in good condition.
Building and Process Structural | 2 | The precast roof was observed to be in good condition.
Building Architectural | 2 | The door was observed to be in good condition.
Building Architectural | 2 | The door was observed to be in good condition.
Building and Process Structural | 2 | The concrete blockwall was observed to be in good condition.
Building and Process Structural | 2 | The concrete floor and curb was observed to be in good condition.
Building Architectural | 2 | The door was observed to be in good condition.
Building Architectural | 2 | The wall and ceiling paint was observed to be in good condition.
Building and Process Structural | 2 | The staircase was observed to be in good condition.
Building Architectural | 2 | The door was observed to be in good condition. However, paint was noted to be missing on the door frame due to wear and tear.
Building Architectural | 2 | The door was observed to be in good condition. However, minor corrosion and staining was noted on the door frame due to active leak at wall.
Building Architectural | 2 | The door was observed to be in good condition. Door was noted to be rubbing on frame at top of door.
Building Architectural | 2 | The wall paint was observed to be in good condition.
Building and Process Structural | 2 | The roof and steel beam was observed to be in good condition.
Building and Process Structural | 2 | The staircase was observed to be in good condition. Washers were noted to be missing on one side of all bolts for framing and treads.
Building and Process Structural | 2 | The concrete floor was generally observed to be in good condition. Water was observed to be leaking at expansion joint between new slab and existing footing of loading dock area. | leaking at expansion joint
Building and Process Structural | 2 | The walls were observed to be in good condition.
Building and Process Structural | 2 | The concrete beams were observed to be in good condition. Previous patches were noted in a few areas. | Previous patches
Building and Process Structural | 2 | The concrete blockwall was observed to be in good condition.
Building and Process Structural | 2 | The staircase was observed to be in good condition. Washers were noted to be missing on one side of all bolts for framing and treads.
Building Architectural | 2 | The wall and ceiling paint was observed to be in good condition.
Building and Process Structural | 2 | The precast roof was observed to be in good condition.
Building and Process Structural | 2 | The aluminum checker plate was observed to be in good condition.
Building and Process Structural | 2 | The staircase was observed to be in good condition. Washers were noted to be missing on one side of all bolts for framing and treads.
Building and Process Structural | 2 | The aluminum checker plate was observed to be in good condition.
Building and Process Structural | 2 | The access hatch was observed to be in good condition.
Building and Process Structural | 2 | The aluminum checker plate was observed to be in good condition.
Building and Process Structural | 2 | The access hatch was observed to be in good condition.
Building and Process Structural | 2 | The ladder was observed to be in good condition.
Building and Process Structural | 2 | The ladder was observed to be in good condition.
Building Architectural | 2 | The wall paint was observed to be in good condition.
Building and Process Structural | 2 | The grating was observed to be in good condition.
Building and Process Structural | 2 | The ladder was observed to be in good condition.
Building and Process Structural | 2 | The concrete floor was observed to be in good condition.
Building Services | 2 | Smoke Detectors were observed to be in good condition. The Region's operators reported that the smoke detector in the Access House is inaccessible, and could be moved over the top of the staircase.
Building and Process Structural | 2 | The monorail beam was observed to be in good condition.
Building and Process Structural | 2 | The monorail beam was observed to be in good condition.
Building Architectural | 2 | The door was observed to be in good condition.
Building and Process Structural | 2 | The concrete blockwall was observed to be in good condition.
Building and Process Structural | 2 | The precast roof was observed to be in good condition.
Building Architectural | 2 | The wall and ceiling paint was observed to be in good condition.
Building and Process Structural | 2 | The roof could not be inspected as it was submersed at the time of the assessment. The roof was assumed to be in good condition based on its age and the condition of other visible structural components.
Building and Process Structural | 2 | The precast roof was observed to be in good condition.
Building and Process Structural | 2 | The handrail was observed to be in good condition.
Building and Process Structural | 2 | The staircase was observed to be in good condition.
Building Architectural | 2 | The wall and ceiling paint was observed to be in good condition.
Building Architectural | 2 | The door was observed to be in good condition.
Building and Process Structural | 2 | The concrete floor was observed to be in good condition. Minor cracking was noted.
Building Architectural | 2 | The wall and ceiling paint was observed to be in good condition.
Building Architectural | 2 | The door was observed to be in good condition.
Building Architectural | 2 | The door was observed to be in good condition.
Building Architectural | 2 | The door was observed to be in good condition.
Building Architectural | 2 | The aluminum louvre was observed to be in good condition.
Building Architectural | 2 | The aluminum louvre was observed to be in good condition.
Building and Process Structural | 2 | The access hatch was observed to be in good condition.
Building and Process Structural | 2 | The access hatch was observed to be in good condition.
Building Architectural | 2 | The roofing system could not be inspected as it was covered at time of inspection. The roofing system was assumed to be in good condition based on its age and the condition of other visible structural components.
Building Architectural | 2 | The roofing system could not be inspected as it was covered at time of inspection. The roofing system was assumed to be in good condition based on its age and the condition of other visible structural components.
Building Architectural | 2 | The roofing system was observed to be in good condition. Minor ponding was noted. | Minor ponding
Building and Process Structural | 2 | The access hatch was observed to be in good condition. The Region's operators reported that a guardrail with steps should be installed for ease of access (item 13).
Building Architectural | 2 | The roofing system was observed to be in good condition. Roof drains were found to be loose and unattached.
Building Architectural | 2 | The skylight was observed to be in good condition with no visible signs of leakage.
Building Architectural | 2 | The skylight was observed to be in good condition with no visible signs of leakage.
Building Architectural | 2 | The skylight was observed to be in good condition with no visible signs of leakage.
Building Architectural | 2 | The skylight was observed to be in good condition with no visible signs of leakage.
Building Architectural | 2 | The roof was observed to be in good condition. Minor ponding was noted.
Building and Process Structural | 2 | The concrete walls were observed to be in good condition. Water penetration was noted at pipe penetration into diesel fuel room. | Water penetration
Building and Process Structural | 2 | The walkway platform was observed to be in very good condition. Guardrails were noted to be 1020mm above walkway height which is lower than 1070mm minimum as per OBC standards.
Building Architectural | 2 | The louvre was observed to be in good condition.
Building Architectural | 2 | The roofing system could not be inspected as it was covered at time of inspection. The roofing system was assumed to be in good condition based on its age and the condition of other visible components. Cole Engineering completed an internal inspection of
Building Architectural | 2 | The door was observed to be in good condition.
Building and Process Structural | 2 | The precast floor was observed to be in good condition.
Building Architectural | 2 | The wall, ceiling and floor paint was observed to be in good condition.
Building Architectural | 2 | The window was observed to be in good condition.
Building Architectural | 2 | The door was observed to be in good condition.
Building and Process Structural | 2 | The precast roof was observed to be in good condition.
Building and Process Structural | 2 | The precast roof was observed to be in good condition. Staining was noted at joint on west side of room. | Staining
Building and Process Structural | 2 | The grating was observed to be in good condition.
Building and Process Structural | 2 | The steel platform was observed to be in good condition. A kickplate was noted to be missing at the bottom of guardrail. Safety chain was noted to be missing at the top of the ladder. | missing kickplate
Building and Process Structural | 2 | The column and beams were observed to be in good condition.
Building and Process Structural | 2 | The concrete blockwalls were observed to be in good condition. Staining due to a leak was noted on the south wall and north wall.
Building and Process Structural | 2 | The floor was observed to be in good condition. Minor ponding was noted throughout the floor. | Minor ponding
Building Architectural | 2 | The floor coating was observed to be in good condition.
Building Services | 2 | Diesel Storage Tank was observed to be in good condition.
Building Services | 2 | Exhaust Fan-08 was observed to be in good condition.
Building Services | 2 | Diesel Fuel Pumps were observed to be in good condition.
Building Services | 2 | Diesel Fuel System-1 was observed to be in good condition. However, a fire valve was missing. | missing fire valve
Building Services | 2 | Dehumidification Unit-1 was observed to be in good condition.
Building Services | 2 | Fire Backflow Preventer was observed to be in good condition.
Building Services | 2 | Air Conditioning Unit-01 was observed to be in good condition.
Building Services | 2 | Exhaust Fan-03 was observed to be in good condition.
Building Services | 2 | Exhaust Fan-02 was observed to be in good condition.
Building Services | 2 | Exhaust Fan-01 was observed to be in good condition.
Building Services | 2 | Dehumidification Unit-2 was observed to be in good condition. However, the region requests to duct air supply to the basement access room due to high humidity concerns.
Building Services | 2 | Remote Radiator was observed to be in good condition.
Building Services | 2 | Exhaust Fan-06 was observed to be in good condition.
Process Electrical | 3 | The panel was in fair condition, as minor corrosion was observed on the panel. Due to equipment age, the availability of the parts and increased maintenance costs will be an issue.
Process Electrical | 3 | The MCC was in fair condition, as minor corrosion was observed on the panel. Due to equipment age, the availability of replacement parts and increased maintenance costs will be an issue.
Process Electrical | 3 | Minor corrosion was observed on transformer exterior.
Process Electrical | 3 | Minor corrosion was observed on the fixture.
Process Electrical | 3 | Fixtures were in fair condition. One fixture was observed without protective lens.
Process Electrical | 3 | Disconnect Switch was in fair condition.
Process Electrical | 3 | Pump Control Panel was in fair condition.
Process Electrical | 3 | Lighting fixtures were in fair condition according to fixture age.
Process Electrical | 3 | The MCC was in fair condition as minor to moderate corrosion was observed on the panel. Due to equipment age, the availability of replacement parts and increased maintenance costs will be an issue.
Process Electrical | 3 | The panel was in fair condition as minor corrosion was observed on the panel. Due to equipment age, the availability of replacement parts and increased maintenance costs will be an issue.
Process Electrical | 3 | 600 V Washdown Pump Starter was observed to be in fair condition. Minor corrosion was observed on the enclosure surface.
Process Electrical | 3 | Panel Board No.2 was observed to be in fair condition. Minor corrosion was observed on the enclosure surface.
Process Electrical | 3 | Reservoir Transformer was observed to be in fair condition. Minor corrosion was observed.
Process Electrical | 3 | Wash Down Pump Motor Disconnect Switch was observed to be in fair condition. Minor corrosion was observed on the surface.
Process Electrical | 3 | Disconnect Switch MV-1 was observed to be in fair condition. However, it was approaching the end of its service life.
Process Electrical | 3 | Disconnect Switch MV-2 was observed to be in fair condition. However, it was approaching the end of its service life.
Process Electrical | 3 | Disconnect Switches MD-1 & EF-1 were observed to be in fair condition. However, they were approaching the end of their service life.
Process Electrical | 3 | Valve Position Panel was observed to be in fair condition. Minor corrosion was observed on its surface.
Process Electrical | 3 | Lighting Panel 1 was observed to be in fair condition. Minor surface corrosion was observed.
Process Electrical | 3 | Light Switches were observed to be in fair condition. Switches in the Access Houses were outdated and observed with moderate surface corrosion.
Process Electrical | 3 | Jaw Hydro Meter was observed to be in fair condition. Minor corrosion was observed on equipment.
Process Electrical | 3 | Fixtures were in fair condition.
Process Electrical | 3 | Disconnect Switch was in fair condition. Minor corrosion was observed.
Process Electrical | 3 | Disconnect Switch was in fair condition. Minor corrosion was observed.
Process Electrical | 3 | Control Panel was in fair condition.
Process Electrical | 3 | Transformer for LP-C was observed to be in fair condition. Minor corrosion and paint deterioration was observed on the transformer.
Electrical | 3 | Minor local corrosion was observed on the surface of the enclosure.
Electrical | 3 | The glass/plastics lighting fixture above the washroom gallery door was shattered.
Electrical | 3 | Minor corrosion was observed on the surface of lighting fixtures.
Electrical | 3 | Minor corrosion was observed on panel exterior
ES | 3 | Generator test noise impacts were found to exceed the MOE NPC-205 daytime guideline limits while the overhead door was open (Acoustic Audit, Markham Pumping Station, RWDI Air Inc., 2008).
ES | 3 | Minor corrosion was observed on equipment exterior.
ES | 3 | Minor corrosion was observed on equipment exterior.
ES | 3 | Minor corrosion was observed on transformer exterior.
ES | 3 | There are two cables entering the top left hand side of the MCC. These should be sealed with a fire stop product that will allow for approximately 2 hours in the event of a fire.
ES | 3 | The fixture was missing a cover.
ES | 3 | Minor surface corrosion of the equipment was observed.
ES | 3 | Moderate surface corrosion was observed.
Process Electrical | 4 | Lighting Fixture was in poor condition with deposits and corrosion observed throughout.
Process Electrical | 4 | Fixtures were in poor condition with moderate corrosion observed.
Process Electrical | 4 | Fixtures were in poor condition. Moderate corrosion was observed on lighting fixtures.
Process Electrical | 4 | The light was observed to be in fair condition. It had surpassed its service life.
Process Electrical | 4 | 5 Jaw Hydro Meter Enclosure was observed to be in poor condition. Moderate to severe corrosion was observed.
ES | 4 | The surge valve inspection conducted by DEVINE & Associates Ltd. in April 2017 determined that the panels' battery charging circuit was not operating.
ES | 4 | Moderate corrosion of the hydro metering panel was observed.
ES | 4 | Minor corrosion had developed in the base sections of the MCC.
ES | 4 | Minor corrosion was observed.
ES | 4 | Fixtures were observed with minor corrosion.
ES | 4 | Moderate corrosion was observed on the disconnect switch.
ES | 4 | Moderate corrosion was observed on the disconnect switch.
ES | 4 | Fixtures were observed with minor corrosion. One of the fixtures had no bulbs.
Process Mechanical Equipment | 2 | Zone 3 Discharge Header Manual Butterfly Valve 1 9 was in good condition.
Process Mechanical Equipment | 2 | Zone 3 Backflow Preventer BPV-2 was in good condition.
Process Mechanical Equipment | 2 | Zone 3 Backflow Preventer BPV-2 Gate Valve 1 was in good condition.
Process Mechanical Equipment | 2 | Zone 3 Backflow Preventer BPV-2 Gate Valve 2 was in good condition.
Process Mechanical Equipment | 2 | Zone 2 Backflow Preventer BFP-1 was in good condition.
Process Mechanical Equipment | 2 | Zone 2 Backflow Preventer BFP-1 Gate Valve 1 was in good condition.
Process Mechanical Equipment | 2 | Zone 2 Backflow Preventer BFP-1 Gate Valve 2 was in good condition.
Process Mechanical Equipment | 2 | Zone 2 Relief Pipe Gate Valve was in good condition.
Process Mechanical Equipment | 2 | Zone 2 Relief Pipe Pressure Relief Valve was observed to be in good condition.
Process Mechanical Equipment | 2 | Zone 2 Surge Tank Isolation Butterfly Manual Valve V0025 was in good condition.
Process Mechanical Equipment | 2 | Surge Tank 3 Drain Butterfly Valve was in good condition.
Process Mechanical Equipment | 2 | Zone 3 Discharge Header Manual Butterfly Valve 2 was in good condition.
Process Mechanical Equipment | 2 | Surge Tank 2 Isolation Butterfly Valve was in good condition. Minor corrosion was observed on valve hand wheel.
Process Mechanical Equipment | 2 | Surge Tank 3 Drain Butterfly Valve V0024 was observed to be in good condition.
Process Mechanical Equipment | 2 | Surge Tank 3 Special Check Valve was in good condition.
Process Mechanical Equipment | 2 | Surge Tank 2 Drain Butterfly Valve V0036 was observed to be in good condition.
Process Mechanical Equipment | 2 | Surge Tank 4 Isolation Butterfly Valve was in good condition. Minor corrosion was observed on valve hand wheel
Process Mechanical Equipment | 2 | Surge Tank 4 Special Check Valve was in good condition.
Process Mechanical Equipment | 2 | Surge Tank 4 Drain Butterfly Valve was in good condition.
Process Mechanical Equipment | 2 | Zone 3 400mm Discharge Butterfly Valve 3 V0016 was in good condition.
Process Mechanical Equipment | 2 | Zone 3 Discharge Air Release Valve ARV3 was in good condition.
Process Mechanical Equipment | 2 | Zone 3 Discharge Butterfly Valve 4 V0015 was in good condition. Minor corrosion was observed on the valve surface.
Process Mechanical Equipment | 2 | Surge Tank 1 Drain Butterfly Valve was in good condition.
Process Mechanical Equipment | 2 | Cell 1 Outlet Check Valve V0030 was in fair condition. Minor corrosion was observed on valve bolts.
Process Piping | 2 | Reservoir Cell 1 Inlet Piping was assumed to be in good condition.
Process Mechanical Equipment | 2 | Surge Tanks Drain Gate Valve V0046 was in good condition.
Process Mechanical Equipment | 2 | Reservoir Cell 1 Outlet Butterfly Valve V0017 was in good condition.
Process Mechanical Equipment | 2 | Cell 1 Washdown Gate Valve was in good condition.
Process Mechanical Equipment | 2 | Clearwell 1 Motorized Butterfly Valve Actuator was in good condition.
Process Mechanical Equipment | 2 | Clearwell 1 Motorized Inlet Butterfly Valve V0021 was in good condition.
Process Mechanical Equipment | 2 | Clearwell 2 Inlet Motorized Butterfly Valve Actuator was in good condition.
Process Mechanical Equipment | 2 | Clearwell 2 Inlet Motorized Butterfly Valve V0022 was in good condition.
Process Instrumentation SCADA | 2 | Clearwell 1 Level Sensor and Transmitter were observed to be in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 1 Air Release Valve ARV2 was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 1 Discharge Check Valve was in good condition. Minor corrosion of the bolts was observed. Once Zone 2 & Zone 3 surge tanks were commissioned, check valve slam was observed following emergency stops (HydraTek, June 2018). The check va
Process Mechanical Equipment | 2 | Highlift Booster Pump 1 Discharge Motorized Butterfly Valve Actuator was in good condition. The performance of the pump start stop control logic was tested by HydraTek in Dec 2017 and Jan 2018. To reduce transient pressures that arise from the constant sp
Process Piping | 2 | Highlift Booster Pump 1 Piping was observed to be in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 1 Air Release Isolation Gate Valve was in good condition.
Process Piping | 2 | Highlift Booster Pump 2 Piping was observed to be in good condition.
Process Piping | 2 | Highlift Booster Pump 3 Piping was observed to be in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 4 was in good condition. Pump testing was not undertaken as part of this assessment. Based on pump age, rehabilitation is recommended in the next 10 years.
Process Mechanical Equipment | 2 | Highlift Booster Pump Motor Drive 4 was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 4 Air Release Valve ARV2 was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 4 Gate Valve was in good condition.
Process Piping | 2 | Highlift Booster Pump 4 Piping was observed to be in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 4 Discharge Motorized Butterfly Valve V0403 was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 4 Isolation Butterfly Valve V0402 was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 4 Air Release Valve ARV4 was in good condition. Minor corrosion was observed on the bolts.
Process Piping | 2 | Highlift Booster Pump 5 Piping was observed to be in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 5 was in good condition. Minor corrosion was observed on the surface. Pump testing was not undertaken as part of this assessment. Based on pump age, rehabilitation is recommended in the next 10 years.
Process Mechanical Equipment | 2 | Highlift Booster Pump 5 Air Release Valve ARV1 was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 5 Discharge Check Valve V0501 was in good condition. Minor corrosion observed on the surface of bolts. Once Zone 2 & Zone 3 surge tanks were commissioned, check valve slam was observed following emergency stops (HydraTek, June 2018).
Process Mechanical Equipment | 2 | Highlift Booster Pump 7 Discharge Check Valve V0701 was in good condition. Minor corrosion of the bolts was observed. Once Zone 2 & Zone 3 surge tanks were commissioned, check valve slam was observed following emergency stops (HydraTek, June 2018). The ch
Process Mechanical Equipment | 2 | Highlift Booster Pump 5 Gate Valve was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 5 Discharge Motorized Butterfly Valve V0503 was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 5 Discharge Motorized Butterfly Valve Actuator was in good condition. The performance of the pump start-stop control logic was tested by HydraTek in Dec 2017 and Jan 2018. To reduce transient pressures that arise from the constant s
Process Mechanical Equipment | 2 | Highlift Booster Pump 5 Isolation Butterfly Valve V0502 was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 5 Air Release Valve #4 was in good condition. Minor corrosion was observed on the bolts.
Process Piping | 2 | Highlift Booster Pump 6 Piping was observed to be in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 6 was in good condition. Minor corrosion of the bolts was observed. A bolt was missing from the pump shaft casing. Pump testing was not undertaken as part of this assessment. Based on pump age, rehabilitation is recommended in the ne
Process Mechanical Equipment | 2 | Highlift Booster Pump Motor Drive 6 was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 6 Air Release Valve ARV1 was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 6 Discharge Check Valve was in good condition. Minor corrosion of was observed on the surface of valve bolts. Once Zone 2 and Zone 3 surge tanks were commissioned checked valve slam was observed following emergency stops (HydraTek, J
Process Mechanical Equipment | 2 | Highlift Booster Pump 6 Discharge Motorized Butterfly Valve was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 6 Isolation Butterfly Valve V0602 was in good condition. Minor corrosion was observed on bolts.
Process Mechanical Equipment | 2 | Highlift Booster Pump 6 Isolation Butterfly Valve V0045 was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 6 Pressure Relief Valve HCV2 was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump Motor Drive 7 was in good condition.
Process Piping | 2 | Highlift Booster Pump 7 Piping was observed to be in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 7 Gate Valve was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 7 Air Release Valve ARV1 was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 7 Discharge Motorized Butterfly Valve V0703 was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 7 Discharge Motorized Butterfly Valve Actuator was in good condition. The performance of the pump start-stop control logic was tested by HydraTek in Dec 2017 and Jan 2018. To reduce transient pressure that arise from the constant sp
Process Mechanical Equipment | 2 | Highlift Booster Pump 7 Isolation Butterfly Valve V0702 was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 7 Air Release Valve ARV4 was in good condition.
Process Piping | 2 | Highlift Booster Pump 8 Piping was observed to be in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 8 Air Release Valve ARV1 was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 8 Gate Valve was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 8 Isolation Butterfly Valve V0802 was in good condition.
Process Mechanical Equipment | 2 | Clearwell Interconnection Butterfly Valve V0029 was observed to be in good condition.
Process Mechanical Equipment | 2 | Manual Butterfly Valve was in good condition. The handwheel was chained.
Process Mechanical Equipment | 2 | Motorized Butterfly Valve Actuator was in good condition.
Process Mechanical Equipment | 2 | Air Release Valve was in good condition.
Process Mechanical Equipment | 2 | Motorized Butterfly Valve was in good condition.
Process Mechanical Equipment | 2 | Drain Gate Valve was in good condition.
Process Piping | 2 | Reservoir Cell 2 Inlet Piping was assumed to be in good condition.
Process Mechanical Equipment | 2 | Check Valve was in good condition.
Process Piping | 2 | Reservoir Cell 2 Outlet Piping was assumed to be in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump Motor Drive 1 was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 1 was in good condition. Pump testing was not undertaken as part of this assessment. Based on pump age, rehabilitation is recommended in the next 10 years.
Process Mechanical Equipment | 2 | Highlift Booster Pump 1 Air Release Valve ARV4 was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 1 Discharge Butterfly Valve V0102 was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 1 Discharge Motorized Butterfly Valve V0103 was in good condition.
Process Mechanical Equipment | 2 | Cell 1 Reservoir Fill Line Motorized Butterfly Valve V0020 in the Generator Room was observed to be in good condition.
Process Mechanical Equipment | 2 | Washburn Reservoir Zone 1 Inlet Manual Butterfly Valve V0007 was in good condition.
Process Mechanical Equipment | 2 | Zone 2 Discharge Air Release Valve ARV3 was in good condition. Minor corrosion of the bolts was observed.
Process Mechanical Equipment | 2 | Washburn Reservoir Zone 2 Discharge Manual Butterfly Valve V0009 was in good condition.
Process Mechanical Equipment | 2 | Zone 3 Eductor Gate Valve V0038 was in good condition.
Process Mechanical Equipment | 2 | Clearwell 2 Drain Gate Valve V0040 was in good condition.
Process Mechanical Equipment | 2 | Clearwell 1 Drain Gate Valve V0039 was in good condition.
Process Mechanical Equipment | 2 | Surge Tank 3 was observed to be in good condition.
Process Mechanical Equipment | 2 | Surge Tank 1 was observed to be in good condition.
Process Piping | 2 | Zone 3 Discharge Header Piping was assumed to be in good condition.
Process Piping | 2 | Reservoir Cell 1 Overflow Piping was assumed to be in good condition.
Process Piping | 2 | Reservoir Cell 1 Outlet Piping was assumed to be in good condition.
Process Mechanical Equipment | 2 | Reservoir Cell 1 Outlet Butterfly Valve V0018 was in good condition.
Process Mechanical Equipment | 2 | Zone 1 Air Release Valve was in good condition.
Process Piping | 2 | Clearwell 1 Supply Header Piping was assumed to be in good condition.
Process Piping | 2 | Clearwell 2 Supply Header Piping was assumed to be in good condition.
Process Mechanical Equipment | 2 | Zone 1 Manual Butterfly Valve V0012 was in good condition.
Process Mechanical Equipment | 2 | Zone 1 Manual Butterfly Valve #2 was in good condition.
Process Piping | 2 | Zone 2 Discharge Header Piping was assumed to be in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 2 was in good condition. Pump testing was not undertaken as part of this assessment. Based on pump age, rehabilitation is recommended in the next 10 years. Replacement of mechanical seals and bearings, fine tuning of the pump shaft,
Process Mechanical Equipment | 2 | Highlift Booster Pump Motor Drive 2 was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 2 Air Release Isolation Gate Valve was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 2 Air Release Valve ARV 2 was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 2 Discharge Check Valve was in good condition. Minor corrosion of the bolt was observed. Once Zone 2 & Zone 3 surge tanks were commissioned, check valve slam was observed following emergency stops. The check valve is equipped with a
Process Mechanical Equipment | 2 | Highlift Booster Pump 2 Discharge Motorized Butterfly Valve V0203 was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 2 Air Release Valve ARV4 was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 2 Discharge Butterfly Valve V0202 was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 3 was in good condition. Pumping testing was not undertaken as par of this assessment. Based on pump age, rehabilitation is recommended in the next 10 years.
Process Mechanical Equipment | 2 | Highlift Booster Pump Motor Drive 3 was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 3 Air Release Valve ARV2 was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 3 Gate Valve was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 3 Discharge Check Valve was in good condition. Minor corrosion was observed on the surface of valve bolts. Once Zone 2 and Zone 3 surge tanks were commissioned, check valve slam was observed following emergency stops (HydraTek, June | Minor corrosion
Process Mechanical Equipment | 2 | Highlift Booster Pump 3 Isolation Butterfly Valve 1 V0302 was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 3 Pressure Relief Valve (Zone 2) HCV1 was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 3 Isolation Butterfly Valve V0044 was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 3 Discharge Motorized Butterfly Valve Actuator was in good condition. The performance of the pump start stop control logic was tested by HydraTek in Dec 2017 and Jan 2018. To reduce transient pressures that arise from the constant s
Process Mechanical Equipment | 2 | Highlift Booster Pump 3 Discharge Motorized Butterfly Valve V0303 was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 2 Discharge Motorized Butterfly Valve Actuator was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 4 Discharge Check Valve V0401 was in good condition. Minor corrosion was observed on the bolts. Once Zone 2 & Zone 3 surge tanks were commissioned, check valve slam was observed following emergency stops (HydraTek, June 2018). The ch
Process Mechanical Equipment | 2 | Highlift Booster Pump 4 Discharge Motorized Butterfly Valve Actuator was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump Motor Drive 5 was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 6 Discharge Motorized Butterfly Valve Actuator was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 6 Air Release Valve ARV4 was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 6 Gate Valve was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 7 was in good condition. Minor corrosion on bolts was observed. A bolt was missing from the pump shaft casing. Pump testing was not undertaken as part of this assessment. Based on pump age, rehabilitation is recommended in the next 1
Process Mechanical Equipment | 2 | Highlift Booster Pump 8 was in good condition. Corrosion was observed on the surface of shaft casing. A bolt was missing from the pump shaft casing. Pump testing was not undertaken as part of this assessment. Based on pump age, rehabilitation is recommend
Process Mechanical Equipment | 2 | Highlift Booster Pump Motor Drive 8 was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 8 Discharge Motorized Butterfly Valve V0803 was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 8 Discharge Motorized Butterfly Valve Actuator was in good condition.
Process Mechanical Equipment | 2 | Highlift Booster Pump 8 Air Release Valve #4 was in good condition.
Process Mechanical Equipment | 2 | Cell 1 Reservoir Fill Line Motorized Butterfly Valve Actuator in the Generator Room was in good condition.
Process Mechanical Equipment | 2 | Zone 2 Discharge Air Release Valve ARV5 was in good condition.
Process Mechanical Equipment | 2 | Clearwell Gate Valve was in good condition.
ES | 4 | Lack of spare circuits on the MCC.
Building Mechanical | 2 | Minor surface corrosion was observed.
Building Mechanical | 2 | Minor corrosion inside the heater casing was observed.
Building Mechanical | 2 | Very minor corrosion of the casing was observed.
Process Mechanical | 2 | Minor paint wear of the valve casing and handwheel was observed.
Process Mechanical | 2 | Very minor corrosion of the valve was observed.
Instrumentation and Control | 2 | Minor corrosion was observed.
Process Mechanical | 2 | Minor corrosion and paint wear of the handwheel, flanges and bolts was observed.
Process Mechanical | 2 | Minor corrosion and paint wear of the mount was observed.
Process Mechanical | 2 | Minor corrosion and paint wear of the mount was observed.
Building Mechanical | 2 | Minor surface corrosion was observed.
Building Mechanical | 2 | Minor dents in the ducting was observed.
Structural | 2 | Step cracking in mortar joints at top of north wall in screen room.
Process Mechanical | 2 | Cracking of the insulation around the piping was observed.
Process Mechanical | 2 | Cracking of the insulation around the piping was observed.
Process Mechanical | 2 | Moderate surface corrosion and paint wear was observed.
Structural | 2 | Hairline cracking on underside of floor by northeast corner opening
Structural | 2 | Minor spalling with exposed reinforcement at corehole openings
Building Mechanical | 2 | A dent on the heater vent was observed.
Building Mechanical | 2 | Minor corrosion was observed around the bolts.
Building Mechanical | 2 | Minor corrosion and grease were observed on the surface of the detector.
Building Mechanical | 2 | Minor corrosion and grease were observed on the surface of the detector.
Building Mechanical | 2 | Minor corrosion was observed on the surface of the detector.
Building Mechanical | 2 | Minor corrosion and grease were observed on the surface of the detector.
Instrumentation and Control | 2 | Very minor surface corrosion was observed on the gauge connection.
Process Mechanical | 2 | Very minor surface corrosion was observed on the bolts.
Instrumentation and Control | 2 | Very minor surface corrosion was observed.
Process Mechanical | 2 | Minor surface corrosion was noted.
Building Mechanical | 2 | Minor corrosion was observed on the valve handwheel.
Building Mechanical | 2 | Very minor corrosion was observed on the valve surface.
Instrumentation and Control | 2 | Deposit was observed throughout.
Instrumentation and Control | 2 | Deposit was observed throughout.
Instrumentation and Control | 2 | Minor surface corrosion was noted.
Process Electrical | 5 | Washdown Pump Starter (old) was observed to be in poor condition. Moderate corrosion was observed on its surface. A new washdown pump starter had been installed, however the original starter had not been uninstalled.
Process Mechanical | 2 | Minor corrosion on bolts and grease were observed.
Building Mechanical | 2 | Minor corrosion of the bolts was observed.
Building Mechanical | 2 | Minor corrosion of the bolts was observed.
Building Mechanical | 2 | Minor corrosion of the bolts was observed.
Building Mechanical | 2 | Minor corrosion of the bolts was observed.
Building Mechanical | 2 | Minor corrosion of bolts was observed.
Building Mechanical | 2 | Minor corrosion of the bolts was observed.
Building Mechanical | 2 | Very minor corrosion was observed.
Building Mechanical | 2 | Very minor corrosion was observed.
Building Mechanical | 2 | The plastic cover of the stainless sink splash panel was peeling.
Building Mechanical | 2 | Very minor corrosion was observed.
Structural | 2 | Cracking with efflorescence deposits was noted at the southwest corner of the room | Cracking with efflorescence deposits
Structural | 2 | Hairline cracking.
Building Mechanical | 2 | Very minor corrosion was observed on the motor surface. | Very minor corrosion
Building Mechanical | 2 | Very minor corrosion was observed on the motor surface.
Building Mechanical | 2 | Minor corrosion was observed on the piping support.
Process Mechanical | 2 | Minor surface corrosion was noted.
Process Mechanical | 2 | Very minor surface corrosion was observed.
Process Mechanical | 2 | Very minor surface corrosion and paint peeling were noted.
Process Mechanical | 2 | Water condensation was observed on the valve surface.
Process Mechanical | 2 | Very minor surface was observed on the bolts.
Structural | 2 | Damp east wall at basement b4 level.
Process Mechanical | 2 | The valve had two asset tag: 00079718 and 00044244. Based on the asset inventory list provided by the Region, 00044244 is the ID for a spare check valve in the facility. The asset tag should be removed.
Process Mechanical | 2 | Water condensation was observed on the valve surface. The Region's OMM reported that the valve maybe oversized as it takes longer to close since the Raw Sewage Pump 3 was replaced. The extended closing time causes the wet well to drain to approximately 1
Process Electrical | 5 | Bypass mode was in operation. Operation issues with this VFD was reported by Region Staff.
Process Mechanical | 2 | Minor corrosion surface was observed.
Process Mechanical | 2 | Minor corrosion surface was observed.
PM | 2 | The valve had two asset tags (00002251 and 00042968). Only the asset associated with the original tag (00002251) is inventoried.
BM | 2 | Minor corrosion of the bolts was observed.
BM | 2 | No certification for the overhead crane was provided. Overhead cranes are required by CSA B167 to be inspected annually and certified by a professional engineer for the load listing on the crane.
PM | 2 | Very minor discolouration and corrosion of the valve was observed. | Very minor discolouration
PM | 2 | Very minor discolouration and surface corrosion of the valve was observed. | Very minor corrosion
PM | 2 | Very minor corrosion of the bolts was observed. | Very minor surface corrosion
PM | 2 | Very minor discolouration and corrosion of the valve was observed.
PM | 2 | Minor corrosion of the valve was observed.
HSS | 2 | Exposed wires for the security system can easily be cut. | Exposed wires
SW | 2 | Minor cracking of the asphalt was noted. | Minor cracking
AC | 3 | Moderate corrosion at the base of the metal siding was observed. | Minor corrosion
AC | 3 | Minor corrosion at the base of the hollow metal door frame was observed. | Missing block
SW | 2 | Tire ruts in grassy areas were reported by Region staff.
SW | 2 | A large crack was observed at the south end of the concrete walkway. | A large crack
SW | 2 | Very minor cracking and staining was observed southeast of the pumping station building. | Very minor cracking
SW | 2 | Minor corrosion of the bollard casing was observed. | Minor corrosion
AC | 3 | Minor corrosion at the base of the hollow metal door frame was observed.
AC | 3 | Minor corrosion at the base of the hollow metal door frame was observed. | not latch automatically
AC | 3 | Peeling paint on roof in sampling room was observed.
SW | 2 | Minor damage to the visible portion of the culvert was observed. | Minor damage
SC | 2 | Soft concrete in top 5-10mm was noted. | Soft concrete
SC | 2 | Soft concrete in top 5-10mm was noted.
SC | 2 | Hairline cracking of the slab was observed. | Hairline cracking
SC | 2 | Hairline cracking of the slab was observed.
SC | 2 | Cracking with efflorescence deposits was noted primarily in the bay next to the dividing wall. | Cracking with efflorescence deposits
SC | 2 | Cracking with efflorescence deposits was noted primarily in the bay next to the dividing wall.
SC | 2 | A build up of calcium deposits was noted on the ladder.
SC | 2 | A build up of calcium deposits was noted on the ladder.
SC | 2 | Previous repairs had been completed using a material that is not NSF certified. | Not NSF certified
SC | 2 | Previous repairs had been completed using a material that is not NSF certified. | Previous repairs
AC | 3 | Jamb weatherstripping was missing a fastener and had become displaced.
AC | 3 | Jamb weatherstripping was missing a fastener and had become displaced. | Minor hairline cracking
PM | 2 | Very minor surface corrosion of the pipe was observed.
PM | 2 | Minor surface corrosion of the pipe section within the valve chambers was observed. | Minor surface corrosion
PM | 2 | Minor surface corrosion of the suction piping was observed.
PM | 2 | Very minor corrosion of the suction piping was observed.
SIC | 2 | The cable was tied and wrapped directly to the conduits entering the PAC panel. To be rated for the space, the cable should be properly run through a conduit to enter the panel.
PM | 2 | Minor surface corrosion of the valve was observed. | Minor surface corrosion
PM | 2 | Minor surface corrosion of the valve was observed.
PM | 2 | Minor surface corrosion of the valve was observed.
BM | 2 | The unit is installed to reduce condensation in the valve room. However, corrosion and paint peeling on the process equipment and piping in the valve room was observed.
PM | 2 | Very minor surface corrosion was observed. | Very minor surface corrosion
PM | 2 | Minor surface corrosion of the valve was observed. | Minor surface corrosion
PM | 2 | Minor surface corrosion of the valve was observed.
BM | 2 | No certification for the overhead crane was provided. Overhead cranes are required by CSA B167 to be inspected annually and certified by a professional engineer for the load listing on the crane. | No certification
PM | 2 | Minor surface corrosion of the valve was observed. | Minor surface corrosion
PM | 2 | Very minor surface corrosion of the valve was observed. | Very minor surface corrosion
SIC | 2 | The PAC panel is a NEMA 1 enclosure (rather than a NEMA 12 that is was manufactured to) due to the open knockouts at the side of the panel.
HSS | 2 | Eye wash signage was not permanently mounted on the wall.
HSS | 2 | Eye wash signage was not permanently mounted on the wall.
HSS | 2 | The fire extinguisher was installed behind a door. Fire extinguishers shall be conspicuously located where they are readily accessible and immediately available in the event of fire.
SC | 2 | Staining was noted at the joint on the east side of pumping station above the generator. The staining is evidence of past roof leaks which did not appear to be active. | leaks
SC | 2 | Cracking joint material between slabs was observed. | Cracking joint material
SC | 2 | Cracking was noted at the joint between the blocks and the frame of the overhead door.
SC | 2 | Local cracking/ drying out of joints between panels was observed. | Local cracking
SC | 2 | No certification for the overhead crane was provided.
PM | 2 | The existing site plan (drawing C001) shows that the surge anticipator valve piping discharges to the storm sewer on McCowan Road. A dechlorination system was not present onsite. The flow should be dechlorinated prior to discharge to the storm system in a
SC | 2 | A build up of calcium deposits was noted on the ladder. | calcium deposits
SC | 2 | A build up of calcium deposits was noted on the ladder. | A build up of calcium deposits
SC | 2 | The steel pipe clamps and anchors were observed to be corroded.
SC | 2 | No chains were installed around the sump area.
SC | 2 | No chains were installed around the sump area.
SC | 2 | Approximately 1 foot of standing water was noted at the base of the chamber.
SC | 2 | One side at the bottom of the ladder was observed to be bent.
SC | 2 | Minor bug holes were noted around the valve stem.
SC | 2 | A layer of mud was observed on the base slab.
SW | 2 | The post to tie back the gate when open was bent (not in an upright position).
SC | 2 | Corrosion spots were observed on three columns. | corrosion spots
SC | 2 | Corrosion spots were observed on three columns.
SC | 2 | Spalling concrete due to the expansion of the waterstop around the south inlet/outlet sump pit was observed. | Spalling concrete
SC | 2 | Deteriorated joints were noted. | Deteriorated joints
SC | 2 | Cracking with efflorescence deposits was noted primarily by the dividing wall and at the access hatch location. | Cracking with efflorescence deposits
SC | 2 | Cracking with efflorescence deposits were noted on the roof next to the dividing wall and by the east wall.
SC | 2 | Exposed aggregates were observed. | Exposed aggregates
SC | 2 | Calcium deposits were noted on the ladders. | Calcium deposits
AC | 3 | Frame was showing signs of corrosion at base of jambs.
SC | 2 | Efflorescence deposits by the access hatch were observed. | Efflorescence deposits
SC | 2 | The hatch did not appear to be watertight as staining from moisture penetration was observed on the east wall. | moisture penetration
SC | 2 | Efflorescence deposits by the access hatch were observed. | Efflorescence deposits
SC | 2 | Standing water was noted at the bottom of the valve chamber. | Standing water
SC | 2 | No certification for the overhead crane was provided.
AC | 3 | Paint finish was faded.
AC | 3 | Frame was showing signs of minor corrosion.
PM | 2 | The pressure gauge was secured to the chlorine piping with electrical tape.
HSS | 2 | The fire extinguisher was not mounted on the wall.
PM | 2 | The sections of pipe within the Valve House were observed with staining and minor corrosion.
PM | 2 | Record drawings show the overflow piping discharges to Storm Manhole 58. A dechlorination system was not present onsite. The flow should be dechlorinated prior to discharge to the storm system in accordance with Condition 10 of Schedule B of the Region's
SW | 2 | Minor cracking of the asphalt was noted. | Minor cracking
SW | 2 | Minor damage to the visible portion of the culvert was observed. | Minor damage
SW | 2 | Minor corrosion of the piping was observed. | Minor corrosion
SC | 2 | Cracking with efflorescence deposits was observed. | Cracking with efflorescence deposits
Process Electrical | 5 | Bypass mode was in operation. Operation issues with this VFD was reported by Region Staff.
PM | 2 | Minor cracking of concrete insulation around the piping was observed. | Minor cracking of concrete insulation
PM | 2 | Very minor surface corrosion was observed.
SC | 2 | Hairline cracking was observed.
AC | 3 | Minor weathering of the paint coating was observed.
BM | 2 | Moderate paint wear on dehumidifier duct system was observed.
SIC | 2 | Modem was placed on a table with the associated cable loose on the floor. The modem should be properly secured or placed in a cabinet.
SC | 2 | Cracking with efflorescence deposits was observed.
SC | 2 | Minor corrosion was observed.
SC | 2 | Cracking with efflorescence deposits was observed.
SC | 2 | Minor corrosion was observed.
SC | 2 | Minor hairline cracking was observed.
SW | 2 | Gravel was observed west of PS building. Mud was observed at south side of the PS building. Seeding and maintenance as required.
SW | 2 | Broken branches in tree on the west side of the reservoir were observed. | Broken branches
AC | 3 | Corrosion of door hinges was observed.
AC | 3 | Minor weathering of the paint coating was observed. | Minor physical damage
SW | 2 | Minor cracking of the retaining wall was observed. | Minor cracking
SW | 2 | Minor damage to the visible portion of the culvert was observed. | Minor damage
Process Electrical | 5 | Bypass mode was in operation. Operation issues with this VFD was reported by Region Staff. | Minor surface corrosion
HSS | 2 | Eye wash was not permanently mounted on a wall.
SIC | 2 | Cover for the analyzer was missing.
PM | 2 | Very minor surface corrosion was observed.
SC | 2 | Hairline cracking by pipe penetrations was observed. | Hairline cracking
SC | 2 | Minor cracking at pipe strap locations was observed. | Minor cracking
SC | 2 | The monorail did not extend for Pump 1. A portable Conestoga (2200lb capacity) floor crane was found in the lower level.
SC | 2 | The overhead crane was due for its annual inspection. Overhead cranes are required by CSAB167 to be inspected annually and certified by a professional engineer for the load listing on the crane.
AC | 3 | Minor weathering of the paint coating was observed. | Minor localized defects
AC | 3 | Minor weathering of the paint coating was observed.
AC | 3 | Minor impact damage to the siding was observed. | Missing screws in hinge
PM | 2 | AECOM's pump tests showed lower efficiency when compared to the original pump curve. Results however, were considered to be with in an acceptable range (AECOM, 2015).
PM | 2 | AECOM's pump tests showed lower efficiency when compared to the original pump curve. Results however, were considered to be with in an acceptable range (AECOM, 2015).
PM | 2 | AECOM's pump tests showed lower efficiency when compared to the original pump curve. Results however, were considered to be with in an acceptable range (AECOM, 2015).
PM | 2 | AECOM's pump tests showed lower efficiency when compared to the original pump curve. Results however, were considered to be with in an acceptable range (AECOM, 2015).
BM | 2 | Red tape was installed on the duct from the exhaust fan to indicate low headroom. No safety signage was present.
BM | 2 | Very minor corrosion of the screen was observed. | Very minor corrosion
BM | 2 | Very minor corrosion of the screen was observed.
BM | 2 | Very minor corrosion of the screen was observed.
BM | 2 | Minor surface corrosion of the screen was observed. | Minor surface corrosion
BM | 2 | Minor surface corrosion of the screen was observed.
BM | 2 | Minor corrosion of the screen was observed.
BM | 2 | Minor corrosion of the screen was observed.
SW | 2 | Catch basin was covered with debris | debris
HSS | 2 | The equipment was overdue for inspection and should not be used until an inspection has been completed.
SC | 2 | Minor hairline cracking | Minor hairline cracking
SC | 2 | Bent ladder rung | Bent
ES | 5 | The equipment was labeled "NO GOOD" and was assumed to be non-functional.
SW | 2 | Minor damage to the visible portion of the culvert was observed. | Minor damage
PM | 2 | AECOM's report identified that no more than two pumps can be operated at a time, as with more that two pumps running at the same time suction velocity will exceed the maximum recommended velocity of the suction line (AECOM, 2015).
AC | 3 | Minor corrosion was observed on the door guides. | Minor cracks in mortar joints
PM | 2 | Minor surface corrosion was observed. | Minor surface corrosion
PM | 2 | Minor corrosion of the valve was observed. | Minor corrosion
PM | 2 | Minor corrosion of the flanges was observed.
PM | 2 | Minor surface corrosion was observed.
PM | 2 | Minor surface corrosion of the flanges was observed.
PM | 2 | Minor corrosion of the flanges was observed.
PM | 2 | Minor corrosion of the flanges was observed.
PM | 2 | Very minor surface corrosion of the flanges was observed. | Very minor surface corrosion
PM | 2 | Minor corrosion of the flanges was observed.
PM | 2 | Moderate surface corrosion of the flanges was observed.
PM | 2 | Minor surface corrosion of the valves was observed.
PM | 2 | Minor corrosion of the flanges was observed.
PM | 2 | Minor surface corrosion of the valve was observed.
PM | 2 | Minor surface corrosion was observed.
PM | 2 | Very minor corrosion was observed.
PM | 2 | Minor corrosion of the flanges and handwheel was observed.
PM | 2 | Very minor surface corrosion was observed.
PM | 2 | Minor surface corrosion of the valves was observed.
PM | 2 | Minor corrosion of the valve was observed.
PM | 2 | Very minor surface corrosion of the flanges was observed.
PM | 2 | Very minor corrosion of the flanges was observed.
PM | 2 | Minor surface corrosion of the actuator was observed.
PM | 2 | Very minor corrosion of the bolts was observed.
PM | 2 | Very minor surface corrosion of the valve was observed.
PM | 2 | Very minor surface corrosion of the valve was observed.
AC | 3 | Paint finish was faded. | Faded paint finish
AC | 3 | Threshold and weatherstripping was showing signs of corrosion/wear.
AC | 3 | Threshold and weatherstripping was showing signs of corrosion/wear. | Minor cracks
ES | 5 | The fuse box was not in service.
SC | 2 | Minor ponding at north wall. | Minor ponding
SC | 2 | Previous crack injection at leaking conduit penetration on north wall. | Previous crack injection
SC | 2 | Loose nuts, bolts and washers at multiple locations.
Process Electrical |  | An electrical connection for a portable generator was not provided. According to Section 9.11 of the Region’s Water & Wastewater Facilities Design Manual (Jan. 20112), standby power shall be provided for sewage pumping stations.
SW | 2 | Bollards were not installed at the diesel fuel room area on the east side of the pumping station.
AC | 3 | Paint finish was faded. | Damaged gaskets
AC | 4 | Significant wear and localized flaking of floor coating was observed throughout. | corrosion
AC | 4 | Significant wear and localized flaking of floor coating was observed throughout.
AC | 5 | Firestopping was missing around penetrations in the wall between the Control Room and Pump Area.
SC | 2 | Minor corrosion spots were noted but appeared to be from nails used to secure the concrete forms.
SC | 2 | Minor corrosion spots were noted but appeared to be from nails used to secure the concrete forms.
SC | 2 | Previous repairs had been completed using a material that is no NSF certified.
SC | 2 | Previous repairs had been completed using a material that is not NSF certified.
SC | 2 | Corrosion spots were observed.
SC | 2 | Exposed corroded rebar at bottom of wall
SC | 2 | A crack was noted in the precast slab in the middle of the pump area from the skylight to the south wall. | A crack
SC | 2 | Cracking was noted at the joint between the blocks and the wall of the washroom. | Cracking
SC | 2 | Previously repaired cracks were noted throughout.
SC | 2 | Failed previous patch was noted.
SC | 2 | Hairline cracking in the roof slab was observed.
SC | 2 | Cracking with efflorescence deposits noted.
SC | 2 | Minor pitting was observed.
PM | 2 | Record drawings show the drain piping discharges to Manhole 'B', which then pumps to Storm Manhole 58. A dechlorination system was not present onsite. The flow should be dechlorinated prior to discharge to the storm system in accordance with Condition 10
PM | 2 | The sampling station drain was not working and the piping was held together by tape.
SC | 2 | Efflorescence Deposits | Efflorescence deposits
PM | 2 | There was very little clearance between the handwheel and platform. | little clearance
PM | 2 | The handwheel for the valve encroaches on the space needed to use the ladder to and from the platform.

## ADJ
Condition | Keyword
3 | Obsolete
3 | Missing
3 | Outdated
3 | Shattered
1 | New
2 | Good
4 | Not-operating
5 | Broken
3 | Uneven
5 | Failed
3 | Corroded
4 | not-operational
4 | not-in-service

## SC
Condition | Keyword | InspectorsComments
2 | A build up of calcium deposits | A build up of calcium deposits was noted on the ladder.
3 | A crack | A crack was noted in the precast slab in the middle of the pump area from the skylight to the south wall.
3 | A gap in joint | The steel ladder was observed to be in fair condition. A gap in a joint in the ladder was noted.
3 | A Layer of slime | A layer of slime was noted at the bottom of the ladder due to standing water.
3 | A sign of leakage | The crane beams was observed to be in good condition. Signs of leakage were noted at mount on north wall.
3 | Active leak
3 | Active leaking
3 | Active leaking crack | The concrete walls were generally observed to be in fair condition. Cracking with efflorescence deposits was noted on walls adjacent to reservoir. Active leaking crack was noted on the east wall.
3 | Active leaks | Staining was noted at the joint on the east side of pumping station above the generator. The staining is evidence of past roof leaks which did not appear to be active.
3 | Atmpspheric conditions
4 | Bent | Bent ladder rung
5 | Broken
3 | Bug holes | Bug holes/voids were noted at grade on the north side of the building.
3 | Bughole
3 | Bugholes
3 | Build up of calcium deposits | A build up of calcium deposits was noted on the ladder.
3 | Buried | The concrete foundation could not be inspected as it is buried. The foundation was assumed to be in fair condition based on its age and the condition of other visible structural components.
3 | Calcium deposit | Calcium deposits were noted on the ladders.
3 | Calcium deposits | Calcium deposits were noted on the ladders.
3 | Clogged | The floor drain in the valve chamber was clogged. Approximately 1 ft of standing water was noted at the time of the assessment.
3 | Concrete spalling | The concrete walls were observed to be in fair condition. Concrete spalling was on the north wall. Signs of leakage were noted at crane beam mount on north wall.
3 | Corroded | Corroded exposed reinforcement was observed by the vents.
3 | Corroded exposed rebar | The roof was observed to be in fair condition. Corroded exposed rebar was observed.
3 | Corroded metal disk | The Cell 1 Roof Slab was in good condition. Corroded metal disk were noted typically throughout the underside of the underside of the roof slab. Embedded wood was also noted throughout the underside of the roof slab. The existing joint filler in expansio
3 | Corrosion | The manhole cover and frame was observed to be in fair condition. Corrosion of the frame was noted.
3 | Corrosion spots | Corrosion spots were noted at the wall to slab interface.
3 | Corrosion staining | — The ladder located on the northwest corner of Cell 2 was found to have corrosion staining. The ladder was securely affixed to the wall. However, corrosion was noted on a few anchors.
3 | Crack | The walls of Cell 2 were in fair to good condition. The majority of deficiencies were noted on the west dividing wall and at the north end of the east well. 30.6m of cracking was noted to be previously repaired with a cementitious waterproofing. Around 4
3 | Crack injection repairs | The concrete floor was observed to be in fair condition. Previous crack injection repairs were noted on the underside of the floor.
3 | Cracking | The walls of Cell 2 were in fair to good condition. The majority of deficiencies were noted on the west dividing wall and at the north end of the east well. 30.6m of cracking was noted to be previously repaired with a cementitious waterproofing. Around 4
3 | Cracking in mortar
3 | Cracking in the mortar | Cracking in the mortar was also noted in corners of the pump room.
3 | Cracking joint material | Cracking joint material between slabs was observed.
3 | Cracking with efflorescence deposit | Cracking with efflorescence deposits was noted throughout the walls.
3 | Cracking with efflorescence deposits | The roof was observed to be in fair condition. Cracking with efflorescence deposits were noted in a few areas.
3 | Cracking with honeycombing
3 | Cracking with rust spots | The walls were observed to be in good condition. Cracking with efflorescence deposits, rust spots and honeycombing were noted. Joint sealants were found to be deteriorated.
3 | Cracking with sign of leak
3 | Cracking with sign of leakage
3 | Cracking with signs of leakage | The walls were observed to be in fair condition. Cracking with signs of leakage was noted on walls adjacent to the clearwells.
3 | Cracks | The walls of Cell 2 were in fair to good condition. The majority of deficiencies were noted on the west dividing wall and at the north end of the east well. 30.6m of cracking was noted to be previously repaired with a cementitious waterproofing. Around 4
4 | Damage | The grating was observed to be generally in fair condition. Damage was noted on portions of the grating likely due to items being dropped.
4 | Damaged | The access hatch was observed to be in fair condition. Lifting handles were noted to be damaged or missing due to snow plow.
3 | Damp | The valve chamber was not entered as it is a confined space. The concrete floor was observed to be in fair condition from above. The valve chamber was in atmpspheric conditions. Damp was noted at the bottom of the valve chamber.
3 | Deposits | The guardrails were observed to be in fair condition. Deposits were noted.
3 | Deteriorated joint sealant
3 | Deteriorated joint sealants | The concrete walls were observed to be in fair condition. Cracking with efflorescence deposits and deteriorated joint sealants at previous infilled openings were noted. Signs of potential leaks were noted at the top of the wall.
3 | Deteriorated joints | Deteriorated joints were noted.
3 | Deterioration | The ladder was observed to be in fair condition due to age. The valve chamber was in atmospheric conditions and damp was noted, which may increase the deterioration rate of the ladder.
2 | Discoloration
3 | Drying out of joints | Local cracking/ drying out of joints between panels was observed.
3 | Efflorescence deposits | The precast concrete roof was observed to be in good condition. Minor rust spots were noted.
3 | Embedded wood | The Cell 1 Roof Slab was in good condition. Corroded metal disk were noted typically throughout the underside of the underside of the roof slab. Embedded wood was also noted throughout the underside of the roof slab. The existing joint filler in expansio
3 | Evidence of age | Evidence of age/standing water was noted.
3 | Evidence of aged | Evidence of age/standing water was noted.
3 | Evidence of aging | Evidence of age/standing water was noted.
3 | Exposed aggregates | Exposed aggregates were observed.
3 | Exposed corroded rebar | Exposed corroded rebar at bottom of wall
3 | Exposed reinforcement | Corroded exposed reinforcement was observed by the vents.
3 | Exposed steel | The beams were observed to be in fair to poor condition. Exposed steel was noted to be corroded.
5 | Fail
5 | Failed
3 | Failed previous patch | Failed previous patch was noted.
3 | Fair | The walls were observed to be in fair condition due to age.
3 | Gap in joint | The steel ladder was observed to be in fair condition. A gap in a joint in the ladder was noted.
2 | Good
3 | Hairline cracking | Hairline cracking of the slab was observed.
3 | Hairline cracking with efflorescence deposits | Hairline cracking with efflorescence deposits noted on majority of columns.
3 | Heavy amount of deposits | The guardrail was observed to be in fair condition. A heavy amount of deposits were noted. Kickplate at bottom was missing.
3 | Height | The guardrails were observed to be in fair condition. Due to additional topping on floor, guardrails are less than 1070mm in height as mandated by code. This should be rectified when grinding and resurfacing of the loading area is completed.
3 | Honeycombing
4 | Large gap | The staircase and handrails were observed to be in fair condition. A large gap between the top of stair tread and bottom of base plate was noted.
4 | Large opening | The platform was observed to be in fair condition. A large opening for the float system was located at the bottom of the ladder, posing a slip and fall hazard.
3 | Large span | The grating was observed to be in fair condition. Span of grating at surge tanks is too large and has bent the grating.
4 | Large spanning
3 | Layer of slime | A layer of slime was noted at the bottom of the ladder due to standing water.
3 | Leaking at expansion joint | The concrete floor was generally observed to be in good condition. Water was observed to be leaking at expansion joint between new slab and existing footing of loading dock area.
3 | Local cracking | Local cracking/ drying out of joints between panels was observed.
3 | Loose bolts
3 | Loose joint filler | The underside of the Cell 2 roof slab was in good condition. Corroded form ties were noted typically throughout the underside of the roof slab. Existing joint filler in the expansion joint was also noted to be loose. However, no active leaking was noted.
3 | Loose nuts | Loose nuts, bolts and washers at multiple locations.
3 | Loose nuts, bolts and washers
3 | Loose safety extension | The ladder was observed to be in good condition. Safety extension at top of ladder is loose and could fall.
3 | Loose washers
3 | Loss of cement | The walls of Cell 1 were in fair to good condition. Previously repaired cracking was noted on the dividing common wall between the Cell 1 and Cell 2 walls. The lower 0.6m in height at the base of the common dividing wall showed signs of loss of cement/ex
2 | Minor bug hole | The concrete roof was observed to be in good condition. Half of the roof underside was covered in insulation. Minor bugholes were noted around vent pipe penetration.
2 | Minor bug holes | The concrete roof was observed to be in good condition. Half of the roof underside was covered in insulation. Minor bugholes were noted around vent pipe penetration.
2 | Minor bugholes | The concrete roof was observed to be in good condition. Half of the roof underside was covered in insulation. Minor bugholes were noted around vent pipe penetration.
3 | Minor corrosion
2 | Minor corrosion spots | Minor corrosion spots were noted but appeared to be from nails used to secure the concrete forms.
3 | Minor cracking | The concrete roof was observed to be in fair condition. Minor cracking with efflorescence was noted. Corroded form ties were noted throughout.
3 | Minor cracking with efflorescence deposits | The columns were observed to be in good condition. Minor cracking with efflorescence deposits were noted.
3 | Minor delamination | Corroded previous anchors and supports were noted. Minor delamination of concrete was noted on north wall. Previous patching was also observed. Walls were observed to be in good condition.
2 | Minor deposit buildup | The aluminum ladder was observed to be in good condition. Minor deposit buildup was noted.
2 | Minor deposit build-up | The aluminum guardrail was observed to be in good condition. Minor deposit buildup was noted.
2 | Minor discoloration | The hatch was observed to be in good condition with some minor discoloration.
2 | Minor hairline cracking | Minor hairline cracking
3 | Minor honeycombing | The columns were observed to be in fair condition. Minor honeycombing was noted at base pedestal. Cracking with efflorescence was noted on struts at a few areas.
3 | Minor paint wear | The steel ladder was in fair condition with some minor paint wear also observed.
3 | Minor pitting | Minor pitting was observed.
2 | Minor ponding | Minor ponding at north wall.
3 | Minor rust spots | The walls were observed to be in fair condition. Minor rust spots were noted.
3 | Minor step-cracking | The concrete block walls were observed to be in good condition. Minor step cracking was noted in the mortar joints.
3 | Minor wear | The concrete roof was observed to be in fair condition. Minor wear with exposed aggregates was noted on the underside.
3 | Missing | The steel hatch was observed to be in fair condition. Gasket was missing between hatch and shaft. Minor corrosion and paint wear was also observed.
2 | Missing grating-clips
3 | Missing joint sealant | The floor was observed to be in good condition. Joint sealant was found to either be missing or debonded from the concrete. Insufficient sloping was noted within the drainage trough. Guardrail was noted to be missing by drainage trench.
3 | Missing kickplate | The handrail was observed to be in good condition. However, kickplate was noted to be missing at intermediate landing. The Region's Operations mentioned that the kickplate was installed after the inspection.
2 | Missing washers | The platform was observed to be in good condition. Washers were noted to be missing on one side of all bolts.
3 | Moderate corrosion | The manhole cover and frame was observed to be in fair condition. Moderate corrosion of the frame was observed.
3 | Moderate surface corrosion | The manhole cover and frame was observed to be in fair condition. Moderate surface corrosion was noted.
3 | Moisture penetration | The hatch did not appear to be watertight as staining from moisture penetration was observed on the east wall.
1 | New
2 | No visible leaks | The underside of the roof was observed to be in good condition with no visible leaks.
3 | Not certified | The concrete floor was observed to be in fair condition. Joint sealants were observed to be in fair condition but not NSF 61 certified.
2 | Not extended | The stainless steel ladder was observed to be in good condition. The safety extension rail could not be extended and should be repaired/replaced.
3 | Not NSF certified | Previous repairs had been completed using a material that is not NSF certified.
3 | Paint wear | The steel ladder was observed to be in fair condition. Paint wear on the rungs was noted.
3 | Parts of grating had been cut | The grating was observed to be in fair condition. Parts of grating has been cut for previous decommissioned equipment.
3 | Parts of grating has been cut | The grating was observed to be in fair condition. Parts of grating has been cut for previous decommissioned equipment.
3 | Pitting | Pitting was observed.
3 | Ponding water | The concrete platform was observed to be in fair condition. Additional topping and drainage channels were added to try to resolve ponding water issue. The Region's operators reported that ponding water/ice on surface of the loading area creates a slip/tri
3 | Ponding water issue | The concrete platform was observed to be in fair condition. Additional topping and drainage channels were added to try to resolve ponding water issue. The Region's operators reported that ponding water/ice on surface of the loading area creates a slip/tri
3 | Previous crack injection | The walls were generally observed to be in good condition. Previous crack injection was noted at the hatch location.
3 | Previous crack injection repair
3 | Previous crack injection repairs
3 | Previous patches | The concrete beams were observed to be in good condition. Previous patches were noted in a few areas.
3 | Previous repaired cracks | Previously repaired cracks were noted throughout.
3 | Previous repairs | Previous repairs had been completed using a material that is not NSF certified.
3 | Rough surface | The concrete floor was observed to be in fair condition. Previous crack injections were noted. A rough surface was noted in a few areas which may pose a trip hazard.
3 | Rust spots | Rust spots and worn surfaces with exposed aggregates were observed.
2 | Securely affixed
2 | Securely anchored | Stairs observed to be in good condition and securely anchored.
3 | Seperation of mortar from block in corner
4 | Severe corrosion
3 | Sharp corners | The platform was observed to be in good condition. Washers were noted to be missing on one side of all bolts. Top of ladder ends with sharp corners may pose a hazard.
4 | Significant corrosion
3 | Signs of leakage | The crane beams was observed to be in good condition. Signs of leakage were noted at mount on north wall.
3 | Slime | A layer of slime was noted at the bottom of the ladder due to standing water.
3 | Small Hairline cracking | Hairline cracking of the slab was observed.
3 | Soft concrete | Soft concrete in top 5-10mm was noted.
3 | Spacing | The ladder was observed to be in fair condition. Rung spacing was observed to be greater than code requirements.
3 | Spalled concrete | The concrete walls were observed to be in fair condition. Spalled concrete was noted at south end at base of wall.
3 | Spalling | The concrete walls were observed to be in fair condition. Spalling was typically noted at form tie locations.
3 | Spalling concrete | Spalling concrete due to the expansion of the waterstop around the south inlet/outlet sump pit was observed.
5 | Spanning in wrong direction | The platform was observed to be in fair condition. A portion of grating was noted to be spanning in the wrong direction.
3 | Staining | The access stairs and handrails were observed to be in fair condition. Staining and discolouration was noted. Although the stairs were installed in recent years, the environment of the access house had accelerated the corrosion. Stairs can be replaced wit
3 | Standing water | Evidence of age/standing water was noted.
3 | Step-cracking
3 | Stuck handle | The stainless steel ladder was observed to be in good condition. The retractable safety handle was noted to be stuck.
3 | Submersed | The base slab could not be inspected as it was submersed at the time of the assessment. The slab was assumed to be in fair condition based on its age and the condition of other visible structural components.
3 | Too high | The ladder was observed to be in fair condition. Bottom rung was observed to be too high off the floor. Anchor bolts were noted to be corroded.
2 | Vegetation | The aluminum hatch was observed to be in good condition. Vegetation in hatch frame should be cleaned out periodically.
1 | Very good
3 | Voids | Bug holes/voids were noted at grade on the north side of the building.
3 | Water penetration | The concrete walls were observed to be in good condition. Water penetration was noted at pipe penetration into diesel fuel room.
3 | Water ponding
3 | Weathered paint | Paint was observed to be weathered and missing in some areas. Minor corrosion was noted at missing paint locations.
4 | Wide crack | The concrete columns were generally observed to be in fair condition. A wide crack was observed on the south side of the pipe gallery.
4 | Wide vertical crack | The concrete walls were observed to be in fair condition. Bottom edge of wall against clearwells has been previously crack injected. Wide vertical crack was observed next to cell #2 submarine door.
3 | Corroded safety extension
3 | Surface corrosion on anchor
3 | Spalled parging
3 | Embedded corroded plates
3 | Discoloured joint sealant
2 | Crossed asset tag

## AC
Condition | Keyword
3 | Weathering
3 | Weathered paint
3 | Wear and tear
3 | Wear
1 | Very good
3 | Tree growth
3 | Tree
4 | Significant wear
4 | Significant flaking
4 | Significant Corrosion
4 | Severe wear
4 | Severe flaking
4 | Severe Corrosion
3 | Sealants
3 | Ponding
3 | Peeling paint
3 | Peeling
3 | Paint peeling
3 | Not inspected
1 | New
3 | Moderate weathering
3 | Moderate wear
3 | Moderate flaking
3 | Moderate corrosion
3 | Missing
2 | Minor weathering
3 | Minor wear
2 | Minor localized defects
3 | Minor flaking
3 | Minor corrosion
3 | Localized flaking
2 | Localized defects
2 | Localized defect
2 | Good
3 | Flaking
3 | Faded
3 | Debonded and cracking
3 | Debonded
3 | Damaged
3 | Cracking and debonded
3 | Cracking
3 | Corrosion
3 | Peeled/Missing paint
3 | Bubbled/missing paint
3 | Peeling/missing paint
3 | Corrosion on hardware
3 | Localized delamination of coating
2 | Crossed asset tag

## HSS
Condition | Keyword
2 | Very minor corrosion
1 | Very good
3 | Surface corrosion
4 | Severe surface corrosoin
4 | Severe corrosion
3 | Paint wear and minor corrosion
3 | Paint wear
3 | Obsolete
5 | Not working
5 | Not operational
3 | Not in service
3 | No spill containment
2 | No certification
1 | New
3 | Moderate surface corrosion
3 | Moderate paint wear
3 | Moderate corrosion
3 | Missing fire valve
3 | Missing
3 | Minor surface corrosion
3 | Minor corrosion and paint wear
3 | Minor corrosion
4 | Major surface corrosion
4 | Major corrosion
3 | Leakage
3 | Leak
2 | Good
3 | Fire hazard
3 | Fair
3 | Discolouration
2 | Dirty
3 | Corrosion
5 | Broken
2 | Crossed asset tag

## BM
Condition | Keyword
2 | Very minor corrosion
1 | Very good
3 | Surface corrosion
4 | Severe surface corrosoin
4 | Severe corrosion
3 | Paint wear and minor corrosion
3 | Paint wear
3 | Obsolete
5 | Not working
5 | Not operational
3 | Not in service
3 | No spill containment
2 | No certification
1 | New
3 | Moderate surface corrosion
3 | Moderate paint wear
3 | Moderate corrosion
3 | Missing fire valve
3 | Missing
3 | Minor surface corrosion
3 | Minor corrosion and paint wear
3 | Minor corrosion
4 | Major surface corrosion
4 | Major corrosion
3 | Leakage
3 | Leak
2 | Good
3 | Fire hazard
3 | Fair
3 | Discolouration
3 | Dirty grilles
3 | Corrosion
5 | Broken
2 | no tag
2 | Crossed asset tag

## ES
Condition | Keyword
5 | Broken
3 | Corroded
3 | Corrosion
3 | Deposits
3 | Deteriorating panel-sealant
3 | Deterioration
3 | Dust built up
3 | Exceed guideline
5 | Failed
3 | Fair
2 | Good
4 | Lack of spare circuit
4 | Lack of spare circuits
3 | Minor corrosion
3 | Minor discoloration
3 | Minor local corrosion
3 | Minor mechanical damage
3 | Minor surface corrosion
3 | Missing
3 | Moderate corrosion
3 | Moderate surface corrosion
1 | New
3 | No availability of replacement
2 | No mechanical protection
5 | Non-functional
5 | Not in service
4 | Not-operating
4 | Not-operating
4 | Not-operational
3 | Obsolete
4 | Operation issues
3 | Outdated
3 | Oxidation
4 | Severe corrosion
4 | Severe surface corrosion
3 | Shattered
3 | Shattered
3 | Uneven
1 | Very good
2 | Very minor corrosion
2 | Very minor surface corrosion
2 | Crossed asset tag
3 | Flickering fixtures

## SW
Condition | Keyword
3 | Water
2 | Very minor paint wear
3 | Very minor corrosion
3 | Vegetation in the cracks
3 | Vegetation
3 | Uneven
3 | Unattached
2 | Staining
4 | Splitting and cracks
3 | Splitting and crack
3 | Splitting
3 | Significantly displaced
5 | Severe localized deformations
4 | Pothole
3 | Ponding
3 | Partially blocked
3 | Paint wear
1 | New
3 | Moderate surface corrosion
4 | Moderate localized deformations
3 | Moderate cracking in asphalt
4 | Moderate corrosion
3 | Missing
3 | Minor to moderate cracking
3 | Minor to moderate corrosion
3 | Minor surface corrosion
3 | Minor paint wear
3 | Minor localized deformations
3 | Minor curb displacement
3 | Minor cracking
3 | Minor corrosion and paint wear
3 | Minor corrosion
3 | low spots with no sod
3 | Localized deformations
3 | Localized deformation
3 | Gravel displacement
2 | Good
3 | Fair
3 | exposed granulars
3 | Displaced
3 | Discolouration
3 | Deformed
4 | Deformations
4 | Deformation
3 | Curb vertical rotation
3 | Curb vertical displacement and rotation
3 | Curb vertical displacement
3 | Crumbling pavement
3 | Cracks and splitting
3 | Cracks
3 | Cracked and deformed
3 | Cracked
3 | Crack and splitting
3 | Crack
4 | Broken and uneven
3 | Broken
4 | Blocked
3 | Low spots with no sod
3 | Exposed granulars
3 | Minor deficiencies with barbed wire
3 | eroded
2 | Crossed asset tag
3 | Moderate asphalt cracks
3 | Settled headwall and outlet pipe
3 | Localized areas
3 | Damaged sod
3 | Damged sod and exposed top soil
3 | Exposed top soil
3 | Deformed gate mesh
3 | Broken gate mesh
3 | Peeling fence paint
3 | Broken gate wheel

## PM
Condition | Keyword
3 | Uneven
3 | Surface corrosion
3 | Staining of the concrete insulation
3 | Staining
3 | Shattered
4 | Severe surface corrosion
4 | Severe paint wear
4 | Severe paint peeling
4 | Severe corrosion
4 | Performance issues
4 | Performance issue
3 | Paint wear
3 | Paint peeling and local corrosion
3 | Paint peeling
3 | Paint over valve and handwheel
3 | Outdated
3 | Obsolete
4 | not-operational
5 | Not-operating
4 | Not-operating
4 | Not performing well
1 | New
3 | Moderate surface corrosion
3 | Moderate paint wear
3 | Moderate paint peeling
3 | Moderate corrosion
3 | Missing
3 | Minor to moderate corrosion
3 | Minor surface corrosion
3 | Minor paint wear
3 | Local paint wear
3 | Local paint peeling
3 | Local corrosion and paint peeling
3 | Local corrosion
4 | Leaks
4 | Leaking
4 | Leakage
2 | Good
5 | Failed
3 | Corrosion
3 | Corroded
5 | Broken
4 | Active leaking
3 | Minor corrosion over paint
2 | Crossed asset tag
3 | Surficial corrosion
3 | Not accessible as within aluminum jacket
3 | Corroded gearbox and rising stem
3 | Corroded bolts and washers
3 | Corroded ball valve levers
3 | Minor spot corrosion
3 | Spot corrosion
3 | Corroded washers

## SIC
Condition | Keyword
3 | Wear and tear
3 | Uneven
3 | Shattered
4 | Severe surface corrosion
4 | Severe corrosion
3 | Outdated
3 | Obsolete
4 | Not-operational
4 | Not-operating
4 | Not-in-service
5 | Not-in-service
5 | Not operational
1 | New
3 | Moderate surface corrosion
3 | Moderate corrosion
3 | Missing cover
3 | Missing
3 | Minor surface corrosion
3 | Minor corrosion
3 | Loose screws
3 | Loose screw
2 | Good
5 | Failed
3 | Corrosion
3 | Corroded
5 | Broken
2 | Dust
2 | Crossed asset tag