## Sheet1
seqNum | assetTag | CategoryCode | facility | assetName | COF | Description | installYear | repCost | defect1Input | Process | building | inspectorName | LocationTag | LocationORIGINAL | TransmitterModel | TransducerModel | TransducerSerial | InstMeva | installationDate | remainingESL | InstType | ServiceArea | FacilityType | LifeCycleCategory | SerialNo | Parent | RotatingItem | Site | condition | defect1 | defect2 | defect3 | observations | RehabRepairCost | RehabRepairYear | RehabRepairCost2 | RehabRepairYear2 | photoName | repProjectName | rehabProjectName | rehab2ProjectName | Status | InspectionYear | manufacturer | rehabComment1 | rehabCost1 | rehabComment2 | rehabCost2 | defect2Input | defect3Input
5141 |  | HSS | S | (New) Fire Extinguisher | 1 |  | 2025 | 100 | Missing |  |  |  | 00019610 | [6 empty] | 8 | [8 empty] | 2 |  |  |  | The fire extinguisher was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  |  | Nobleton North ET Capital Project 1 |  |  |  | 2019 |  |  | 0 |  | 0
4996 |  | SW | S | (New) Sanitary Service | 2 | Provide sanitary service for tank. | 2025 | 120000 | No existing sanitary service for tank. |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_20201029_091308 |  |  |  |  | 0 |  | Install sanitary service for building and connect to nearby sanitary sewer. | 75000 |  | 0
4942 |  | SW | S | 300mm Underground Watermain Valve | 3 | 300mm Water valve, in valve box (within Region property line, adjacent to Dalton Road) | 1984 | 10000 | Lid could not be opened |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_20201029_093855 |  |  |  |  | 0 |  |  | 0 |  | 0
4943 |  | SW | S | 300mm Watermain | 5 | 125m of 300mm watermain. Material unknown | 1984 | 137000 |  |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_20201029_093855 |  |  |  |  | 0 |  |  | 0 |  | 0
4944 |  | SW | S | 375mm Storm Sewer | 3 | 375mm storm sewer (tank drain/overflow), concrete pipe, approx. length is 120m | 1984 | 120000 |  |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | [5 empty] | 0 |  |  | 0 |  | 0
4951 |  | SW | S | Access Road | 1 | Access road from Dalton Road to site entrance. Approx length of 90m and 4.0m wide | 1984 | 30000 | Tire ruts and low spots at various locations. |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_20201029_093755 |  |  |  |  | 0 |  | Place and compact granular material as required at low spots and tire ruts. | 7000 |  | 0
5128 |  | ES | S | Aircraft Obstruction Lights | 3 | Two warning lights, bulbs replaced in 2016 | 2016 | 5000 | Good |  |  |  | 00019634 | [6 empty] | 18 | [8 empty] | 2 |  |  |  | The aircraft obstruction lights was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3873 | Nobleton North ET Capital Project 2 |  |  |  | 2019 |  |  | 0 |  | 0
4940 |  | SW | S | Asphalt Driveway | 1 | Paved surface on site, and driveway entrance. Approximately 250m2. | 1984 | 20000 | Asphalt around concrete pad at tank pedestal settled, and damaged. |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_20201029_092545 |  |  |  |  | 0 |  | Remove and replace asphalt and granulars around pedestal entrance to ensure positive drainage away from entrance. | 5000 |  | 0 | Minor asphalt cracking along south edge of driveway entrance
4914 | 00025271 | SIC | S | Bell Antenna 1 | 1 | Cellular Antenna, installation year assumed to be 2010 based on its physical condition | 2010 | 10000 | Good |  |  |  | 790900008 | Sutton Elevated Tank | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Antenna |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3867 |  |  |  | OPERATING | 2020 |  |  | 0 |  | 0
4915 | 00025272 | SIC | S | Bell Antenna 2 | 1 | Cellular Antenna, installation year assumed to be 2010 based on its physical condition | 2010 | 10000 | Good |  |  |  | 790900008 | Sutton Elevated Tank | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Antenna |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3867 |  |  |  | OPERATING | 2020 |  |  | 0 |  | 0
4916 | 00025273 | SIC | S | Bell Antenna 3 | 1 | Cellular Antenna, installation year assumed to be 2010 based on its physical condition | 2010 | 10000 | Good |  |  |  | 790900008 | Sutton Elevated Tank | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Antenna |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3867 |  |  |  | OPERATING | 2020 |  |  | 0 |  | 0
4919 | 00025276 | SIC | S | Bell Antenna 4 | 1 | Cellular Antenna, installation year assumed to be 2010 based on its physical condition | 2010 | 10000 | Good |  |  |  | 790900008 | Sutton Elevated Tank | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Antenna |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3874 |  |  |  | OPERATING | 2020 |  |  | 0 |  | 0
4939 |  | SW | S | Chainlink Fence | 2 | 1.8m high, chainlink fence, with 3 barbed wires at top. Approx. 165m in length | 1984 | 25000 | Top barbed wire was cut, affecting approximately 10m in length. |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_20201029_091640 |  |  |  |  | 0 |  | Re-install top barbed wire for section that is damaged. | 500 |  | 0
4923 | 00025424 | HSS | S | Chlorine Residual Kit | 2 | Hach II Pocket Colorimeter, Chlorine Residual Kit | 2010 | 700 | Missing |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Health and Safety | ` |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | OPERATING | 2020 | M00482 |  | 0 |  | 0
4941 |  | SW | S | Concrete Curb | 1 | Concrete curb at dirveway entrances (both east and west). Approximately 20m in length | 1984 | 2500 | Minor damage and cracking on curb. |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_20201029_092855 |  |  |  |  | 0 |  |  | 0 |  | 0
4931 | 00078381 | BM | S | Electric Baseboard Heater | 2 | Baseboard Convection Heater, 120/1/60, Manufacturer: Dimplex, installation year assumed to be 2016 | 2016 | 500 | good |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Building Mechanical |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_5647 |  |  |  | OPERATING | 2020 | M00366 |  | 0 |  | 0
5129 |  | ES | S | Electrical Conduit System | 3 | Conduit system including conduit for electrical services, installation year assumed to be 2010. | 2010 | 25000 | good |  |  |  | #N/A | Glenway RES Outside Sanitary Pumping Station | [5 empty] | 11 |  | Area 2N Linear Water & Wells | [5 empty] | OPERATING | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. |  |  | 0 |  | PXL_20201029_134547192 | Mt Albert North ET Capital Project 2 |  |  | W-WW | 2020 |  |  | 0 |  | 0
5049 | 00044398 | AC | S | Elevated Tank Access Double Doors | 1 | Exterior double metal door, installation year assumed to be 1984 | 1984 | 5500 | corrosion at bottom of door frame |  |  |  | 790900008 | Sutton Elevated Tank | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Architectural |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3836 |  |  |  | OPERATING | 2020 |  |  | 0 |  | 0
5098 |  | SC | S | Elevated Tank Aluminum Ladder (Ground to Platform) | 4 |  | 1984 | 30000 | good |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3845 |  |  |  |  | 0 |  |  | 0 |  | 0
5099 |  | SC | S | Elevated Tank Aluminum Ladder (Platform to Roof) | 4 |  | 1984 | 15000 | good |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3857 |  |  |  |  | 0 |  |  | 0 |  | 0
5101 |  | SC | S | Elevated Tank Aluminum Ladder (Platform to Tank Floor Access Hatch) | 4 |  | 1984 | 4000 | good |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3853 |  |  |  |  | 0 |  |  | 0 |  | 0
5100 |  | SC | S | Elevated Tank Aluminum Ladder (Roof to Tank) | 4 |  | 1984 | 15000 | failed |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3889 |  |  |  |  | 0 |  |  | 0 |  | 0
5097 |  | SC | S | Elevated Tank Aluminum Platform | 4 |  | 1984 | 50000 | good |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3846 |  |  |  |  | 0 |  |  | 0 |  | 0
5107 |  | HSS | S | Elevated Tank Anchor Point | 4 | Platform level | 2007 | 3000 | good |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3850 |  |  |  |  | 0 |  |  | 0 |  | 0
4891 | 00004221 | PM | S | Elevated Tank Bypass Line Check Valve | 3 | Diameter: 150mm, Manufacturer: McAvity | 1984 | 1500 | Minor to moderate surface corrosion |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Process Mechanical |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_5651 |  |  |  | OPERATING | 2020 | M00100 |  | 0 |  | 0
4890 | 00004220 | PM | S | Elevated Tank Bypass Line Gate Valve 1 | 3 | Diameter: 150mm, Manufacturer: McAvity | 1984 | 1500 | Minor to moderate surface corrosion |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Process Mechanical |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_5568 |  |  |  | OPERATING | 2020 | M00100 |  | 0 |  | 0
4892 | 00004222 | PM | S | Elevated Tank Bypass Line Gate Valve 2 | 3 | Diameter: 150mm, Manufacturer: McAvity | 1984 | 1500 | Minor surface corrosion |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Process Mechanical |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_5557 |  |  |  | OPERATING | 2020 | M00100 |  | 0 |  | 0
4893 | 00004223 | PM | S | Elevated Tank Bypass Line Gate Valve 3 | 3 | Diameter: 150mm, Manufacturer: McAvity | 1984 | 1500 | Minor surface corrosion |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Process Mechanical |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_5551 |  |  |  | OPERATING | 2020 | M00100 |  | 0 |  | 0
4894 | 00004224 | PM | S | Elevated Tank Bypass Line Gate Valve 4 | 3 | Diameter: 150mm, Manufacturer: McAvity | 1984 | 1500 | Minor surface corrosion |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Process Mechanical |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_5550 |  |  |  | OPERATING | 2020 | M00100 |  | 0 |  | 0
5138 |  | PM | S | Elevated Tank Bypass Line Piping | 4 | Diameter: 150mm, approximate length: 10m | 1984 | 5500 | Moderate surface corrosion |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_5642 |  |  |  |  | 0 |  |  | 0 |  | 0 | Couplings installed on the pipe were rusted.
5133 |  | SC | S | Elevated Tank Cathodic Protection | 3 |  | 1984 | 0 | The elevated tank did not have cathodic protection. The Region is planning to have the cathodic protection system installed. | [10 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | [5 empty] | 0 |  |  | 0 |  | 0
4910 | 00017903 | SIC | S | Elevated Tank Chlorine Analyzer | 3 |  | 1984 | 15000 | outdated |  |  |  | 00016061 | Sutton ET Valve Room | CL17 |  |  | Chlorine |  | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control | 30600007459 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | PXL_20201029_133942071 |  |  |  | OPERATING | 2020 | M00482 |  | 0 |  | 0
5093 |  | SC | S | Elevated Tank Concrete Structure | 4 |  | 1984 | 900000 | good |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3845 |  |  |  |  | 0 |  |  | 0 |  | 0
5106 |  | HSS | S | Elevated Tank Davit Base Socket | 4 | Roof | 2007 | 4000 | good |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3879 |  |  |  |  | 0 |  |  | 0 |  | 0
5095 |  | SC | S | Elevated Tank Exterior Coating | 3 |  | 1984 | 600000 | fair |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3835 |  |  |  |  | 0 |  |  | 0 |  | 0
4935 | 00083317 | SIC | S | Elevated Tank Flow Transmitter | 3 | installation year assumed to be 2010 based on its physical condition | 2010 | 10000 | good |  |  |  | 00016061 | Sutton ET Valve Room | 93WA4-18D3/0 | 93WA4 |  | Flow |  | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control | M1027302000 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | PXL_20201029_134330909 |  |  |  | OPERATING | 2020 | M00405 |  | 0 |  | 0
5131 |  | ES | S | Elevated Tank Grounding | 3 | installation year assumed to be 2010 | 2010 | 10000 | good |  |  |  | 790900018 | [6 empty] | 44 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. |  |  | 0 |  | IMG_3844 |  |  |  |  | 0 |  |  | 0 |  | 0
5115 |  | SC | S | Elevated Tank Guardrail | 3 |  | 1984 | 30000 | good |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3873 |  |  |  |  | 0 |  |  | 0 |  | 0
5108 |  | SC | S | Elevated Tank Inlet Pipe Support | 3 |  | 1984 | 30000 | good |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3845 |  |  |  |  | 0 |  |  | 0 |  | 0
4889 | 00004219 | PM | S | Elevated Tank Inlet/Outlet Line Gate Valve | 3 | Diameter: 300mm, Manufacturer: McAvity | 1984 | 3000 | Leak in packing |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Process Mechanical |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_5556 |  |  |  | OPERATING | 2020 | M00100 |  | 0 |  | 0 | Minor to moderate corrosion on valve body
5137 |  | PM | S | Elevated Tank Inlet/Outlet Piping | 4 | Diameter: 300mm, approximate length: 35m | 1984 | 40000 | Very minor surface corrosion |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_5591 |  |  |  |  | 0 |  |  | 0 |  | 0
5096 |  | SC | S | Elevated Tank Interior Coating | 3 |  | 1984 | 375000 | poor |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3889 |  |  |  |  | 0 |  |  | 0 |  | 0
5130 |  | ES | S | Elevated Tank Lightning Protection System | 3 | 1 lightning air protection terminal | 2004 | 5000 | good |  |  |  | 790900018 | [6 empty] | 11 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. |  |  | 0 |  | IMG_3867 | Mt Albert North ET Capital Project 2 |  |  |  | 0 |  |  | 0 |  | 0
4934 | 00083307 | SIC | S | Elevated Tank Network Access Closet | 4 | installation year assumed to be 2010 | 2010 | 25000 | good |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control | 14E-088/SUETDR_NAC |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | PXL_20201029_134521784 |  |  |  | OPERATING | 2020 | M00844 |  | 0 |  | 0
4913 | 00017906 | SIC | S | Elevated Tank Network Radio Modem 1 | 2 | likely installed in the Network Access Closet, installation year assumed to be 2010 | 2010 | 5000 |  |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | SCADA | 831070 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | OPERATING | 2020 | M01018 |  | 0 |  | 0 | included in 00083307
4912 | 00017905 | SIC | S | Elevated Tank Network Radio Modem 2 | 2 | likely installed in the Network Access Closet, installation year assumed to be 2010 | 2010 | 5000 |  |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | SCADA | 831046 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | OPERATING | 2020 | M01018 |  | 0 |  | 0
4905 | 00017896 | SIC | S | Elevated Tank Network UPS 1 | 2 | likely installed in the Network Access Closet, installation year assumed to be 2010 | 2010 | 3000 |  |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | SCADA | JB0241022055R |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | OPERATING | 2020 | M00183 |  | 0 |  | 0
4928 | 00052825 | SIC | S | Elevated Tank Network UPS 2 | 2 | likely installed in the Network Access Closet, installation year assumed to be 2010 | 2010 | 3000 |  |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | SCADA | GF104A0100 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | OPERATING | 2020 | M00728 |  | 0 |  | 0
5109 |  | SC | S | Elevated Tank Outlet Pipe Support | 3 |  | 1984 | 30000 | good |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3845 |  |  |  |  | 0 |  |  | 0 |  | 0
5139 |  | PM | S | Elevated Tank Overflow Piping | 4 | Diameter: 150mm, approximate length: 40m | 1984 | 25000 | Moderate surface corrosion |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_5634 |  |  |  |  | 0 |  |  | 0 |  | 0 | Couplings installed on the pipe were rusted.
4950 |  | ES | S | Elevated Tank Pedestal Lighting | 2 | 6 NEMA 4 fixtures, installation year assumed to be 2010. | 2010 | 6000 | good |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | PXL_20201029_135009897 |  |  |  |  | 0 |  |  | 0 |  | 0
4901 | 00006889 | SIC | S | Elevated Tank Pressure Gauge | 1 |  | 1984 | 500 | Minor surface corrosion |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | PXL_20201029_134817672 |  |  |  | OPERATING | 2020 | M00627 |  | 0 |  | 0
4926 | 00044946 | SIC | S | Elevated Tank Pressure Transmitter | 3 | Installation year assumed to be 2010 based on its physical condition | 2010 | 2000 | good |  |  |  | 00016061 | Sutton ET Valve Room | PMC71 |  |  |  |  | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control | F900091509C |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | PXL_20201029_134314017 |  |  |  | OPERATING | 2020 | M00405 |  | 0 |  | 0
5126 |  | BM | S | Elevated Tank Removable Louvred Vent | 1 |  | 1984 | 5000 | good |  |  |  | 790900018 | [6 empty] | 44 | [8 empty] | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. |  |  | 0 |  | IMG_3848 |  |  |  |  | 2019 |  |  | 0 |  | 0
5104 |  | SC | S | Elevated Tank Roof Access Hatch (Access to Tank Interior) | 2 |  | 1984 | 10000 | good |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3883 |  |  |  |  | 0 |  |  | 0 |  | 0
5103 |  | SC | S | Elevated Tank Roof Access Hatch (Access Tube to Tank Roof) | 2 |  | 1984 | 10000 | good |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3883 |  |  |  |  | 0 |  |  | 0 |  | 0
5105 |  | HSS | S | Elevated Tank Roof Dismount Post | 4 |  | 1984 | 3000 | Moderate surface corrosion |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 2023 | 0 | 0 | IMG_3883 |  |  |  |  | 0 |  | Surface prep and paint dismount post in safety yellow colour. | 2000 |  | 0
5094 |  | SC | S | Elevated Tank Steel Tank | 5 |  | 1984 | 1300000 | good |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3835 |  |  |  |  | 0 |  |  | 0 |  | 0
5102 |  | SC | S | Elevated Tank Submarine Floor Access Hatch | 3 |  | 1984 | 3000 | good |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3853 |  |  |  |  | 0 |  |  | 0 |  | 0
4937 | 00083320 | SIC | S | Elevated Tank SUETDR Control Panel | 4 | PAC control panel, installation year assumed to be 2017 | 2017 | 80000 | good |  |  |  | 00016062 | Sutton ET Tank Base | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control | 14E-088/SUETDR_PAC |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | PXL_20201029_134934038 |  |  |  | OPERATING | 2020 | M00844 |  | 0 |  | 0
4932 | 00081400 | SIC | S | Elevated Tank SUETDR Control Panel Ethernet Switch | 2 | likely installed in SUETDR Control Panel, installation year assumed to be 2017 | 2017 | 3000 |  |  |  |  | 00016062 | Sutton ET Tank Base | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control | FOC2004Z1FF |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | OPERATING | 2020 | M01002 |  | 0 |  | 0
4938 | 00083386 | SIC | S | Elevated Tank SUETDR Control Panel UPS | 2 | likely installed in SUETDR Control Panel, installation year assumed to be 2017 | 2017 | 3000 |  |  |  |  | 00016062 | Sutton ET Tank Base | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control | GK053A0127 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | PXL_20201029_134934038 |  |  |  | OPERATING | 2020 | M10181 |  | 0 |  | 0
4933 | 00083219 | SIC | S | Elevated Tank SUETDR OIT Panel | 3 | Advantech Monitor Panel, installation year assumed to be 2017 based on its physical condition | 2017 | 10000 | good |  |  |  | 00016062 | Sutton ET Tank Base | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control | KSA1476816 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | PXL_20201029_134143670 |  |  |  | OPERATING | 2020 | M10189 |  | 0 |  | 0
4936 | 00083318 | SIC | S | Elevated Tank SUETDR OIT Panel CPU | 2 | installed in SUETDR OIT Panel, installation year assumed to be 2017 | 2017 | 1500 |  |  |  |  | 00016062 | Sutton ET Tank Base | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control | ACG2001486 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | PXL_20201029_134143670 |  |  |  | OPERATING | 2020 | M10189 |  | 0 |  | 0
5117 |  | SC | S | Elevated Tank Tank Vent | 3 |  | 1984 | 5000 | good |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3879 |  |  |  |  | 0 |  |  | 0 |  | 0
5140 |  | PM | S | Elevated Tank Vent/Vacuum Relief Unit | 3 | Installation year assumed to be 1984. | 1984 | 10000 | Minor surface corrosion on steel collar |  |  |  | 19817 | [6 empty] | 25 | [8 empty] | 2 |  |  |  | The elevated tank vent was observed to be in good condition. Elevated tank vent to be replaced at the end of remaining service life. |  | 2022 |  |  | IMG_3875 |  |  |  |  | 2019 |  | Surface prep and touch-up vent collar | 2000
4927 | 00045975 | ES | S | Generator Transfer Panel | 3 | Manufacturer: Siemens, Model No.:EQG630D. Installation year assumed to be 1984. | 1984 | 5000 | minor corrosion around the circuit breakers |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Electrical System | 12167-067 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | PXL_20201029_134356166 |  |  |  | OPERATING | 2020 | M00125 |  | 0 |  | 0
4900 | 00006888 | ES | S | Heat Trace Control Panel | 3 |  | 1984 | 5000 | outdated |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Electrical System |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | PXL_20201029_134021130 |  |  |  | OPERATING | 2020 |  |  | 0 |  | 0
5127 | 00006888 | ES | S | Inlet/Outlet Riser Heat Trace System | 3 |  | 1984 | 10000 | good |  |  |  | 00016061 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_5575 |  |  |  |  | 0 |  |  | 0 |  | 0
4897 | 00084446 | ES | S | Lighting Panel A | 3 | Mannufacturer:Square D; ; serial number: 12398972110010001, 120/240V, 200A, 42CCT; old tag is 00006883. The panel was installed approximately in 2016. | 2016 | 14000 | corrosion on enclosure |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Electrical System | T3A |  |  | W-WW | 0 |  |  |  |  | 0 | 2025 | 0 | 0 | PXL_20201029_134229876 |  |  |  | OPERATING | 2020 | M00129 | Replace the enclosure with NEMA 3R type. | 4000 |  | 0 | The enclosure was not NEMA 3R type. | The enclosure to be replaced with NEMA 3R type
4908 | 00017900 | SIC | S | Network Antenna 1 | 2 | Installation year assumed to be 2010 based on its physical condition | 2010 | 10000 | good |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | SCADA |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | PXL_20201029_133504866 |  |  |  | OPERATING | 2020 |  |  | 0 |  | 0
4909 | 00017901 | SIC | S | Network Antenna 2 | 2 | Installation year assumed to be 2010 based on its physical condition | 2010 | 10000 | good |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | SCADA |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | PXL_20201029_133504866 |  |  |  | OPERATING | 2020 |  |  | 0 |  | 0
4947 |  | ES | S | Outdoor Lighting Fixture | 1 | 1 LED flood light, installation year assumed to be 2010. | 2010 | 900 | good |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | PXL_20201029_133518930 |  |  |  |  | 0 |  |  | 0 |  | 0
5001 | 00044308 | BM | S | Portable Dehumidifier | 2 | Portable dehumidifier by Electrolux Home Products, Model CAD304NWL, 115/60/1; capacity 30 pints/day | 2016 | 300 | good |  |  |  | 00016061 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_5623 |  |  |  |  | 0 |  |  | 0 |  | 0
4929 | 00077743 | ES | S | Portable Generator | 3 | Manufacturer: Honda, Model Name: EU3000, specs: 120V, 20A. Installation year assumed to be 2017 | 2017 | 2000 | good |  |  |  | 790900008 | Sutton Elevated Tank | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Building Mechanical | EAVJ-1144610 |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | PXL_20201029_134627924 |  |  |  | OPERATING | 2020 | M00506 |  | 0 |  | 0
4903 | 00012111 | SW | S | Site Drainage (soft surfaces) | 1 | Site drainage on site, including grassed areas. | 1984 | 15000 | Along edge of pavement, tire ruts damaged sod |  |  |  | 790900008 | Sutton Elevated Tank | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Siteworks |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_20201029_091412 |  |  |  | OPERATING | 2020 |  | Remove top soil and sod along edge of pavement, and replace with gravel shoulder. | 7500 | Remove and replace sod at low spots of soft surface around site. | 2000 | Low spots at various locations around site, not draining storm water properly
4902 | 00012107 | SW | S | Site Gate | 2 | East, Gate, Double Lockable | 1984 | 3000 | Minor damage |  |  |  | 790900008 | Sutton Elevated Tank | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Siteworks |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_20201029_092823 |  |  |  | OPERATING | 2020 |  |  | 0 |  | 0
4930 | 00078380 | SIC | S | Security System | 3 | Three panels in total, installation year assumed to be 2010 based on the physical condition | 2010 | 10000 | good |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Health and Safety |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | PXL_20201029_134421959 |  |  |  | OPERATING | 2020 | M00076 |  | 0 |  | 0
4945 |  | SW | S | Storm Maintenance Hole No. 2 | 2 | Located at Dalton Road ROW, approximately 2.0m deep. | 1984 | 15000 | Damaged maintenance hole adjustment unit for frame. |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_20201029_094643 |  |  |  |  | 0 |  | Remove and replace adjustment unit for maintenance hole frame. | 1000 |  | 0
4946 |  | SW | S | Storm Maintenance Hole No.3 | 2 | Located approximately 5m from elevated tank pedestal. Approximately 2.5m deep. | 1984 | 17500 | Maintenance hole was buried below pavement. |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_20201029_095120 |  |  |  |  | 0 |  | Excavate around maintenance hole and raise frame/lid to grade. Reinstate asphalt pavement around lid. | 2500 |  | 0
4924 | 00035519 | BM | S | Sump Pump and Drain Piping | 2 | Submersible Sump Pump, by Mastercraft, 120/1/60, 1/3hp, capacity: 10.4 m3/h. The sump pump pumping connected to elevated tank overflow pipe | 1984 | 2000 | good |  |  |  | 00016061 | Sutton ET Valve Room | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Process Mechanical |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_5618 |  |  |  | OPERATING | 2020 |  |  | 0 |  | 0
4906 | 00017897 | SIC | S | Sump Pump Float Switch | 2 | installed in the sump pump pit, installation year assumed to be 2010 based on its physical condition. | 2010 | 500 | good |  |  |  | 00016061 | Sutton ET Valve Room |  |  |  | Level |  | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | PXL_20201029_134846156 |  |  |  | OPERATING | 2020 |  |  | 0 |  | 0
5114 |  | SW | S | Valve Chamber Access Ladder | 3 |  | 1984 | 2500 | good |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3913 |  |  |  |  | 0 |  |  | 0 |  | 0
5113 |  | SW | S | Valve Chamber Manhole Frame and Cover | 2 |  | 1984 | 1500 | good |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3911 |  |  |  |  | 0 |  |  | 0 |  | 0
5112 |  | SW | S | Valve Chamber Precast Concrete Chamber | 2 |  | 1984 | 50000 | good |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3913 |  |  |  |  | 0 |  |  | 0 |  | 0
5111 |  | SC | S | Valve Room Concrete Roof | 4 |  | 1984 | 15000 | good |  |  |  | 00016061 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3905 |  |  |  |  | 0 |  |  | 0 |  | 0
4949 |  | ES | S | Valve Room Emergency Lighting | 1 | Emergency lighting with 1 battery unit and 1 remote head, a new battery was installed in July 2020. | 2010 | 1000 | good |  |  |  | 00016061 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | PXL_20201029_133917415 |  |  |  |  | 0 |  |  | 0 |  | 0
5048 | 00006879 | AC | S | Valve Room Interior Single Door | 1 | Installation year assumed to be 1984 | 1984 | 3500 | fair |  |  |  | 00016061 | Sutton ET Tank Base | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Architectural |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3903 |  |  |  | OPERATING | 2020 |  |  | 0 |  | 0
4948 |  | ES | S | Valve Room Lighting Fixtures | 1 | 2 NEMA 4 fixtures, installation year assumed to be 2010. | 2010 | 2000 | good |  |  |  | 00016061 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | PXL_20201029_134544370 |  |  |  |  | 0 |  |  | 0 |  | 0
4907 | 00017898 | SIC | S | Valve Room Low Temperature Alarm | 2 | Valve room low temperature alarm, installation year assumed to be 2010 based on its physical condition. | 2010 | 500 | good |  |  |  | 00016061 | Sutton ET Valve Room | T631A1063 |  |  | Temperature |  | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control | NOT AVAILABLE |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | PXL_20201029_134218182 |  |  |  | OPERATING | 2020 | M00076 |  | 0 |  | 0
5110 |  | SC | S | Valve Room Masonry Blockwall | 4 |  | 1984 | 8000 | hairline cracking at corner |  |  |  | 00016061 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3903 |  |  |  |  | 0 |  |  | 0 |  | 0 | fair
5089 |  | AC | S | Valve Room Wall and Ceiling Paint | 1 | Installation year assumed to be 1987 | 1987 | 2000 | good |  |  |  | 00016061 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3905 |  |  |  |  | 0 |  |  | 0 |  | 0
5003 |  | PM | S | Watermain Pipe Extended Stem Gate Valve 1 | 3 | Diameter: 300mm | 2016 | 5000 | Minor corrosion on wrench nut |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_5482 |  |  |  |  | 0 |  |  | 0 |  | 0
5005 |  | PM | S | Watermain Pipe Extended Stem Gate Valve 2 | 3 | Diameter: 300mm | 2016 | 5000 | Minor corrosion on wrench nut |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_5485 |  |  |  |  | 0 |  |  | 0 |  | 0
5004 |  | PM | S | Watermain Pipe Extended Stem Gate Valve 2 | 3 | Diameter: 300mm | 2016 | 5000 | Minor corrosion on wrench nut |  |  |  | 790900008 | [6 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_5489 |  |  |  |  | 0 |  |  | 0 |  | 0
4918 | 00025275 | SIC | S | York Region Antenna 5 | 1 | UHF SCADA Yagi Antenna, installation year assumed to be 2010 based on the physical condition | 2010 | 10000 | Good |  |  |  | 790900008 | Sutton Elevated Tank | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Antenna |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3869 |  |  |  | OPERATING | 2020 |  |  | 0 |  | 0
4917 | 00025274 | SIC | S | York Region Antenna 6 | 1 | UHF Yagi Antenna, installation year assumed to be 2010 based on the physical condition | 2010 | 10000 | Good |  |  |  | 790900008 | Sutton Elevated Tank | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Antenna |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3869 |  |  |  | OPERATING | 2020 |  |  | 0 |  | 0
4920 | 00025277 | SIC | S | York Region Antenna 7 | 1 | UHF Whip Traffic Antenna, installation year assumed to be 2010 based on the physical condition | 2010 | 10000 | Good |  |  |  | 790900008 | Sutton Elevated Tank | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Antenna |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3874 |  |  |  | OPERATING | 2020 |  |  | 0 |  | 0
4921 | 00025278 | SIC | S | York Region Antenna 8 | 1 | UHF Whip Traffic Antenna, installation year assumed to be 2010 based on the physical condition | 2010 | 10000 | Good |  |  |  | 790900008 | Sutton Elevated Tank | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Antenna |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3874 |  |  |  | OPERATING | 2020 |  |  | 0 |  | 0
4922 | 00025279 | SIC | S | York Region Antenna 9 | 1 | UHF Whip Traffic Antenna, installation year assumed to be 2010 based on the physical condition | 2010 | 10000 | Good |  |  |  | 790900008 | Sutton Elevated Tank | [5 empty] | 0 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Antenna |  |  |  | W-WW | 0 |  |  |  |  | 0 | 0 | 0 | 0 | IMG_3874 |  |  |  | OPERATING | 2020 |  |  | 0 |  | 0