## Sheet1
seqNum | facility | CategoryCode | assetName | LocationTag | Description | installYear | remainingESL | repCost | InspectionYear | CalcProcess | Process | building | inspectorName | assetTag | LocationORIGINAL | installationDate | condition | COF | defect1 | defect2 | defect3 | observations | RehabRepairCost | RehabRepairYear | RehabRepairCost2 | RehabRepairYear2 | photoName | repProjectName | rehabProjectName | rehab2ProjectName | LifeCycleCategory | TransmitterModel | TransducerModel | TransducerSerial | Status | rehabComment1 | rehabCost1 | rehabComment2 | rehabCost2 | defect1Input | defect2Input | defect3Input | InstType | InstMeva | ServiceArea | FacilityType | SerialNo | Parent | RotatingItem | Site | manufacturer
4475 | SPS7 | SW | Maintenance Hole No.1 | 7 |  | 1999 |  | 30000 | 0 | [8 empty] | 2 | [8 empty] | IMG_2068 | [12 empty] | good
4476 | SPS7 | SW | Maintenance Hole No.2 | 7 |  | 1979 |  | 30000 | 0 | [8 empty] | 2 | [8 empty] | IMG_2078 | [12 empty] | good
4477 | SPS7 | SW | Pavement | 7 | Approximately 75 m2 of pavement for access road | 1979 |  | 9750 | 0 | [8 empty] | 2 | [5 empty] | 2031 |  | 2026 | IMG_2074 | [8 empty] | Asphalt resurfacing | 6375 | Minor crack repair/filling | 4900 | Minor cracks observed on the pavement. Good condition.
4478 | SPS7 | SW | Swale No.1 | 7 | Approximately 4 m in length, 1 m in width and 0.5 m in depth | 1979 |  | 500 | 0 | [8 empty] | 2 | [5 empty] | 2026 |  |  | IMG_2067 | [8 empty] | Clearing debris from the swale | 150 |  |  | good
4479 | SPS7 | SW | Swale No.2 | 7 | Approximately 7.5 m in length, 1 m in width and 0.5 m in depth | 1979 |  | 900 | 0 | [8 empty] | 2 | [5 empty] | 2026 |  |  | IMG_2065 | [8 empty] | Clearing debris from the swale | 320 |  |  | good
4480 | SPS7 | SW | Stormwater Culvert | 7 | Approximately 6.5 m in length and 400 mm in diameter | 1979 |  | 5400 | 0 | [8 empty] | 2 | [8 empty] | IMG_2066 | [12 empty] | good
4506 | SPS7 | PM | Wastewater Pump 1 | 10 | Submersible, dry pit, centrifugal wastewater pump, 22 kW, 1750 rpm, 600/3/60; by Flygt model 3170.180; explosion proof enclosure (Class 1, Zone 1); | 1979 |  | 35000 | 0 | [8 empty] | 4 | [8 empty] | IMG_0969 | [12 empty] | good | needs regular maintenance
4507 | SPS7 | PM | Wastewater Pump 2 | 10 | Submersible, dry pit, centrifugal wastewater pump, 22 kW, 1750 rpm, 600/3/60; by Flygt model 3170.180; explosion proof enclosure (Class 1, Zone 1); | 1979 |  | 35000 | 0 | [8 empty] | 4 | [8 empty] | IMG_0957 | [12 empty] | good | needs regular maintenance
4508 | SPS7 | PM | Pump 1 Suction Gate Valve | 10 | Isolation gate valve, 200 DIA, Flanged, NRS, Pump #1 suction line, by Seguro | 1979 |  | 3000 | 0 | [8 empty] | 4 | [8 empty] | IMG_0994 | [12 empty] | Fair Condition | maintenance
4509 | SPS7 | PM | Pump 1 Discharge Gate Valve | 10 | Isolation gate valve, Pump #1 discharge line, 200 DIA, flanged, NRS, by Seguro | 1979 |  | 3000 | 0 | [8 empty] | 4 | [8 empty] | IMG_0996 | [12 empty] | Fair Condition | maintenance
4510 | SPS7 | PM | Pump 1 Discharge Swing Check Valve | 10 | AWWA Swing Check Valve, with lever and spring, Pump #1 discharge line, 200 DIA, flanged, by Kennedy | 1985 |  | 5000 | 0 | [8 empty] | 4 | [8 empty] | IMG_0997 | [12 empty] | Fair Condition | maintenance
4511 | SPS7 | PM | Pump 2 Discharge Swing Check Valve | 10 | AWWA Swing Check Valve, with lever and spring, Pump #2 discharge line, 200 DIA, flanged, by Kennedy | 1985 |  | 5000 | 0 | [8 empty] | 4 | [8 empty] | IMG_0955 | [12 empty] | Fair Condition | maintenance
4512 | SPS7 | PM | Pump 2 Suction Gate Valve | 10 | Isolation gate valve, 200 DIA, Flanged, NRS, Pump #2 suction line, by Seguro | 1979 |  | 3000 | 0 | [8 empty] | 4 | [8 empty] | IMG_0965 | [12 empty] | Fair condition | maintenance
4513 | SPS7 | PM | Pump 2 Discharge Gate Valve | 10 | Isolation gate valve, Pump #2 discharge line, 200 DIA, flanged, NRS, by Clow | 1979 |  | 3000 | 0 | [8 empty] | 4 | [8 empty] | IMG_0983 | [12 empty] | Fair condition | maintenance
4514 | SPS7 | PM | Discharge piping | 10 | 200 DIA suction and discharge piping, DI, Victaulic couplings | 1979 |  | 10000 | 0 | [8 empty] | 4 | [8 empty] | IMG_1005 | [12 empty] | Fair condition | maintenance
4515 | SPS7 | PM | Bypass Gate Valve | 7 | Bypass gate valve in bypass MH, 100 DIA flanged c/w 100 DIA, 90 deg elbow (up) and blind flange. | 1979 |  | 3000 | 0 | [8 empty] | 3 | [8 empty] | IMG_0933 | [12 empty] | Fair condition | backflow preventing mechanism shall be installed in the drain to the wet well.
4516 | SPS7 | PM | Overflow | 8 | 400 DIA overflow pipe with manual gate to open-close; CPM pipe c/w 15 DIA steel bars at outlet, | 1979 |  | 10000 | 0 | [8 empty] | 3 | [8 empty] | IMG_7253 | [12 empty] | Fair condition | maintenance; a backflow preventing mechanism shall be installed in the wet well overflow.
4517 | SPS7 | PM | Bar screen and trash basket | 8 | Bar screen and trash basket. | 1979 |  | 8000 | 0 | [8 empty] | 3 | [8 empty] | IMG_7252 | [12 empty] | fair condition | maintenance
4518 | SPS7 | PM | Gate valve | 7 | Force main 200 DIA isolation gate valve; NRS, by Seguro, located in pass valve MH. | 1979 |  | 3000 | 0 | [8 empty] | 4 | [8 empty] | IMG_0933 | [12 empty] | goodcondition | maintenance
4549 | SPS7 | ES | outdoor lighting | 7 | 3 wall pack fixtures | 1987 |  | 1500 | 0 | [8 empty] | 2 | [8 empty] | IMG_5034 | [12 empty] | good
4550 | SPS7 | ES | hydro meter | 7 | hydro meter | 2014 |  | 5000 | 0 | [8 empty] | 3 | [8 empty] | IMG_5037 | [12 empty] | good
4551 | SPS7 | ES | exit sign | 7 | exit sign | 2014 |  | 500 | 0 | [8 empty] | 2 | [8 empty] | IMG_5038 | [12 empty] | good
4552 | SPS7 | ES | main level lighting | 9 | 4 linear fluroscent | 2014 |  | 1600 | 0 | [8 empty] | 2 | [8 empty] | IMG_5041 | [12 empty] | fixture above MCC did not turn on | to be replaced with LEDs in next upgrade
4553 | SPS7 | ES | automatic transfer switch | 9 | automatic transfer switch | 1987 |  | 30000 | 0 | [8 empty] | 3 | [8 empty] | IMG_5043 | [12 empty] | good
4554 | SPS7 | ES | MCC | 9 | MCC, 4 columns | 1987 |  | 35000 | 0 | [8 empty] | 3 | [8 empty] | IMG_5045 | [12 empty] | good
4555 | SPS7 | ES | Main Breaker | 9 | Main Breaker;; ; ; 600V, 200A | 1987 |  | 12000 | 0 | [8 empty] | 3 | [8 empty] | IMG_5050 | [12 empty] | good
4556 | SPS7 | ES | Capacitors | 9 | Capacitors | 1987 |  | 2500 | 0 | [8 empty] | 3 | [8 empty] | IMG_5056 | [12 empty] | good
4557 | SPS7 | ES | Pump Control Panel | 9 | Pump Control Panel | 1987 |  | 15000 | 0 | [8 empty] | 3 | [8 empty] | IMG_5058 | [12 empty] | good
4558 | SPS7 | ES | Pump #1 Starter | 9 | Pump #1 Starter | 1987 |  | 6000 | 0 | [8 empty] | 3 | [8 empty] | IMG_5059 | [12 empty] | good
4559 | SPS7 | ES | Pump #2 Starter | 9 | Pump #2 Starter | 1987 |  | 6000 | 0 | [8 empty] | 3 | [8 empty] | IMG_5061 | [12 empty] | good
4560 | SPS7 | ES | supply fan Starter | 9 | supply fan Starter | 1987 |  | 6000 | 0 | [8 empty] | 2 | [8 empty] | IMG_5063 | [12 empty] | good
4561 | SPS7 | ES | lighting panel | 9 | lighting panel | 1987 |  | 5000 | 0 | [8 empty] | 3 | [8 empty] | IMG_5066 | [12 empty] | good
4562 | SPS7 | ES | lighting transformer | 9 | lighting transformer, 7.5kVA | 1987 |  | 9000 | 0 | [8 empty] | 3 | [8 empty] | IMG_5070 | [12 empty] | good
4563 | SPS7 | ES | standby generator | 9 | standby generator, 75kW | 1987 |  | 140000 | 0 | [8 empty] | 3 | [8 empty] | IMG_5077 | [12 empty] | good
4564 | SPS7 | ES | Pump Ds and control keyboard | 10 | 2 Pump Ds and control keyboard | 1987 |  | 10000 | 0 | [8 empty] | 3 | [8 empty] | IMG_0953 | [12 empty] | good
4565 | SPS7 | ES | supply fan DS | 10 | supply fan DS | 1987 |  | 2000 | 0 | [8 empty] | 2 | [8 empty] | IMG_0982 | [12 empty] | good
4566 | SPS7 | ES | drywell lighting | 10 | 4 wall-pack fixtures | 1987 |  | 2400 | 0 | [8 empty] | 2 | [8 empty] | IMG_1006 | [12 empty] | good | to be replaced with class 1, div 2 LEDs in next upgrade
4567 | SPS7 | ES | wet well lighting | 8 | 3 fixtures | 1987 |  | 2400 | 0 | [8 empty] | 2 | [8 empty] | IMG_7225 | [12 empty] | good | to be replaced with LEDs in next upgrade
4569 | SPS7 | SIC | PLC RPU607 | 9 | PLC | 2014 |  | 60000 | 0 | [8 empty] | 4 | [8 empty] | IMG_5059 | [12 empty] | good
4570 | SPS7 | SIC | Autodialer | 9 | Autodialer | 2014 |  | 6000 | 0 | [8 empty] | 2 | [8 empty] | IMG_5079 | [12 empty] | good
4571 | SPS7 | SIC | level transmitter | 9 | level transmitter | 2014 |  | 12000 | 0 | [8 empty] | 3 | [8 empty] | IMG_5046 | [12 empty] | good
4572 | SPS7 | SIC | wet well floats | 8 | 3 floats | 2014 |  | 1500 | 0 | [8 empty] | 3 | [8 empty] | IMG_7242 | [12 empty] | good
4573 | SPS7 | SIC | dry well floats | 10 | 2 floats | 2014 |  | 1000 | 0 | [8 empty] | 3 | [8 empty] | IMG_7273 | [12 empty] | good
4574 | SPS7 | SIC | temperature switch | 10 | 2 temperature switches | 2014 |  | 3000 | 0 | [8 empty] | 2 | [8 empty] | IMG_0981 | [12 empty] | good
4575 | SPS7 | SIC | pressure gauge | 10 | 2 pressure gauges | 2014 |  | 2000 | 0 | [8 empty] | 2 | [8 empty] | IMG_0956 | [12 empty] | good
4576 | SPS7 | SIC | Anthenna | 7 | Anthenna | 2014 |  | 8000 | 0 | [8 empty] | 2 | [8 empty] | IMG_6173 | [12 empty] | good
4637 | SPS7 | BM | Intake damper | 10 | damper and actuator | 1985 |  | 4000 | 0 | [8 empty] | 3 | [8 empty] | IMG_6177 | [12 empty] | To be upgrade with generator replacement.
4638 | SPS7 | BM | Eyewash combo | 9 | eyewash | 2000 |  | 1000 | 0 | [8 empty] | 3 | [5 empty] | 2024 |  |  | IMG_6179 | [9 empty] | 3000 |  |  | Emergency eyewashes are required to provide tepid water. No water heater was installed. No instantaneous heater would be required.
4639 | SPS7 | BM | Backflow preventer | 9 | backflow, conbraco, , 1" | 2010 |  | 2500 | 0 | [8 empty] | 2 | [8 empty] | IMG_6184
4640 | SPS7 | BM | Generator Exhaust | 10 | ductwork and dampers | 1985 |  | 5000 | 0 | [8 empty] | 3 | [8 empty] | IMG_6187 | [12 empty] | Exhaust system to be replaced with generator replacement.
4641 | SPS7 | BM | Diesel Fuel system | 10 | fuel tank and piping | 2008 |  | 20000 | 0 | [8 empty] | 2 | [8 empty] | IMG_6198 | [12 empty] | It was noted on site that the diesel fuel system is not up to current TSSA regulations and will need to be upgraded in the future. AB inspection report provided detailed deficiency list.
4642 | SPS7 | BM | Dry well supply fan | 9 | Supply fan with duct heater | 1985 |  | 4500 | 0 | [8 empty] | 3 | [8 empty] | IMG_6203
4643 | SPS7 | BM | Generator Exhaust | 10 | ductwork and dampers | 1985 |  | 5000 | 0 | [8 empty] | 3 | [8 empty] | IMG_6211 | [12 empty] | Exhaust system to be replaced with generator replacement.
4644 | SPS7 | BM | Wet Well Intake | 8 | Intake Louver | 1985 |  | 1500 | 0 | [8 empty] | 2 | [5 empty] | 2022 |  |  | IMG_6165 | [9 empty] | 3000 |  |  | Intake louver does not meet the code requirement for clearances to an unclassified space. Adjacent door is 450mm. NFPA 820 points out that 0.9m from an opening is a classified area. Wet well intake should be sealed closed. New Intake vent from roof to be | Louver has some physical damage.
4645 | SPS7 | BM | Wet well Exhaust fan | 8 | exhaust fan and ductwork | 1985 |  | 7500 | 0 | [8 empty] | 2 | [8 empty] | IMG_6217 | [12 empty] | Fan enclosure has severe corrosion
4646 | SPS7 | BM | Sump Pump | 10 | sump pump | 2010 |  | 1500 | 0 | [8 empty] | 3 | [8 empty] | IMG_0964
4647 | SPS7 | BM | Unit Heater | 10 | unit heater, chromalox, , 5kw | 1984 |  | 2500 | 0 | [8 empty] | 2 | [8 empty] | IMG_0982
4648 | SPS7 | BM | Dehumidifier | 10 | Dehumidifier | 1984 |  | 3000 | 0 | [8 empty] | 3 | [8 empty] | IMG_0999 | [12 empty] | wall mounted unit did not appear to be working.
4692 | SPS7 | SC | Dry Well Concrete Structure | 10 |  | 1987 |  | 135000 | 0 | [8 empty] | 4 | [8 empty] | IMG_7235 | [12 empty] | fair
4693 | SPS7 | SC | Dry Well Masonry Blockwall | 10 |  | 1987 |  | 15000 | 0 | [8 empty] | 4 | [8 empty] | IMG_7299 | [12 empty] | good
4694 | SPS7 | SC | Dry Well Precast Concrete Roof | 10 |  | 1987 |  | 15000 | 0 | [8 empty] | 4 | [8 empty] | IMG_7299 | [12 empty] | good
4695 | SPS7 | SC | Dry Well Monorail Crane Beam | 10 |  | 1987 |  | 5000 | 0 | [8 empty] | 3 | [8 empty] | IMG_7299 | [12 empty] | good
4696 | SPS7 | SC | Dry Well Access Ladder | 10 | Upper | 1987 |  | 5000 | 0 | [8 empty] | 3 | [8 empty] | IMG_7289 | [12 empty] | Fair
4697 | SPS7 | SC | Dry Well Guardrail | 10 |  | 1987 |  | 4000 | 0 | [8 empty] | 3 | [8 empty] | IMG_7306 | [12 empty] | good
4698 | SPS7 | SC | Dry Well Aluminum Grating | 10 |  | 1987 |  | 1500 | 0 | [8 empty] | 3 | [8 empty] | IMG_7306 | [12 empty] | good
4699 | SPS7 | SC | Wet Well Concrete Structure | 8 |  | 1987 |  | 130000 | 0 | [8 empty] | 4 | [8 empty] | IMG_7270 | [12 empty] | fair | previous coating on walls has failed | active leaking and abandoned previous anchors at ladder
4700 | SPS7 | SC | Wet Well Aluminum Platform | 8 |  | 1987 |  | 10000 | 0 | [8 empty] | 3 | [8 empty] | IMG_7270 | [12 empty] | fair | minor pitting and calcium deposits
4701 | SPS7 | SC | Wet Well Access Ladder | 8 | Exterior to platform | 1987 |  | 5000 | 0 | [8 empty] | 3 | [8 empty] | IMG_7270 | [12 empty] | fair | minor pitting and calcium deposits
4702 | SPS7 | SC | Wet Well Access Ladder | 8 | Platform to base | 1987 |  | 5000 | 0 | [8 empty] | 3 | [8 empty] | IMG_7246 | [12 empty] | fair | minor pitting and calcium deposits
4703 | SPS7 | SC | Wet Well Masonry Blockwall | 8 |  | 1987 |  | 6000 | 0 | [8 empty] | 4 | [8 empty] | IMG_7225 | [12 empty] | fair
4704 | SPS7 | SC | Wet Well Monorail Crane Beam | 8 |  | 1987 |  | 2000 | 0 | [8 empty] | 2 | [8 empty] | IMG_7225 | [12 empty] | fair | minor corrosion noted
4705 | SPS7 | AC | Exterior Brick Veneer | 9 |  | 1987 |  | 12000 | 0 | [8 empty] | 1 | [8 empty] | IMG_7223 | [12 empty] | minor cracking in mortar
4706 | SPS7 | AC | Roofing System | 9 |  | 1987 |  | 10000 | 0 | [8 empty] | 2 | [8 empty] | IMG_7233 | [12 empty] | fair
4707 | SPS7 | AC | Wet Well Wall and Ceiling Paint | 8 |  | 1987 |  | 1000 | 0 | [8 empty] | 1 | [8 empty] | IMG_7225 | [12 empty] | fair
4708 | SPS7 | AC | Wet Well Access Door | 8 |  | 1987 |  | 3500 | 0 | [8 empty] | 1 | [8 empty] | IMG_7227 | [12 empty] | local missing paint
4709 | SPS7 | AC | Dry Well Access Door | 10 |  | 1987 |  | 5500 | 0 | [8 empty] | 1 | [8 empty] | IMG_7231 | [12 empty] | fair
4710 | SPS7 | AC | Dry Well Wall and Ceiling Paint | 10 |  | 1987 |  | 15000 | 0 | [8 empty] | 1 | [8 empty] | IMG_7277 | [12 empty] | localized missing paint
4711 | SPS7 | SC | Dry Well Access Ladder | 10 | Lower | 1987 |  | 5000 | 0 | [8 empty] | 3 | [8 empty] | IMG_7289 | [12 empty] | Fair
4712 | SPS7 | SC | Dry Well Access Platform | 10 |  | 1987 |  | 5000 | 0 | [8 empty] | 3 | [8 empty] | IMG_7289 | [12 empty] | Fair
4713 | SPS7 | SC | Wet Well Precast Concrete Roof | 8 |  | 1987 |  | 1500 | 0 | [8 empty] | 4 | [8 empty] | IMG_7225 | [12 empty] | fair