## Sheet1
seqNum | facility | CategoryCode | assetName | LocationTag | Description | installYear | remainingESL | repCost | InspectionYear | CalcProcess | Process | building | inspectorName | assetTag | LocationORIGINAL | installationDate | condition | COF | defect1 | defect2 | defect3 | observations | RehabRepairCost | RehabRepairYear | RehabRepairCost2 | RehabRepairYear2 | photoName | repProjectName | rehabProjectName | rehab2ProjectName | LifeCycleCategory | TransmitterModel | TransducerModel | TransducerSerial | Status | rehabComment1 | rehabCost1 | rehabComment2 | rehabCost2 | defect1Input | defect2Input | defect3Input | InstType | InstMeva | ServiceArea | FacilityType | SerialNo | Parent | RotatingItem | Site | manufacturer
4481 | SPS8 | SW | Bollard No.1 | 11 |  | 1979 | 6 | 1000 | 0 | [7 empty] | 3 | 2 | Concrete base of the bollard is fully exposed. fair condition was observed. |  |  | The asset was observed to be in fair condition.Bury the concrete base of the bollard. Asset to be replaced in the intermediate term. | 185 |  |  |  | IMG_2102 | SPS8 Capital Project 1 | [7 empty] | Bury the concrete base of the bollard. | 185 |  |  | Concrete base of the bollard is fully exposed. Fair condition.
4482 | SPS8 | SW | Bollard No.2 | 11 |  | 1979 | 6 | 1000 | 0 | [7 empty] | 3 | 2 | Concrete base of the bollard is fully exposed. fair condition was observed. |  |  | The asset was observed to be in fair condition.Bury the concrete base of the bollard. Asset to be replaced in the intermediate term. | 185 |  |  |  | IMG_2104 | SPS8 Capital Project 1 | [7 empty] | Bury the concrete base of the bollard. | 185 |  |  | Concrete base of the bollard is fully exposed. Fair condition.
4483 | SPS8 | SW | Bollard No.3 | 11 |  | 1979 | 6 | 1000 | 0 | [7 empty] | 3 | 2 | Concrete base of the bollard is fully exposed. fair condition was observed. |  |  | The asset was observed to be in fair condition.Bury the concrete base of the bollard. Asset to be replaced in the intermediate term. | 185 |  |  |  | IMG_2108 | SPS8 Capital Project 1 | [7 empty] | Bury the concrete base of the bollard. | 185 |  |  | Concrete base of the bollard is fully exposed. Fair condition.
4484 | SPS8 | SW | Pavement | 11 | Approximately 60 m2 of pavement for access road | 1979 | 6 | 7800 | 0 | [7 empty] | 3 | 2 | Minor cracks observed on the pavement. good condition was observed. |  |  | The asset was observed to be in fair condition.Minor crack repair/filling on the pavement Asset to be replaced in the intermediate term. | 4900 |  | 5100 |  | IMG_7316 | SPS8 Capital Project 1 | [7 empty] | Minor crack repair/filling on the pavement | 4900 | Asphalt resurfacing | 5100 | Minor cracks observed on the pavement. Good condition.
4485 | SPS8 | SW | Maintenance Hole No.1 | 11 |  | 1979 | 6 | 30000 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_2097 | SPS8 Capital Project 1 | [11 empty] | good
4486 | SPS8 | SW | Stormwater Culvert | 11 | Approximately 6.5 m in length and 300 mm in diameter | 1979 | 6 | 6700 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_2095 | SPS8 Capital Project 1 | [11 empty] | good
4487 | SPS8 | SW | Swale No.1 | 11 | Approximately 6.5 m in length, 2 m in width and 0.5 m in depth | 1979 | 6 | 800 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition.Clear debris from the swale Asset to be replaced in the intermediate term. | 550 |  |  |  | IMG_2083 | SPS8 Capital Project 1 | [7 empty] | Clear debris from the swale | 550 |  |  | good
4488 | SPS8 | SW | Swale No.2 | 11 | Approximately 5 m in length, 2.5 m in width and 0.5 m in depth | 1979 | 6 | 600 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition.Clear debris from the swale. Asset to be replaced in the intermediate term. | 530 |  |  |  | IMG_2091 | SPS8 Capital Project 1 | [7 empty] | Clear debris from the swale. | 530 |  |  | good
4521 | SPS8 | PM | Wastewater Pump 1 | 14 | Submersible, dry pit, centrifugal wastewater pump, 22 kW, 1750 rpm, 600/3/60; by Flygt model 3170.180; explosion proof enclosure (Class 1, Zone 1); | 1979 | 6 | 35000 | 0 | [7 empty] | 2 | 4 |  | Needs regular maintenance was observed. |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_1084 | SPS8 Capital Project 1 | [11 empty] | good | needs regular maintenance
4522 | SPS8 | PM | Wastewater Pump 2 | 14 | Submersible, dry pit, centrifugal wastewater pump, 22 kW, 1750 rpm, 600/3/60; by Flygt model 3170.180; explosion proof enclosure (Class 1, Zone 1); | 1979 | 6 | 35000 | 0 | [7 empty] | 2 | 4 |  | Needs regular maintenance was observed. |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_1071 | SPS8 Capital Project 1 | [11 empty] | good | needs regular maintenance
4523 | SPS8 | PM | Pump 1 Suction Gate Valve | 14 | Isolation gate valve, 200 DIA, Flanged, NRS, Pump #1 suction line, by Seguro | 1979 | 2 | 3000 | 0 | [7 empty] | 3 | 4 | Fair condition was observed. | Maintenance was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_1087 | SPS8 Capital Project 1 | [11 empty] | Fair condition | maintenance
4524 | SPS8 | PM | Pump 1 Discharge Gate Valve | 14 | Isolation gate valve, Pump #1 discharge line, 200 DIA, flanged, NRS, by Seguro | 1984 | 2 | 3000 | 0 | [7 empty] | 3 | 4 | Fair condition was observed. | Maintenance was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_1092 | SPS8 Capital Project 1 | [11 empty] | Fair Condition | maintenance
4525 | SPS8 | PM | Pump 1 Discharge Swing Check Valve | 14 | AWWA Swing Check Valve valve, with lever and spring, Pump #1 discharge line, 200 DIA, flanged, by Kennedy | 1984 | 2 | 5000 | 0 | [7 empty] | 3 | 4 | Fair condition was observed. | Maintenance was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_1091 | SPS8 Capital Project 1 | [11 empty] | Fair condition | maintenance
4526 | SPS8 | PM | Pump 2 Suction Gate Valve | 14 | Isolation gate valve, 200 DIA, Flanged, NRS, Pump #2 suction line, by Seguro | 1979 | 2 | 3000 | 0 | [7 empty] | 3 | 4 | Fair condition was observed. | Maintenance was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_1092 | SPS8 Capital Project 1 | [11 empty] | Fair condition | maintenance
4527 | SPS8 | PM | Pump 2 Discharge Gate Valve | 14 | Isolation gate valve, Pump #2 discharge line, 200 DIA, flanged, NRS, by Seguro | 1979 | 2 | 3000 | 0 | [7 empty] | 3 | 4 | Fair condition was observed. | Maintenance was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_1077 | SPS8 Capital Project 1 | [11 empty] | Fair condition | maintenance
4528 | SPS8 | PM | Pump 2 Discharge Swing Check Valve | 14 | AWWA Swing Check Valve valve, with lever and spring, Pump #2 discharge line, 200 DIA, flanged, by Kennedy | 1984 | 2 | 5000 | 0 | [7 empty] | 3 | 4 | Fair condition was observed. | Maintenance was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_1076 | SPS8 Capital Project 1 | [11 empty] | fair condition | maintenance
4529 | SPS8 | PM | Station Piping | 14 | DI, suction and discharge piping and fittings of 200 DIA; victaulic couplings | 1979 | 2 | 10000 | 0 | [7 empty] | 3 | 4 | Fair condition was observed. | Maintenance was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_1046 | SPS8 Capital Project 1 | [11 empty] | fair condition | maintenance
4530 | SPS8 | PM | Bypass Gate Valve | 11 | Bypass gate valve in bypass MH, 100 DIA flanged c/w 100 DIA, 90 deg elbow (up) and blind flange. - backflow preventing mechanism shall be installed in the drain to the wet well. | 1979 | 2 | 3000 | 0 | [7 empty] | 3 | 3 | Mh was flooded to view the valve condition was observed. | A backflow preventing mechanism shall be installed in the drain to the wet well. drain shall be cleaned to make it functional was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_1048 | SPS8 Capital Project 1 | [11 empty] | MH was flooded to view the valve condition | A backflow preventing mechanism shall be installed in the drain to the wet well. Drain shall be cleaned to make it functional.
4531 | SPS8 | PM | Gate valve | 11 | Force main 200 DIA isolation gate valve; NRS, located in pass valve MH. | 1979 | 2 | 3000 | 0 | [7 empty] | 3 | 4 | Mh was flooded to view the valve condition was observed. | A backflow preventing mechanism shall be installed in the drain to the wet well. drain shall be cleaned to make it functional was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_1048 | SPS8 Capital Project 1 | [11 empty] | MH was flooded to view the valve condition | A backflow preventing mechanism shall be installed in the drain to the wet well. Drain shall be cleaned to make it functional.
4532 | SPS8 | PM | Bar screen and trash basket | 12 | Bar screen and trash basket. | 1979 | 2 | 8000 | 0 | [7 empty] | 3 | 3 | Fiar condition was observed. | Maintenance was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_7336 | SPS8 Capital Project 1 | [11 empty] | fiar condition | maintenance
4533 | SPS8 | PM | Overflow pipe | 12 | 400 DIA overflow pipe with manual gate to open-close | 1979 | 2 | 10000 | 0 | [7 empty] | 3 | 3 | Fiar condition was observed. | Maintenance; a backflow preventing mechanism shall be installed in the wet well overflow was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_7339 | SPS8 Capital Project 1 | [11 empty] | Fiar condition | maintenance; a backflow preventing mechanism shall be installed in the wet well overflow.
4595 | SPS8 | ES | outdoor lighting | 11 | 2 fixtures | 1984 | 6 | 1000 | 0 | [7 empty] | 2 | 2 |  | To be replaced with leds in next upgrade was observed. |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5087 | SPS8 Capital Project 1 | [11 empty] | good | to be replaced with LEDs in next upgrade
4596 | SPS8 | ES | hydro meter | 11 |  | 2010 | 14 | 5000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. |  |  |  |  | IMG_5089 | SPS8 Capital Project 2 | [11 empty] | good
4597 | SPS8 | ES | main level lighting | 13 |  | 1984 | 6 | 1600 | 0 | [7 empty] | 2 | 2 |  | To be replaced with leds in next upgrade was observed. |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5108 | SPS8 Capital Project 1 | [11 empty] | good | to be replaced with LEDs in next upgrade
4598 | SPS8 | ES | automatic transfer switch | 13 |  | 1984 | 6 | 30000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5110 | SPS8 Capital Project 1 | [11 empty] | good
4599 | SPS8 | ES | Main Breaker | 13 |  | 1984 | 6 | 12000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5118 | SPS8 Capital Project 1 | [11 empty] | good
4600 | SPS8 | ES | Pump Control Panel | 13 |  | 1984 | 6 | 15000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5129 | SPS8 Capital Project 1 | [11 empty] | good
4601 | SPS8 | ES | Pump #2 Starter | 13 |  | 1984 | 6 | 6000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5133 | SPS8 Capital Project 1 | [11 empty] | good
4602 | SPS8 | ES | supply fan Starter | 13 |  | 1984 | 6 | 6000 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5134 | SPS8 Capital Project 1 | [11 empty] | good
4603 | SPS8 | ES | lighting panel | 13 |  | 1984 | 6 | 5000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5136 | SPS8 Capital Project 1 | [11 empty] | good
4604 | SPS8 | ES | lighting transformer | 13 |  | 1984 | 6 | 9000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5142 | SPS8 Capital Project 1 | [11 empty] | good
4605 | SPS8 | ES | standby generator | 13 |  | 1984 | 6 | 140000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | PXL_20210518_143537219 | SPS8 Capital Project 1 | [11 empty] | good
4606 | SPS8 | ES | supply fan DS | 14 |  | 1984 | 6 | 2000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_1055 | SPS8 Capital Project 1 | [11 empty] | good
4607 | SPS8 | ES | drywell lighting | 14 |  | 1984 | 6 | 2400 | 0 | [7 empty] | 2 | 2 |  | To be replaced with leds in next upgrade was observed. |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_1051 | SPS8 Capital Project 1 | [11 empty] | good | to be replaced with LEDs in next upgrade
4608 | SPS8 | ES | exit sign | 13 |  | 2014 | 18 | 500 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. |  |  |  |  | IMG_5099 | SPS8 Capital Project 2 | [11 empty] | good
4609 | SPS8 | ES | MCC | 13 |  | 1984 | 6 | 35000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5121 | SPS8 Capital Project 1 | [11 empty] | good
4610 | SPS8 | ES | Capacitors | 13 |  | 1984 | 6 | 2500 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5127 | SPS8 Capital Project 1 | [11 empty] | good
4611 | SPS8 | ES | Pump #1 Starter | 13 |  | 1984 | 6 | 6000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5131 | SPS8 Capital Project 1 | [11 empty] | good
4612 | SPS8 | ES | Pump Ds and control keyboard | 14 |  | 1984 | 6 | 10000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_1062 | SPS8 Capital Project 1 | [11 empty] | good
4613 | SPS8 | ES | wet well lighting | 12 |  | 1984 | 6 | 2400 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_1126 | SPS8 Capital Project 1 | [11 empty] | good
4614 | SPS8 | SIC | PLC RPU607 | 13 |  | 2014 | 8 | 60000 | 0 | [7 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5102 | SPS8 Capital Project 1 | [11 empty] | good
4615 | SPS8 | SIC | Autodialer | 13 |  | 2014 | 8 | 6000 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5109 | SPS8 Capital Project 1 | [11 empty] | good
4616 | SPS8 | SIC | wet well floats | 12 |  | 1984 | 6 | 1500 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_1125 | SPS8 Capital Project 1 | [11 empty] | good
4617 | SPS8 | SIC | dry well floats | 14 |  | 1984 | 6 | 1000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_1066 | SPS8 Capital Project 1 | [11 empty] | good
4618 | SPS8 | SIC | temperature switch | 14 |  | 1984 | 6 | 3000 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_1064 | SPS8 Capital Project 1 | [11 empty] | good
4619 | SPS8 | SIC | pressure gauge | 14 |  | 1984 | 6 | 2000 | 0 | [7 empty] | 3 | 2 |  | To be replaced in near future was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_1074 | SPS8 Capital Project 1 | [11 empty] | fair | to be replaced in near future
4620 | SPS8 | SIC | level transmitter | 13 |  | 2014 | 8 | 12000 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_5113 | SPS8 Capital Project 1 | [11 empty] | good
4621 | SPS8 | SIC | Anthenna | 11 |  | 2014 | 8 | 8000 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | [5 empty] | SPS8 Capital Project 1 | [11 empty] | good
4649 | SPS8 | BM | Wet Well Exhaust Fan | 12 | Exhaust Fan | 1984 | 2 | 5000 | 0 | [7 empty] | 3 | 3 | Fan enclosure had severe corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_6237 | SPS8 Capital Project 1 | [11 empty] | Fan enclosure had severe corrosion.
4650 | SPS8 | BM | Backflow preventer | 12 | backflow, conbraco, , 1" | 2010 | 19 | 2500 | 0 | [7 empty] | 3 | 2 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the long term. |  |  |  |  | IMG_6245 | SPS8 Capital Project 2
4651 | SPS8 | BM | Intake Air Damper | 13 | damper and actuator | 2003 | 12 | 4000 | 0 | [7 empty] | 3 | 3 | Intake system to be replaced with generator replacement was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term. |  |  |  |  | IMG_6255 | SPS8 Capital Project 2 | [11 empty] | Intake system to be replaced with generator replacement.
4652 | SPS8 | BM | Eyewash sink combo | 13 | Eyewash | 2000 | 9 | 1000 | 0 | [7 empty] | 3 | 2 | Emergency eyewashes are required to provide tepid water. no water heater was installed. no instantaneous heater would be required was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 3000 |  |  |  |  | SPS8 Capital Project 1 | [8 empty] | 3000 |  |  | Emergency eyewashes are required to provide tepid water. No water heater was installed. No instantaneous heater would be required.
4653 | SPS8 | BM | Unit Heater | 13 | unit heater, chromalox, BUH-07D, , 7.5 kw | 1985 | 6 | 3000 | 0 | [7 empty] | 3 | 2 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_6259 | SPS8 Capital Project 1
4654 | SPS8 | BM | Dry well supply fan | 13 | fan and inline duct heater | 1985 | 6 | 4500 | 0 | [7 empty] | 3 | 2 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_6266 | SPS8 Capital Project 1
4655 | SPS8 | BM | Diesel Fuel System | 13 | fuel tank and piping | 2008 | 17 | 20000 | 0 | [7 empty] | 3 | 2 | It was noted on site that the diesel fuel system is not up to current tssa regulations and will need to be upgraded in the future. ab inspection report provided detailed deficiency list was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term. |  |  |  |  | IMG_6270 | SPS8 Capital Project 2 | [11 empty] | It was noted on site that the diesel fuel system is not up to current TSSA regulations and will need to be upgraded in the future. AB inspection report provided detailed deficiency list.
4656 | SPS8 | BM | Intake Damper #2 | 13 | damper for supply fan | 1985 | 6 | 2000 | 0 | [7 empty] | 3 | 2 | Damper used with dry well supply fan was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | [5 empty] | SPS8 Capital Project 1 | [11 empty] | Damper used with dry well supply fan.
4657 | SPS8 | BM | Generator Exhaust | 13 | ductwork and damper | 1985 | 2 | 4000 | 0 | [7 empty] | 3 | 3 | Exhaust system to be replace when generator is being replaced was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. |  |  |  |  | IMG_6297 | SPS8 Capital Project 1 | [11 empty] | Exhaust system to be replace when generator is being replaced.
4658 | SPS8 | BM | Dehumidifer | 14 | Dehumidifer, Canadian Tire, 43-5405-6, 09818460hk, 7.0L/24hr | 2003 | 12 | 1500 | 0 | [7 empty] | 3 | 2 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the long term. |  |  |  |  | IMG_1050 | SPS8 Capital Project 2
4659 | SPS8 | BM | Sump Pump | 14 | sump pump, myers, MW50-11P, 030C14D, | 2003 | 12 | 1500 | 0 | [7 empty] | 3 | 3 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the long term. |  |  |  |  | IMG_1067 | SPS8 Capital Project 2
4714 | SPS8 | AC | Exterior Brick Veneer | 13 |  | 1987 | 6 | 12000 | 0 | [7 empty] | 3 | 1 |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_7316 | SPS8 Capital Project 1 | [11 empty] | fair
4715 | SPS8 | AC | Roofing System | 13 |  | 1987 | 6 | 10000 | 0 | [7 empty] | 3 | 2 |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_7312 | SPS8 Capital Project 1 | [11 empty] | fair
4716 | SPS8 | AC | Wet Well Wall and Ceiling Paint | 12 |  | 1987 | 6 | 1000 | 0 | [7 empty] | 3 | 1 |  |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_7314 | SPS8 Capital Project 1 | [11 empty] | fair
4717 | SPS8 | AC | Wet Well Access Door | 12 |  | 1987 | 6 | 3500 | 0 | [7 empty] | 3 | 1 |  | Localized missing paint was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_7313 | SPS8 Capital Project 1 | [11 empty] | fair | localized missing paint
4718 | SPS8 | AC | Dry Well Access Door | 14 |  | 1987 | 6 | 5500 | 0 | [7 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_7316 | SPS8 Capital Project 1 | [11 empty] | good
4719 | SPS8 | AC | Dry Well Wall and Ceiling Paint | 14 |  | 1987 | 6 | 15000 | 0 | [7 empty] | 3 | 1 | Localized missing paint was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | IMG_7374 | SPS8 Capital Project 1 | [11 empty] | localized missing paint
4720 | SPS8 | SC | Wet Well Concrete Structure | 12 |  | 1987 | 26 | 130000 | 0 | [7 empty] | 3 | 4 |  | Previous coating on walls has failed was observed. |  | The asset was observed to be in fair condition. Provisions for structural repairs. Asset to be replaced at the end of remaining service life. |  | 2023 |  | 2038 | IMG_7349 |  | SPS8 Capital Project 1 | SPS8 Capital Project 2 | [9 empty] | fair | previous coating on walls has failed
4721 | SPS8 | SC | Wet Well Aluminum Platform | 12 |  | 1987 | 26 | 10000 | 0 | [7 empty] | 3 | 3 |  |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7349 | [12 empty] | fair
4722 | SPS8 | SC | Wet Well Access Ladder | 12 | Exterior to platform | 1987 | 26 | 5000 | 0 | [7 empty] | 3 | 3 |  |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7349 | [12 empty] | fair
4723 | SPS8 | SC | Wet Well Access Ladder | 12 | Platform to base | 1987 | 26 | 5000 | 0 | [7 empty] | 3 | 2 |  |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7343 | [12 empty] | fair
4724 | SPS8 | SC | Wet Well Masonry Blockwall | 12 |  | 1987 | 26 | 6000 | 0 | [7 empty] | 3 | 4 |  |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7314 | [12 empty] | fair
4725 | SPS8 | SC | Wet Well Precast Concrete Roof | 12 |  | 1987 | 26 | 1500 | 0 | [7 empty] | 3 | 4 |  |  |  | The asset was observed to be in fair condition. Provisions for structural repairs. Asset to be replaced at the end of remaining service life. |  | 2023 |  | 2038 | IMG_7314 |  | SPS8 Capital Project 1 | SPS8 Capital Project 2 | [9 empty] | fair
4726 | SPS8 | SC | Wet Well Monorail Crane Beam | 12 |  | 1987 | 26 | 2000 | 0 | [7 empty] | 3 | 2 | Minor corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7314 | [12 empty] | minor corrosion
4727 | SPS8 | SC | Dry Well Concrete Structure | 14 |  | 1987 | 26 | 135000 | 0 | [7 empty] | 3 | 4 |  |  |  | The asset was observed to be in fair condition. Provisions for structural repairs. Asset to be replaced at the end of remaining service life. |  | 2023 |  | 2038 | IMG_7366 |  | SPS8 Capital Project 1 | SPS8 Capital Project 2 | [9 empty] | fair
4728 | SPS8 | SC | Dry Well Access Ladder | 14 | Lower | 1987 | 26 | 5000 | 0 | [7 empty] | 3 | 2 |  |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7366 | [12 empty] | fair
4729 | SPS8 | SC | Dry Well Access Ladder | 14 | Upper | 1987 | 26 | 5000 | 0 | [7 empty] | 3 | 2 |  |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7366 | [12 empty] | fair
4730 | SPS8 | SC | Dry Well Access Platform | 14 |  | 1987 | 26 | 5000 | 0 | [7 empty] | 3 | 2 |  |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7366 | [12 empty] | fair
4731 | SPS8 | SC | Dry Well Masonry Blockwall | 14 |  | 1987 | 26 | 15000 | 0 | [7 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7374 | [12 empty] | good
4732 | SPS8 | SC | Dry Well Precast Concrete Roof | 14 |  | 1987 | 26 | 15000 | 0 | [7 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. |  | 2031 |  |  | IMG_7374 |  | SPS8 Capital Project 1 | [10 empty] | good
4733 | SPS8 | SC | Dry Well Monorail Crane Beam | 14 |  | 1987 | 26 | 5000 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7374 | [12 empty] | good
4734 | SPS8 | SC | Dry Well Guardrail | 14 |  | 1987 | 26 | 4000 | 0 | [7 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7372 | [12 empty] | good
4735 | SPS8 | SC | Dry Well Aluminum Grating | 14 |  | 1987 | 26 | 1500 | 0 | [7 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | IMG_7372 | [12 empty] | good