## Sheet1
seqNum | facility | CategoryCode | assetName | LocationTag | Description | installYear | remainingESL | repCost | InspectionYear | CalcProcess | Process | building | inspectorName | assetTag | LocationORIGINAL | installationDate | condition | COF | defect1 | defect2 | defect3 | observations | RehabRepairCost | RehabRepairYear | RehabRepairCost2 | RehabRepairYear2 | photoName | repProjectName | rehabProjectName | rehab2ProjectName | LifeCycleCategory | TransmitterModel | TransducerModel | TransducerSerial | Status | rehabComment1 | rehabCost1 | rehabComment2 | rehabCost2 | defect1Input | defect2Input | defect3Input | InstType | InstMeva | ServiceArea | FacilityType | SerialNo | Parent | RotatingItem | Site | manufacturer
4481 | SPS8 | SW | Bollard No.1 | 11 |  | 1979 |  | 1000 | 0 | [8 empty] | 2 | [5 empty] | 2026 |  |  | IMG_2102 | [8 empty] | Bury the concrete base of the bollard. | 185 |  |  | Concrete base of the bollard is fully exposed. Fair condition.
4482 | SPS8 | SW | Bollard No.2 | 11 |  | 1979 |  | 1000 | 0 | [8 empty] | 2 | [5 empty] | 2026 |  |  | IMG_2104 | [8 empty] | Bury the concrete base of the bollard. | 185 |  |  | Concrete base of the bollard is fully exposed. Fair condition.
4483 | SPS8 | SW | Bollard No.3 | 11 |  | 1979 |  | 1000 | 0 | [8 empty] | 2 | [5 empty] | 2026 |  |  | IMG_2108 | [8 empty] | Bury the concrete base of the bollard. | 185 |  |  | Concrete base of the bollard is fully exposed. Fair condition.
4484 | SPS8 | SW | Pavement | 11 | Approximately 60 m2 of pavement for access road | 1979 |  | 7800 | 0 | [8 empty] | 2 | [5 empty] | 2026 |  | 2031 | IMG_7316 | [8 empty] | Minor crack repair/filling on the pavement | 4900 | Asphalt resurfacing | 5100 | Minor cracks observed on the pavement. Good condition.
4485 | SPS8 | SW | Maintenance Hole No.1 | 11 |  | 1979 |  | 30000 | 0 | [8 empty] | 2 | [8 empty] | IMG_2097 | [12 empty] | good
4486 | SPS8 | SW | Stormwater Culvert | 11 | Approximately 6.5 m in length and 300 mm in diameter | 1979 |  | 6700 | 0 | [8 empty] | 2 | [8 empty] | IMG_2095 | [12 empty] | good
4487 | SPS8 | SW | Swale No.1 | 11 | Approximately 6.5 m in length, 2 m in width and 0.5 m in depth | 1979 |  | 800 | 0 | [8 empty] | 2 | [5 empty] | 2026 |  |  | IMG_2083 | [8 empty] | Clear debris from the swale | 550 |  |  | good
4488 | SPS8 | SW | Swale No.2 | 11 | Approximately 5 m in length, 2.5 m in width and 0.5 m in depth | 1979 |  | 600 | 0 | [8 empty] | 2 | [5 empty] | 2026 |  |  | IMG_2091 | [8 empty] | Clear debris from the swale. | 530 |  |  | good
4521 | SPS8 | PM | Wastewater Pump 1 | 14 | Submersible, dry pit, centrifugal wastewater pump, 22 kW, 1750 rpm, 600/3/60; by Flygt model 3170.180; explosion proof enclosure (Class 1, Zone 1); | 1979 |  | 35000 | 0 | [8 empty] | 4 | [8 empty] | IMG_1084 | [12 empty] | good | needs regular maintenance
4522 | SPS8 | PM | Wastewater Pump 2 | 14 | Submersible, dry pit, centrifugal wastewater pump, 22 kW, 1750 rpm, 600/3/60; by Flygt model 3170.180; explosion proof enclosure (Class 1, Zone 1); | 1979 |  | 35000 | 0 | [8 empty] | 4 | [8 empty] | IMG_1071 | [12 empty] | good | needs regular maintenance
4523 | SPS8 | PM | Pump 1 Suction Gate Valve | 14 | Isolation gate valve, 200 DIA, Flanged, NRS, Pump #1 suction line, by Seguro | 1979 |  | 3000 | 0 | [8 empty] | 4 | [8 empty] | IMG_1087 | [12 empty] | Fair condition | maintenance
4524 | SPS8 | PM | Pump 1 Discharge Gate Valve | 14 | Isolation gate valve, Pump #1 discharge line, 200 DIA, flanged, NRS, by Seguro | 1984 |  | 3000 | 0 | [8 empty] | 4 | [8 empty] | IMG_1092 | [12 empty] | Fair Condition | maintenance
4525 | SPS8 | PM | Pump 1 Discharge Swing Check Valve | 14 | AWWA Swing Check Valve valve, with lever and spring, Pump #1 discharge line, 200 DIA, flanged, by Kennedy | 1984 |  | 5000 | 0 | [8 empty] | 4 | [8 empty] | IMG_1091 | [12 empty] | Fair condition | maintenance
4526 | SPS8 | PM | Pump 2 Suction Gate Valve | 14 | Isolation gate valve, 200 DIA, Flanged, NRS, Pump #2 suction line, by Seguro | 1979 |  | 3000 | 0 | [8 empty] | 4 | [8 empty] | IMG_1092 | [12 empty] | Fair condition | maintenance
4527 | SPS8 | PM | Pump 2 Discharge Gate Valve | 14 | Isolation gate valve, Pump #2 discharge line, 200 DIA, flanged, NRS, by Seguro | 1979 |  | 3000 | 0 | [8 empty] | 4 | [8 empty] | IMG_1077 | [12 empty] | Fair condition | maintenance
4528 | SPS8 | PM | Pump 2 Discharge Swing Check Valve | 14 | AWWA Swing Check Valve valve, with lever and spring, Pump #2 discharge line, 200 DIA, flanged, by Kennedy | 1984 |  | 5000 | 0 | [8 empty] | 4 | [8 empty] | IMG_1076 | [12 empty] | fair condition | maintenance
4529 | SPS8 | PM | Station Piping | 14 | DI, suction and discharge piping and fittings of 200 DIA; victaulic couplings | 1979 |  | 10000 | 0 | [8 empty] | 4 | [8 empty] | IMG_1046 | [12 empty] | fair condition | maintenance
4530 | SPS8 | PM | Bypass Gate Valve | 11 | Bypass gate valve in bypass MH, 100 DIA flanged c/w 100 DIA, 90 deg elbow (up) and blind flange. - backflow preventing mechanism shall be installed in the drain to the wet well. | 1979 |  | 3000 | 0 | [8 empty] | 3 | [8 empty] | IMG_1048 | [12 empty] | MH was flooded to view the valve condition | A backflow preventing mechanism shall be installed in the drain to the wet well. Drain shall be cleaned to make it functional.
4531 | SPS8 | PM | Gate valve | 11 | Force main 200 DIA isolation gate valve; NRS, located in pass valve MH. | 1979 |  | 3000 | 0 | [8 empty] | 4 | [8 empty] | IMG_1048 | [12 empty] | MH was flooded to view the valve condition | A backflow preventing mechanism shall be installed in the drain to the wet well. Drain shall be cleaned to make it functional.
4532 | SPS8 | PM | Bar screen and trash basket | 12 | Bar screen and trash basket. | 1979 |  | 8000 | 0 | [8 empty] | 3 | [8 empty] | IMG_7336 | [12 empty] | fiar condition | maintenance
4533 | SPS8 | PM | Overflow pipe | 12 | 400 DIA overflow pipe with manual gate to open-close | 1979 |  | 10000 | 0 | [8 empty] | 3 | [8 empty] | IMG_7339 | [12 empty] | Fiar condition | maintenance; a backflow preventing mechanism shall be installed in the wet well overflow.
4595 | SPS8 | ES | outdoor lighting | 11 | 2 fixtures | 1984 |  | 1000 | 0 | [8 empty] | 2 | [8 empty] | IMG_5087 | [12 empty] | good | to be replaced with LEDs in next upgrade
4596 | SPS8 | ES | hydro meter | 11 |  | 2010 |  | 5000 | 0 | [8 empty] | 3 | [8 empty] | IMG_5089 | [12 empty] | good
4597 | SPS8 | ES | main level lighting | 13 |  | 1984 |  | 1600 | 0 | [8 empty] | 2 | [8 empty] | IMG_5108 | [12 empty] | good | to be replaced with LEDs in next upgrade
4598 | SPS8 | ES | automatic transfer switch | 13 |  | 1984 |  | 30000 | 0 | [8 empty] | 3 | [8 empty] | IMG_5110 | [12 empty] | good
4599 | SPS8 | ES | Main Breaker | 13 |  | 1984 |  | 12000 | 0 | [8 empty] | 3 | [8 empty] | IMG_5118 | [12 empty] | good
4600 | SPS8 | ES | Pump Control Panel | 13 |  | 1984 |  | 15000 | 0 | [8 empty] | 3 | [8 empty] | IMG_5129 | [12 empty] | good
4601 | SPS8 | ES | Pump #2 Starter | 13 |  | 1984 |  | 6000 | 0 | [8 empty] | 3 | [8 empty] | IMG_5133 | [12 empty] | good
4602 | SPS8 | ES | supply fan Starter | 13 |  | 1984 |  | 6000 | 0 | [8 empty] | 2 | [8 empty] | IMG_5134 | [12 empty] | good
4603 | SPS8 | ES | lighting panel | 13 |  | 1984 |  | 5000 | 0 | [8 empty] | 3 | [8 empty] | IMG_5136 | [12 empty] | good
4604 | SPS8 | ES | lighting transformer | 13 |  | 1984 |  | 9000 | 0 | [8 empty] | 3 | [8 empty] | IMG_5142 | [12 empty] | good
4605 | SPS8 | ES | standby generator | 13 |  | 1984 |  | 140000 | 0 | [8 empty] | 3 | [8 empty] | PXL_20210518_143537219 | [12 empty] | good
4606 | SPS8 | ES | supply fan DS | 14 |  | 1984 |  | 2000 | 0 | [8 empty] | 3 | [8 empty] | IMG_1055 | [12 empty] | good
4607 | SPS8 | ES | drywell lighting | 14 |  | 1984 |  | 2400 | 0 | [8 empty] | 2 | [8 empty] | IMG_1051 | [12 empty] | good | to be replaced with LEDs in next upgrade
4608 | SPS8 | ES | exit sign | 13 |  | 2014 |  | 500 | 0 | [8 empty] | 2 | [8 empty] | IMG_5099 | [12 empty] | good
4609 | SPS8 | ES | MCC | 13 |  | 1984 |  | 35000 | 0 | [8 empty] | 3 | [8 empty] | IMG_5121 | [12 empty] | good
4610 | SPS8 | ES | Capacitors | 13 |  | 1984 |  | 2500 | 0 | [8 empty] | 3 | [8 empty] | IMG_5127 | [12 empty] | good
4611 | SPS8 | ES | Pump #1 Starter | 13 |  | 1984 |  | 6000 | 0 | [8 empty] | 3 | [8 empty] | IMG_5131 | [12 empty] | good
4612 | SPS8 | ES | Pump Ds and control keyboard | 14 |  | 1984 |  | 10000 | 0 | [8 empty] | 3 | [8 empty] | IMG_1062 | [12 empty] | good
4613 | SPS8 | ES | wet well lighting | 12 |  | 1984 |  | 2400 | 0 | [8 empty] | 2 | [8 empty] | IMG_1126 | [12 empty] | good
4614 | SPS8 | SIC | PLC RPU607 | 13 |  | 2014 |  | 60000 | 0 | [8 empty] | 4 | [8 empty] | IMG_5102 | [12 empty] | good
4615 | SPS8 | SIC | Autodialer | 13 |  | 2014 |  | 6000 | 0 | [8 empty] | 2 | [8 empty] | IMG_5109 | [12 empty] | good
4616 | SPS8 | SIC | wet well floats | 12 |  | 1984 |  | 1500 | 0 | [8 empty] | 3 | [8 empty] | IMG_1125 | [12 empty] | good
4617 | SPS8 | SIC | dry well floats | 14 |  | 1984 |  | 1000 | 0 | [8 empty] | 3 | [8 empty] | IMG_1066 | [12 empty] | good
4618 | SPS8 | SIC | temperature switch | 14 |  | 1984 |  | 3000 | 0 | [8 empty] | 2 | [8 empty] | IMG_1064 | [12 empty] | good
4619 | SPS8 | SIC | pressure gauge | 14 |  | 1984 |  | 2000 | 0 | [8 empty] | 2 | [8 empty] | IMG_1074 | [12 empty] | fair | to be replaced in near future
4620 | SPS8 | SIC | level transmitter | 13 |  | 2014 |  | 12000 | 0 | [8 empty] | 2 | [8 empty] | IMG_5113 | [12 empty] | good
4621 | SPS8 | SIC | Anthenna | 11 |  | 2014 |  | 8000 | 0 | [8 empty] | 2 | [21 empty] | good
4649 | SPS8 | BM | Wet Well Exhaust Fan | 12 | Exhaust Fan | 1984 |  | 5000 | 0 | [8 empty] | 3 | [8 empty] | IMG_6237 | [12 empty] | Fan enclosure had severe corrosion.
4650 | SPS8 | BM | Backflow preventer | 12 | backflow, conbraco, , 1" | 2010 |  | 2500 | 0 | [8 empty] | 2 | [8 empty] | IMG_6245
4651 | SPS8 | BM | Intake Air Damper | 13 | damper and actuator | 2003 |  | 4000 | 0 | [8 empty] | 3 | [8 empty] | IMG_6255 | [12 empty] | Intake system to be replaced with generator replacement.
4652 | SPS8 | BM | Eyewash sink combo | 13 | Eyewash | 2000 |  | 1000 | 0 | [8 empty] | 2 | [5 empty] | 2024 | [12 empty] | 3000 |  |  | Emergency eyewashes are required to provide tepid water. No water heater was installed. No instantaneous heater would be required.
4653 | SPS8 | BM | Unit Heater | 13 | unit heater, chromalox, BUH-07D, , 7.5 kw | 1985 |  | 3000 | 0 | [8 empty] | 2 | [8 empty] | IMG_6259
4654 | SPS8 | BM | Dry well supply fan | 13 | fan and inline duct heater | 1985 |  | 4500 | 0 | [8 empty] | 2 | [8 empty] | IMG_6266
4655 | SPS8 | BM | Diesel Fuel System | 13 | fuel tank and piping | 2008 |  | 20000 | 0 | [8 empty] | 2 | [8 empty] | IMG_6270 | [12 empty] | It was noted on site that the diesel fuel system is not up to current TSSA regulations and will need to be upgraded in the future. AB inspection report provided detailed deficiency list.
4656 | SPS8 | BM | Intake Damper #2 | 13 | damper for supply fan | 1985 |  | 2000 | 0 | [8 empty] | 2 | [21 empty] | Damper used with dry well supply fan.
4657 | SPS8 | BM | Generator Exhaust | 13 | ductwork and damper | 1985 |  | 4000 | 0 | [8 empty] | 3 | [8 empty] | IMG_6297 | [12 empty] | Exhaust system to be replace when generator is being replaced.
4658 | SPS8 | BM | Dehumidifer | 14 | Dehumidifer, Canadian Tire, 43-5405-6, 09818460hk, 7.0L/24hr | 2003 |  | 1500 | 0 | [8 empty] | 2 | [8 empty] | IMG_1050
4659 | SPS8 | BM | Sump Pump | 14 | sump pump, myers, MW50-11P, 030C14D, | 2003 |  | 1500 | 0 | [8 empty] | 3 | [8 empty] | IMG_1067
4714 | SPS8 | AC | Exterior Brick Veneer | 13 |  | 1987 |  | 12000 | 0 | [8 empty] | 1 | [8 empty] | IMG_7316 | [12 empty] | fair
4715 | SPS8 | AC | Roofing System | 13 |  | 1987 |  | 10000 | 0 | [8 empty] | 2 | [8 empty] | IMG_7312 | [12 empty] | fair
4716 | SPS8 | AC | Wet Well Wall and Ceiling Paint | 12 |  | 1987 |  | 1000 | 0 | [8 empty] | 1 | [8 empty] | IMG_7314 | [12 empty] | fair
4717 | SPS8 | AC | Wet Well Access Door | 12 |  | 1987 |  | 3500 | 0 | [8 empty] | 1 | [8 empty] | IMG_7313 | [12 empty] | fair | localized missing paint
4718 | SPS8 | AC | Dry Well Access Door | 14 |  | 1987 |  | 5500 | 0 | [8 empty] | 1 | [8 empty] | IMG_7316 | [12 empty] | good
4719 | SPS8 | AC | Dry Well Wall and Ceiling Paint | 14 |  | 1987 |  | 15000 | 0 | [8 empty] | 1 | [8 empty] | IMG_7374 | [12 empty] | localized missing paint
4720 | SPS8 | SC | Wet Well Concrete Structure | 12 |  | 1987 |  | 130000 | 0 | [8 empty] | 4 | [8 empty] | IMG_7349 | [12 empty] | fair | previous coating on walls has failed
4721 | SPS8 | SC | Wet Well Aluminum Platform | 12 |  | 1987 |  | 10000 | 0 | [8 empty] | 3 | [8 empty] | IMG_7349 | [12 empty] | fair
4722 | SPS8 | SC | Wet Well Access Ladder | 12 | Exterior to platform | 1987 |  | 5000 | 0 | [8 empty] | 3 | [8 empty] | IMG_7349 | [12 empty] | fair
4723 | SPS8 | SC | Wet Well Access Ladder | 12 | Platform to base | 1987 |  | 5000 | 0 | [8 empty] | 2 | [8 empty] | IMG_7343 | [12 empty] | fair
4724 | SPS8 | SC | Wet Well Masonry Blockwall | 12 |  | 1987 |  | 6000 | 0 | [8 empty] | 4 | [8 empty] | IMG_7314 | [12 empty] | fair
4725 | SPS8 | SC | Wet Well Precast Concrete Roof | 12 |  | 1987 |  | 1500 | 0 | [8 empty] | 4 | [8 empty] | IMG_7314 | [12 empty] | fair
4726 | SPS8 | SC | Wet Well Monorail Crane Beam | 12 |  | 1987 |  | 2000 | 0 | [8 empty] | 2 | [8 empty] | IMG_7314 | [12 empty] | minor corrosion
4727 | SPS8 | SC | Dry Well Concrete Structure | 14 |  | 1987 |  | 135000 | 0 | [8 empty] | 4 | [8 empty] | IMG_7366 | [12 empty] | fair
4728 | SPS8 | SC | Dry Well Access Ladder | 14 | Lower | 1987 |  | 5000 | 0 | [8 empty] | 2 | [8 empty] | IMG_7366 | [12 empty] | fair
4729 | SPS8 | SC | Dry Well Access Ladder | 14 | Upper | 1987 |  | 5000 | 0 | [8 empty] | 2 | [8 empty] | IMG_7366 | [12 empty] | fair
4730 | SPS8 | SC | Dry Well Access Platform | 14 |  | 1987 |  | 5000 | 0 | [8 empty] | 2 | [8 empty] | IMG_7366 | [12 empty] | fair
4731 | SPS8 | SC | Dry Well Masonry Blockwall | 14 |  | 1987 |  | 15000 | 0 | [8 empty] | 4 | [8 empty] | IMG_7374 | [12 empty] | good
4732 | SPS8 | SC | Dry Well Precast Concrete Roof | 14 |  | 1987 |  | 15000 | 0 | [8 empty] | 4 | [8 empty] | IMG_7374 | [12 empty] | good
4733 | SPS8 | SC | Dry Well Monorail Crane Beam | 14 |  | 1987 |  | 5000 | 0 | [8 empty] | 2 | [8 empty] | IMG_7374 | [12 empty] | good
4734 | SPS8 | SC | Dry Well Guardrail | 14 |  | 1987 |  | 4000 | 0 | [8 empty] | 3 | [8 empty] | IMG_7372 | [12 empty] | good
4735 | SPS8 | SC | Dry Well Aluminum Grating | 14 |  | 1987 |  | 1500 | 0 | [8 empty] | 2 | [8 empty] | IMG_7372 | [12 empty] | good