## Sheet1
seqNum | Description | Process | building | inspectorName | LocationTag | LocationORIGINAL | manufacturer | TransmitterModel | TransducerModel | TransducerSerial | InstMeva | installYear | installationDate | remainingESL | InstType | ServiceArea | FacilityType | LifeCycleCategory | SerialNo | Parent | RotatingItem | Status | Site | condition | assetName | CategoryCode | COF | facility | RehabRepairCost2 | RehabRepairYear2 | repCost | repProjectName | rehabProjectName | rehab2ProjectName | InspectionYear | photoName | assetTag | rehabComment1 | rehabCost1 | rehabComment2 | rehabCost2 | defect1Input | defect2Input | defect3Input | defect1 | defect2 | defect3 | RehabRepairYear | observations | RehabRepairCost
7041 | 1 single, 1 double |  |  |  | 00029225 | [6 empty] | 2009 | [11 empty] | 0 | Exterior Access Doors | AC | 1 | NSPS |  |  | 9000 |  |  |  | 0 | ROY-NOB-1365 | [5 empty] | weathered exterior paint | minor corrosion at bottom of door frame
7047 |  |  |  |  | 00029226 | [6 empty] | 2009 | [11 empty] | 0 | Lower Level Protective Floor Coating | AC | 1 | NSPS |  |  | 3000 |  |  |  | 0 | ROY-NOB-1475 | [5 empty] | fair | localized wear
7043 |  |  |  |  | 00029227 | [6 empty] | 2009 | [11 empty] | 0 | Intermediate Level Interior Access Doors | AC | 1 | NSPS |  |  | 3500 |  |  |  | 0 | ROY-NOB-1436 | [5 empty] | good
7044 |  |  |  |  | 00029226 | [6 empty] | 2009 | [11 empty] | 0 | Lower Level Interior Access Doors | AC | 1 | NSPS |  |  | 3500 |  |  |  | 0 | ROY-NOB-1479 | [5 empty] | minor corrosion on hardware and bottom of door frame
7042 | 2 single doors |  |  |  | 00029228 | [6 empty] | 2009 | [11 empty] | 0 | Main Level Interior Access Doors | AC | 1 | NSPS |  |  | 7000 |  |  |  | 0 | ROY-NOB-1404 | [5 empty] | good
7049 |  |  |  |  | 00029228 | [6 empty] | 2009 | [11 empty] | 0 | Main Level Wall Paint | AC | 1 | NSPS |  |  | 3000 |  |  |  | 0 | ROY-NOB-1404 | [5 empty] | locazlied wear
7048 |  |  |  |  | 00029227 | [6 empty] | 2009 | [11 empty] | 0 | Intermediate Level Protective Floor Coating | AC | 1 | NSPS |  |  | 3000 |  |  |  | 0 | ROY-NOB-1446 | [5 empty] | localized wear
7045 |  |  |  |  | 00029225 | [6 empty] | 2009 | [11 empty] | 0 | Roofing System | AC | 2 | NSPS |  |  | 15000 |  |  |  | 0 | ROY-NOB-1329 | [5 empty] | good
7046 |  |  |  |  | 00029228 | [6 empty] | 2009 | [11 empty] | 0 | Main Level Protective Floor Coating | AC | 1 | NSPS |  |  | 4000 |  |  |  | 0 | ROY-NOB-1391 | [5 empty] | localized wear
6498 | Brick, Exterior Finish, |  |  |  | 00029225 | Nobleton SPS Pumphouse | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Architectural |  |  |  | OPERATING | W-WW | 0 | Exterior Brick Veneer | AC | 1 | NSPS |  |  | 40000 |  |  |  | 0 | ROY-NOB-1327 | 00030046 |  |  |  |  | localized step cracking in mortar
6499 | Louvre Grilles, West Side, Exterior Finish, |  |  |  | 00029225 | Nobleton SPS Pumphouse | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Architectural |  |  |  | OPERATING | W-WW | 0 | NOT USED (Move to Mech) | AC | 1 | NSPS |  |  | 0 |  |  |  | 0 |  | 00030047
6500 | Ceiling, Tectum Panel |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Architectural |  |  |  | OPERATING | W-WW | 0 | Acoustic Ceiling Panels | AC | 1 | NSPS |  |  | 8000 |  |  |  | 0 | ROY-NOB-1420 | 00030058 |  |  |  |  | good
7156 |  |  |  |  | 00029228 | [6 empty] | 2009 | [11 empty] | 0 | Toilet | BM | 1 | NSPS | [6 empty] | 0 | IMG_6784 | [5 empty] | Toilet bowl was stained.
7167 |  |  |  |  | 00029228 | [6 empty] | 2023 | [11 empty] | 0 | *New Asset* Dehumidifier | BM | 2 | NSPS |  |  | 0 |  |  |  | 0 | [6 empty] | There was no dehumidifier installed at the station; however, significant condensation was observed on valves and piping with wet floors beneath. It is recommended to investigate the dehumidification needs and install a suitable unit if necessary. | [5 empty] | 2023 |  | 3000
7157 |  |  |  |  | 00029228 | [6 empty] | 2009 | [11 empty] | 0 | Washroom Sink | BM | 1 | NSPS |  |  | 0 |  |  |  | 0 | IMG_6786
6468 | DCW, Plumbing Fixture, Automatic Trap Primer |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical | 30212 |  |  | OPERATING | W-WW | 0 | Plumbing System | BM | 2 | NSPS |  |  | 25000 |  |  |  | 0 | IMG_6728 | 00022732 |  |  |  |  | good
6361 | EF 501, Motor, Induction |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00015 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 0 | Exhaust Fan 501 Motor | BM | 2 | NSPS |  |  | 0 |  |  |  | 0 | IMG_6707 | 00028900
6363 | Valve, Thermostatic Mixing |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00074 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical | 5307 |  |  | OPERATING | W-WW | 0 | Tempered Water Mixing Valve | BM | 1 | NSPS |  |  | 0 |  |  |  | 0 | IMG_6650 | 00029686
6367 | EF 503, Motor, Induction |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00015 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 0 | Exhaust Fan 503 Motor | BM | 2 | NSPS |  |  | 0 |  |  |  | 0 |  | 00029691
6368 | EF 502, Motor, Induction |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00015 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 0 | Exhaust Fan 502 Motor | BM | 2 | NSPS |  |  | 0 |  |  |  | 0 |  | 00029692
6364 | EF 504, Motor, Induction |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00021 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical | ILI3760 |  |  | OPERATING | W-WW | 0 | Exhaust Fan 504 Motor | BM | 2 | NSPS |  |  | 0 |  |  |  | 0 | IMG_6672 | 00029693
6494 | EF 504, Ventilation System, Exhaust Fan |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00327 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical | 401SC65306-00/0016501 |  |  | OPERATING | W-WW | 0 | Exhaust Fan 504 | BM | 2 | NSPS |  |  | 4500 |  |  |  | 0 | IMG_6672 | 00029694 |  |  |  |  | good
6474 | EF 503, Ventilation System, Exhaust Fan |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00327 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 0 | Exhaust Fan 503 | BM | 2 | NSPS |  |  | 3500 |  |  |  | 0 | IMG_6683 | 00029695 |  |  |  |  | good
6487 | EF 502, Ventilation System, Exhaust Fan |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00327 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 0 | Exhaust Fan 502 | BM | 2 | NSPS |  |  | 6000 |  |  |  | 0 | IMG_6677 | 00029696 |  |  |  |  | good
6477 | MD 510, Ventilation System, Damper |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00861 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 0 | Damper 510 | BM | 2 | NSPS |  |  | 1500 |  |  |  | 0 | IMG_6686 | 00029697 |  |  |  |  | good
6476 | MD 508, Ventilation System, Damper |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00861 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 0 | Damper 508 | BM | 2 | NSPS |  |  | 1500 |  |  |  | 0 | IMG_6680 | 00029698 |  |  |  |  | good
6492 | MD 513, Ventilation System, Damper |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00861 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 0 | Damper 513 | BM | 2 | NSPS |  |  | 2000 |  |  |  | 0 |  | 00029699 |  |  |  |  | good
6491 | EF 501, Ventilation System, Exhaust Fan |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00327 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 0 | Exhaust Fan 501 | BM | 2 | NSPS |  |  | 5000 |  |  |  | 0 | IMG_6702 | 00029701
6471 | MD 507, Ventilation System, Damper |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00861 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 0 | Damper 507 | BM | 2 | NSPS |  |  | 1500 |  |  |  | 0 | IMG_6702 | 00029702 |  |  |  |  | good
6495 | MD 502, Ventilation System, Damper |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00861 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical | N/A |  |  | OPERATING | W-WW | 0 | Damper | BM | 2 | NSPS |  |  | 3000 |  |  |  | 0 | IMG_6698 | 00029703 |  |  |  |  | good
6488 | MD 501, Ventilation System, Damper |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00861 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical | N/A |  |  | OPERATING | W-WW | 0 | Damper 501 | BM | 2 | NSPS |  |  | 5000 |  |  |  | 0 | IMG_6697 | 00029704 |  |  |  |  | good
6486 | MD 509, Ventilation System, Damper |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00861 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical | N/A |  |  | OPERATING | W-WW | 0 | Damper 509 | BM | 2 | NSPS |  |  | 3000 |  |  |  | 0 | IMG_6641 | 00029705 |  |  |  |  | good
6475 | MD 504, Ventilation System, Damper |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00861 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical | N/A |  |  | OPERATING | W-WW | 0 | Damper 504 | BM | 2 | NSPS |  |  | 1500 |  |  |  | 0 | IMG_6642 | 00029706 |  |  |  |  | good
6493 | MD 509, Ventilation System, Damper |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00861 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical | N/A |  |  | OPERATING | W-WW | 0 | Damper 509 | BM | 2 | NSPS |  |  | 2000 |  |  |  | 0 | IMG_6641 | 00029707 |  |  |  |  | good
6479 | MD 506, Ventilation System, Damper |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00861 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical | N/A |  |  | OPERATING | W-WW | 0 | Damper 506 | BM | 2 | NSPS |  |  | 1500 |  |  |  | 0 | IMG_6640 | 00029708 |  |  |  |  | good
6482 | MD 511, Ventilation System, Damper |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00861 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical | N/A |  |  | OPERATING | W-WW | 0 | Damper 511 | BM | 2 | NSPS |  |  | 1500 |  |  |  | 0 | IMG_6639 | 00029709 |  |  |  |  | good
6484 | MD 505, Ventilation System, Damper |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00861 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical | N/A |  |  | OPERATING | W-WW | 0 | Damper 505 | BM | 2 | NSPS |  |  | 1500 |  |  |  | 0 | IMG_6637 | 00029710 |  |  |  |  | good
6469 | LV 502, Ventilation System, Louvre |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical | N/A |  |  | OPERATING | W-WW | 0 | Louvre 502 | BM | 1 | NSPS |  |  | 4000 |  |  |  | 0 |  | 00029711 |  |  |  |  | good
6473 | LV 501, Ventilation System, Louvre |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical | N/A |  |  | OPERATING | W-WW | 0 | Louvre 501 | BM | 1 | NSPS |  |  | 6000 |  |  |  | 0 |  | 00029712
6489 | LV 506, Ventilation System, Louvre |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical | N/A |  |  | OPERATING | W-WW | 0 | Louvre 506 | BM | 1 | NSPS |  |  | 4000 |  |  |  | 0 | IMG_6609 | 00029713 |  |  |  |  | good
6478 | LV 505, Ventilation System, Louvre |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical | N/A |  |  | OPERATING | W-WW | 0 | Louvre 505 | BM | 1 | NSPS |  |  | 4000 |  |  |  | 0 | IMG_6609 | 00029714 |  |  |  |  | good
6490 | LV 504, Ventilation System, Louvre |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical | N/A |  |  | OPERATING | W-WW | 0 | Louvre 504 | BM | 1 | NSPS |  |  | 4000 |  |  |  | 0 | IMG_6609 | 00029715 |  |  |  |  | good
6485 | LV 503, Ventilation System, Louvre |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical | N/A |  |  | OPERATING | W-WW | 0 | Louvre 503 | BM | 1 | NSPS |  |  | 3000 |  |  |  | 0 | IMG_6775 | 00029716 |  |  |  |  | good
6481 | SF 501, Ventilation System, Supply Fan |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical | N/A |  |  | OPERATING | W-WW | 0 | Supply Fan 501 | BM | 2 | NSPS |  |  | 4500 |  |  |  | 0 | IMG_6647 | 00029717 |  |  |  |  | good
6366 | SF 501, Motor, Induction |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical | N/A |  |  | OPERATING | W-WW | 0 | Supply Fan 501 Motor | BM | 2 | NSPS |  |  | 0 |  |  |  | 0 |  | 00029718
6470 | EUH 502, Unit, Heater |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00366 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical | N/A |  |  | OPERATING | W-WW | 0 | EUH 502 | BM | 2 | NSPS |  |  | 3500 |  |  |  | 0 | IMG_6692 | 00029720 |  |  |  |  | good
6472 | MD 503, Ventilation System, Damper |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00861 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical | N/A |  |  | OPERATING | W-WW | 0 | Damper 503 | BM | 2 | NSPS |  |  | 3000 |  |  |  | 0 | IMG_6694 | 00029721 |  |  |  |  | good
6480 | Exhaust Silencer, Emergency Power, |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 0 | Exhaust Silencer | BM | 2 | NSPS |  |  | 6000 |  |  |  | 0 | IMG_6625 | 00029734 |  |  |  |  | good
6483 | Diesel, Emergency Power, Fuel Tank |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00309 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical | 6431-47 |  |  | OPERATING | W-WW | 0 | Diesel Fuel Tank | BM | 2 | NSPS |  |  | 4500 |  |  |  | 0 | IMG_6611 | 00029737 | Fuel system upgrades to meet TSSA requirements | 40000 |  |  | TSSA upgrades to the fuel system are required to bring system up to code CSA B139 | Tank was missing a WHMIS label. |  |  |  |  | 2024
6497 | EFF 501, Unit, Heater |  |  |  | 00029229 | Nobleton SPS PH Stairwell (404) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 0 | Unit Heater 501 | BM | 2 | NSPS |  |  | 2000 |  |  |  | 0 | IMG_6710 | 00029739 |  |  |  |  | good
6357 | Valve, Backflow Preventer |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00990 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 0 |  | BM | 1 | NSPS |  |  | 0 |  |  |  | 0 |  | 00029747
7094 | BFP, Wilkins |  |  |  | 00029227 | [6 empty] | 2009 | [11 empty] | 0 | Backflow Preventer | BM | 1 | NSPS |  |  | 3000 |  |  |  | 0 | IMG_6742 | 00029747 |  |  |  |  | good
6347 | RP, Valve, Backflow Preventer |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00990 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical | 3106084 |  |  | OPERATING | W-WW | 0 |  | BM | 1 | NSPS |  |  | 0 |  |  |  | 0 |  | 00029748
7095 | BFP, Wilkins |  |  |  | 00029227 | [6 empty] | 2009 | [11 empty] | 0 | Backflow Preventer | BM | 1 | NSPS |  |  | 3000 |  |  |  | 0 | IMG_6745 | 00029748 |  |  |  |  | good
6466 | HWT 501, Heating System, Water Heater Tank |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M10118 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical | FH12271405 |  |  | OPERATING | W-WW | 0 | Water Heater | BM | 2 | NSPS |  |  | 3000 |  |  |  | 0 | IMG_6718 | 00029757
6467 | EUH 503, Unit, Heater |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00366 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 0 | EUH 503 | BM | 2 | NSPS |  |  | 2000 |  |  |  | 0 | IMG_6730 | 00029758 |  |  |  |  | good
6460 | Diesel Exhaust Stack, Other Mechanical System, |  |  |  | 00029225 | Nobleton SPS Pumphouse | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 0 | Diesel Stack | BM | 2 | NSPS |  |  | 20000 |  |  |  | 0 | IMG_6625 | 00029902 |  |  |  |  | good
6464 | Gas, Heating System, Unit Heater |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00366 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 0 |  | BM | 2 | NSPS |  |  | 7500 |  |  |  | 0 | IMG_6659 | 00029909 |  |  |  |  | good
6462 | Louvre Grille, East Side, Other Mechanical System, |  |  |  | 00029225 | Nobleton SPS Pumphouse | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 0 | Louvre (East) | BM | 1 | NSPS |  |  | 0 |  |  |  | 0 |  | 00030044
6461 | Louvre Grille, North Side, Other Mechanical System, |  |  |  | 00029225 | Nobleton SPS Pumphouse | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 0 | Louvre (North) | BM | 1 | NSPS |  |  | 0 |  |  |  | 0 |  | 00030045
6463 | Tank Filling Station and Monitor, Other Mechanical System, |  |  |  | 00029225 | Nobleton SPS Pumphouse | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 0 | Diesel Tank Filling Station | BM | 2 | NSPS |  |  | 0 |  |  |  | 0 | ROY-NOB-1338 | 00030240
6496 | MD 502, Ventilation System, Damper |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00861 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 0 | Damper | BM | 2 | NSPS |  |  | 2000 |  |  |  | 0 |  | 00075849 |  |  |  |  | good
6465 | Unit Heater, Stelpro, SHU0563C |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00366 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical |  |  |  | OPERATING | W-WW | 0 | EUH 502 | BM | 2 | NSPS |  |  | 4000 |  |  |  | 0 | IMG_6757 | 00079982 |  |  |  |  | good | no asset tag
6506 | Lifting Device, 2 Tonne Chain Fall |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00091 |  |  |  |  | 2020 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical | 001548 |  |  | OPERATING | W-WW | 0 | 2 Tonne Chain Fall (Main Level) | BM | 2 | NSPS |  |  | 0 |  |  |  | 0 | roy-nob-1424 | 00083515
6502 | Lifting Device, 2 Tonne Chain Fall |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00091 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Building Mechanical | 721311 |  |  | OPERATING | W-WW | 0 | 2 Tonne Chain Fall (Lower Level) | BM | 2 | NSPS |  |  | 0 |  |  |  | 0 | roy-nob-1485 | 00083516
6416 | Building Electrical, Lighting, Emergency Lighting Pack w/ Exit Sign, Battery, & Remote Heads, Lumacell, , , , 1 Unit |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Lower Level (401) | M00366 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | Emergency Lighting Pack | ES | 2 | NSPS |  |  | 2500 |  |  |  | 0 | ROY-NOB-0863 |  | Replace all non-LED lighting fixtures with LED fixtures rated for Class 1, div 2 |  |  |  | Good
7069 | Process Electrical, Electrical Hydro Meter, Hyrdo One |  |  |  | 00029225 | [6 empty] | 2009 | [6 empty] | Owned by Hydro One |  |  |  |  | 0 | Hydro Meter | ES | 2 | NSPS |  |  | 4000 |  |  |  | 0 | ROY-NOB-0522 | [5 empty] | Good
7091 | Building Electrical, Lighting, Wet Well Wall Mounted HID Lighting Fixture, Appleton, CODE MASTER JR HID LIGHTING S35 Lamp, (120/20V, 50W, 60Hz, Class 1 DIV 1&2, 4x Enclosure), 6 Units |  |  |  | 00029231 | [6 empty] | 2009 | [11 empty] | 0 | Wet Well Lighting | ES | 1 | NSPS |  |  | 11400 |  |  |  | 0 | NOB-ROY-1547 |  | Repalce all non-LED lighting fixtures with LED lighting fixtures rated for Class 1 Div 1. |  |  |  | Paint on light is beinging to errode. Minor rust formation on housing
7070 | Process Electrical, Primary Power, Utility Pad Mounted Transformer, ABB Power T&D Co., ,S/N:08J009047, Customer ID: 0000007240 , (300KVA, 3Ph, Primary: 27600/15935V, Secondary: 600/347V), 1 Unit |  |  |  | 00029225 | [6 empty] | 2009 | [6 empty] | 08J009047; Owned by Hydro One |  |  |  |  | 0 | Utility Pad Mounted Transformer | ES | 3 | NSPS |  |  | 60000 |  |  |  | 0 | ROY-NOB-0527 | [5 empty] | Missing Region Asset Tag, (Unless utility owned)
7072 | Process Electrical, Surge Protector Device, Eaton, 1 Unit |  |  |  | 00029228 | [6 empty] | 2009 | [11 empty] | 0 | Surge Protector Device (SPD) | ES | 2 | NSPS |  |  | 3000 |  |  |  | 0 | ROY-NOB-1122 | [5 empty] | Good
6369 | Diesel, Standby Power Source, Engine |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00045 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical | 06R1022869 |  |  | OPERATING | W-WW | 0 | MOVE TO ELECTRICAL | ES | 2 | NSPS |  |  | 0 |  |  |  | 0 |  | 00022846
6442 | Process Electrical, OC-1 Odour Control Fan Control Panel, ABB, , , ,600V 3Ph, 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00002 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | OC-1 Odour Control Fan Control Panel | ES | 3 | NSPS |  |  | 7900 |  |  |  | 0 | ROY-NOB-0732 | 00022847 | Arc Flash Label to be placed on all 600V equipment |  |  |  | Good | Missing arc flash label.
6362 | LP PS Surge Suppressor, Surge Protection |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | MOVE TO ELECTRICAL | ES | 2 | NSPS |  |  | 0 |  |  |  | 0 |  | 00022848
6438 | Process Electrical, Main Service Circuit Breaker Switch, Eaton |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | Main Service Circuit Breaker Switch | ES | 2 | NSPS |  |  | 20000 |  |  |  | 0 | ROY-NOB-0771 | 00022849 | Arc Flash Label to be placed on all 600V equipment |  |  |  | Good | Missing arc flash label.
6451 | Process Electrical, OC-1 Odour Control Unit MCC Circuit Breaker switch, |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | OC-1 Odour Control Unit MCC Circuit Breaker Switch | ES | 2 | NSPS |  |  | 2700 |  |  |  | 0 | ROY-NOB-0611 | 00022850 | Arc Flash Label to be placed on all 600V equipment |  |  |  | Good | Missing arc flash label.
6450 | Electrical Equipment, Spare MCC Circuit Breaker Switch, EATON, 15A Breaker, (600V, 3Ph, 4W), 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | Spare MCC Circuit Breaker Switch | ES | 2 | NSPS |  |  | 2700 |  |  |  | 0 | ROY-NOB-0585 | 00022851 | Arc Flash Label to be placed on all 600V equipment |  |  |  | Good | Missing arc flash label.
6457 | Process Electrical, T-PS Transformer MCC Circuit Breaker, EATON, 40A Breaker, (600V, 3Ph, 4W), 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | T-PS MCC Circuit Breaker | ES | 2 | NSPS |  |  | 4000 |  |  |  | 0 | ROY-NOB-0588 | 00022852 | Arc Flash Label to be placed on all 600V equipment |  |  |  | Good | Missing arc flash label.
6434 | Process Electrical, EF-501 Exhuast Fan 1 MCC Circuit Breaker Switch, EATON, 15A Breaker, (600V, 3Ph, 4W), 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | EF-501 MCC Circuit Breaker | ES | 2 | NSPS |  |  | 2700 |  |  |  | 0 | ROY-NOB-0580 | 00022853 | Arc Flash Label to be placed on all 600V equipment |  |  |  | Good | Missing arc flash label.
6437 | Process Electrical, EF-502 Exhuast Fan 2 MCC Circuit Breaker Switch, EATON, 15A Breaker, (600V, 3Ph, 4W), 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | EF-502 MCC Circuit Breaker Switch | ES | 2 | NSPS |  |  | 2700 |  |  |  | 0 | ROY-NOB-0580 | 00022854 | Arc Flash Label to be placed on all 600V equipment |  |  |  | Good | Missing arc flash label.
6443 | Electrical Equipment, HWT-501 Hot Water Tank MCC Circuit Breaker Switch, EATON, 15A Breaker, (600V, 3Ph, 4W), 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | HWT 501 MCC Circuit Breaker | ES | 2 | NSPS |  |  | 2700 |  |  |  | 0 | ROY-NOB-0581 | 00022855 | Arc Flash Label to be placed on all 600V equipment |  |  |  | Good | Missing arc flash label.
6447 | Electrical Equipment, SF 501 Supply Fan 1 MCC Circuit Breaker Switch, EATON, 15A Breaker, (600V, 3Ph, 4W), 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | SF-501 MCC Circuit Breaker | ES | 2 | NSPS |  |  | 2700 |  |  |  | 0 | ROY-NOB-0581 | 00022856 | Arc Flash Label to be placed on all 600V equipment |  |  |  | Good | Missing arc flash label.
6430 | Process Electrical, MS-3 Monorail System MCC Circuit Breaker Switch, EATON, 15A Breaker, (600V, 3Ph, 4W), 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | MS-3 MCC Circuit Breaker Switch | ES | 2 | NSPS |  |  | 2700 |  |  |  | 0 | NOB-ROY-0582 | 00022857 | Arc Flash Label to be placed on all 600V equipment |  |  |  | Good | Missing arc flash label.
6429 | Process Electrical, EF-504 Exhaust Fan 4 MCC Circuit Breaker Switch, EATON, 15A Breaker, (600V, 3Ph, 4W), 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | EF-504 MCC Circuit Breaker Switch | ES | 2 | NSPS |  |  | 2700 |  |  |  | 0 | ROY-NOB-0582 | 00022858 | Arc Flash Label to be placed on all 600V equipment |  |  |  | Good | Missing arc flash label.
6431 | Process Electrical, EFF-501 & EUH-501 MCC Circuit Breaker Switch, EATON, 20A Breaker, (600V, 3Ph, 4W), 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | EFF 501 & EUH 501 MCC Circuit Breaker Switch, | ES | 2 | NSPS |  |  | 3000 |  |  |  | 0 | ROY-NOB-0583 | 00022859 | Arc Flash Label to be placed on all 600V equipment |  |  |  | Good | Missing arc flash label.
6436 | Process Electrical, EUH-501 MCC Controller, Eaton Cutler-Hammer |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | EUH-501 MCC Controller | ES | 2 | NSPS |  |  | 7900 |  |  |  | 0 | ROY-NOB-0583 | 00022860 | Arc Flash Label to be placed on all 600V equipment |  |  |  | Good | Missing arc flash label.
6441 | Process Electrical, EUH-502 MCC Circuit Breaker Switch, EATON, 15A Breaker, (600V, 3Ph, 4W), 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | EUH 502 MCC Circuit Breaker | ES | 2 | NSPS |  |  | 2700 |  |  |  | 0 | ROY-NOB-0584 | 00022861 |  |  |  |  | Good
6454 | Process Electrical, EUH-503 MCC Circuit Breaker Switch, EATON, 15A Breaker, (600V, 3Ph, 4W), 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | EUH-503 MCC Circuit Breaker | ES | 2 | NSPS |  |  | 2700 |  |  |  | 0 | NOB-ROY-0584 | 00022862 | Arc Flash Label to be placed on all 600V equipment. |  |  |  | Good | Missing arc flash label.
6448 | Process Electrical, Sump Pump Duplex Panel Disconnect Switch, EATON, 20A Breaker, (600V, 3Ph, 4W), 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | Sump Pump Duplex Panel Disconnect Switch | ES | 2 | NSPS |  |  | 3000 |  |  |  | 0 | NOB-ROY-0393 | 00022863
6446 | Spare, Switch, MCC Disconnect |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | Spare Switch | ES | 1 | NSPS |  |  | 0 |  |  |  | 0 | NOB-ROY-0585 | 00022864 |  |  |  |  | Good
6432 | Process Electrical, RP-1 Rotary Phase Converter |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | RP-1 Rotary Phase Converter | ES | 2 | NSPS |  |  | 7000 |  |  |  | 0 |  | 00028925 |  |  |  |  | Asset no observed on site.
6428 | Process Electrical, Starter, EF-501 Variable Frequency Drive (VFD), ABB, HVAC ACH550, ACH550-VCR-02A7-6+F267, Size 1, 2HP |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00002 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical | 2091100285 |  |  | OPERATING | W-WW | 0 | EF-501 VFD | ES | 3 | NSPS |  |  | 15000 |  |  |  | 0 | ROY-NOB-0652 | 00029687 | Arc Flash Label to be placed on all 600V equipment. |  |  |  | Good | Missing arc flash label.
6444 | Process Electrical, Starter, EF-504 Variable Frequency Drive (VFD), ABB, HVAC ACH550, ACH550-VCR-02A7-6+F267, Size 1, 2HP |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00002 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical | 2091100820 |  |  | OPERATING | W-WW | 0 | EF-504 VFD | ES | 3 | NSPS |  |  | 15000 |  |  |  | 0 | ROY-NOB-0642 | 00029688 |  |  |  |  | Good
6445 | Process Electrical, Starter, EF-502 Variable Frequency Drive (VFD), ABB ,HVAC ACH550, ACH550-VCR-02A7-6+F267, Size 1, 2HP |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00002 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical | 2091100670 |  |  | OPERATING | W-WW | 0 | EF 502 VFD | ES | 3 | NSPS |  |  | 15000 |  |  |  | 0 | ROY-NOB-0647 | 00029689 |  |  |  |  | Good
6427 | Process Electrical, Starter, SF-501 Variable Frequency Drive (VFD), ABB, HVAC ACH550, ACH550-VCR-02A7-6+F267, Size 1, 2HP |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00002 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical | 2095100731 |  |  | OPERATING | W-WW | 0 | SF-501 VFD | ES | 3 | NSPS |  |  | 15000 |  |  |  | 0 | ROY-NOB-0652 | 00029690 |  |  |  |  | Good
6440 | Building Electrical, EF-503 Local Disconnect Switch |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | EF-503 Local Disconnect Switch | ES | 2 | NSPS |  |  | 0 |  |  |  | 0 | ROY-NOB-0637 | 00029700 |  |  |  |  | Good
6453 | Building Electrical, Lighting Combination Unit w/ Exit Sign, Battery, & Remote Heads, Lumacell, 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00606 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical | N/A |  |  | OPERATING | W-WW | 0 | Emergency Lighting Combination Unit | ES | 1 | NSPS |  |  | 2500 |  |  |  | 0 | ROY-NOB-0819 | 00029724 | Replace all non-LED lighting fixtures with LED fixtures. |  |  |  | Good
6449 | Building Electrical, CP-03 Control Panel, MAAK TECHNOLOGIES GROUP INC, ,W178-002-3, (120VAC, 1A, 1Ph, 60Hz), CCT#15&#31, 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical | W178-002-3 |  |  | OPERATING | W-WW | 0 | CP-03 Control Panel | ES | 2 | NSPS |  |  | 100000 |  |  |  | 0 | ROY-NOB-0573 | 00029725 |  |  |  |  | Good
6433 | Process Electrical, MCC-PS1 Main Breaker, Eaton, |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | MCC-PS1 Main Disconnect Switch | ES | 3 | NSPS |  |  | 15800 |  |  |  | 0 | ROY-NOB-0316 | 00029726 | Arc Flash Label Required on all 600V Equipment |  |  |  | Good | Missing arc flash label.
6439 | Process Electrical, Starter, PSP-1 Dry Pit Pump 1 Variable Frequency Drive (VFD), Eaton Cutler-Hammer, SVX9000, Size 4, 100HP |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | PSP-1 Dry Pit Pump 1 VFD | ES | 3 | NSPS |  |  | 50000 |  |  |  | 0 | ROY-NOB-0606 | 00029727 | Arc Flash Label Required on all 600V Equipment |  |  |  | Good | Missing arc flash label.
6455 | Process Electrical, Starter, PSP-2 Dry Pit Pump 2 Variable Frequency Drive (VFD), Eaton Cutler-Hammer, SVX9000, Size 4, 100HP |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | PSP-2 Dry Pit Pump 2 VFD | ES | 3 | NSPS |  |  | 50000 |  |  |  | 0 | ROY-NOB-0600 | 00029728 | Arc Flash Label Required on all 600V Equipment |  |  |  | Good | Missing arc flash label.
6426 | Process Electrical, Starter, PSP-3 Dry Pit Pump 3 Variable Frequency Drive (VFD), Eaton Cutler-Hammer, SVX9000, Size 4, 100HP, |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | PSP-3 Dry Pit Pump 3 VFD | ES | 3 | NSPS |  |  | 50000 |  |  |  | 0 | ROY-NOB-0594 | 00029729 | Arc Flash Label Required on all 600V Equipment |  |  |  | Good | Missing arc flash label.
6456 | Process Electrical, Standby Power , ATS-1 Local Disconnect Switch, Eaton |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | ATS-1 Local Disconnect Switch | ES | 2 | NSPS |  |  | 8500 |  |  |  | 0 | ROY-NOB-0781 | 00029730 |  |  |  |  | Good | Missing arc flash label.
6452 | Process Electricall, Standby Power, Battery Charger, Vulcan Electric, Model: DS-24 LV / HV, S/N: C159751, , (INPUT: 120V 4.5A 60Hz), (OUTPUT: 24V, 12A, 12Cell), 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00143 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical | C159751 |  |  | OPERATING | W-WW | 0 | Standby Battery Charger | ES | 2 | NSPS |  |  | 5900 |  |  |  | 0 | ROY-NOB-0618 | 00029731 |  |  |  |  | Good
6360 | Surge Protection |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00044 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | MOVE TO ELECTRICAL | ES | 2 | NSPS |  |  | 0 |  |  |  | 0 |  | 00029732
6458 | Process Electrical, Standby Power , Generator Standby Power Source, MTU Onsite Energy, M/N: 350NXC6DT3, S/N: 305433-1-1-0209, Engine: 60 Series-Detroit,(347/600V, 421A, 3Ph, 4W, 0.8PF, 60Hz, 350kW, 438KVA) , 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M10085 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical | 305433-1-1-0209 |  |  | OPERATING | W-WW | 0 | Generator Standby Power Source | ES | 2 | NSPS |  |  | 170000 |  |  |  | 0 | ROY-NOB-01619 | 00029733 | Arc Flash Label Required on all 600V Equipment |  |  |  | Good | Missing arc flash label.
6459 | Lighting, Emergency, Exit Sign |  |  |  | 00029229 | Nobleton SPS PH Stairwell (404) | M00606 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | Emergency Lighting Exit Sign | ES | 1 | NSPS |  |  | 300 |  |  |  | 0 | ROY-NOB-0827 | 00029742 | Replace all non-LED lighting fixtures with LED fixtures. |  |  |  | Good
7035 | Building Electrical, Lighting, Emergency Double Remote Head, Lumacell, RS2012V9W, 1 Unit |  |  |  | 00029229 | [6 empty] | 2009 | [11 empty] | 0 | Emergency Lighting Double Remote Head | ES | 1 | NSPS |  |  | 350 |  |  |  | 0 | ROY-NOB-0843 | 00029742 | Replace all non-LED lighting fixtures with LED fixtures. |  |  |  | Good
7037 | Building Electrical, Lighting, Emergency, Single Remote Head, Lumacell, 3 Units |  |  |  | 00029229 | [6 empty] | 2009 | [11 empty] | 0 | Emergency Lighting Single Remote Head | ES | 1 | NSPS |  |  | 510 |  |  |  | 0 | ROY-NOB-0930 | 00029742 | Replace all non-LED lighting fixtures with LED fixtures. |  |  |  | Good
6422 | Process Electrical, PSP-3 Dry Pit Pump 3 Control Panel & MCC Circuit Breaker Switch, Eaton Cutler-Hammer, Breaker: 200A, 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00044 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | PSP-3 Dry Pit Pump 3 Control Panel & Circuit Breaker | ES | 3 | NSPS |  |  | 26700 |  |  |  | 0 | ROY-NOB-0592 | 00029743 | ARC FLASH Label required on all 600V Equipment |  |  |  | Good | Missing arc flash label.
6421 | Process Electrical, PSP-2 Dry Pit Pump Control Panel and MCC Circuit Breaker Switch, Eaton Cutler-Hammer, Breaker: 200A, 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00044 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | PSP-2 Dry Pit Pump 2 Control Panel and Circuit Breaker Switch | ES | 3 | NSPS |  |  | 26700 |  |  |  | 0 | ROY-NOB-0597 | 00029744 | ARC FLASH Label required on all 600V Equipment |  |  |  | Good | Missing arc flash label.
7088 | Process Electrical, PSP-1 Dry Pit Pump 1 Control Panel & MCC Circuit Breaker Switch, Eaton Cutler-Hammer, Breaker: 200A, 1 Unit |  |  |  | 00029228 | [6 empty] | 2009 | [11 empty] | 0 | PSP-1 Dry Pit Pump 1 Control Panel & Circuit Breaker | ES | 3 | NSPS |  |  | 26700 |  |  |  | 0 | ROY-NOB-0603 | 00029745 | ARC FLASH Label required on all 600V Equipment |  |  |  | Good | Missing arc flash label.
6424 | SLP-1, Switch, Local Disconnect |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00044 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | SLP-1 Local Disconnect Switch | ES | 2 | NSPS |  |  | 0 |  |  |  | 0 |  | 00029745
6419 | Process Electrical, Motors, NBSSJA_RSP_PMP1_MTR RSP Pump 1 Motor, Hidrostal, TYP: HEVT4-YMKK + ND1B70-0, M. NR : 178684, , , 1 Unit |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00955 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical | 178684 |  |  | OPERATING | W-WW | 0 | NBSSJA_RSP_PMP1_MTR RSP Pump 1 Motor | ES | 4 | NSPS |  |  | 30000 |  |  |  | 0 | ROY-NOB-0980 | 00029766 |  |  |  |  | Good
6418 | Process Electrical, Motors, NBSSJA_RSP_PMP2_MTR RSP Pump 2 Motor, Hidrostal, TYP: HEVT4-YMKK + ND1B70-0, M. NR : 178682, , , , 1 Unit |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00955 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical | 178682 |  |  | OPERATING | W-WW | 0 | NBSSJA_RSP_PMP2_MTR RSP Pump 2 Motor | ES | 4 | NSPS |  |  | 30000 |  |  |  | 0 | ROY-NOB-0991 | 00029767 |  |  |  |  | Good
6415 | Process Electrical, Motors, NBSSJA_RSP_PMP3_MTR RSP Pump 3 Motor, Hidrostal, TYP: HEVT4-YMKK + ND1B70-0, M. NR : 178683 |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00955 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical | 178683 |  |  | OPERATING | W-WW | 0 | NBSSJA_RSP_PMP3_MTR RSP Pump 3 Motor | ES | 4 | NSPS |  |  | 30000 |  |  |  | 0 | ROY-NOB-1003 | 00029768 |  |  |  |  | Good
6417 | Process Electrical, Control Panel, P-501 & P-502 Sump Pump 1 & 2 Control Panel, Unit |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | P-501 & P-502 Sump Pump Control Panel | ES | 2 | NSPS |  |  | 15000 |  |  |  | 0 | ROY-NOB-0972 | 00029779 |  |  |  |  | Good
6414 | Building Electrical, Lighting, Exterior Wall Pack Light , Main Entrance, , , , , ,1 Unit |  |  |  | 00029225 | Nobleton SPS Pumphouse | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical System |  |  |  | OPERATING | W-WW | 0 | Exterior Wall Pack Light | ES | 1 | NSPS |  |  | 1250 |  |  |  | 0 | ROY-NOB-0534 | 00029893 | Replace non-LED lighting fixtures with LED lighting fixtures rated for exterior use. |  |  |  | Good
7032 | Building Electrical, Lighting, Exterior Flood Lights, 2 Units |  |  |  | 00029225 | [6 empty] | 2009 | [11 empty] | 0 | Exterior Flood Light | ES | 1 | NSPS |  |  | 1500 |  |  |  | 0 | ROY-NOB-0481 | 00029893 | Replace all non-LED lighting fixtures with LED fixtures. |  |  |  | photosensor seems to be not working
6423 | Building Electrical, Lighting, 2X48 Fluorescent Lighting Fixture, , , , , 9 Units |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | Intermediate Level Fluorescent Lighting Fixture | ES | 1 | NSPS |  |  | 7200 |  |  |  | 0 | ROY-NOB-0860 | 00029900 | Replace all non-LED lighting fixtures with LED fixtures. |  |  |  | Good
7078 | Building Electrical, Lighting, 2X48 Fluorescent Lighting Fixture, , , , , 11 Units |  |  |  | 00029226 | [6 empty] | 2009 | [11 empty] | 0 | 2X48 Fluorescent Lighting Fixture | ES | 1 | NSPS |  |  | 8800 |  |  |  | 0 | ROY-NOB-1069 | 00029900 | Replace all non-LED lighting fixtures with LED fixtures. |  |  |  | Good
7034 | Building Electrical, Lighting, Emergency Lighting Pack w/ Exit Sign, Battery, & Remote Heads, Lumacell, 1 Unit |  |  |  | 00029226 | [6 empty] | 2009 | [11 empty] | 0 | Emergency Lighting Pack | ES | 1 | NSPS |  |  | 2500 |  |  |  | 0 | ROY-NOB-1062 | 00029907 | Replace all non-LED lighting fixtures with LED fixtures rated for Class 1 Div 2. |  |  |  | Good
7093 | Process Electrical, Sump Pump P-501 Motor | [10 empty] | 2009 | [11 empty] | 0 | Sump Pump P-501 Motor | ES | 1 | NSPS |  |  | 0 |  |  |  | 0 | ROY-NOB-1170 | 00029913
7067 | Builidng Electrical, T-PS Transformer, Eaton Cutler-Hammer, (30kVA ,600-120/208VAC, 3Ph, 3W, 60Hz), 1 Unit |  |  |  | 00029228 | [6 empty] | 2009 | [11 empty] | 0 | T-PS Transformer | ES | 3 | NSPS |  |  | 15800 |  |  |  | 0 | ROY-NOB-0589 | 00087840 | Arc Flash Label to be placed on all 600V Equipment |  |  |  | Good | Missing arc flash label.
7090 | Process Electrical, Motor Control Center (MCC), Eaton Cutler-Hammer, (347/600V, 400A, 3Ph, 4W), 12 Sections |  |  |  | 00029228 | [6 empty] | 2009 | [11 empty] | 0 | Motor Control Center MCC | ES | 4 | NSPS |  |  | 130000 |  |  |  | 0 | ROY-NOB-0577 | 00087842 | Arc Flash Label to be placed on all 600V equipment. |  |  |  | Good | Missing arc flash label.
7081 | Process Electrical, Standby Power , ATS-1 Automatic Transfer Switch, Eaton Cutler-Hammer, ATC 300R |  |  |  | 00029228 | [6 empty] | 2009 | [11 empty] | 0 | ATS-1 Automatic Transfer Switch | ES | 2 | NSPS |  |  | 37500 |  |  |  | 0 | ROY-NOB-0772 | 00087842 | Arc Flash Label to be placed on all 600V equipment. |  |  |  | Good | Missing arc flash label.
7068 | Building Electrical, LP-PS1 Lighting Distribution Panel/ Panelboard, ,PRL1a , ,(225A, 42CCT,120/208V,60Hz), 1 Unit |  |  |  | 00029228 | [6 empty] | 2009 | [11 empty] | 0 | LP-PS1 Lighting Distribution Panel/Panelboard | ES | 2 | NSPS |  |  | 11900 |  |  |  | 0 | ROY-NOB-0186 | 00087843 |  |  |  |  | Good
7089 | Process Electrical, EUH-504 MCC Circuit Breaker Switch, EATON, 15A Breaker, (600V, 3Ph, 4W), 1 Unit |  |  |  | 00029228 | [6 empty] | 2009 | [11 empty] | 0 | EUH-504 MCC Circuit Breaker | ES | 2 | NSPS |  |  | 3500 |  |  |  | 0 | NOB-ROY-0611 | N/A | Arc Flash Label to be placed on all 600V equipment. Missing York Region Asset Tag. |  |  |  | Good | Missing arc flash label.
7086 | Building Electrical, Lighting, 2X48 Fluorescent Lighting Fixture, , , , , 9 Units |  |  |  | 00029228 | [6 empty] | 2009 | [11 empty] | 0 | Main Level Fluorescent Lighting Fixture | ES | 1 | NSPS |  |  | 7200 |  |  |  | 0 | ROY-NOB-0936 | N/A | Replace all non-LED lighting fixtures with LED fixtures. |  |  |  | Good
7075 | Process Electrical, PSP-2 Disconnect Switch, Eaton Cutler-Hammer, (600V, 200A, 3Ph, Nema 3R) |  |  |  | 00029227 | [6 empty] | 2009 | [11 empty] | 0 | PSP-2 Disconnect Switch | ES | 1 | NSPS |  |  | 1800 |  |  |  | 0 | ROY-NOB-0867 | N/A | Arc Flash Label to be placed on all 600V Equipment Missing York Region Asset Tag. |  |  |  | Good
7077 | Building Electrical, Lighting, 2X48 Fluorescent Lighting Fixture, 5 Units |  |  |  | 00029229 | [6 empty] | 2009 | [11 empty] | 0 | 2X48 Fluorescent Lighting Fixture | ES | 1 | NSPS |  |  | 4000 |  |  |  | 0 | ROY-NOB-0936 | N/A | Replace all non LED fixtures with LED Fixtures |  |  |  | Good
7076 | Process Electrical, PSP-1 Disconnect Switch, Eaton, (600V, 200A, 3Ph, Nema 3R), |  |  |  | 00029227 | [6 empty] | 2009 | [11 empty] | 0 | PSP-1 Disconnect Switch | ES | 1 | NSPS |  |  | 1800 |  |  |  | 0 | ROY-NOB-0868 | N/A | Arc Flash Label to be placed on all 600V Equipment Missing York Region Asset Tag |  |  |  | Good | Missing arc flash label.
7073 | Process Electrical, Standby Power, EG-PS-1 Generator Breaker, GE, (600V,450A,3Ph) ,1 Unit |  |  |  | 00029228 | [6 empty] | 2009 | [11 empty] | 0 | EG-PS1 | ES | 2 | NSPS |  |  | 15000 |  |  |  | 0 | ROY-NOB-0802 | N/A | Arc Flash Label to be placed on all 600V Equipment Missing York Region Asset Tag |  |  |  | Good | Missing arc flash label.
7074 | Process Electrical, PSP-3 Disconnect Switch, Eaton, (600V, 200A, 3Ph, Nema 3R) |  |  |  | 00029227 | [6 empty] | 2009 | [11 empty] | 0 | PSP-3 Disconnect Switch | ES | 1 | NSPS |  |  | 1800 |  |  |  | 0 | ROY-NOB-0866 | N/A | Arc Flash Label to be placed on all 600V Equipment Missing York Region Asset Tag |  |  |  | Good | Missing arc flash label.
7154 |  |  |  |  | 00029228 | [6 empty] | 2009 | [11 empty] | 0 | Eye Wash Station | HSS | 2 | NSPS |  |  | 500 |  |  |  | 0 | IMG_6616
7155 | HS_FE3 |  |  |  | 00029226 | [6 empty] | 2009 | [11 empty] | 0 | Fire Extinguisher | HSS | 1 | NSPS |  |  | 100 |  |  |  | 0 | IMG_6756
7165 | HS_FE2 |  |  |  | 00029227 | [6 empty] | 2009 | [11 empty] | 0 | Fire Extinguisher | HSS | 1 | NSPS |  |  | 100 |  |  |  | 0 | IMG_6755
7166 | HS_FE1 |  |  |  | 00029228 | [6 empty] | 2009 | [11 empty] | 0 | Fire Extinguisher | HSS | 1 | NSPS |  |  | 100 |  |  |  | 0 | IMG_6656
6412 | Unit 1, Fall Arrest System, Davit Arm Base |  |  |  | 00029233 | Nobleton SPS PH Site | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Health and Safety |  |  |  | OPERATING | W-WW | 0 | Davit Arm Base | HSS | 3 | NSPS |  |  | 0 |  |  |  | 0 |  | 00022730
6413 | Unit 2, Fall Arrest System, Davit Arm Base |  |  |  | 00029233 | Nobleton SPS PH Site | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Health and Safety |  |  |  | OPERATING | W-WW | 0 | Davit Arm Base | HSS | 3 | NSPS |  |  | 0 |  |  |  | 0 |  | 00022731
6410 | Entry / Exit Monitor, |  |  |  | 00029229 | Nobleton SPS PH Stairwell (404) | M00757 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Health and Safety |  |  |  | OPERATING | W-WW | 0 |  | HSS | 2 | NSPS |  |  | 0 |  |  |  | 0 |  | 00030052
6409 | Process Instrumentation, Health and Safety Compliance Systems, Chemical Spill Kit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M10095 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Health and Safety |  |  |  | OPERATING | W-WW | 0 | Chemical Spill Kit | HSS | 2 | NSPS |  |  | 500 |  |  |  | 0 |  | 00079981 |  |  |  |  | Asset not observed on site.
7161 | 200mm, SS |  |  |  | 00029226 | [6 empty] | 2009 | [11 empty] | 2 | Pump 3 Piping | PM | 3 | NSPS |  |  | 0 |  |  |  | 0 | roy-nob-1194 | [5 empty] | Condensation on pipe flanges
7162 | 250mm, SS |  |  |  | 00029227 | [6 empty] | 2009 | [11 empty] | 2 | Bypass Piping | PM | 3 | NSPS |  |  | 0 |  |  |  | 0 | roy-nob-1157
7160 | 200mm, SS |  |  |  | 00029226 | [6 empty] | 2009 | [11 empty] | 2 | Pump 2 Piping | PM | 3 | NSPS |  |  | 0 |  |  |  | 0 | roy-nob-1194 | [5 empty] | Condensation on pipe flanges
7164 | Purafil, S.O. No. 81509, Serial L08-0221, DS-300 |  |  |  | 00029231 | [6 empty] | 2009 | [11 empty] | 0 | Odour Control Unit | PM | 3 | NSPS |  |  | 0 |  |  |  | 0 | roy-nob-1551 | [5 empty] | The odour control unit is not in use. The Region did not report any odour complaints for the station.
7163 | 100mm, SS |  |  |  | 00029227 | [6 empty] | 2009 | [11 empty] | 2 | Surge Relief Piping | PM | 2 | NSPS |  |  | 0 |  |  |  | 0 | roy-nob-1138
7159 | 200mm, SS |  |  |  | 00029226 | [6 empty] | 2009 | [11 empty] | 2 | Pump 1 Piping | PM | 3 | NSPS |  |  | 0 |  |  |  | 0 | roy-nob-1183 | [5 empty] | Condensation on pipe flanges
7158 | 250mm, SS |  |  |  | 00029227 | [6 empty] | 2009 | [11 empty] | 2 | Discharge Header Piping | PM | 4 | NSPS |  |  | 0 |  |  |  | 0 | roy-nob-1139 | [5 empty] | Heavy condensation and a wet floor beneath the piping was observed.
6503 | 50 mm Air, Relief, Valve |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00926 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 0 | Bypass Combined Air Relief Valve | PM | 1 | NSPS |  |  | 3000 |  |  |  | 0 | roy-nob-1161 | 00016583 |  |  |  |  | good
6330 | 100 mm Line 1 Drain, Valve, Gate |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00210 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 0 | Pump 1 Drain Gate Valve | PM | 1 | NSPS |  |  | 3000 |  |  |  | 0 | ROY-NOB-1205 | 00022721 |  |  |  |  | good
6331 | 100 mm Line 2 Drain, Valve, Gate |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00210 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 0 | Pump 2 Drain Gate Valve | PM | 1 | NSPS |  |  | 3000 |  |  |  | 0 | ROY-NOB-1198 | 00022722 |  |  |  |  | good
6336 | 100 mm Line 3 Drain, Valve, Gate |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00210 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 0 | Pump 3 Drain Gate Valve | PM | 1 | NSPS |  |  | 3000 |  |  |  | 0 | roy-nob-1206 | 00022723 |  |  |  |  | good
6353 | 75 mm Drain, Valve, Gate |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00210 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 0 | Discharge Header Drain Gate Valve | PM | 1 | NSPS |  |  | 2500 |  |  |  | 0 | roy-nob-1145 | 00022791 | replace cam lock and elbow | 1500 |  |  | drain pipe was severely corroded | cam lock corroded | very minor surface corrosion |  |  |  | 2021
6352 | 100 mm Pressure Relief Line Feed, Valve, Plug |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00926 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical | M368280 |  |  | OPERATING | W-WW | 0 | Pressure Relief Line Plug Valve | PM | 1 | NSPS |  |  | 3000 |  |  |  | 0 | roy-nob-1133 | 00022792 |  |  |  |  | good
6354 | Piping, Pressure Regulator |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00145 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical | 0852W |  |  | OPERATING | W-WW | 0 | not found | PM | 1 | NSPS |  |  | 0 |  |  |  | 0 |  | 00022793
6365 | 250 mm PGV 03B, Valve, Plug |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00926 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 0 | Bypass Plug Valve | PM | 1 | NSPS |  |  | 7000 |  |  |  | 0 | roy-nob-1211 | 00022865 |  |  |  |  | good
6350 | 250 mm PGV 03A, Valve, Plug |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00926 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical | M318740 |  |  | OPERATING | W-WW | 0 | Discharge Header Plug Valve | PM | 2 | NSPS |  |  | 7000 |  |  |  | 0 | roy-nob-1152 | 00029749 |  |  |  |  | good
6359 | PGV 02A, Valve, Plug |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00926 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical | M231210 |  |  | OPERATING | W-WW | 0 | Pump 1 Discharge Plug Valve | PM | 2 | NSPS |  |  | 5000 |  |  |  | 0 | roy-nob-1144 | 00029750 |  |  |  |  | good
6356 | 200 mm PGV 02B, Valve, Plug |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00926 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical | M518270 |  |  | OPERATING | W-WW | 0 | Pump 2 Discharge Plug Valve | PM | 2 | NSPS |  |  | 5000 |  |  |  | 0 | roy-nob-1143 | 00029751 |  |  |  |  | good
6349 | 200 mm PGV 02C, Valve, Plug |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00926 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical | M231210 |  |  | OPERATING | W-WW | 0 | Pump 3 Discharge Plug Valve | PM | 2 | NSPS |  |  | 5000 |  |  |  | 0 | roy-nob-1142 | 00029752 |  |  |  |  | good
6355 | 200 mm PGV 01C, Valve, Plug |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical | N/A |  |  | OPERATING | W-WW | 0 | Pump 3 Suction Plug Valve Stem and Handwheel | PM | 2 | NSPS |  |  | 5000 |  |  |  | 0 | roy-nob-1130 | 00029754 |  |  |  |  | good
6348 | 200 mm PGV 01B, Valve, Plug |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M10119 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 0 | Pump 2 Suction Plug Valve Stem and Handwheel | PM | 2 | NSPS |  |  | 5000 |  |  |  | 0 | ROY-NOB-1135 | 00029755 |  |  |  |  | good
6358 | 200 mm PGV 01A, Valve, Plug |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical | N/A |  |  | OPERATING | W-WW | 0 | Pump 1 Suction Plug Valve Stem and Handwheel | PM | 2 | NSPS |  |  | 5000 |  |  |  | 0 | roy-nob-1136 | 00029756 |  |  |  |  | good
6351 | 100 mm Sewage, Valve, Pressure Relief |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00818 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical | 109-214 |  |  | OPERATING | W-WW | 0 | Pressure Relief Valve | PM | 2 | NSPS |  |  | 8000 |  |  |  | 0 | roy-nob-1131 | 00029761 |  |  |  |  | good
6342 | CV 01A, Valve, Check |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00926 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 0 | Pump 1 Discharge Check Valve | PM | 2 | NSPS |  |  | 5000 |  |  |  | 0 | roy-nob-1185 | 00029762 |  |  |  |  | good
6327 | 200 mm CV 01B, Valve, Check |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00926 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 0 | Pump 2 Discharge Check Valve | PM | 2 | NSPS |  |  | 5000 |  |  |  | 0 | roy-nob-1195 | 00029763 |  |  |  |  | Good
6338 | 200 mm CV 01C, Valve, Check |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00926 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 0 | Pump 3 Discharge Check Valve | PM | 2 | NSPS |  |  | 5000 |  |  |  | 0 | roy-nob-1204 | 00029764 |  |  |  |  | good
6329 | RSP Pump 1, Inline Centrifugal, NBSSJA_RSP_PMP1, 53 L/s 54m TDH |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00955 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical | 241E-8492-2 |  |  | OPERATING | W-WW | 0 | Sewage Pump 1 | PM | 4 | NSPS |  |  | 100000 |  |  |  | 0 | ROY-NOB-1180 | 00029769 | pump impeller and motor balance | 10000 |  |  | fair | excess vibration based on visual inspection |  |  |  |  | 2021
6335 | RSP Pump 2, Inline Centrifugal, NBSSJA_RSP_PMP2, 53 L/s 54 M TDH |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00955 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical | 241E-8492-1 |  |  | OPERATING | W-WW | 0 | Sewage Pump 2 | PM | 4 | NSPS |  |  | 100000 |  |  |  | 0 | roy-nob-1191 | 00029770 | pump balance | 15000 |  |  | Fair | excessive vibration based on visual inspection |  |  |  |  | 2021
6345 | RSP Pump 3, Inline Centrifugal, NBSSJA_RSP_PMP3 53 L/S 54 M THD |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00955 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical | 241E-8492-3 |  |  | OPERATING | W-WW | 0 | Sewage Pump 3 | PM | 4 | NSPS |  |  | 100000 |  |  |  | 0 | roy-nob-1202 | 00029771 | pump balance | 15000 |  |  | fair | excessive vibration based on viusal inspection |  |  |  |  | 2021
6332 | 200 mm Suction 1, Valve, Plug |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00926 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical | N/A |  |  | OPERATING | W-WW | 0 | Pump 1 Suction Plug Valve | PM | 2 | NSPS |  |  | 5000 |  |  |  | 0 | roy-nob-1175 | 00029772 |  |  |  |  | Minor localized paint peeling
6328 | 200 mm plug valve PSP-2 |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00926 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 0 | Pump 2 Suction Plug Valve | PM | 2 | NSPS |  |  | 5000 |  |  |  | 0 | ROY-NOB-1187 | 00029773 |  |  |  |  | Minor localized paint peeling
6346 | 200 mm RSP PMP3 Line, Valve, Plug |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00926 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical | N/A |  |  | OPERATING | W-WW | 0 | Pump 3 Suction Plug Valve | PM | 2 | NSPS |  |  | 5000 |  |  |  | 0 | roy-nob-1199 | 00029774 |  |  |  |  | Minor localized paint peeling
6333 | 75 mm P 502, Valve, Check |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00926 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 0 | Sump Pump 2 Discharge Check Valve | PM | 2 | NSPS |  |  | 2500 |  |  |  | 0 | roy-nob-1174 | 00029775 |  |  |  |  | good
6337 | 75 mm P 501, Valve, Check |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00926 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 0 | Sump Pump 1 Discharge Check Valve | PM | 2 | NSPS |  |  | 2500 |  |  |  | 0 | roy-nob-1174 | 00029776 |  |  |  |  | good
6343 | 75 mm P 501, Valve, Plug |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00211 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 0 | Sump Pump 1 Discharge Plug Valve | PM | 2 | NSPS |  |  | 3000 |  |  |  | 0 | roy-nob-1168 | 00029777 |  |  |  |  | good
6340 | 75 mm P 502, Valve, Plug |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00211 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 0 | Sump Pump 2 Discharge Plug Valve | PM | 2 | NSPS |  |  | 3000 |  |  |  | 0 | roy-nob-1168 | 00029778 |  |  |  |  | good
6334 | P 502, Pump, Sump |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 0 | Sump Pump 2 | PM | 2 | NSPS |  |  | 10000 |  |  |  | 0 | roy-nob-1171 | 00029910 |  |  |  |  | surface corrosion
6344 | P 501, Pump, Sump |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 0 | Sump Pump 1 | PM | 2 | NSPS |  |  | 8000 |  |  |  | 0 | roy-nob-1170 | 00029912 |  |  |  |  | surface corrosion
6339 | P 501, Motor, Induction |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 0 | Sump Pump 1 Motor | PM | 2 | NSPS |  |  | 2000 |  |  |  | 0 | roy-nob-1171 | 00029913 |  |  |  |  | fair
6341 | P 502, Motor, Induction |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical |  |  |  | OPERATING | W-WW | 0 | Sump Pump 2 Motor | PM | 2 | NSPS |  |  | 2000 |  |  |  | 0 | roy-nob-1171 | 00029914 |  |  |  |  | fair
6370 | 250 mm Flowmeter, Flow Meter, |  |  |  | 00029227 | Nobleton SPS PH Stairwell (404) | M00405 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical | AB0027010E6 |  |  | OPERATING | W-WW | 0 | Discharge Header Magnetic Flow Meter | PM | 3 | NSPS |  |  | 20000 |  |  |  | 0 | roy-nob-1151 | 00030043 |  |  |  |  | good
6504 | 250 mm Station by-pass plug valve |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical | M238710 |  |  | OPERATING | W-WW | 0 | Bypass Plug Valve | PM | 2 | NSPS |  |  | 7000 |  |  |  | 0 | roy-nob-1147 | 00046890 |  |  |  |  | good
6373 | 600 mm x 600 mm Sluice Gate 3, Inlet, Valve |  |  |  | 00029232 | Nobleton SPS PH Wet Well Chamber - Lower Level (407) | [5 empty] | 2008 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical | 550-1048496 |  |  | OPERATING | W-WW | 0 | Sluice Gate 3 | PM | 3 | NSPS |  |  | 10000 |  |  |  | 0 | roy-nob-1535 | 00079976 |  |  |  |  | good
6372 | 600 mm x 600 mm Sluice Gate 2, Inlet, Valve |  |  |  | 00029232 | Nobleton SPS PH Wet Well Chamber - Lower Level (407) | [5 empty] | 2008 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical | 550-1048496 |  |  | OPERATING | W-WW | 0 | Sluice Gate 2 | PM | 3 | NSPS |  |  | 10000 |  |  |  | 0 | roy-nob-1534 | 00079977 |  |  |  |  | good
6371 | 600 mm x 600 mm Sluice Gate 1, Inlet, Valve |  |  |  | 00029232 | Nobleton SPS PH Wet Well Chamber - Lower Level (407) | [5 empty] | 2008 |  |  |  | Area 6 Wastewater Treatment |  | Process Mechanical | 550-1048496 |  |  | OPERATING | W-WW | 0 | Sluice Gate 1 | PM | 3 | NSPS |  |  | 10000 |  |  |  | 0 | roy-nob-1533 | 00079978 |  |  |  |  | good
7065 |  |  |  |  | 00029233 | [6 empty] | 2009 | [11 empty] | 0 | Odour Control Access Ladder | SC | 3 | NSPS |  |  | 3000 |  |  |  | 0 | ROY-NOB-1562 | [5 empty] | good
7063 |  |  |  |  | 00029232 | [6 empty] | 2009 | [11 empty] | 0 | Wet Well Concrete Structure | SC | 5 | NSPS |  |  | 500000 |  |  |  | 0 | ROY-NOB-1497 | [5 empty] | concrete spalling on underside of roof by access hatch
7056 |  |  |  |  | 00029231 | [6 empty] | 2009 | [11 empty] | 0 | Wet Well Access Ladder | SC | 2 | NSPS |  |  | 10000 |  |  |  | 0 | ROY-NOB-1510 | [5 empty] | minor pitting
7059 | Into wet well 2 |  |  |  | 00029232 | [6 empty] | 2009 | [11 empty] | 0 | Wet Well Access Ladder (Chamber 2) | SC | 2 | NSPS |  |  | 5000 |  |  |  | 0 | ROY-NOB-1526 | [5 empty] | poor | pitting noted
7057 |  |  |  |  | 00029231 | [6 empty] | 2009 | [11 empty] | 0 | Wet Well Access Ladder | SC | 2 | NSPS |  |  | 10000 |  |  |  | 0 | ROY-NOB-1509 | [5 empty] | minor pitting
7066 |  |  |  |  | 00029233 | [6 empty] | 2009 | [11 empty] | 0 | Odour Control Access Hatch | SC | 2 | NSPS |  |  | 6000 |  |  |  | 0 | ROY-NOB-1561 | [5 empty] | good
7050 | Floor, Concrete |  |  |  | 00029227 | [6 empty] | 2009 | [11 empty] | 0 | Intermediate Level Concrete Floor Slab | SC | 4 | NSPS |  |  | 50000 |  |  |  | 0 | ROY-NOB-1446 | [5 empty] | good
7051 | Floor, Concrete |  |  |  | 00029226 | [6 empty] | 2009 | [11 empty] | 0 | Lower Level Concrete Floor Slab | SC | 4 | NSPS |  |  | 260000 |  |  |  | 0 | ROY-NOB-1475 | [5 empty] | typical hairline cracking
7053 |  |  |  |  | 00029227 | [6 empty] | 2009 | [11 empty] | 0 | Intermediate Level Concrete Walls | SC | 4 | NSPS |  |  | 300000 |  |  |  | 0 | ROY-NOB-1435 | [5 empty] | fair | typical previous repairs | localized cracking observed
7055 | Wet Well, Access, Hatch, Steel |  |  |  | 00029231 | [6 empty] | 2009 | [11 empty] | 0 | Wet Well Access Hatch | SC | 2 | NSPS |  |  | 6000 |  |  |  | 0 | ROY-NOB-1490 | [5 empty] | fair
7058 | Into wet well 1 |  |  |  | 00029232 | [6 empty] | 2009 | [11 empty] | 0 | Wet Well Access Ladder (Chamber 1) | SC | 2 | NSPS |  |  | 5000 |  |  |  | 0 | ROY-NOB-1538 | [5 empty] | pitting noted
7061 | Into inlet chamber |  |  |  | 00029232 | [6 empty] | 2009 | [11 empty] | 0 | Wet Well Access Ladder (Inlet Chamber) | SC | 2 | NSPS |  |  | 5000 |  |  |  | 0 | ROY-NOB-1511 | [5 empty] | poor | pitting noted
7060 | Into wet well 3 |  |  |  | 00029232 | [6 empty] | 2009 | [11 empty] | 0 | Wet Well Access Ladder (Chamber 3) | SC | 2 | NSPS |  |  | 5000 |  |  |  | 0 | ROY-NOB-1513 | [5 empty] | pitting noted
7064 |  |  |  |  | 00029233 | [6 empty] | 2009 | [11 empty] | 0 | Odour Control Precast Concrete Chamber | SC | 3 | NSPS |  |  | 50000 |  |  |  | 0 | ROY-NOB-1562 | [5 empty] | water ingress from joint between roof and walls
7054 |  |  |  |  | 00029225 | [6 empty] | 2009 | [11 empty] | 0 | Wood Truss Roof | SC | 3 | NSPS |  |  | 12000 |  |  |  | 0 | ROY-NOB-1327 | [5 empty] | good | hidden under finishes
7052 |  |  |  |  | 00029226 | [6 empty] | 2009 | [11 empty] | 0 | Lower Level Concrete Walls | SC | 3 | NSPS |  |  | 600000 |  |  |  | 0 | ROY-NOB-1467 | [5 empty] | fair | typical previous repairs
7062 | 4 total |  |  |  | 00029232 | [6 empty] | 2009 | [11 empty] | 0 | Wet Well Aluminum Grating | SC | 2 | NSPS |  |  | 5000 |  |  |  | 0 | ROY-NOB-1507 | [5 empty] | minor pitting noted
6319 | Monorail, Hoist Beam |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00366 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Structural |  |  |  | OPERATING | W-WW | 0 | Lower Level Monorail Hoist Beam | SC | 2 | NSPS |  |  | 8000 |  |  |  | 0 | ROY-NOB-1483 | 00029908 |  |  |  |  | good
6320 | Basement Pump Removal, Hatch, Aluminum |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Structural |  |  |  | OPERATING | W-WW | 0 | Intermediate Level Pump Hatch | SC | 2 | NSPS |  |  | 5000 |  |  |  | 0 | ROY-NOB-1440 | 00029911 |  |  |  |  | fair
6322 | Generator and MCC, Floor Slab, Concrete |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Structural |  |  |  | OPERATING | W-WW | 0 | (NOT REQUIRED) | SC | 3 | NSPS |  |  | 0 |  |  |  | 0 |  | 00029936
6325 | Basement, Stair, Concrete |  |  |  | 00029229 | Nobleton SPS PH Stairwell (404) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Structural |  |  |  | OPERATING | W-WW | 0 | Concrete Staircase | SC | 3 | NSPS |  |  | 60000 |  |  |  | 0 | ROY-NOB-1428 | 00030051 |  |  |  |  | good
6324 | Monorail, Hoist Beam |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00366 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Structural |  |  |  | OPERATING | W-WW | 0 | Main Level Monorail Hoist Beam | SC | 3 | NSPS |  |  | 7000 |  |  |  | 0 | ROY-NOB-1418 | 00030057 |  |  |  |  | good
6321 | Wall, Concrete Block |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Structural |  |  |  | OPERATING | W-WW | 0 | Main Level Masonry Blockwall | SC | 4 | NSPS |  |  | 50000 |  |  |  | 0 | ROY-NOB-1404 | 00030060 |  |  |  |  | localized step cracking
6323 | Basement Pump Removal, Hatch, Aluminum Floor |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Structural |  |  |  | OPERATING | W-WW | 0 | Main Level Pump Hatch | SC | 2 | NSPS |  |  | 5000 |  |  |  | 0 | ROY-NOB-1389 | 00030061 |  |  |  |  | fair
6501 | Floor, Concrete |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Architectural |  |  |  | OPERATING | W-WW | 0 | Main Level Concrete Floor Slab | SC | 4 | NSPS |  |  | 80000 |  |  |  | 0 | ROY-NOB-1391 | 00030062 |  |  |  |  | good
6318 | Wet Well, Access, Hatch, Steel |  |  |  | 00029231 | Nobleton SPS Pumphouse | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Structural |  |  |  | OPERATING | W-WW | 0 | Wet Well Access Hatch | SC | 2 | NSPS |  |  | 6000 |  |  |  | 0 | ROY-NOB-1489 | 00030241 |  |  |  |  | fair
7084 | Process Instrumentation, Communcation Antenna 2 |  |  |  | 00029225 | [6 empty] | 2009 | [11 empty] | 0 | Communication Antenna 2 | SIC | 1 | NSPS |  |  | 8000 |  |  |  | 0 | ROY-NOB-0478 | [5 empty] | Good
6395 | Process Instrumentation, BAS Panel Power Supply Aux/Control Transformer, Empire Controls Ltd., S/n :002-E, (120/24V, 15A, 1Ph), CCT No. 15 |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00183 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | 002-E |  |  | OPERATING | W-WW | 0 | BAS Power Supply AUX/Control Transformer | SIC | 2 | NSPS |  |  | 1000 |  |  |  | 0 | ROY-NOB-0693 | [5 empty] | Good
7083 | Process Instrumentation, Communication Antenna 1 |  |  |  | 00029225 | [6 empty] | 2009 | [11 empty] | 0 | Communication Antenna 1 | SIC | 2 | NSPS |  |  | 8000 |  |  |  | 0 | ROY-NOB-0496 | [5 empty] | Wire-Antenna connection is taped together.
7082 | Process Instrumentation, Monitor/Indicator, RFLM-1 Tank Fill Monitor, Clemmer |  |  |  | 00029225 | [6 empty] | 2009 | [11 empty] | 0 | RFLM-1 Tank Fill Monitor | SIC | 2 | NSPS |  |  | 2100 |  |  |  | 0 | ROY-NOB-0494 | [5 empty] | Good | No Region Asset Tag.
7040 | Process Instrumentation, Building Automation System (BAS) Remote Station Panel, Empire Controls Ltd., S/n : 001-E, (24V, 4A, 1Ph, CCT No. 15) |  |  |  | 00029228 | [6 empty] | 2009 | [6 empty] | 001-E |  |  |  |  | 0 | Building Automation System (BAS) Remote Station Panel | SIC | 2 | NSPS |  |  | 11900 |  |  |  | 0 | ROY-NOB-0696 | 00022712 |  |  |  |  | Good
6394 | Process Instrumentation, Network, Computer |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | 76487-OEM-0028092-70355 |  |  | OPERATING | W-WW | 0 | Computer | SIC | 1 | NSPS |  |  | 0 |  |  |  | 0 |  | 00022713 |  |  |  |  | Asset not observed on site.
6392 | Network, Monitor |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | MY20HVGS801165A |  |  | OPERATING | W-WW | 0 |  | SIC | 2 | NSPS |  |  | 0 |  |  |  | 0 |  | 00022714 |  |  |  |  | Asset not observed on site.
6396 | Process Instrumentation, Network, Printer |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M10115 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | JNKA63216 |  |  | OPERATING | W-WW | 0 | Printer | SIC | 1 | NSPS |  |  | 0 |  |  |  | 0 |  | 00022715 |  |  |  |  | Asset not observed on site.
6378 | Process Instrumentation, Sump 1 Float Switch |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control |  |  |  | OPERATING | W-WW | 0 | Sump 1 Float Switch | SIC | 1 | NSPS |  |  | 1900 |  |  |  | 0 | ROY-NOB-0965 | 00022716 |  |  |  |  | Good
6379 | Process Instrumentation, Sump 2 Float Switch |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control |  |  |  | OPERATING | W-WW | 0 | Sump 2 Float Switch | SIC | 1 | NSPS |  |  | 1900 |  |  |  | 0 | ROY-NOB-0965 | 00022717 |  |  |  |  | Good
6377 | Process Instrumention, Sump 3 Float Switch |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control |  |  |  | OPERATING | W-WW | 0 | Sump 3 Float Switch | SIC | 1 | NSPS |  |  | 1900 |  |  |  | 0 | ROY-NOB-0965 | 00022718 |  |  |  |  | Good
6382 | Process Instrumentation, Sump 4 Float Switch |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control |  |  |  | OPERATING | W-WW | 0 | Sump 4 Float Switch | SIC | 1 | NSPS |  |  | 1900 |  |  |  | 0 | ROY-NOB-0965 | 00022719 |  |  |  |  | Good
6380 | Process Instrumentation, Flood Alarm & Float Switch |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control |  |  |  | OPERATING | W-WW | 0 | Flood Alarm Float Switch | SIC | 2 | NSPS |  |  | 1900 |  |  |  | 0 | ROY-NOB-1057 | 00022720 |  |  |  |  | Good
6384 | Process Instrumentation, Suction Line 1, Pressure Gauge |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00893 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control |  |  |  | OPERATING | W-WW | 0 | Pump 1 Suction Pressure Gauge | SIC | 1 | NSPS |  |  | 630 |  |  |  | 0 | ROY-NOB-1179 | 00022724 |  |  |  |  | Good
6383 | Process Instrumentation, Discharge Line 1 Pressure Gauge |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00893 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control |  |  |  | OPERATING | W-WW | 0 | Pump 1 Discharge Pressure Gauge | SIC | 1 | NSPS |  |  | 630 |  |  |  | 0 | ROY-NOB-1184 | 00022725 |  |  |  |  | Good
6376 | Process Instrumentation, Suction Line 2 Pressure Gauge, |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00893 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control |  |  |  | OPERATING | W-WW | 0 | Pump 2 Suction Pressure Gauge | SIC | 1 | NSPS |  |  | 630 |  |  |  | 0 | ROY-NOB-1189 | 00022726 |  |  |  |  | Good
6374 | Process Instrumentation, Discharge Line 2 Pressure Gauge, |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00893 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control |  |  |  | OPERATING | W-WW | 0 | Pump 2 Discharge Pressure Gauge | SIC | 1 | NSPS |  |  | 630 |  |  |  | 0 | ROY-NOB-1191 | 00022727 |  |  |  |  | Good
6375 | Process Instrumentation, Suction Line 3 Pressure Gauge |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00893 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control |  |  |  | OPERATING | W-WW | 0 | Pump 3 Suction Pressure Gauge | SIC | 1 | NSPS |  |  | 630 |  |  |  | 0 | ROY-NOB-1201 | 00022728 |  |  |  |  | Good
6381 | Process Instrumentation, Discharge Line 3 Pressure Gauge |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00893 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control |  |  |  | OPERATING | W-WW | 0 | Pump 3 Discharge Pressure Gauge | SIC | 1 | NSPS |  |  | 630 |  |  |  | 0 | ROY-NOB-1207 | 00022729 |  |  |  |  | Good
6390 | Process Instrumentation, Before Meter Upper DCW Pressure Gauge, TRERICE |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00893 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control |  |  |  | OPERATING | W-WW | 0 | Before Meter Upper DCW Pressure Gauge | SIC | 1 | NSPS |  |  | 630 |  |  |  | 0 | ROY-NOB-0873 | 00022794 |  |  |  |  | Good
6389 | Process Instrumentation, After Meter Lower DCW Pressure Gauge |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00893 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control |  |  |  | OPERATING | W-WW | 0 | After Meter Lower DCW Pressure Gauge | SIC | 1 | NSPS |  |  | 630 |  |  |  | 0 |  | 00022795
6403 | Process Electrical, Netwrok, NBSSJA Ethernet Switch, Layer 3 Ethernet Switch, Interior PAC Panel, S/N: FOC1803Z3RU |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M01002 |  |  |  |  | 2015 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | FOC1803Z3RU |  |  | OPERATING | W-WW | 0 | NBSSJA Ethernet Switch | SIC | 2 | NSPS |  |  | 24800 |  |  |  | 0 | ROY-NOB-0573 | 00025449 |  |  |  |  | Good
6398 | Process Instrumentation, Temperature Switch & Temeprature Low Alarm, Honeywell |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00076 | T631B |  |  | Temperature | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control |  |  |  | OPERATING | W-WW | 0 | Temperature Switch/Alarm | SIC | 1 | NSPS |  |  | 9000 |  |  |  | 0 | ROY-NOB-0689 | 00029682 |  |  |  |  | Good
6505 | Automation, Controller, |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00547 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control |  |  |  | OPERATING | W-WW | 0 |  | SIC | 1 | NSPS |  |  | 0 |  |  |  | 0 |  | 00029683
6435 | Process Instrumentation, ADP-2 ALARM DIALER PANEL, MAAK Technologies Group, S/N: W178-002-12 |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical | W178-002-12 |  |  | OPERATING | W-WW | 0 | ADP-2 Alarm Dialer Panel | SIC | 2 | NSPS |  |  | 5900 |  |  |  | 0 | ROY-NOB-0565 | 00029722 |  |  |  |  | Good
6393 | Process Instrumentation, Quad Gas II Gas Monitoring System for CH4, H2S, and O2, MSA, P/N: 215346, S/N: 145104-1, 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M10086 |  |  |  | CH4, H2S, O2 | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | 145104-1 |  |  | OPERATING | W-WW | 0 | Quad Gas II Gas Monitoring System | SIC | 3 | NSPS |  |  | 3750 |  |  |  | 0 | ROY-NOB-0545 | 00029723 |  |  |  |  | Good
6397 | Process Instrumentation, DC RVLM 2 Tank Level Monitor & Indicator, Clemmer LS |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00309 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control |  |  |  | OPERATING | W-WW | 0 | DC-RVLM-2 Tank Monitor | SIC | 2 | NSPS |  |  | 2100 |  |  |  | 0 | ROY-NOB-0713 | 00029736 |  |  |  |  | Good
6411 | Process Instrumentation, Security System (including Card Readers, Panels, Networks, and Key Pads) |  |  |  | 00029229 | Nobleton SPS PH Stairwell (404) | M00757 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Health and Safety |  |  |  | OPERATING | W-WW | 0 | Security System | SIC | 2 | NSPS |  |  | 50000 |  |  |  | 0 | ROY-NOB-7987 | 00029741 |  |  |  |  | Good
6425 | Process Instrumentation, Temperature Switch & Temeprature Low Alarm, Honeywell, 1 Unit |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00076 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | Temperature Switch/Alarm | SIC | 1 | NSPS |  |  | 9000 |  |  |  | 0 | ROY-NOB-0870 | 00029746 |  |  |  |  | Good
6420 | Process Instrumentation, Temperature Switch & Temeprature Low Alarm, Honeywell, 1 Unit |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M00076 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Electrical |  |  |  | OPERATING | W-WW | 0 | Temperature Switch/Alarm | SIC | 1 | NSPS |  |  | 9000 |  |  |  | 0 | ROY-NOB-1018 | 00029765 |  |  |  |  | Good
6388 | Nobleton SPS, Sampler, Raw |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00526 |  |  |  |  | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | 208E02193 |  |  | OPERATING | W-WW | 0 | Sampler | SIC | 1 | NSPS |  |  | 0 |  |  |  | 0 | roy-nob-1129 | 00031101
6385 | Process Instrumentation, Monitor/Sensor, NBSSJA_RSP_G021, A09-3014618-30-001 O2 Gas Monitor, MSA, Ultima XE, |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M10086 | ULTIMAX |  |  | O2 Gas | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | A09-3014616-30-001 |  |  | OPERATING | W-WW | 0 | O2 Gas Monitor | SIC | 3 | NSPS |  |  | 19800 |  |  |  | 0 | ROY-NOB-1048 | 00042930 |  |  |  |  | Gas Monitor connections have sustained minor corrosion
6386 | Process Instrumentation , Sensor/Monitor, NBSSJA_RSP_GH2S1, A09-3014618-20-001 H2S Gas Monitor, MSA, Ultima XE |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M10086 | ULTIMAX |  |  | H2S Gas | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | A09-3014616-20-001 |  |  | OPERATING | W-WW | 0 | H2S Gas Monitor | SIC | 3 | NSPS |  |  | 23700 |  |  |  | 0 | ROY-NOB-1046 | 00042931 |  |  |  |  | Good
6387 | Process Instrumentation, Sensor/Monitor, NBSSJA_RSP_GLEL1, A09-3014616-10-001 CH4 & LEL Gas Monitorr, MSA, Ultima XE, |  |  |  | 00029226 | Nobleton SPS PH Dry Well - Lower Level (401) | M10086 | ULTIMAX |  |  | LEL Gas | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | A09-3014616-10-001 |  |  | OPERATING | W-WW | 0 | CH4 Gas Monitor | SIC | 3 | NSPS |  |  | 23700 |  |  |  | 0 | ROY-NOB-1024 | 00042932 |  |  |  |  | Good
7085 | Process Instrumentation, Extreme Environment weather Monitoring System (HSPA System with Telemetry), Hoskin Scientific, Model: HSPALINK-E14, |  |  |  | 00029225 | [6 empty] | 2009 | [11 empty] | 0 | Extreme Environment Monitoring System | SIC | 3 | NSPS |  |  | 12600 |  |  |  | 0 | ROY-NOB-0503 | 00075982 |  |  |  |  | Rust formation on base metal structure.
6407 | Process Instrumentation, Monitor/Indicator, Level, NBSSJA_GEN_TK1_LIT1 Diesel Tank Level Indicator & Capacitive Level Indicator |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M10252 |  | Echopod DL24-0 |  | Level | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | 111215-002559 |  |  | OPERATING | W-WW | 0 | Diesel Tank Level Indicator NBSSJA_GEN_TK1_LIT1 | SIC | 2 | NSPS |  |  | 2100 |  |  |  | 0 | ROY-NOB-0715 | 00077601 |  |  |  |  | Good
6391 | Process Instrumentation, NBSSJA_RSP_FIT1 Station Discharge Magnetic Flowmeter, Endress+Hauser, ,S/N: K712f319000, 1 Unit |  |  |  | 00029227 | Nobleton SPS PH Dry Well - Intermediate Level (402) | M00405 | Promag 400 (5X4CXX-1D93/156) | Promag W | C100A316000 | Flow | 2015 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | K712F319000 |  |  | OPERATING | W-WW | 0 | Discharge Header Flow Meter Transmitter | SIC | 2 | NSPS |  |  | 47500 |  |  |  | 0 | ROY-NOB-0909 | 00078431 |  |  |  |  | Good
6401 | Process Instrumentation, NBSSJA PAC Panel OIT Computer, Advantech, S/N: ACF6003575 |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M10189 |  |  |  |  | 2015 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | ACF6003575 |  |  | OPERATING | W-WW | 0 | NBSSJA PAC Panel OIT Computer | SIC | 2 | NSPS |  |  | 7000 |  |  |  | 0 | ROY-NOB-0573 | 00078432 |  |  |  |  | Good
6400 | Process Instrumentation, NBSSJA PAC Panel OIT Monitor, Advantech, S/N: KSA10698933 |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M10189 |  |  |  |  | 2015 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | KSA1068933 |  |  | OPERATING | W-WW | 0 | NBSSJA PAC Panel OIT Monitor | SIC | 2 | NSPS |  |  | 7000 |  |  |  | 0 | ROY-NOB-0573 | 00078433 |  |  |  |  | Good
6402 | Process Instrumentation, NBSSJA Uninterruptible Power Supply (UPS) for PAC Tower/PAC Panel, APC, S/N: GJ255A0008 |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M10181 |  |  |  |  | 2015 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | GJ255A0008 |  |  | OPERATING | W-WW | 0 | NBSSJA UPS for PAC Tower/PAC Panel | SIC | 2 | NSPS |  |  | 8000 |  |  |  | 0 | ROY-NOB-0573 | 00078434 |  |  |  |  | Good
6406 | Process Instrumentation, NBSSJA_WWEL_LIT2 Wet Well 1 Hydrostatic Level Indicator, Endress + Hauser, RIA 452, S/N: K1005904264 |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00405 | RIA452 | FMX21-97D7/0 | E600B215122 | Level | 2015 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | K1005904264 |  |  | OPERATING | W-WW | 0 | NBSSJA_WWEL_LIT2 Wet Well 1 Hydrostatic Level Indicator | SIC | 2 | NSPS |  |  | 2100 |  |  |  | 0 | ROY-NOB-0671 | 00078443 |  |  |  |  | Good
6405 | Process Instrumentation, NBSSJA_WWEL_LIT1, Wet Well 1 Ultrasonic Level Transmitter, Endress+Hauser, FMU90, S/N: K1003E150E6, 1 Unit |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00405 | PROSONIC S FMU90 (N12EA161AA1A) | Prosonic FDU91 |  | Level | 2015 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | K1003E150E6 |  |  | OPERATING | W-WW | 0 | NBSSJA_WWEL_LIT1 Wet Well 1 Ultrasonic Level Transmitter | SIC | 2 | NSPS |  |  | 19900 |  |  |  | 0 | ROY-NOB-0670 | 00078444 |  |  |  |  | Good
6399 | Process Instrumentation, NBSSJA Backup Control Panel, Summa Engineering Ltd, M/N: NBSSJA_BKUP, S/N: 14E-088/NBSSJA_BKUP, (120VAC 1Ph 60Hz) , 1 Unit, Enclosure Type 12 |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | 1002018 |  |  |  |  | 2015 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | 14E-088/NBSSJA_BKUP |  |  | OPERATING | W-WW | 0 | NBSSJA Backup Control Panel, | SIC | 3 | NSPS |  |  | 15000 |  |  |  | 0 | ROY-NOB-0666 | 00078445 |  |  |  |  | Good
6404 | Process Electrical, Netwrok, NBSSJA Radio 1, 900MHZ Radio, Interior PAC Panel, S/N: 1808703 |  |  |  | 00029228 | Nobleton SPS PH Main Level (403) | M00455 |  |  |  |  | 2015 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control | 1808703 |  |  | OPERATING | W-WW | 0 | NBSSJA Radio 1 | SIC | 2 | NSPS |  |  | 24800 |  |  |  | 0 | ROY-NOB-0573 | 00078456 |  |  |  |  | Good
6408 | Process Instrumentation, NBSS_WWELL_LSOF Wet Well High High Level Switch |  |  |  | 00029231 | Nobleton SPS PH Wet Well Chamber - Upper Level (406) | M00061 | ENM-10 |  |  | High High Level | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Instrumentation and Control |  |  |  | OPERATING | W-WW | 0 | NBSS_WWELL_LSOF Wet Well High High Level Switch | SIC | 2 | NSPS |  |  | 1900 |  |  |  | 0 |  | 00080339 |  |  |  |  | Asset not observed on site.
7092 | Process Instrumentation, BAS Panel Power Supply UPS , APC, |  |  |  | 00029228 | [6 empty] | 2009 | [11 empty] | 0 | BAS Power Supply AUX/Control Transformer | SIC | 2 | NSPS |  |  | 10000 |  |  |  | 0 | ROY-NOB-0706 | N/A |  |  |  |  | Good | No York Region Asset Tag
7029 |  |  |  |  | 00029225 | [6 empty] | 2009 | [11 empty] | 0 | Fire Hydrant fire hydrant | SW | 2 | NSPS |  |  | 4000 |  |  |  | 0 | ROY-NOB-1247 | [5 empty] | Localized paint peeling and minor corrosion
7028 |  |  |  |  | 00029225 | [6 empty] | 2009 | [11 empty] | 3 | Driveway (Asphalt) | SW | 1 | NSPS |  |  | 41500 |  |  |  | 0 | ROY-NOB-1287 | [5 empty] | some minor asphalt cracking | Minor cracking at gate | Moderate crack with vegetation along length of driveway and at area in front of station entrance
7031 |  |  |  |  | 00029225 | [6 empty] | 2009 | [11 empty] | 0 | Maintenance Hole Cover | SW | 1 | NSPS |  |  | 900 |  |  |  | 0 | ROY-NOB-1225 | [5 empty] | Good
7030 | chainlink |  |  |  | 00029225 | [6 empty] | 2009 | [11 empty] | 0 | Fencing | SW | 1 | NSPS |  |  | 20000 |  |  |  | 0 | ROY-NOB-1262 | [5 empty] | minor damage at the bottom of some part | very minor deformations throughout
6326 | Wet Well Concrete Pad, Other Sitework, |  |  |  | 00029225 | Nobleton SPS Pumphouse | [5 empty] | 2009 |  |  |  | Area 6 Wastewater Treatment |  | Siteworks |  |  |  | OPERATING | W-WW | 0 | Wet Well Concrete Pad | SW | 2 | NSPS |  |  | 5100 |  |  |  | 0 | ROY-NOB-1563 | 00030242 |  |  |  |  | Good