## Sheet1
CategoryCode | seqNum | assetTag | facility | assetName | installYear | COF | condition | observations | remainingESL | Description | Process | building | inspectorName | LocationTag | LocationORIGINAL | defect1 | manufacturer | TransmitterModel | TransducerModel | TransducerSerial | InstMeva | installationDate | InstType | ServiceArea | FacilityType | LifeCycleCategory | SerialNo | Parent | RotatingItem | Site | defect2 | defect3 | repCost | RehabRepairCost | RehabRepairYear | RehabRepairCost2 | RehabRepairYear2 | photoName | repProjectName | rehabProjectName | rehab2ProjectName | Status | InspectionYear | rehabComment1 | rehabCost1 | rehabComment2 | rehabCost2 | defect1Input | defect2Input | defect3Input
SCS | 5595 |  | KCF | Access Tube Coating | 1982 | 1 | 3 | The asset was observed to be in fair condition. Overcoat dry side of the access tube in the next capital project. Asset to be replaced at the end of remaining service life. | 22 |  |  |  |  | 00002335 |  | One small 1/4'' rust spot was noted. | [16 empty] | 30000 | 17000 | 2023 |  |  | IMG_6991 |  | King City Fisher ET Capital Project 1 |  |  | 0 |  | 0 |  | 0
ES | 5492 |  | KCF | Aircraft Obstruction Lights | 2010 | 3 | 3 | The asset was observed to be in fair condition. | 5 | Two warning lights, assumed installation year: 2010 |  |  |  | 00002335 |  | The incandescent fixture was not working after the bulbs were replaced. It is recommended to replace the unit with LED fixture controller. | [16 empty] | 1000 |  |  |  |  | IMG_6982 | King City Fisher ET Capital Project 1 |  |  |  | 2019 |  |  |  |  | Good
SIC | 5380 | 00018269 | KCF | Antenna 1 (York Region) | 2015 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 |  |  |  |  | 00002335 | King City Fisher Elevated Tank | [8 empty] | Area 2N Linear Water & Wells |  | SCADA |  |  |  | W-WW |  |  | 11000 |  |  |  |  | IMG_6986 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SIC | 5395 | 00025309 | KCF | Antenna 10 (York Region) | 2015 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 | York Region Traffic UHF Whip |  |  |  | 00002335 | King City Fisher Elevated Tank | [8 empty] | Area 2S Linear Water & Wells | W - Storage Elevated Tank | Antenna |  |  |  | W-WW |  |  | 11000 |  |  |  |  | IMG_6980 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SIC | 5396 | 00025310 | KCF | Antenna 11 (Rogers) | 2015 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 | Rogers PCS Antenna |  |  |  | 00002335 | King City Fisher Elevated Tank | [8 empty] | Area 2S Linear Water & Wells | W - Storage Elevated Tank | Antenna |  |  |  | W-WW |  |  | 11000 |  |  |  |  | IMG_6980 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SIC | 5397 | 00025311 | KCF | Antenna 12 (Rogers) | 2015 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 | Rogers PCS Antenna |  |  |  | 00002335 | King City Fisher Elevated Tank | [8 empty] | Area 2S Linear Water & Wells | W - Storage Elevated Tank | Antenna |  |  |  | W-WW |  |  | 11000 |  |  |  |  | IMG_6980 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SIC | 5398 | 00025312 | KCF | Antenna 13 (Bell) | 2015 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 | Bell GPS Antenna |  |  |  | 00002335 | King City Fisher Elevated Tank | [8 empty] | Area 2S Linear Water & Wells | W - Storage Elevated Tank | Antenna |  |  |  | W-WW |  |  | 11000 |  |  |  |  | IMG_6982 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SIC | 5399 | 00025313 | KCF | Antenna 14 (Bell) | 2015 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 | Bell MMDS (Wireless) Antenna |  |  |  | 00002335 | King City Fisher Elevated Tank | [8 empty] | Area 2S Linear Water & Wells | W - Storage Elevated Tank | Antenna |  |  |  | W-WW |  |  | 11000 |  |  |  |  | IMG_6982 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SIC | 5400 | 00025314 | KCF | Antenna 15 (Rogers) | 2015 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 | Rogers PCS Antenna |  |  |  | 00002335 | King City Fisher Elevated Tank | [8 empty] | Area 2S Linear Water & Wells | W - Storage Elevated Tank | Antenna |  |  |  | W-WW |  |  | 11000 |  |  |  |  | IMG_6982 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SIC | 5401 | 00025315 | KCF | Antenna 16 (York Region) | 2015 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 | York Region Traffic UHF Whip |  |  |  | 00002335 | King City Fisher Elevated Tank | [8 empty] | Area 2S Linear Water & Wells | W - Storage Elevated Tank | Antenna |  |  |  | W-WW |  |  | 11000 |  |  |  |  | IMG_6986 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SIC | 5402 | 00025316 | KCF | Antenna 17 (Rogers) | 2015 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 | Rogers PCS Antenna |  |  |  | 00002335 | King City Fisher Elevated Tank | [8 empty] | Area 2S Linear Water & Wells | W - Storage Elevated Tank | Antenna |  |  |  | W-WW |  |  | 11000 |  |  |  |  | IMG_6986 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SIC | 5403 | 00025317 | KCF | Antenna 18 (Rogers) | 2015 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 | Rogers PCS Antenna |  |  |  | 00002335 | King City Fisher Elevated Tank | [8 empty] | Area 2S Linear Water & Wells | W - Storage Elevated Tank | Antenna |  |  |  | W-WW |  |  | 11000 |  |  |  |  | IMG_6986 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SIC | 5404 | 00025318 | KCF | Antenna 19 (Bell) | 2015 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 | Bell PCS Antenna |  |  |  | 00002335 | King City Fisher Elevated Tank | [8 empty] | Area 2S Linear Water & Wells | W - Storage Elevated Tank | Antenna |  |  |  | W-WW |  |  | 11000 |  |  |  |  | IMG_6980 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SIC | 5381 | 00018270 | KCF | Antenna 2 (York Region) | 2015 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 |  |  |  |  | 00002335 | King City Fisher Elevated Tank | [8 empty] | Area 2N Linear Water & Wells |  | SCADA |  |  |  | W-WW |  |  | 11000 |  |  |  |  | IMG_6986 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SIC | 5405 | 00025319 | KCF | Antenna 20 (Bell) | 2015 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 | Bell MMDS (Wireless) Antenna |  |  |  | 00002335 | King City Fisher Elevated Tank | [8 empty] | Area 2S Linear Water & Wells | W - Storage Elevated Tank | Antenna |  |  |  | W-WW |  |  | 11000 |  |  |  |  | IMG_6980 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SIC | 5387 | 00025300 | KCF | Antenna 3 (Bell) | 2015 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 | Bell PCS Antenna |  |  |  | 00002335 | King City Fisher Elevated Tank | [8 empty] | Area 2S Linear Water & Wells | W - Storage Elevated Tank | Antenna |  |  |  | W-WW |  |  | 11000 |  |  |  |  | IMG_6967 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SIC | 5388 | 00025301 | KCF | Antenna 4 (Rogers) | 2015 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 | Rogers PCS Antenna |  |  |  | 00002335 | King City Fisher Elevated Tank | [8 empty] | Area 2S Linear Water & Wells | W - Storage Elevated Tank | Antenna |  |  |  | W-WW |  |  | 11000 |  |  |  |  | IMG_6967 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SIC | 5389 | 00025302 | KCF | Antenna 5 (Rogers) | 2015 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 | Rogers Wireless Microwave Dish |  |  |  | 00002335 | King City Fisher Elevated Tank | [8 empty] | Area 2S Linear Water & Wells | W - Storage Elevated Tank | Antenna |  |  |  | W-WW |  |  | 11000 |  |  |  |  | IMG_6977 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SIC | 5390 | 00025304 | KCF | Antenna 6 (Rogers) | 2015 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 | Rogers PCS Antenna |  |  |  | 00002335 | King City Fisher Elevated Tank | [8 empty] | Area 2S Linear Water & Wells | W - Storage Elevated Tank | Antenna |  |  |  | W-WW |  |  | 11000 |  |  |  |  | IMG_6966 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SIC | 5391 | 00025305 | KCF | Antenna 7 (Rogers) | 2015 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 | Rogers PCS Antenna |  |  |  | 00002335 | King City Fisher Elevated Tank | [8 empty] | Area 2S Linear Water & Wells | W - Storage Elevated Tank | Antenna |  |  |  | W-WW |  |  | 11000 |  |  |  |  | IMG_6966 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SIC | 5392 | 00025306 | KCF | Antenna 8 (Rogers) | 2015 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 | Rogers PCS Antenna |  |  |  | 00002335 | King City Fisher Elevated Tank | [8 empty] | Area 2S Linear Water & Wells | W - Storage Elevated Tank | Antenna |  |  |  | W-WW |  |  | 11000 |  |  |  |  | IMG_6966 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SIC | 5393 | 00025307 | KCF | Antenna 8 (York Region) | 2015 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 | York Region SCADA UHF Whip |  |  |  | 00002335 | King City Fisher Elevated Tank | [8 empty] | Area 2S Linear Water & Wells | W - Storage Elevated Tank | Antenna |  |  |  | W-WW |  |  | 11000 |  |  |  |  | IMG_6979 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SIC | 5394 | 00025308 | KCF | Antenna 9 (York Region) | 2015 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 | York Region UHF Yagi |  |  |  | 00002335 | King City Fisher Elevated Tank | [8 empty] | Area 2S Linear Water & Wells | W - Storage Elevated Tank | Antenna |  |  |  | W-WW |  |  | 11000 |  |  |  |  | IMG_6979 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SW | 5433 |  | KCF | Asphalt Driveway | 1984 | 2 | 3 | The asset was observed to be in fair condition. Repave top surface of asphalt. Asset to be replaced in the intermediate term. | 16 | Asphalt driveway |  |  |  | 17512 |  | Cracks were observed at various locations of driveway. | [16 empty] | 30000 | 7500 | 2023 | 0 |  | IMG_20210505_102347 | King City Fisher ET Capital Project 2 | King City Fisher ET Capital Project 1 |  |  | 0 | Repave top surface of asphalt | 7500 |  | 0 | Cracks at various locations of driveway
SW | 5432 |  | KCF | Chainlink Fence | 1984 | 2 | 3 | The asset was observed to be in fair condition. Minor corrosion was noted on the north, west, and south sids of the fence. The esat side of the fence is new. Asset to be replaced in the long term. | 20 | 1.8m hight chainlink fence around site. Approx. length 170m |  |  |  | 17512 |  | Minor corrosion was noted on the north, west, and south sids of the fence. The esat side of the fence is new. | [16 empty] | 20000 |  |  |  |  | IMG_20210505_101038 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | Fair.
HSS | 5406 | 00035218 | KCF | Chlorine Residual Kit | 2015 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 |  |  |  |  | 00017520 | King City Fisher Elevated Tank |  | M00482 | [6 empty] | Area 2S Linear Water & Wells | W - Storage Elevated Tank | Health and Safety | 10070E152349 |  |  | W-WW |  |  | 2500 |  |  |  |  | IMG_0105 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SW | 5434 |  | KCF | Concrete Pad (at entrance) | 1984 | 1 | 3 | The asset was observed to be in fair condition. Asset to be replaced at the end of its service life. | 25 |  |  |  |  | 17512 |  | Minor damage was observed. | [16 empty] | 3000 |  |  |  |  | IMG_20210505_102424 |  |  |  |  | 0 |  |  |  |  | Minor damage
SW | 5440 |  | KCF | Dechlorination Chamber | 2020 | 3 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of their service life. | 50 | Dechlorination chamber, precast 1100x1100mm box MH. |  |  |  | 17512 | [18 empty] | 30000 |  |  |  |  | IMG_20210505_100819 |  |  |  |  | 0 |  |  |  |  | Good condition
SW | 5559 |  | KCF | Dechlorination Chamber Access Hatch | 2020 | 1 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of its service life. | 50 |  |  |  |  | 00000011 | [18 empty] | 5000 |  |  |  |  | IMG_6993 |  |  |  |  | 0 |  |  |  |  | good
SW | 5544 |  | KCF | Dechlorination Chamber Concrete Structure | 2020 | 1 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of its service life. | 50 |  |  |  |  | 17512 | [18 empty] | 20000 |  |  |  |  | IMG_6993 |  |  |  |  | 0 |  |  |  |  | good
SW | 5545 |  | KCF | Dechlorination Chamber FRP Ladder | 2020 | 1 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of its service life. | 50 |  |  |  |  | 17512 | [18 empty] | 2000 |  |  |  |  | IMG_6994 |  |  |  |  | 0 |  |  |  |  | good
SW | 5368 | 00008866 | KCF | Double Lockable Swing Gate | 2020 | 1 | 1 | The asset was observed to be in very good condition. Asset to be replaced in the long term. | 20 |  |  |  |  | 17512 | King City Fisher Elevated Tank | [8 empty] | Area 1S Linear Water & Wells | W - Storage Elevated Tank | Siteworks |  |  |  | W-WW |  |  | 4000 |  |  |  |  | IMG_20210505_100551 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | Good
ES | 5493 |  | KCF | Electrical Duct System and Conduit System | 2010 | 3 | 4 | The asset was observed to be in poor condition. Install cable messenger or a dedicated communication cable chute to access tube for better cable organization. | 25 | Electrical underground duct system and conduit system |  |  |  | 00002335 |  | The cables installed in the access tube poses safety concern as cable cluster prevents safe and effective rescue. | [16 empty] | 75000 | 52000 | 2022 | 0 |  | IMG_6991 |  | King City Fisher ET Capital Project 1 |  |  | 2019 | Install cable messenger to access tube for better cable organization. | 50000 |  | 0 | The cables installed in the access tube poses safety concern as cable cluster prevents safe and effective rescue.
AC | 5522 |  | KCF | Electrical Room Access Door (Single) | 2019 | 1 | 1 | The asset was observed to be in very good condition. Asset to be replaced in the long term. | 15 |  |  |  |  | 17513 | [18 empty] | 3500 |  |  |  |  | IMG_6954 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
BM | 5503 |  | KCF | Electrical Room Air Ducting | 2020 | 2 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 30 |  |  |  |  | 17513 | [18 empty] | 1000 |  |  |  |  | IMG_0765 |  |  |  |  | 0 |  |  |  |  | Good
SC | 5530 |  | KCF | Electrical Room Concrete Floor Slab | 1982 | 3 | 2 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 35 |  |  |  |  | 17513 | [18 empty] | 22000 | 2000 | 2030 |  |  | IMG_6955 |  | King City Fisher ET Capital Project 2 |  |  | 0 |  |  |  |  | good
SC | 5535 |  | KCF | Electrical Room Concrete Roof | 2020 | 3 | 1 | The asset was observed to be in very good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 55 |  |  |  |  | 00000001 | [18 empty] | 6000 | 1000 | 2030 |  |  | IMG_6956 |  | King City Fisher ET Capital Project 2 |  |  | 0 |  |  |  |  | good
BM | 5459 | 00089467 | KCF | Electrical Room Exhaust Fan | 2020 | 2 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 30 | Manufacturer: Broan-Nutone, Model: L500 |  |  |  | 17513 | [18 empty] | 5000 |  |  |  |  | IMG_0240 |  |  |  |  | 0 |  |  |  |  | Good
SIC | 5480 | 00089471 | KCF | Electrical Room High Temperature Switch | 2020 | 1 | 1 | The asset was observed to be in very good condition. Asset to be replaced in the long term. | 15 | KCETFS_BLDS_TSHL1, Manufacturer: Honeywell |  |  |  | 00000001 | King City FS ET Electrical Room | [17 empty] | 500 |  |  |  |  | IMG_4881 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
ES | 5477 |  | KCF | Electrical Room Linear Light Fixtures | 2020 | 2 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 25 | 3 LED 4 inches lighting fixtures |  |  |  | 17513 | [18 empty] | 3000 |  |  |  |  | IMG_4839 |  |  |  |  | 0 |  |  |  |  | good
SIC | 5482 | 00088518 | KCF | Electrical Room Low Temperature Switch | 2020 | 1 | 1 | The asset was observed to be in very good condition. Asset to be replaced in the long term. | 15 | KCETFS_BLDS_TSHL1, Manufacturer: Honeywell |  |  |  | 00000001 | King City FS ET Electrical Room | [17 empty] | 500 |  |  |  |  | IMG_4884 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SC | 5542 |  | KCF | Electrical Room Masonry Blockwall | 2020 | 4 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 50 |  |  |  |  | 17513 | [18 empty] | 15000 |  |  |  |  | IMG_6955 |  |  |  |  | 0 |  |  |  |  | good
BM | 5461 |  | KCF | Electrical Room Motorized Damper | 2020 | 2 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 30 | Size: 500x500 mm, Manufacturer: Nailor, Model: 1020-IB/-IBF, damper includes Belimo actuator LF120 (120/1/60) interlocked with electrical room exhaust fan |  |  |  | 17513 | [18 empty] | 2500 |  |  |  |  | IMG_0199 |  |  |  |  | 0 |  |  |  |  | good condition
AC | 5524 |  | KCF | Electrical Room Protective Floor Coating | 2019 | 1 | 1 | The asset was observed to be in very good condition. Asset to be replaced in the long term. | 15 |  |  |  |  | 17513 | [18 empty] | 1500 |  |  |  |  | IMG_6955 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
BM | 5460 | 00089470 | KCF | Electrical Room Unit Heater | 2020 | 2 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 30 | Manufacturer: Ouellet, Model: OAS03000AM |  |  |  | 17513 | [18 empty] | 3000 |  |  |  |  | IMG_0247 |  |  |  |  | 0 |  |  |  |  | Good
AC | 5523 |  | KCF | Electrical Room Wall and Ceiling Paint | 2019 | 1 | 1 | The asset was observed to be in very good condition. Asset to be replaced in the long term. | 15 |  |  |  |  | 17513 | [18 empty] | 4000 |  |  |  |  | IMG_6956 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
AC | 5529 |  | KCF | Electrical Room Window | 2019 | 1 | 1 | The asset was observed to be in very good condition. Asset to be replaced in the long term. | 15 |  |  |  |  | 17513 | [18 empty] | 3000 |  |  |  |  | IMG_6950 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
AC | 5520 | 00008877 | KCF | Elevated Tank Access Door (Double) | 1982 | 1 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 15 |  |  |  |  | 00017522 | King City FS ET Valve Room | [17 empty] | 5500 |  |  |  |  | IMG_6946 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | Good
HSS | 5596 |  | KCF | Elevated Tank Access Tube Anchor Point (Roof Level) | 2015 | 4 | 2 | The asset was observed to be in good condition. Replace the exisitng anchor point with concrete roof mounted dismount post. Asset to be replaced at the end of the service life. | 0 |  |  |  |  | 00002335 |  | The installed D ring was not designed for fall arrest shock load. | [16 empty] | 4000 |  |  | 0 |  | IMG_6991 | King City Fisher ET Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | good
SC | 5601 |  | KCF | Elevated Tank Access Tube Manway Hatch | 1982 | 2 | 2 | The asset was observed to be in fair condition. Replace the manway with a new 24'' diameter submarine style manway. | 3 |  |  |  |  | 00002335 |  | Metal staining was observed. | [16 empty] | 20000 |  |  |  |  | DSCN4047 | King City Fisher ET Capital Project 1 |  |  |  | 0 |  | 0 |  | 0
SC | 5517 | 00008873 | KCF | Elevated Tank Aluminum Ladder (Ground to Platform) | 1982 | 4 | 2 | The asset was observed to be in good condition. Fall arrest system is required to be replaced. Asset to be replaced at the end of remaining service life. | 0 |  |  |  |  | 00002335 | King City FS ET Tank Base | Fall arrest system requires replacement. | [14 empty] | The ladder is non-complaint as it is only 15'' wide, it shoule be 16'' wide. |  | 30000 |  |  |  |  | IMG_6960 | King City Fisher ET Capital Project 1 |  |  |  | 0 |  |  |  |  | good
SC | 5528 |  | KCF | Elevated Tank Aluminum Ladder (Platform to Roof) | 1982 | 4 | 2 | The asset was observed to be in good condition. Replace the fall arrest system of the ladder. Asset to be replaced at the end of remaining service life. | 0 |  |  |  |  | 00002335 |  | Fall arrest system requires replacement. | [14 empty] | The ladder is non-compliant, only 14'' wide. Base on the code it should be 16'' |  | 15000 |  |  |  |  | IMG_6971 | King City Fisher ET Capital Project 1 |  |  |  | 0 |  |  |  |  | good
SC | 5537 |  | KCF | Elevated Tank Aluminum Ladder (Roof to Tank) | 1982 | 4 | 3 | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 0 |  |  |  |  | 00002335 |  | Fall arrest system requires replacement. | [14 empty] | Localized corrosion was observed throughout. | The ladder is non-compliantm, it is only 15'' wide. Based on the code, it should be 16'' wide. | 15000 |  |  |  |  | IMG_6974 | King City Fisher ET Capital Project 1 |  |  |  | 0 |  |  |  |  | Fair | Minor localized corrosion
SC | 5536 |  | KCF | Elevated Tank Aluminum Staircase | 2020 | 3 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 55 |  |  |  |  | 00017512 | [18 empty] | 8000 |  |  |  |  | IMG_6957 |  |  |  |  | 0 |  |  |  |  | good
HSS | 5597 |  | KCF | Elevated Tank Anchor Point (Platform Level) | 2015 | 4 | 2 | The asset was observed to be in good condition.The anchor point to be re-mounted. | 35 |  |  |  |  | 00002335 |  | The anchor point should be re-mounted; top of the anchor point is too far in. It does not provide enough thread. | [16 empty] | 4000 | 500 | 2021 | 0 |  | img_6973 |  | King City Fisher ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
PM | 5499 |  | KCF | Elevated Tank Bypass Line | 2018 | 3 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 28 | Diameter: 100mm, approximate length: 2 meters. |  |  |  | 00017520 | King City FS ET Valve Room | [17 empty] | 1000 |  |  |  |  | IMG_0136 |  |  |  |  | 0 |  |  |  |  | Good
PM | 5356 | 00089496 | KCF | Elevated Tank Bypass Line Check Valve | 2018 | 3 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 28 | Diameter: 100mm |  |  |  | 00017520 | King City FS ET Valve Room | [8 empty] | Area 2N Linear Water & Wells |  | Process Mechanical | M261770 |  |  | W-WW |  |  | 2200 |  |  |  |  | IMG_0136 |  |  |  |  | 0 |  |  |  |  | Good
PM | 5357 | 00089497 | KCF | Elevated Tank Bypass Line Gate Valve | 2018 | 3 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 28 | Diameter: 100mm |  |  |  | 00017520 | King City FS ET Valve Room | [8 empty] | Area 2N Linear Water & Wells |  | Process Mechanical |  |  |  | W-WW |  |  | 1200 |  |  |  |  | IMG_0136 |  |  |  |  | 0 |  |  |  |  | Good
SC | 5515 | 00008871 | KCF | Elevated Tank Concrete Floor Slab | 1982 | 3 | 2 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 35 |  |  |  |  | 00017522 | King City FS ET Valve Room | [17 empty] | 45000 | 2000 | 2030 |  |  | IMG_6957 |  | King City Fisher ET Capital Project 2 |  |  | 0 |  |  |  |  | good
SC | 5519 | 00008875 | KCF | Elevated Tank Concrete Structure | 1982 | 4 | 2 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 35 |  |  |  |  | 00002335 | King City Fisher Elevated Tank | [17 empty] | 900000 | 30000 | 2030 | 0 |  | DSCN4001 |  | King City Fisher ET Capital Project 2 |  |  | 0 | Coat exterior roof of concrete structure to seal tank from elements | 30000 |  | 0 | good | Top of concrete tank is bare and exposed to the elements
SCS | 5531 |  | KCF | Elevated Tank Exterior Coating | 1982 | 4 | 4 | The asset was observed to be in poor condition.The exterior of this tank will need to be removed and replaced within the next 1 to 3 years, although this is purely for cosmetic reasons and not because of any structural concerns regarding metal loss. This | 3 |  |  |  |  | 00002335 |  | There is substantial chalking of the roof, down to previous layers, as well as on the shell and lower cone. | [14 empty] | Some corrosion areas are visible on the lower cone and around the spray-foam insulating layer at the base of the cone. | There is also corrosion at the seam where the steel roof meets the concrete dome, with much of the sealant deteriorated. | 830000 |  |  |  |  | IMG_6945 | King City Fisher ET Capital Project 1 |  |  |  | 0 |  |  |  |  | Fair | Corrosion/bubbling on painters ring
PM | 5498 |  | KCF | Elevated Tank Frostproof Vent/Vacuum Relief Unit | 2011 | 3 | 3 | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 21 |  |  |  |  | 00002335 | King City FS ET Valve Room | Minor surface corrosion was observed. | [16 empty] | 6000 |  |  |  |  | IMG_6987 |  |  |  |  | 2019 |  |  |  |  | minor surface corrosion
ES | 5491 |  | KCF | Elevated Tank Grounding | 1982 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. | 25 |  |  |  |  | 00002335 | [18 empty] | 10000 |  |  |  |  | IMG_0769 |  |  |  |  | 0 |  |  |  |  | good
PM | 5500 |  | KCF | Elevated Tank Inlet/Outlet Line | 1982 | 5 | 2 | The asset was observed to be in good condition. | 32 | Diameter: 400mm, approximate length: 50 meters |  |  |  | 00002335 | King City FS ET Valve Room | [17 empty] | 73000 |  |  |  |  | DSCN4033 |  |  |  |  | 0 |  |  |  |  | good
PM | 5353 | 00089501 | KCF | Elevated Tank Inlet/Outlet Line Air Relief Valve | 2018 | 2 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 28 | Manufacturer: Val Matic Corp. Diameter: 50mm. |  |  |  | 00017520 | King City FS ET Valve Room | [8 empty] | Area 2N Linear Water & Wells |  | Process Mechanical |  |  |  | W-WW |  |  | 2500 |  |  |  |  | IMG_0053 |  |  |  |  | 0 |  |  |  |  | Good
PM | 5410 | 00042995 | KCF | Elevated Tank Inlet/Outlet Line Altitude Valve | 2011 | 4 | 3 | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 21 | Diameter: 400mm |  |  |  | 00017520 | King City FS ET Valve Room | Minor surface corrosion was observed on bolts. | M00038 | [6 empty] | Area 2N Linear Water & Wells |  | Process Mechanical | 131-FH-1C |  |  | W-WW |  |  | 31500 |  |  |  |  | IMG_0093 |  |  |  |  | 0 |  |  |  |  | Minor surface corrosion on bolts
PM | 5355 | 00089492 | KCF | Elevated Tank Inlet/Outlet Line Butterfly Valve | 2018 | 3 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 28 | Diameter: 400mm |  |  |  | 00017520 | King City FS ET Valve Room |  | M00331 | [6 empty] | Area 2N Linear Water & Wells |  | Process Mechanical | M021570 |  |  | W-WW |  |  | 6700 |  |  |  |  | IMG_0083 |  |  |  |  | 0 |  |  |  |  | Good
PM | 5497 | 00089496 | KCF | Elevated Tank Inlet/Outlet Line Butterfly Valve Actuator | 2018 | 3 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 28 |  |  |  |  | 00017520 | King City FS ET Valve Room | [11 empty] | M021570 | [5 empty] | 10200 |  |  |  |  | IMG_0816 |  |  |  |  | 0 |  |  |  |  | Good
PM | 5507 | 00089501 | KCF | Elevated Tank Inlet/Outlet Line Expansion Joint | 2020 | 3 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 30 | Diameter: 400mm |  |  |  | 00017520 | [18 empty] | 2500 |  |  |  |  | IMG_0147 |  |  |  |  | 0 |  |  |  |  | Good
PM | 5411 | 00042996 | KCF | Elevated Tank Inlet/Outlet Line Gate Valve | 2011 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 21 | Diameter: 400mm |  |  |  | 00017520 | King City FS ET Valve Room |  | M00671 | [6 empty] | Area 2N Linear Water & Wells |  | Process Mechanical | AW236106W40L.400 |  |  | W-WW |  |  | 6000 |  |  |  |  | IMG_0130 |  |  |  |  | 0 |  |  |  |  | Good
SIC | 5419 | 00043006 | KCF | Elevated Tank Inlet/Outlet Pipe Flowmeter | 2011 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 12 | Diameter: 400mm |  |  |  | 00017522 | King City FS ET Tank Base |  | M00125 | [6 empty] | Area 2N Linear Water & Wells |  | Process Mechanical |  |  |  | W-WW |  |  | 16000 |  |  |  |  | IMG_0211 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SIC | 5413 | 00042998 | KCF | Elevated Tank Inlet/Outlet Pipe Flowmeter Transmitter | 2011 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 12 | Manufacturer: Siemens, Model: Sitrans FM Magflo |  |  |  | 00017520 | King City FS ET Valve Room |  | M00125 |  |  |  | Flow |  |  | Area 2N Linear Water & Wells |  | Instrumentation and Control | 7ME6920-1AA10-1AA0 |  |  | W-WW |  |  | 10000 |  |  |  |  | IMG_0836 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SIC | 5485 | 00089491 | KCF | Elevated Tank Inlet/Outlet Pipe Free Chlorine Analyzer | 2015 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 | KCETFS_TWR_AIT2 |  |  |  | 00017520 | King City FS ET Valve Room | [11 empty] | BS 90725-08 | [5 empty] | 10000 |  |  |  |  | IMG_0794 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | GOOD
ES | 5490 | 00043008 | KCF | Elevated Tank Inlet/Outlet Pipe Heat Tracing | 2010 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 15 | assumed installation year: 2010 |  |  |  | 00002335 | [12 empty] | R1-050-DP | [5 empty] | 15000 |  |  |  |  | IMG_0767 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SIC | 5407 | 00040717 | KCF | Elevated Tank Inlet/Outlet Pipe Pressure Gauge | 2020 | 1 | 1 | The asset was observed to be in very good condition. Asset to be replaced in the long term. | 15 |  |  |  |  | 00017520 | King City FS ET Valve Room |  | M00151 | [6 empty] | Area 1N Linear Water & Wells |  | Instrumentation and Control |  |  |  | W-WW |  |  | 500 |  |  |  |  | IMG_0066 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SIC | 5430 | 00077561 | KCF | Elevated Tank Inlet/Outlet Pipe Pressure Transmitter | 2020 | 3 | 1 | The asset was observed to be in very good condition. Asset to be replaced in the long term. | 15 | KCETFS_TWR_PIT1 |  |  |  | 00017510 | King City FS ET Valve Room |  | M00405 | PMC71-UAC-1P1RAAAU | [5 empty] | Area 1N Linear Water & Wells |  | Instrumentation and Control | 9301431509C |  |  | W-WW |  |  | 3000 |  |  |  |  | IMG_4903 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SC | 5558 |  | KCF | Elevated Tank Inlet/Outlet Pipe Support | 1982 | 4 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 25 |  |  |  |  | 00002335 | [18 empty] | 30000 |  |  |  |  | IMG_6965 |  |  |  |  | 0 |  |  |  |  | good
SIC | 5427 | 00044090 | KCF | Elevated Tank Inlet/Outlet Pipe Total Chlorine Analyzer | 2015 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 | KCETFS_TWR_AIT1 |  |  |  | 00017520 | King City FS ET Valve Room |  | M00125 | [6 empty] | Area 2N Linear Water & Wells |  | Instrumentation and Control | BS 90725-08 |  |  | W-WW |  |  | 8000 |  |  |  |  | IMG_0794 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | GOOD
SCS | 5539 |  | KCF | Elevated Tank Interior Coating | 2000 | 4 | 2 | The asset was observed to be in good condition. Replace the asset at the end of its service life. | 19 |  |  |  |  | 00002335 |  | There were a few small corrosion spots on the lower cone and on the wet side access tube and ladder. | [16 empty] | 480000 |  |  |  |  | IMG_6974 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SIC | 5429 | 00045456 | KCF | Elevated Tank Level Indicator Transmitter | 2015 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced in a long term. | 11 | KCETFS_TWR_LIT1 |  |  |  | 00017520 | King City FS ET Valve Room |  | 1010702 | PMC71-UAC1P2RAAAU |  |  | Level |  |  | Area 2N Linear Water & Wells |  | Instrumentation and Control | A401E51509C |  |  | W-WW |  |  | 3000 |  |  |  |  | IMG_0835 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
ES | 5494 |  | KCF | Elevated Tank Lightning Protection System | 2010 | 3 | 3 | The asset was observed to be in fair condition. Reinstall the lightning rod to the highest point of the elevated tank . | 25 |  |  |  |  | 00002335 |  | One of the lightning rods were not erected. | [16 empty] | 5000 | 500 | 2022 | 0 |  | IMG_6989 |  | King City Fisher ET Capital Project 1 |  |  | 2019 | Reinstall the lightning rod to the highest point of the elevated tank | 1000 |  | 0 | One of the lightning rods were not erected.
PM | 5600 |  | KCF | Elevated Tank Mixing System | 2015 | 3 | 2 | The elevated tank mixing system was observed to be in good condition. | 25 |  |  |  |  | 00002335 | [18 empty] | 85000 | 0 |  | 0 |  | DSCN4029 |  |  |  |  | 2019 |  | 0 |  | 0
PM | 5501 |  | KCF | Elevated Tank Overflow Line | 1982 | 4 | 2 | The asset was observed to be in good condition. | 32 | Diameter: 300mm, approximately: 55 meters |  |  |  | 00002335 | King City FS ET Valve Room | [17 empty] | 60000 |  |  |  |  | IMG_6994 |  |  |  |  | 0 |  |  |  |  | Good
PM | 5455 |  | KCF | Elevated Tank Overflow Line Duckbill Valve | 2018 | 3 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 28 | Diameter: 300mm |  |  |  | 17512 | [18 empty] | 4000 |  |  |  |  | IMG_6994 |  |  |  |  | 0 |  |  |  |  | Good
SC | 5543 |  | KCF | Elevated Tank Overflow Pipe Support | 1982 | 4 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 25 |  |  |  |  | 00002335 | [18 empty] | 30000 |  |  |  |  | IMG_6965 |  |  |  |  | 0 |  |  |  |  | good
AC | 5527 |  | KCF | Elevated Tank Protective Floor Coating | 2019 | 1 | 1 | The asset was observed to be in very good condition. Asset to be replaced in the long term. | 15 |  |  |  |  | 00017522 | [18 empty] | 3000 |  |  |  |  | IMG_6957 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SC | 5532 |  | KCF | Elevated Tank Roof Access Hatch | 1982 | 3 | 3 | The asset was observed to be in good condition. The asset has surpassed its service life and should be replaced. | 5 |  |  |  |  | 00002335 |  | The support arm of the roof hatch was corroded. | [16 empty] | 5000 |  |  |  |  | IMG_6981 | King City Fisher ET Capital Project 1 |  |  |  | 0 |  |  |  |  | Fair
SC | 5533 |  | KCF | Elevated Tank Roof Guardrail | 1982 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 25 |  |  |  |  | 00002335 | [18 empty] | 5000 |  |  |  |  | IMG_6981 |  |  |  |  | 0 |  |  |  |  | Fair
SC | 5594 |  | KCF | Elevated Tank Sacrificial Anode Cathodic Protection System | 1982 | 3 | 3 | The Elevated Tank Sacrificial Anode Cathodic Protection System was observed to be in fair condition. Replace the cathodic protection system with a control box in the next capital project. | 5 |  |  |  |  | 00002335 |  | Corroded sacrificial anodes were observed. | [16 empty] | 30000 | 0 | 0 | 0 | 0 | DSCN4020 | King City Fisher ET Capital Project 1 |  |  |  | 2019 |  | 0 |  | 0
SC | 5534 |  | KCF | Elevated Tank Steel Tank | 1982 | 5 | 3 | The asset was observed to be in fair condition. Seal gap between access tube and tank. Replacement of the external painters rail. Remove and replacement spray-on urethane insulation (lower cone) including sarnafil cover. Supply and install an exterior dri | 35 |  |  |  |  | 00002335 |  | Gap between access tube and tank was observed. | [14 empty] | Access tube is narrow and congested due to communication cables. (Recommendation provided in Electrical system for cable management) | The external painters rail was noted to be corroded. D-Ring was not installed. The existing polyurethane insulation has signs of deterioration. Elevated tank roof couplings were corroded. | 1100000 | 174000 | 2022 |  |  | IMG_6945 |  | King City Fisher ET Capital Project 1 |  |  | 0 | Seal gap between access tube and tank | 5000 | Install new cable raceway | 50000 | Fair | Gap between access tube and tank | access tube is narrow and congested due to communication cables
PM | 5496 | 00089498 | KCF | Elevated Tank Surge Protection Line | 2020 | 3 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 30 | diameter: 75mm, Approximate length: 10 meters. |  |  |  | 00017520 | [18 empty] | 3000 |  |  |  |  | img_0065 |  |  |  |  | 0 |  |  |  |  | good
PM | 5495 | 00089498 | KCF | Elevated Tank Surge Protection Line Gate Valve | 2020 | 1 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 30 | diameter: 75mm |  |  |  | 00017520 | King City FS ET Valve Room | [17 empty] | 1200 |  |  |  |  | img_0068 |  |  |  |  | 0 |  |  |  |  | good
PM | 5354 | 00089500 | KCF | Elevated Tank Surge Protection Line Surge Relief Valve | 2018 | 2 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 28 | Diameter: 75mm |  |  |  | 00017520 | King City FS ET Valve Room | [8 empty] | Area 2N Linear Water & Wells |  | Process Mechanical | 2674429-1 |  |  | W-WW |  |  | 5000 |  |  |  |  | IMG_0075 |  |  |  |  | 0 |  |  |  |  | Good
SC | 5540 |  | KCF | Elevated Tank Tank Access Hatch | 1982 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 5 |  |  |  |  | 00002335 |  | The hatch hold open is broke. The hatch should be replaced. | [16 empty] | 5000 |  |  |  |  | IMG_6981 | King City Fisher ET Capital Project 1 |  |  |  | 0 |  |  |  |  | Fair
SC | 5541 |  | KCF | Elevated Tank Valve Room and Electrical Room Aluminum Guardrail | 2020 | 3 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 50 |  |  |  |  | 00017522 | [18 empty] | 5000 |  |  |  |  | IMG_6958 |  |  |  |  | 0 |  |  |  |  | good
PM | 5453 |  | KCF | Elevated Tank Water Main Air Release Valve | 2012 | 2 | 3 | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 22 | Diameter: 50mm, the valve drained to dechlorination chamber |  |  |  | 17512 |  | Minor surface corrosion was observed. | [16 empty] | 2500 |  |  |  |  | IMG_9998 |  |  |  |  | 0 |  |  |  |  | Minor surface corrosion
PM | 5358 |  | KCF | Elevated Tank Water Main Butterfly Valve 1 | 2011 | 3 | 3 | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 21 | Diameter: 400mm, Manufacturer: Kennedy-Clow |  |  |  | 17512 |  | Minor surface corrosion was observed. | [7 empty] | Area 2N Linear Water & Wells |  | Process Mechanical |  |  |  | W-WW |  |  | 7000 |  |  |  |  | IMG_9976 |  |  |  |  | 0 |  |  |  |  | Minor to moderate corrosion
PM | 5359 |  | KCF | Elevated Tank Water Main Drain Gate Valve 1 | 2011 | 2 | 3 | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 21 | Diameter: 100mm |  |  |  | 17512 |  | Minor surface corrosion was observed. | [7 empty] | Area 2N Linear Water & Wells |  | Process Mechanical |  |  |  | W-WW |  |  | 1500 |  |  |  |  | IMG_9979 |  |  |  |  | 0 |  |  |  |  | Minor to moderate corrosion
PM | 5383 |  | KCF | Elevated Tank Water Main Drain Gate Valve 2 | 2011 | 2 | 3 | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 21 | Diameter: 100mm |  |  |  | 17512 |  | Minor surface corrosion was observed. | M00352 | [6 empty] | Area 2N Linear Water & Wells |  | Process Mechanical |  |  |  | W-WW |  |  | 1500 |  |  |  |  | IMG_9986 |  |  |  |  | 0 |  |  |  |  | Minor to moderate corrosion
PM | 5454 |  | KCF | Elevated Tank Water Main Gate Valve | 2012 | 2 | 3 | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 22 | Diameter: 50mm |  |  |  | 17512 |  | Minor surface corrosion was observed. | [16 empty] | 1000 |  |  |  |  | IMG_9998 |  |  |  |  | 0 |  |  |  |  | Minor surface corrosion
ES | 5479 |  | KCF | Emergency Lighting Fixtures | 2020 | 2 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 25 | 5 in total: 1 combination unit, 4 remote heads |  |  |  | 00017522 | [18 empty] | 4500 |  |  |  |  | IMG_4820 |  |  |  |  | 0 |  |  |  |  | good
SIC | 5363 | 00006490 | KCF | Eyewash Piping Pressure Gauge | 2020 | 1 | 1 | The asset was observed to be in very good condition. Asset to be replaced in the long term. | 15 |  |  |  |  | 00017520 | King City FS ET Valve Room |  | M00967 | [6 empty] | Area 1N Linear Water & Wells |  | Instrumentation and Control |  |  |  | W-WW |  |  | 500 |  |  |  |  | img_0041 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
HSS | 5458 | 00089477 | KCF | Eyewash Station | 2020 | 3 | 1 | The asset was observed to be in very good condition. Asset to be replaced in the long term. | 15 |  |  |  |  | 00017520 | [18 empty] | 2000 |  |  |  |  | IMG_0040 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | Good
BM | 5456 | 00089476 | KCF | Eyewash System Backflow Preventer | 2020 | 2 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 30 | Diameter: 50mm, Manufacturer: Watts, Model: LF009M1QT. |  |  |  | 17513 | [18 empty] | 2500 |  |  |  |  | IMG_0031 |  |  |  |  | 0 |  |  |  |  | Good
BM | 5457 | 00089473 | KCF | Eyewash System Water Heater | 2020 | 2 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 30 | Manufacturer: Eemax, Model: EX190T1; Capacity: 19kW |  |  |  | 00017520 | [12 empty] | 1775365 | [5 empty] | 3000 |  |  |  |  | IMG_0031 |  |  |  |  | 0 |  |  |  |  | Good
SIC | 5423 | 00043011 | KCF | Facility Card Readers | 2020 | 1 | 1 | The asset was observed to be in very good condition. Asset to be replaced in the long term. | 15 |  |  |  |  | 00017522 | King City Fisher Elevated Tank |  | M00488 | [6 empty] | Area 1N Linear Water & Wells |  | Health and Safety |  |  |  | W-WW |  |  | 1000 |  |  |  |  | img_4830 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | Good
SIC | 5414 | 00041999 | KCF | Facility Security Alarm Auto Dialer | 2020 | 1 | 1 | The asset was observed to be in very good condition. Asset to be replaced in the long term. | 15 |  |  |  |  | 00017522 | King City FS ET Valve Room |  | M00455 | [6 empty] | Area 1N Linear Water & Wells |  | Electrical System | NX-8E |  |  | W-WW |  |  | 2000 |  |  |  |  | IMG_4831 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SIC | 5362 | 00006489 | KCF | Facility Security Closet | 2020 | 3 | 1 | The asset was observed to be in very good condition. Asset to be replaced in the long term. | 15 |  |  |  |  | 17513 | King City FS ET Electrical Room |  | M00016 | [6 empty] | Area 1N Linear Water & Wells |  | Health and Safety |  |  |  | W-WW |  |  | 10000 |  |  |  |  | IMG_4868 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
HSS | 5508 |  | KCF | Fire Extinguisher | 2020 | 1 | 1 | The asset was observed to be in very good condition. Asset to be replaced in the long term. | 15 | 1 Fire Extinguisher |  |  |  | 00017520 | [18 empty] | 300 |  |  |  |  | IMG_0050 | King City Fisher ET Capital Project 2 |  |  |  | 1019 |  |  |  |  | good
ES | 5418 | 00043004 | KCF | Generator Transfer Switch Panel | 2010 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 15 | Assumed installation year: 2010 |  |  |  | 00017522 | King City FS ET Valve Room | [8 empty] | Area 2N Linear Water & Wells |  | Electrical System | AL 1M0200B |  |  | W-WW |  |  | 12000 |  |  |  |  | IMG_4821 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
ES | 5420 | 00043008 | KCF | Heat Tracing Panel | 2010 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 15 | Assumed installation year: 2010 |  |  |  | 00017520 | King City FS ET Valve Room |  | M10099 | [6 empty] | Area 2N Linear Water & Wells |  | Electrical System | R1-050-DP |  |  | W-WW |  |  | 5000 |  |  |  |  | IMG_4914 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good | consider upgrade
SIC | 5417 | 00043001 | KCF | KCETFS-PAC Control Panel CompactLogix | 2020 | 1 | 1 | The asset was observed to be in very good condition. Asset to be replaced in the long term. | 15 | inside of PAC Control Panel |  |  |  | 17513 | King City FS ET Electrical Room |  | M00005 | [6 empty] | Area 1N Linear Water & Wells |  | Instrumentation and Control |  |  |  | W-WW |  |  | 4000 |  |  |  |  | IMG_4877 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SIC | 5424 | 00043013 | KCF | KCETFS-PAC Control Panel UPS | 2020 | 1 | 1 | The asset was assumed to be in very good condition. Asset to be replaced in the long term. | 15 | Inside control panel |  |  |  | 17513 | King City FS ET Electrical Room |  | M00718 | [6 empty] | Area 1N Linear Water & Wells |  | Electrical System | GD151A0396 |  |  | W-WW |  |  | 4000 |  |  |  |  | IMG_4877 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SIC | 5412 | 00041997 | KCF | KCETFS-PAC PLC panel | 2020 | 4 | 1 | The asset was observed to be in very good condition. Asset to be replaced in the long term. | 15 |  |  |  |  | 17513 | King City FS ET Electrical Room | [8 empty] | Area 1N Linear Water & Wells |  | Instrumentation and Control | 10-106-B |  |  | W-WW |  |  | 55000 |  |  |  |  | IMG_4877 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
ES | 5376 | 00089474 | KCF | Lighting Panel LP-A | 2020 | 3 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 25 | 110/240V, 225A, 42 Circuit |  |  |  | 17513 | King City FS ET Valve Room |  | M00119 | [6 empty] | Area 1N Linear Water & Wells |  | Electrical System |  |  |  | W-WW |  |  | 18000 |  |  |  |  | IMG_4847 |  |  |  |  | 0 |  |  |  |  | good
ES | 5384 | 00014597 | KCF | Main Disconnect Switch | 2020 | 3 | 1 | The asset was observed to be in very good condition. Install Arc Flash Warning Label to the main disconnect switch Asset to be replaced at the end of remaining service life. | 25 | 600V, 100A |  |  |  | 17513 | King City FS ET Valve Room | Arc Flashing was missing. | M00119 | [6 empty] | Area 1N Linear Water & Wells |  | Electrical System |  |  |  | W-WW |  |  | 10000 | 200 | 2022 | 0 |  | IMG_4841 |  | King City Fisher ET Capital Project 1 |  |  | 0 | Install Arch Flash Warning Label to the main disconnect switch | 100 |  | 0 | good
ES | 5488 | 00006494 | KCF | Mezzanine LED Lighting Fixtures | 2020 | 2 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 25 | 8 LED lighting fixtures in total |  |  |  | 00017522 | [18 empty] | 6500 |  |  |  |  | IMG_4829 |  |  |  |  | 0 |  |  |  |  | good
SIC | 5426 | 00089481 | KCF | Network Access Closet | 2020 | 4 | 1 | The asset was observed to be in very good condition. Asset to be replaced in the long term. | 15 |  |  |  |  | 17513 | King City FS ET Electrical Room |  | M00505 | [6 empty] | Area 1N Linear Water & Wells |  | Instrumentation and Control |  |  |  | W-WW |  |  | 15000 |  |  |  |  | IMG_4870 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SIC | 5378 | 00018167 | KCF | Network Access Closet Radio Modem | 2020 | 1 | 1 | The asset was assumed to be in very good condition. Asset to be replaced in the long term. | 15 | KCTWRAD101, located inside of network access closet. |  |  |  | 17513 | King City FS ET Electrical Room |  | M01018 | [6 empty] | Area 1N Linear Water & Wells |  | SCADA | 853317 |  |  | W-WW |  |  | 2000 |  |  |  |  | IMG_4870 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SIC | 5425 | 00043014 | KCF | Network Access Closet Radio Modem | 2020 | 1 | 1 | The asset was assumed to be in very good condition. Asset to be replaced in the long term. | 15 | Part Number: INET II - DGSN, Manufacturer: GE |  |  |  | 17513 | King City FS ET Electrical Room | [8 empty] | Area 1N Linear Water & Wells |  | Instrumentation and Control |  |  |  | W-WW |  |  | 2000 |  |  |  |  | IMG_4870 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SIC | 5428 | 00044124 | KCF | Network Access Closet UPS | 2020 | 1 | 1 | The asset was assumed to be in very good condition. Asset to be replaced in the long term. | 15 | Manufacturer: Powerware |  |  |  | 17513 | King City FS ET Electrical Room |  | M00718 | [6 empty] | Area 1N Linear Water & Wells |  | Electrical System | GE404A0166 |  |  | W-WW |  |  | 4000 |  |  |  |  | IMG_4870 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
ES | 5478 |  | KCF | Outdoor Light Fixture | 2020 | 2 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 25 | 1 wall pack |  |  |  | 17512 | [18 empty] | 1000 |  |  |  |  | IMG_4815 |  |  |  |  | 0 |  |  |  |  | good
SW | 5439 |  | KCF | Overflow Pipe | 1984 | 4 | 3 | The asset was assumed to be in fair condition. Asset to be replaced at the end of their service life. | 25 | 300mm concrete overflow pipe from tank to property line. Approximate length 13m |  |  |  | 17512 | [18 empty] | 18000 | [9 empty] | 0
ES | 5489 | 00006494 | KCF | Pedestal Lighting Fixtures | 1982 | 2 | 2 | The asset was observed to be in good condition; however they were original. Replacement is recommend in the next capital project. | 9 | two in total, installation year assumed to be 2015 |  |  |  | 00017522 | [18 empty] | 5000 |  |  |  |  | IMG_4834 | King City Fisher ET Capital Project 1 |  |  |  | 0 |  |  |  |  | good
BM | 5606 | 00048027 | KCF | Platform Ventilation Louvre | 1982 | 1 | 2 | The asset was observed to be in good condition. | 23 |  |  |  |  | 00002335 | Nobleton North ET Upper Service Platform |  | M00069 | [6 empty] | Area 4 Water Treatment |  | Building Mechanical |  |  |  | W-WW |  |  | 3000 |  |  |  |  | IMG_6968 |  |  |  | OPERATING | 2019 |  |  |  |  | good
BM | 5506 |  | KCF | Plumbing and Drainage | 2020 | 2 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 30 | Drain piping for air release valve, water sampling tank, and eyewash system. Water drain to the sump pit in the valve room. The drain is connect to Sanitary Sewer. |  |  |  | 00017520 | [18 empty] | 5000 |  |  |  |  | img_0061 |  |  |  |  | 0 |  |  |  |  | good
ES | 5431 | 00077741 | KCF | Portable Generator | 2017 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 22 | Manufacturer: Honda, Model: EU3000i |  |  |  | 17513 | King City Fisher Elevated Tank |  | M00506 | [6 empty] | Area 2S Linear Water & Wells | W - Storage Elevated Tank | Building Mechanical | EAVJ-1144608 |  |  | W-WW |  |  | 3500 |  |  |  |  | IMG_0862 |  |  |  |  | 0 |  |  |  |  | good
SW | 5438 |  | KCF | Sanitary Service | 2020 | 3 | 1 | The asset was assumed to be in very good condition based on its age. Asset to be replaced at the end of their service life. | 50 | 115mm sanitary service from building to PL. Approximately 13m in length |  |  |  | 17512 | [18 empty] | 12000 | [9 empty] | 0
BM | 5504 |  | KCF | Service Water Line | 2020 | 2 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 30 | Service Water Line for heated eyewash station. |  |  |  | 00017520 | [18 empty] | 1000 |  |  |  |  | img_0070 |  |  |  |  | 0 |  |  |  |  | good
SW | 5369 | 00008870 | KCF | Site Drainage (soft surfaces) | 1982 | 1 | 3 | The asset was observed to be in fair condition. Place more granular/top soil adjacent to pad to ensure drainage away from pads. Asset to be replaced in the intermediate term. | 25 |  |  |  |  | 17512 | King City FS ET Valve Room | Low spots adjacent to concrete pads was observed. | [7 empty] | Area 2N Linear Water & Wells |  | Siteworks |  |  |  | W-WW | Exposed top soil was observed in various locations around site. |  | 25000 | 7000 | 2023 |  |  | IMG_20210505_103102 | King City Fisher ET Capital Project 1 | King City Fisher ET Capital Project 1 |  |  | 0 | Place more granular/top soil adjacent to pad to ensure drainage away from pads. | 4000 | Re-sod or place seed in areas with exposed topsoil. | 3000 | Low spots adjacent to concrete pads | Exposed top soil in various locations around site.
HSS | 5509 |  | KCF | Smoke Detectors | 2020 | 1 | 1 | The asset was observed to be in very good condition. Asset to be replaced in the long term. | 15 | Smoke Detector (1), one in valve room, the other in electrical room. |  |  |  | 00017520 | [18 empty] | 1000 |  |  |  |  | IMG_0253 | King City Fisher ET Capital Project 2 |  |  |  | 1019 |  |  |  |  | good
SW | 5547 |  | KCF | Valve Chamber Access Hatch | 1982 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. | 50 |  |  |  |  | 17512 | [18 empty] | 5000 |  |  |  |  | IMG_6995 |  |  |  |  | 0 |  |  |  |  | Fair
SW | 5546 |  | KCF | Valve Chamber Aluminum Ladder | 1982 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. | 50 |  |  |  |  | 17512 | [18 empty] | 3000 |  |  |  |  | IMG_6996 |  |  |  |  | 0 |  |  |  |  | fair
SW | 5560 |  | KCF | Valve Chamber Concrete Structure | 1982 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. | 50 |  |  |  |  | 00000012 |  | Minor rust spots on wall and roof was observed. | [16 empty] | 50000 |  |  |  |  | IMG_6998 |  |  |  |  | 0 |  |  |  |  | fair | minor rust spots on wall and roof
AC | 5521 |  | KCF | Valve Room Access Door (Single) | 2019 | 1 | 1 | The asset was observed to be in very good condition. Asset to be replaced in the long term. | 15 |  |  |  |  | 00017520 | [18 empty] | 3500 |  |  |  |  | IMG_6947 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | Good
SC | 5538 |  | KCF | Valve Room Concrete Floor Slab | 1982 | 3 | 2 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 35 |  |  |  |  | 00017520 | [18 empty] | 38000 | 2000 | 2030 |  |  | IMG_6948 |  | King City Fisher ET Capital Project 2 |  |  | 0 |  |  |  |  | good
SC | 5516 | 00008872 | KCF | Valve Room Concrete Roof | 1982 | 4 | 2 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 35 |  |  |  |  | 00017520 | King City FS ET Valve Room | [17 empty] | 10000 | 1000 | 2030 |  |  | IMG_0209 |  | King City Fisher ET Capital Project 2 |  |  | 0 |  |  |  |  | good
BM | 5408 | 00089466 | KCF | Valve Room Dehumidifier | 2020 | 2 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 30 | Manufacturer: Ebac Industrial Products Inc. Model: WM-150 |  |  |  | 00017520 | King City FS ET Valve Room | [8 empty] | Area 1N Linear Water & Wells |  | Building Mechanical |  |  |  | W-WW |  |  | 3000 |  |  |  |  | IMG_0184 |  |  |  |  | 0 |  |  |  |  | good
BM | 5360 | 00089468 | KCF | Valve Room Exhaust Fan | 2020 | 2 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 30 | Manufacturer: Broan-Nutone Model L900. |  |  |  | 00017520 | King City FS ET Valve Room | [8 empty] | Area 1N Linear Water & Wells |  | Process Mechanical |  |  |  | W-WW |  |  | 5000 |  |  |  |  | IMG_0140 |  |  |  |  | 0 |  |  |  |  | Good condition
SIC | 5481 | 00089471 | KCF | Valve Room High Temperature Switch | 2020 | 1 | 1 | The asset was observed to be in very good condition. Asset to be replaced in the long term. | 15 | KCETFS_BLDS_TSHL1, Manufacturer: Honey |  |  |  | 00017520 | King City FS ET Valve Room | [17 empty] | 500 |  |  |  |  | IMG_4895 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
ES | 5366 | 00006494 | KCF | Valve Room LED Lighting Fixtures | 2020 | 2 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 25 | 3 LED lighting fixtures in total |  |  |  | 17513 | King City FS ET Valve Room | [8 empty] | Area 1N Linear Water & Wells |  | Electrical System |  |  |  | W-WW |  |  | 2500 |  |  |  |  | IMG_4894 |  |  |  |  | 0 |  |  |  |  | good
SIC | 5484 | 00088517 | KCF | Valve Room Low Temperature switch | 2020 | 1 | 1 | The asset was observed to be in very good condition. Asset to be replaced in the long term. | 15 | KCETFS_BLDS_TSHL1, Manufacturer: Honeywell |  |  |  | 00017510 | King City FS ET Valve Room | [17 empty] | 500 |  |  |  |  | IMG_4898 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SC | 5557 |  | KCF | Valve Room Masonry Blockwall | 1982 | 4 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 35 |  |  |  |  | 00017520 | [18 empty] | 25000 |  |  |  |  | IMG_6951 |  |  |  |  | 0 |  |  |  |  | good
SC | 5518 | 00008874 | KCF | Valve Room Mechanical Pipe Support | 2020 | 3 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 55 |  |  |  |  | 00017520 | King City FS ET Valve Room | [17 empty] | 5000 |  |  |  |  | IMG_6948 |  |  |  |  | 0 |  |  |  |  | good
BM | 5462 |  | KCF | Valve Room Motorized Damper | 2020 | 2 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 30 | Size: 500x500 mm, Manufacturer: Nailor, Model: 1020-IB/-IBF, damper includes Belimo actuator LF120 (120/1/60) interlocked with valve room exhaust fan |  |  |  | 00017520 | [18 empty] | 2500 |  |  |  |  | IMG_0203 |  |  |  |  | 0 |  |  |  |  | Good
AC | 5526 |  | KCF | Valve Room Protective Floor Coating | 2019 | 1 | 1 | The asset was observed to be in very good condition. Asset to be replaced in the long term. | 15 |  |  |  |  | 00017520 | [18 empty] | 2000 |  |  |  |  | IMG_6948 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
SIC | 5487 |  | KCF | Valve Room Sump Pit Float Switch | 2020 | 1 | 1 | The asset was observed to be in very good condition. Asset to be replaced in the long term. | 15 |  |  |  |  | 00017520 | King City FS ET Valve Room | [17 empty] | 500 |  |  |  |  | IMG_0117 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | Good
BM | 5352 | 00089469 | KCF | Valve Room Unit Heater | 2020 | 2 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 30 | Capacity: 5 kW, Manufacturer: Ouellet, Model: OAS05000AM |  |  |  | 00017520 | King City FS ET Valve Room |  | M00037 | [6 empty] | Area 1N Linear Water & Wells |  | Building Mechanical |  |  |  | W-WW |  |  | 3500 |  |  |  |  | IMG_0143 |  |  |  |  | 0 |  |  |  |  | Good
AC | 5525 |  | KCF | Valve Room Wall and Ceiling Paint | 2019 | 1 | 1 | The asset was observed to be in very good condition. Asset to be replaced in the long term. | 15 |  |  |  |  | 00017520 | [18 empty] | 5000 |  |  |  |  | IMG_6951 | King City Fisher ET Capital Project 2 |  |  |  | 0 |  |  |  |  | good
BM | 5505 |  | KCF | Water Sampling Sink and Piping | 2020 | 2 | 1 | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. | 30 |  |  |  |  | 00017520 | [18 empty] | 1000 |  |  |  |  | img_0101 |  |  |  |  | 0 |  |  |  |  | good
SW | 5441 |  | KCF | Watermain | 1984 | 5 | 3 | The asset was assumed to be in fair condition. | 25 | 400mm ductile iron watermain. Approx. total length 18m |  |  |  | 17512 | [18 empty] | 25000 | [9 empty] | 0