## Sheet1
CategoryCode | seqNum | assetTag | facility | assetName | installYear | COF | condition | observations | remainingESL | Description | Process | building | inspectorName | LocationTag | LocationORIGINAL | defect1 | manufacturer | TransmitterModel | TransducerModel | TransducerSerial | InstMeva | installationDate | InstType | ServiceArea | FacilityType | LifeCycleCategory | SerialNo | Parent | RotatingItem | Site | defect2 | defect3 | repCost | RehabRepairCost | RehabRepairYear | RehabRepairCost2 | RehabRepairYear2 | photoName | repProjectName | rehabProjectName | rehab2ProjectName | Status | InspectionYear | rehabComment1 | rehabCost1 | rehabComment2 | rehabCost2 | defect1Input | defect2Input | defect3Input
SC | 5554 |  | KWPH | Reservoir Steel Tank | 1984 | 5 | 3 | The asset was observed to be in fair condition. Address structural deficiencies. Asset to be replaced at the end of remaining service life. | 22 |  |  |  |  | 00006881 |  | Leakage staining noted on interior of tank at top of wall was observed. | [16 empty] | 1500000 | 150000 | 2025 | 0 |  | IMG_7031 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | 0 |  | 0 |  | 0 | leakage staining noted on interior of tank at top of wall
SCS | 5567 |  | KWPH | Reservoir Interior Coating | 1984 | 4 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 12 |  |  |  |  | 00006881 | [18 empty] | 750000 | 0 |  | 0 |  | IMG_7014 | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | good
SCS | 5555 |  | KWPH | Reservoir Exterior Coating | 1984 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 12 |  |  |  |  | 00006881 | [18 empty] | 575000 | 0 |  | 0 |  | IMG_7011 | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | good
SW | 5452 |  | KWPH | 750mm Watermain | 2008 | 5 | 3 | The asset was assumed to be in fair condition. Asset to be replaced at end of service life. | 47 | 750mm CPP watermain on site. Approx. 30m in length |  |  |  | 00006881 | [18 empty] | 100000 | 0 |  | 0 | [6 empty] | 0 |  | 0 |  | 0
SW | 5575 |  | KWPH | Chamber No.2 Concrete Structure | 2008 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 47 |  |  |  |  | 00006881 | [18 empty] | 100000 | 0 |  | 0 |  | IMG_7091 |  |  |  |  | 0 |  | 0 |  | 0 | good
SC | 5569 |  | KWPH | Valve Chamber Concrete Structure | 1984 | 4 | 3 | The asset was observed to be in fair condition. Structural repairs to address deficiency. Provisions for structural repairs. Asset to be replaced at the end of remaining service life. | 22 |  |  |  |  | 00016091 |  | Localized rust spots were observed. | [16 empty] | 100000 | 10000 | 2025 | 10000 | 2038 | IMG_7077 |  | Keswick West Park Heights Reservoir Capital Project 1 | Keswick West Park Heights Reservoir Capital Project 2 |  | 0 |  | 0 |  | 0 | localized rust spots
SW | 5443 |  | KWPH | Asphalt Driveway | 1984 | 2 | 3 | The asset was observed to be in fair condition.Reconstruct or repave asphalt surfaces on site in the next capital project. | 6 | Asphalt driveway, including parking spots andasphalt around tank. |  |  |  | 00006881 |  | Large amount of cracking observed at driveway and parking spots. | [14 empty] | Edge of asphalt along asphalt around reservoir was damaged and breaking off. |  | 65000 |  |  |  |  | IMG_20210510_095755 | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 | Reconstruct or repave asphalt surfaces on site. | 60000 | Remove and replace full depth asphalt at location that is damaged (along the edge). Raise gravel shoulder between tank and asphalt to ensure positive drainage away from tank and across pavement | 15000 | Large amount of cracking observed at driveway and parking spots. | Edge of asphalt along asphalt around tank is damaged and breaking off.
SW | 5451 |  | KWPH | 600mm Watermain | 1984 | 5 | 3 | The asset was assumed to be in fair condition. Asset to be replaced at end of service life. | 23 | 600mm ductile iron watermain on site. Approx. 20m in length |  |  |  | 00006881 | [18 empty] | 60000 | 0 |  | 0 | [6 empty] | 0 |  | 0 |  | 0
SIC | 5206 | 00083300 | KWPH | Facility PAC Control Panel | 2014 | 4 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 11 |  |  |  |  | 00016092 | West Park Heights Res Chemical Storage Room |  | M00899 | [6 empty] | Area 3 Water Treatment |  | Electrical System | 03-01-D |  |  | W-WW |  |  | 60000 | 0 |  | 0 |  | img_1313 | Keswick West Park Heights Reservoir Capital Project 2 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
PM | 5267 | 00055035 | KWPH | Reservoir Inlet/Outlet Line Piping | 2014 | 5 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 23 | Diameter: 450mm, approximately 33 meters. |  |  |  | 00016086 | West Park Heights Res Tank | [8 empty] | Area 3 Water Treatment | [5 empty] | W-WW |  |  | 54000 | 0 |  | 0 |  | IMG_0405 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | Good
PM | 5170 | 00017994 | KWPH | Chlorination System 2 | 2002 | 4 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 9 | US Filter -Wallce & Tiernan, model V10k |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room |  | M00899 | [6 empty] | Area 3 Water Treatment |  | Process Mechanical | 234300009501-001887 |  |  | W-WW |  |  | 45000 | 0 |  | 0 |  | IMG_0503 | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
PM | 5168 | 00017993 | KWPH | Chlorination System 1 | 2002 | 4 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 9 | US Filter -Wallce & Tiernan, model V10k |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room |  | M00899 | [6 empty] | Area 3 Water Treatment |  | Process Mechanical | 234300009501-001891 |  |  | W-WW |  |  | 45000 | 0 |  | 0 |  | IMG_0493 | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SW | 5589 |  | KWPH | Chamber No.1 Concrete Structure | 2008 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. | 47 |  |  |  |  | 00016092 | [18 empty] | 40000 | 0 |  | 0 |  | IMG_7086 |  |  |  |  | 0 |  | 0 |  | 0 | good
SW | 5447 |  | KWPH | Storm Sewer | 1984 | 3 | 3 | The asset was assumed to be in fair condition. Asset to be replaced at the end of its service life. | 23 | 450mm conc. storm sewer from drain chamber to maintenance hole. Approx. 23m in length to PL |  |  |  | 00006881 | [18 empty] | 38000 | 0 |  | 0 | [6 empty] | 0 |  | 0 |  | 0
PM | 5614 | 00055035 | KWPH | Reservoir Valving and Mixing System | 2014 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 23 | 3 tideflex variable orfice inlet nozzles and two waterflex outlet check valves. |  |  |  | 00016086 | [18 empty] | 35000 | 0 |  | 0 |  | IMG_0405 |  |  |  |  | 0 |  | 0 |  | 0 | Good
ES | 5624 |  | KWPH | Reservoir Tank Grounding | 2014 | 0 | 3 | The asset was observed to be in fair condition. Connect the grounding rods to the base of the steel tank. | 26 |  |  |  |  | 00016092 |  | At some locations, the grounding rods were not connected to the weld connectors at the base of the steel tank. | [16 empty] | 30000 | 5000 | 2026 | 0 | 0 | IMG_1227 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | 0 |  | 0 |  | 0
SW | 5442 |  | KWPH | Chainlink Fence | 1984 | 2 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 6 | Chainlink fence around site, approximately 205m. |  |  |  | 00006881 |  | Signs of corrosion at various locations of the fence. | [16 empty] | 25000 | 0 |  | 0 |  | IMG_20210510_095527 | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | Signs of corrosion at various locations of the fence.
PM | 5472 |  | KWPH | Chamber No.1 Watermain Butterfly Valve | 2008 | 3 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 17 | Diameter: 750mm, with AWWA square operator nut and extension stem |  |  |  | 00016092 |  | Minor surface corrosion was observed. | [16 empty] | 20000 | 0 |  | 0 |  | IMG_0686 | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | Minor surface corrosion
PM | 5617 |  | KWPH | Chamber No.2 Watermain Butterfly Valve 1 | 2008 | 3 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 17 | Diameter: 750mm, with AWWA square operator nut and extension stem |  |  |  | 00016092 |  | Minor surface corrosion was observed. | [16 empty] | 20000 | 0 |  | 0 |  | IMG_0726 | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | Minor surface corrosion
PM | 5471 |  | KWPH | Chamber No.2 Watermain Butterfly Valve 2 | 2008 | 3 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 17 | Diameter: 750mm, with AWWA square operator nut and extension stem | [5 empty] | Minor surface corrosion was observed. | [16 empty] | 20000 | 0 |  | 0 |  | IMG_0725 | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | Minor surface corrosion
PM | 5470 |  | KWPH | Chamber No.2 Watermain Butterfly Valve 3 | 2008 | 3 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 17 | Diameter: 750mm, with AWWA square operator nut and extension stem | [5 empty] | Minor surface corrosion was observed. | [16 empty] | 20000 | 0 |  | 0 |  | IMG_0724 | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | minor surface corrosion
SIC | 5610 | 00006896 | KWPH | Chlorination Building Security Panels | 2014 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 | Three (3) honeywell panels in total |  |  |  | 00016086 | [12 empty] | RANGER 8980 | [5 empty] | 20000 | 0 |  | 0 |  | IMG_4753 | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | good
SIC | 5465 | 00004230 | KWPH | Chlorine Weight Scale | 2002 | 3 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the short term. | 5 | Avery Weigh-Tronix |  |  |  | 00016089 |  | Minor surface corrosion was observed. | [16 empty] | 20000 | 0 |  | 0 |  | IMG_0494 | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | minor surface corrosion
ES | 5195 | 00006893 | KWPH | Panel Board LP A | 2002 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 12 |  |  |  |  | 00016090 | West Park Heights Res Control Room |  | M00129 | [6 empty] | Area 3 Water Treatment |  | Electrical System | T2 |  |  | W-WW |  |  | 20000 | 0 |  | 0 |  | img_1301 | Keswick West Park Heights Reservoir Capital Project 2 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SW | 5216 | 00011149 | KWPH | Site Drainage (soft surfaces) | 1984 | 1 | 3 | The asset was observed to be in fair condition. | 25 | Site drainage on soft surfaces |  |  |  | 00006881 | West Park Heights Reservoir | Various locations damaged by tires or animals. | [7 empty] | Area 3 Water Treatment | W - Storage Reservoir | Siteworks |  |  |  | W-WW |  |  | 20000 | 0 |  | 0 |  | IMG_20210510_100127 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | Various locations damaged by tires or animals.
SW | 5449 |  | KWPH | Reservoir Overflow Pipe | 1984 | 4 | 3 | The asset was assumed to be in fair condition. Asset to be replaced at the end of its service life. | 23 | 450mm ductile iron overflow pipe from reservoir to drain chamber. Approx. 8.0m in length |  |  |  | 00006881 | [18 empty] | 17500 | 0 |  | 0 | [6 empty] | 0 |  | 0 |  | 0
ES | 5261 | 00055029 | KWPH | Panel Board LP B | 2014 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 18 | LP B, Panel Board, Lighting Panel |  |  |  | 00016090 | West Park Heights Res Control Room | [8 empty] | Area 3 Water Treatment | [5 empty] | W-WW |  |  | 15000 | 0 |  | 0 |  | IMG_4759 | Keswick West Park Heights Reservoir Capital Project 2 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
PM | 5259 | 00055027 | KWPH | Valve Chamber Inlet/Outlet Line Butterfly Valve 1 | 2014 | 3 | 3 | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 23 | Diameter: 450mm, Val-Matic Model 2018XF, electric actuator by Rotork Type IQS-12FA10-B4, 120/1/60 |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | Surface corrosion was observed. | M00926 | [6 empty] | Area 3 Water Treatment | [5 empty] | W-WW |  |  | 15000 | 0 |  | 0 |  | IMG_0572 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | Surface corrosion
PM | 5181 | 00055021 | KWPH | Valve Chamber Inlet/Outlet Line Butterfly Valve 2 | 2014 | 3 | 3 | The asset was observed to be in fair condition. Replace the asset at the end of its service life. | 23 | Diameter: 450mm, Val-Matic Model |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | Minor surface corrosion was observed. | [7 empty] | Area 3 Water Treatment |  | Process Mechanical |  |  |  | W-WW |  |  | 15000 | 0 |  | 0 |  | IMG_0588 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | Minor surface corrosion
SC | 5587 |  | KWPH | Reservoir Side Access Hatch 2 | 1984 | 3 | 3 | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 22 |  |  |  |  | 00006881 |  | Minor surface corrosion was observed. | [16 empty] | 14000 | 0 |  | 0 |  | IMG_7012 |  |  |  |  | 0 |  | 0 |  | 0 | Minor surface corrosion
SC | 5553 | 00011171 | KWPH | Chemical Room Concrete Blockwall | 1984 | 4 | 3 | The asset was observed to be in fair condition. Structural repairs to address deficiency. Provisions for structural repairs. Asset to be replaced at the end of remaining service life. | 22 |  |  |  |  | 00016089 |  | Step cracking in mortar was observed. | [16 empty] | 12000 | 4000 | 2025 | 4000 | 2038 | IMG_7068 |  | Keswick West Park Heights Reservoir Capital Project 1 | Keswick West Park Heights Reservoir Capital Project 2 |  | 0 |  | 0 |  | 0 | step cracking in mortar
ES | 5193 | 00006891 | KWPH | Generator Panel | 2002 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 12 | 24 Circuits |  |  |  | 00016090 | West Park Heights Res Control Room |  | M00059 | [6 empty] | Area 3 Water Treatment |  | Electrical System | GP3P60-20 |  |  | W-WW |  |  | 12000 | 0 |  | 0 |  | img_1295 | Keswick West Park Heights Reservoir Capital Project 2 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SIC | 5464 | 00055023 | KWPH | Reservoir Inlet/Outlet Line Bidirectional Flowmeter | 2014 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 | KSTKWP_TWR_LIT1, Endress+Hauser, Promag, diameter: 250mm |  |  |  | 00016091 | [18 empty] | 12000 | 0 |  | 0 |  | IMG_0578 | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | Good
PM | 5268 | 00055036 | KWPH | Reservoir Overflow Piping | 1984 | 4 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 23 | Diameter: 350mm, above ground,approximately 12 meters. |  |  |  | 00016086 | West Park Heights Res Tank | [8 empty] | Area 3 Water Treatment | [5 empty] | W-WW |  |  | 12000 | 0 |  | 0 |  | IMG_4697 | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | Good
PM | 5258 | 00055026 | KWPH | Valve Chamber Inlet/Outlet Line Butterfly Valve 1 Electric Actuator | 2014 | 3 | 3 | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 23 | Rotork Type IQS-12FA10-B4, 120/1/60 |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | Minor paint peeling was observed. | M00120 | [6 empty] | Area 3 Water Treatment |  |  | 0122960102 |  |  | W-WW |  |  | 11000 | 0 |  | 0 |  | IMG_0682 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | minor paint peeling
PM | 5252 | 00055020 | KWPH | Valve Chamber Inlet/Outlet Line Butterfly Valve 2 Electric Actuator | 2014 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 23 | Diameter: 450mm |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber |  | M00120 | [6 empty] | Area 3 Water Treatment |  |  | 0122960101 |  |  | W-WW |  |  | 11000 | 0 |  | 0 |  | IMG_1398 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SIC | 5198 | 00006896 | KWPH | Chlorination Building Entry Security System | 2014 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 | Security System includind card readerS and password enter panel. |  |  |  | 00016086 | West Park Heights Res Control Room |  | M00026 | [6 empty] | Area 3 Water Treatment |  | Health and Safety | RANGER 8980 |  |  | W-WW |  |  | 10000 | 0 |  | 0 |  | IMG_4701 | Keswick West Park Heights Reservoir Capital Project 2 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
AC | 5564 |  | KWPH | Chlorination Building Exterior Brick Veneer | 1984 | 1 | 2 | The asset was observed to be in good condition. Since Asset to be replaced in the long term. | 6 |  |  |  |  | 00006881 |  | Minor localized spalling/erosion at bottom was observed. | [16 empty] | 10000 | 0 |  | 0 |  | IMG_7052 | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | localized spalling/erosion at bottom
AC | 5512 | 00011174 | KWPH | Chlorination Building Roofing System | 2014 | 2 | 2 | The asset was observed to be in good condition. Base on the visual observation, the asset may not requrie any replacement in 10 years from now. Replacement of the roofing system is recommended in the long term. | 11 |  |  |  |  | 00016086 | West Park Heights Reservoir | [17 empty] | 10000 | 0 |  | 0 |  | IMG_7046 | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | good
SW | 5579 |  | KWPH | Drain Chamber Concrete Structure | 1984 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 23 |  |  |  |  | 00016092 | [18 empty] | 10000 | 0 |  | 0 |  | IMG_7058 |  |  |  |  | 0 |  | 0 |  | 0 | good
SC | 5566 | 00011171 | KWPH | Electrical Room Concrete Blockwall | 1984 | 4 | 3 | The asset was observed to be in fair condition. Structural repairs to address deficiency. Provisions for structural repairs. Asset to be replaced at the end of remaining service life. | 22 |  |  |  |  | 00016090 |  | Mortar step cracking was observed. | [16 empty] | 10000 | 3000 | 2025 | 3000 | 2038 | IMG_7055 |  | Keswick West Park Heights Reservoir Capital Project 1 | Keswick West Park Heights Reservoir Capital Project 2 |  | 0 |  | 0 |  | 0 | mortar step cracking
SIC | 5271 | 00083301 | KWPH | Facility PAC Control Panel OIT Display and Panel | 2014 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 |  |  |  |  | 00016090 | West Park Heights Reservoir |  | M10189 | [6 empty] | Area 3 Water Treatment | W - Storage Reservoir | Instrumentation and Control | KSA1450204 |  |  | W-WW |  |  | 10000 | 0 |  | 0 |  | IMG_4767 | Keswick West Park Heights Reservoir Capital Project 2 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SIC | 5232 | 00017995 | KWPH | Free Chlorine Residual Analyzer | 2002 | 3 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 6 |  |  |  |  | 00016088 | West Park Heights Res Chemical Entry Room | The asset was outdated. | M00482 | CL17 |  |  | Chlorine |  |  | Area 3 Water Treatment |  | Instrumentation and Control | 030800008011 |  |  | W-WW |  |  | 10000 | 0 |  | 0 |  | IMG_4713 | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | outdated.
SIC | 5238 | 00018001 | KWPH | Network Antenna | 2014 | 1 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 | Installation year assumed to be 2010 |  |  |  | 00016090 | West Park Heights Res Control Room | [8 empty] | Area 3 Water Treatment |  | SCADA |  |  |  | W-WW |  |  | 10000 | 0 |  | 0 |  | img_7047 | Keswick West Park Heights Reservoir Capital Project 2 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SIC | 5619 | 00048031 | KWPH | OMNI Antenna & Cable | 2014 | 1 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 |  |  |  |  | 00006881 | Nobleton North ET Tank Roof | [8 empty] | Area 4 Water Treatment |  | SCADA/ Instrumentation/ Control | SC488-SF3SNF |  |  | W-WW |  |  | 10000 |  |  |  |  | img_7044 | Keswick West Park Heights Reservoir Capital Project 2 |  |  | OPERATING | 2019 |  |  |  |  | Good
SC | 5510 | 00011170 | KWPH | Reservoir Access Ladder | 2014 | 3 | 2 | The asset was observed to be in good condition. Replace the fall arrresst system. Asset to be replaced at the end of remaining service life. | 53 | Metal ladder to the top of Reservoir |  |  |  | 00006881 | West Park Heights Reservoir | Fall arrest system is not compliant to current csa standards. | [16 empty] | 10000 | 4000 | 2021 | 0 |  | IMG_7011 |  | Keswick West Park Heights Reservoir Health and Safety Project |  |  | 0 |  | 0 |  | 0 | Fall arrest system is not compliant to current CSA standards
SW | 5448 |  | KWPH | Reservoir Drain Piping | 1984 | 4 | 3 | The asset was assumed to be in fair condition. Asset to be replaced at the end of its service life. | 23 | 300mm reservoir drain from reservoir to drain chamber, length: 8 meters |  |  |  | 00006881 | [18 empty] | 10000 | 0 |  | 0 | [6 empty] | 0 |  | 0 |  | 0
SC | 5586 |  | KWPH | Reservoir Roof Guardrail | 2014 | 3 | 3 | The asset was observed to be in fair condition. Repair the cracked pipe sleeve. Asset to be replaced at the end of remaining service life. | 53 |  |  |  |  | 00006881 |  | Localized cracked pipe sleeve was observed. | [16 empty] | 10000 | 1000 | 2025 | 0 |  | IMG_7041 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | 0 |  | 0 |  | 0 | localized cracked pipe sleeve
SC | 5588 |  | KWPH | Reservoir Side Access Hatch 1 | 1984 | 3 | 3 | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 22 |  |  |  |  | 00006881 |  | Minor surface corrosion was observed. | [16 empty] | 10000 | 0 |  | 0 |  | IMG_7019 |  |  |  |  | 0 |  | 0 |  | 0 | minor surface corrosion
SIC | 5233 | 00017996 | KWPH | Total Chlorine Residual Analyzer | 2002 | 3 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 6 | Assume to be original |  |  |  | 00016088 | West Park Heights Res Chemical Entry Room | The asset was outdated. | M00482 | CL17 |  |  | Total Chlorine |  |  | Area 3 Water Treatment |  | Instrumentation and Control | 030800008013 |  |  | W-WW |  |  | 10000 | 0 |  | 0 |  | IMG_4710 | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | outdated.
SIC | 5620 | 00048032 | KWPH | YAGI Antenna & Cable | 2014 | 1 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 |  |  |  |  | 00006881 | Nobleton North ET Tank Roof | [8 empty] | Area 4 Water Treatment |  | SCADA/ Instrumentation/ Control | RY-9008 |  |  | W-WW |  |  | 10000 |  |  |  |  | IMG_7043 | Keswick West Park Heights Reservoir Capital Project 2 |  |  | OPERATING | 2019 |  |  |  |  | Good
SC | 5511 | 00011171 | KWPH | Chemical Entry Room Concrete Blockwall | 1984 | 4 | 3 | The asset was observed to be in fair condition. Structural repairs to address deficiency. Provisions for structural repairs. Asset to be replaced at the end of remaining service life. | 22 |  |  |  |  | 00016088 | West Park Heights Reservoir | Step cracking in mortar was observed. | [16 empty] | 9000 | 2000 | 2025 | 2000 | 2038 | IMG_7062 |  | Keswick West Park Heights Reservoir Capital Project 1 | Keswick West Park Heights Reservoir Capital Project 2 |  | 0 |  | 0 |  | 0 | step cracking in mortar
ES | 5609 |  | KWPH | Chlorination Building Indoor Lighting Fixtures | 2002 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 12 | 6 fluroscent fixtures |  |  |  | 00016086 | [18 empty] | 9000 | 0 |  | 0 |  | IMG_4717 | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | good
SIC | 5214 | 00006919 | KWPH | Reservoir Pressure-type Level Transmitter | 2014 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 | KSTKWP_TWR_LIT1 |  |  |  | 00016090 | West Park Heights Res Control Room |  | M00020 | [6 empty] | Area 3 Water Treatment |  | Instrumentation and Control | 94A-11316 |  |  | W-WW |  |  | 9000 | 0 |  | 0 |  | IMG_1392 | Keswick West Park Heights Reservoir Capital Project 2 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SC | 5572 |  | KWPH | Chemical Room Concrete Roof | 1984 | 4 | 2 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 22 |  |  |  |  | 00016089 | [18 empty] | 8000 | 1000 | 2031 | 0 |  | IMG_7065 |  | Keswick West Park Heights Reservoir Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
PM | 5466 |  | KWPH | Drain Chamber Drain Line Butterfly Valve | 1984 | 2 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 6 | Diameter: 300mm |  |  |  | 00016086 |  | Surface corrosion was observed. | [16 empty] | 8000 | 0 |  | 0 |  | IMG_0417 | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | surface corrosion
PM | 5184 | 00004246 | KWPH | Chlorine Booster Pump 1 | 2002 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 9 | Grundfos Model A96083903P117420003, 15.41 gpm at 90.6 ft, 0.75hp, 3439 rpm; 240VAC/1/60 |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber |  | M00951 | [6 empty] | Area 3 Water Treatment |  | Process Mechanical | 0002 |  |  | W-WW |  |  | 7500 | 0 |  | 0 |  | IMG_0653 | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
PM | 5185 | 00004247 | KWPH | Chlorine Booster Pump 2 | 2002 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 9 | Grundfos Model A96083903P117420002, 15.41 gpm at 90.6 ft, 0.75hp, 3439 rpm |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber |  | M00951 | [6 empty] | Area 3 Water Treatment |  | Process Mechanical | 0003 |  |  | W-WW |  |  | 7500 | 0 |  | 0 |  | IMG_0658 | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SC | 5578 |  | KWPH | Chemical Entry Concrete Roof | 1984 | 4 | 2 | The asset was observed to be in good condition. Structural repairs to address deficiency. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 22 |  |  |  |  | 00016088 | [18 empty] | 6000 | 1000 | 2031 | 0 |  | IMG_7062 |  | Keswick West Park Heights Reservoir Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
PM | 5467 |  | KWPH | Drain Chamber Overflow Line Flap Gate | 1984 | 2 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 6 | Diameter: 450mm |  |  |  | 00016092 |  | Surface corrosion was observed. | [16 empty] | 6000 | 0 |  | 0 |  | IMG_0417 | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | surface corrosion
SC | 5573 |  | KWPH | Electrical Room Concrete Roof | 1984 | 4 | 2 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 22 |  |  |  |  | 00016090 | [18 empty] | 6000 | 1000 | 2031 | 0 |  | IMG_7055 |  | Keswick West Park Heights Reservoir Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
ES | 5194 | 00006892 | KWPH | Enclosed Switch | 2002 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 12 | 125/250V, 100A |  |  |  | 00016090 | West Park Heights Res Control Room |  | M00129 | [6 empty] | Area 3 Water Treatment |  | Electrical System | T3 |  |  | W-WW |  |  | 6000 | 0 |  | 0 |  | IMG_1300 | Keswick West Park Heights Reservoir Capital Project 2 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
ES | 5613 |  | KWPH | Valve Chamber Indoor Lighting Fixtures | 2002 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 12 | 4 fluroscent fixtures |  |  |  | 00016091 | [18 empty] | 6000 | 0 |  | 0 |  | IMG_7076 | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | good
SW | 5590 |  | KWPH | Chamber No.1 Access Hatch | 2008 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. | 47 |  |  |  |  | 00016092 | [18 empty] | 5000 | 0 |  | 0 |  | IMG_7083 |  |  |  |  | 0 |  | 0 |  | 0 | good
SW | 5585 |  | KWPH | Chamber No.1 Access Ladder | 2008 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. | 47 |  |  |  |  | 00016092 | [18 empty] | 5000 | 0 |  | 0 |  | IMG_7084 |  |  |  |  | 0 |  | 0 |  | 0 | good
SW | 5581 |  | KWPH | Chamber No.2 Access Hatch 1 | 2008 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 47 |  |  |  |  | 00016092 | [18 empty] | 5000 | 0 |  | 0 |  | IMG_7072 |  |  |  |  | 0 |  | 0 |  | 0 | good
SW | 5582 |  | KWPH | Chamber No.2 Access Hatch 2 | 2008 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. | 47 |  |  |  |  | 00016092 | [18 empty] | 5000 | 0 |  | 0 |  | IMG_7072 |  |  |  |  | 0 |  | 0 |  | 0 | good
SW | 5583 |  | KWPH | Chamber No.2 Access Ladder 1 | 2008 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. | 47 |  |  |  |  | 00016092 | [18 empty] | 5000 | 0 |  | 0 |  | IMG_7091 |  |  |  |  | 0 |  | 0 |  | 0 | good
SW | 5584 |  | KWPH | Chamber No.2 Access Ladder 2 | 2008 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. | 47 |  |  |  |  | 00016092 | [18 empty] | 5000 | 0 |  | 0 |  | IMG_0722 |  |  |  |  | 0 |  | 0 |  | 0 | good
BM | 5177 | 00004239 | KWPH | Chemical Entry Room Exhaust Fan | 1984 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 6 | Greenheck Model DSQ-100-B-QD; 1/6hp. 115VAC/1/60, 1140 rpm |  |  |  | 00016088 | West Park Heights Res Chemical Storage Room |  | M00069 | [6 empty] | Area 3 Water Treatment |  | Building Mechanical | 85F04708 |  |  | W-WW |  |  | 5000 | 0 |  | 0 |  | IMG_0469 | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
BM | 5166 | 00004227 | KWPH | Chemical Room Exhaust Fan | 1984 | 2 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 6 | Greenheck Model DSQ-80-DGF-QD; 1550rpm. |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room | Minor surface corrosion was observed. | M00069 | [6 empty] | Area 3 Water Treatment |  | Building Mechanical | 85E01526 |  |  | W-WW |  |  | 5000 | 0 |  | 0 |  | IMG_0532 | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | Minor surface corrosion
ES | 5200 | 00006900 | KWPH | Chlorination Building Emergency Lights | 2002 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 12 | 2 units with battery packs. |  |  |  | 00016086 | West Park Heights Reservoir |  | M00606 | [6 empty] | Area 3 Water Treatment | W - Storage Reservoir | Electrical System |  |  |  | W-WW |  |  | 5000 | 0 |  | 0 |  | IMG_4724 | Keswick West Park Heights Reservoir Capital Project 2 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
ES | 5196 | 00006894 | KWPH | Chlorine Booster Pump 1 Disconnect Switch | 2002 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 12 |  |  |  |  | 00016090 | West Park Heights Res Control Room |  | M00571 | [6 empty] | Area 3 Water Treatment |  | Electrical System |  |  |  | W-WW |  |  | 5000 | 0 |  | 0 |  | img_1302 | Keswick West Park Heights Reservoir Capital Project 2 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
ES | 5197 | 00006895 | KWPH | Chlorine Booster Pump 2 Disconnect Switch | 2002 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 12 |  |  |  |  | 00016090 | West Park Heights Res Control Room |  | M00311 | [6 empty] | Area 3 Water Treatment |  | Electrical System |  |  |  | W-WW |  |  | 5000 | 0 |  | 0 |  | IMG_1304 | Keswick West Park Heights Reservoir Capital Project 2 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SC | 5556 |  | KWPH | Reservoir Roof Hatch 1 | 1984 | 3 | 3 | The asset was assumed to be in fair condition. Asset to be replaced at the end of remaining service life. | 22 |  |  |  |  | 00006881 |  | The hatch was covered in roofing material. | [16 empty] | 5000 | 0 |  | 0 |  | IMG_7038 |  |  |  |  | 0 |  | 0 |  | 0 | covered in roofing material
SC | 5568 |  | KWPH | Reservoir Roof Hatch 2 | 1984 | 3 | 3 | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 22 |  |  |  |  | 00006881 |  | The hatch was covered in roofing material. | [16 empty] | 5000 | 0 |  | 0 |  | IMG_7045 |  |  |  |  | 0 |  | 0 |  | 0 | covered in roofing material
SC | 5571 |  | KWPH | Valve Chamber Access Hatch 1 | 1984 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 22 |  |  |  |  | 00016091 | [18 empty] | 5000 | 0 |  | 0 |  | IMG_7069 |  |  |  |  | 0 |  | 0 |  | 0 | good
SC | 5570 |  | KWPH | Valve Chamber Access Ladder 1 | 1984 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 22 |  |  |  |  | 00016091 | [18 empty] | 5000 | 0 |  | 0 |  | IMG_7077 |  |  |  |  | 0 |  | 0 |  | 0 | good
SC | 5576 |  | KWPH | Valve Chamber Access Ladder 2 | 1984 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 22 |  |  |  |  | 00016091 | [18 empty] | 5000 | 0 |  | 0 |  | IMG_7080 |  |  |  |  | 0 |  | 0 |  | 0 | good
BM | 5190 | 00055017 | KWPH | Valve Chamber Dehumidifier | 2002 | 2 | 3 | The asset was observed to be in fair condition. Asset to be upgraded in the next capital project as the valve chamber was noted to be humid. | 6 | Manufacturer: Ebac Inductrial Products Ltd. model 10264CS-US, capacity 17 PPD; 120/1/60; 350 W; built-in controls |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | Moderate corrosion was observed. | [7 empty] | Area 3 Water Treatment |  | Building Mechanical | 251000341 |  |  | W-WW |  |  | 5000 | 0 |  | 0 |  | IMG_0602 | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | Moderate corrosion
PM | 5254 | 00055022 | KWPH | Valve Chamber Inlet/Outlet Line Flexible Coupling | 2014 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 23 | diameter: 250mm |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | [8 empty] | Area 3 Water Treatment | [5 empty] | W-WW |  |  | 5000 | 0 |  | 0 |  | IMG_1396 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
PM | 5257 | 00055025 | KWPH | Valve Chamber Inlet/Outlet Line Piping | 2014 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 23 | Diameter: 250mm, length: 8 meters |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | [8 empty] | Area 3 Water Treatment | [5 empty] | W-WW |  |  | 5000 | 0 |  | 0 |  | IMG_0619 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | Good
SIC | 5262 | 00055030 | KWPH | Reservoir Inlet/Outlet Line Flowmeter Transmitter | 2014 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 | FIT Display |  |  |  | 00016088 | West Park Heights Res Chemical Entry Room |  | M00405 | [6 empty] | Area 3 Water Treatment |  |  | FA02E916000 |  |  | W-WW |  |  | 4000 | 0 |  | 0 |  | img_4706 | Keswick West Park Heights Reservoir Capital Project 2 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SW | 5215 | 00011144 | KWPH | Swing Gate | 1984 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 6 |  |  |  |  | 00006881 | West Park Heights Reservoir | [8 empty] | Area 3 Water Treatment | W - Storage Reservoir | Siteworks |  |  |  | W-WW |  |  | 4000 | 0 |  | 0 |  | IMG_20210510_095106 | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | Good
SIC | 5463 | 00004234 | KWPH | Vacuum Regulator 1 | 2002 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 6 | Manufacturer: US Filter -Wallce & Tiernan |  |  |  | 00016089 | [12 empty] | BK17251 | [5 empty] | 4000 | 0 |  | 0 |  | IMG_4744 | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | good
SIC | 5171 | 00004235 | KWPH | Vacuum Regulator 2 | 2002 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 6 | Manufacturer: US Filter -Wallce & Tiernan |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room |  | M00899 | [6 empty] | Area 3 Water Treatment |  | Process Mechanical | BK17251 |  |  | W-WW |  |  | 4000 | 0 |  | 0 |  | IMG_4744 | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
PM | 5250 | 00055018 | KWPH | Valve Chamber Blind Flange | 2014 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 23 | Blind flange for an adandonded pipe line. |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | [8 empty] | Area 3 Water Treatment | [5 empty] | W-WW |  |  | 4000 | 0 |  | 0 |  | IMG_0630 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
PM | 5475 |  | KWPH | Chamber No.1 Watermain Air Release Valve | 2008 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 17 | 50 DIA Combination Air Relief/ Vacuum Valve c/w isolation ball valve, by ARI model D-040-C2 |  |  |  | 00016092 | [18 empty] | 3500 | 0 |  | 0 |  | IMG_0744 | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | Good
PM | 5469 |  | KWPH | Chamber No.2 Watermain Air Release Valve | 2008 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 17 | 50 DIA Combination Air Relief/ Vacuum Valve c/w isolation ball valve, by ARI model D-040-C2 | [22 empty] | 3500 | 0 |  | 0 |  | IMG_0730 | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | good
AC | 5551 |  | KWPH | Chemical Entry Access Door (Single) | 1984 | 1 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 6 |  |  |  |  | 00016088 |  | Corrosion was observed at bottom of door frame. | [16 empty] | 3500 | 0 |  | 0 |  | IMG_7060 | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | corrosion at bottom of door frame
AC | 5552 |  | KWPH | Chemical Room Access Door (Single) | 1984 | 1 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 5 |  |  |  |  | 00016089 |  | Worn paint at bottom was observed. | [16 empty] | 3500 | 0 |  | 0 |  | IMG_7062 | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | worn paint at bottom
SIC | 5173 | 00004235 | KWPH | Chlorine Injection Line 1 Eductor | 2002 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 6 |  |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room |  | M00899 | [6 empty] | Area 3 Water Treatment |  | Process Mechanical |  |  |  | W-WW |  |  | 3500 | 0 |  | 0 |  | IMG_0510 | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SIC | 5174 | 00004236 | KWPH | Chlorine Injection Line 1 Electric Actuator | 2002 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 6 | True Blue Model EBV-65 |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room |  | M00894 | [6 empty] | Area 3 Water Treatment |  | Process Mechanical | 9373-083 |  |  | W-WW |  |  | 3500 | 0 |  | 0 |  | IMG_0510 | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | Good
SIC | 5172 | 00004234 | KWPH | Chlorine Injection Line 2 Eductor | 2002 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 6 |  |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room |  | M00899 | [6 empty] | Area 3 Water Treatment |  | Process Mechanical |  |  |  | W-WW |  |  | 3500 | 0 |  | 0 |  | IMG_0510 | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SIC | 5175 | 00004237 | KWPH | Chlorine Injection Line 2 Electric Actuator | 2002 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 6 | True Blue Model EBV-65 |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room |  | M00894 | [6 empty] | Area 3 Water Treatment |  | Process Mechanical | 9373-083 |  |  | W-WW |  |  | 3500 | 0 |  | 0 |  | IMG_0510 | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
AC | 5565 |  | KWPH | Electrical Room Access Door (Single) | 1984 | 1 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 6 |  |  |  |  | 00016090 |  | Corrosion was observed on kick plate at bottom. | [16 empty] | 3500 | 0 |  | 0 |  | IMG_7053 | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | corrosion on kick plate at bottom
BM | 5248 | 00055016 | KWPH | Valve Chamber Air Supply Fan | 2014 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 23 | Twin City Model DSI-120AAL; 115/1/60; 1/8hp, ODP enclosure |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | [8 empty] | Area 3 Water Treatment |  |  | K12-000000078996 |  |  | W-WW |  |  | 3500 | 0 |  | 0 |  | IMG_0642 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
BM | 5167 | 00004228 | KWPH | Chemical Room Motorized Damper | 1984 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 6 | Damper, c/w Honeywell actuator; 120/1/60; |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room | [8 empty] | Area 3 Water Treatment |  | Building Mechanical |  |  |  | W-WW |  |  | 3000 | 0 |  | 0 |  | IMG_0524 | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
BM | 5165 | 00004226 | KWPH | Chemical Room Unit Heater | 2014 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 23 | wall mount Unit Heater, 3.6 kW, 208/1/60; Ouellet Model OCC4800AM-MO-TB6/CCG4800AM-MO-TB6, the heater appear to be new |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room |  | M00037 | [6 empty] | Area 3 Water Treatment |  | Building Mechanical |  |  |  | W-WW |  |  | 3000 | 0 |  | 0 |  | IMG_0519 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | very good
PM | 5616 | 00004246 | KWPH | Chlorine Booster Pump Piping System | 2002 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 9 |  |  |  |  | 00016091 | [12 empty] | 0002 | [5 empty] | 3000 | 0 |  | 0 |  | IMG_0653 | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | good
PM | 5223 | 00017056 | KWPH | Chlorine Injection System Tubing System | 2002 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 9 | Chlorine system tubing system from valve chamber to chlorine room. |  |  |  | 00016086 | West Park Heights Res Tank | [8 empty] | Area 3 Water Treatment |  | Process Mechanical |  |  |  | W-WW |  |  | 3000 | 0 |  | 0 |  | IMG_0618 | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SW | 5580 |  | KWPH | Drain Chamber Access Hatch | 1984 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 23 |  |  |  |  | 00016092 | [18 empty] | 3000 | 0 |  | 0 |  | IMG_7057 |  |  |  |  | 0 |  | 0 |  | 0 | good
SIC | 5269 | 00080207 | KWPH | Facility PAC Control Panel 3 Layer Ethernet Switch | 2014 | 2 | 2 | The asset was assumed to be in good condition. Asset to be replaced in the intermediate term. | 11 | KSETWP Ethernet Switch, Inside PAC control Panel |  |  |  | 00006881 | West Park Heights Reservoir |  | M01002 | [6 empty] | Area 3 Water Treatment | W - Storage Reservoir | Instrumentation and Control | FOC1834Z4H1 |  |  | W-WW |  |  | 3000 | 0 |  | 0 |  |  | Keswick West Park Heights Reservoir Capital Project 2 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SIC | 5244 | 00028277 | KWPH | Facility PAC Control Panel Network Radio Modem | 2014 | 2 | 2 | The asset was assumed to be in good condition. Asset to be replaced in the long term. | 11 | KST1RAD101,Inside PAC control Panel |  |  |  | 00016090 | West Park Heights Res Control Room |  | M01018 | [6 empty] | Area 3 Water Treatment |  | SCADA | 831028 |  |  | W-WW |  |  | 3000 | 0 |  | 0 |  |  | Keswick West Park Heights Reservoir Capital Project 2 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SIC | 5243 | 00028276 | KWPH | Facility PAC Control Panel RPU | 2014 | 2 | 2 | The asset was assumed to be in good condition. Asset to be replaced in the long term. | 11 | Inside PAC control Panel |  |  |  | 00016090 | West Park Heights Res Control Room |  | M00020 | [6 empty] | Area 3 Water Treatment |  | SCADA | 32520A39 |  |  | W-WW |  |  | 3000 | 0 |  | 0 |  |  | Keswick West Park Heights Reservoir Capital Project 2 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SIC | 5275 | 00083387 | KWPH | Facility PAC Control Panel UPS | 2014 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 | Inside PAC control Panel |  |  |  | 00006881 | West Park Heights Reservoir |  | M10181 | [6 empty] | Area 3 Water Treatment | W - Storage Reservoir | Instrumentation and Control | GK053A0118 |  |  | W-WW |  |  | 3000 | 0 |  | 0 |  |  | Keswick West Park Heights Reservoir Capital Project 2 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
SC | 5577 |  | KWPH | Valve Chamber Access Hatch 2 | 1984 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 22 |  |  |  |  | 00016091 | [18 empty] | 3000 | 0 |  | 0 |  | IMG_7056 |  |  |  |  | 0 |  | 0 |  | 0 | good
BM | 5189 | 00004251 | KWPH | Valve Chamber Sump Pump | 1984 | 2 | 4 | The asset was observed to be in poor condition. Asset to be replaced in the intermediate term. | 6 | Submersible Centrifugal Pump with associated piping, 120/1/60 |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | Severe corrosion was observed. | [7 empty] | Area 3 Water Treatment |  | Process Mechanical |  |  |  | W-WW |  |  | 3000 | 0 |  | 0 |  | IMG_0606 | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | Severe corrosion
HSS | 5273 | 00083304 | KWPH | Chemical Entry Room Chlorine Gas Detector | 2014 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 8 | KSTKWP_CL2D_GCL21 |  |  |  | 00016088 | West Park Heights Res Chemical Entry Room |  | M10086 | A-ULTIMAX-PL-18 |  |  | Gas |  |  | Area 3 Water Treatment |  | Instrumentation and Control | A17-400747637 |  |  | W-WW |  |  | 2000 | 0 |  | 0 |  | IMG_4719 | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
BM | 5178 | 00004240 | KWPH | Chemical Entry Room Motorized Damper | 1984 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 6 | Damper, c/w Honeywell actuator; 120/1/60; |  |  |  | 00016088 | West Park Heights Res Chemical Storage Room |  | M00076 | [6 empty] | Area 3 Water Treatment |  | Building Mechanical |  |  |  | W-WW |  |  | 2000 | 0 |  | 0 |  | IMG_0470 | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
HSS | 5229 | 00017992 | KWPH | Chemical Room Chlorine Gas Detector | 2014 | 0 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 8 | KST1CLD101 |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room |  | M00937 | 50-125 |  |  | Chlorine Gas |  |  | Area 3 Water Treatment |  | Instrumentation and Control | A17-0023409 |  |  | W-WW |  |  | 2000 | 0 |  | 0 |  | IMG_1262 | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
AC | 5561 |  | KWPH | Chemical Room Protective Floor Coating | 1984 | 1 | 5 | The asset was observed to be in very poor condition as it had failed. The coating to be applied in the intermediate term. | 5 |  |  |  |  | 00016089 |  | The asset had failed. | [16 empty] | 2000 | 0 |  | 0 |  | IMG_7064 | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | failed
SW | 5574 |  | KWPH | Drain Chamber Access Ladder | 1984 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 23 |  |  |  |  | 00016092 | [18 empty] | 2000 | 0 |  | 0 |  | IMG_7058 |  |  |  |  | 0 |  | 0 |  | 0 | good
SIC | 5272 | 00083302 | KWPH | Facility PAC Control Panel OIT Computer | 2014 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 11 |  |  |  |  | 00006881 | West Park Heights Reservoir |  | M10189 | [6 empty] | Area 3 Water Treatment | W - Storage Reservoir | Instrumentation and Control | 14E-088/KSTKWP_PAC |  |  | W-WW |  |  | 2000 | 0 |  | 0 |  | IMG_4767 | Keswick West Park Heights Reservoir Capital Project 2 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
PM | 5607 |  | KWPH | Valve Chamber Sampling Line | 2002 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 9 |  |  |  |  | 00016091 | [18 empty] | 2000 | 0 |  | 0 |  | IMG_1450 | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | good
PM | 5474 |  | KWPH | Chamber No.2 Watermain Drain Gate Valve 1 | 2008 | 2 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 17 | Diameter: 150mm, with 50 mm square operating nut and extension stem |  |  |  | 00016092 |  | Minor surface corrosion was observed. | [16 empty] | 1500 | 0 |  | 0 |  | IMG_0725 | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | Minor surface corrosion
PM | 5473 |  | KWPH | Chamber No.2 Watermain Drain Gate Valve 2 | 2008 | 2 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 17 | Diameter: 150mm, with 50 mm square operating nut and extension stem |  |  |  | 00016092 |  | Minor surface corrosion was observed. | [16 empty] | 1500 | 0 |  | 0 |  | IMG_0724 | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | minor surface corrosion
AC | 5513 | 00011176 | KWPH | Chlorination Building Louvre Grilles | 1984 | 1 | 2 | The asset was observed to be in good condition. The asset typically has an expected service life longer than 15 years. It is recommended to replace the asset the long term. | 11 | two (2) in total |  |  |  | 00006881 | West Park Heights Reservoir | [17 empty] | 1500 | 0 |  | 0 |  | IMG_1321 | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | good
BM | 5247 | 00055015 | KWPH | Valve Chamber Air Supply ductwork | 2014 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 23 | ducting system: 150DIA PVC c/w thermal insulation in jacket |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | [8 empty] | Area 3 Water Treatment | [5 empty] | W-WW |  |  | 1500 | 0 |  | 0 |  | IMG_0554 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
BM | 5176 | 00004238 | KWPH | Chemical Entry Room Electric Heater | 2014 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 23 | wall mount convection Heater, by Stelpro, 1 kW, 120/1/60 |  |  |  | 00016088 | West Park Heights Res Chemical Entry Room |  | M00037 | [6 empty] | Area 3 Water Treatment |  | Building Mechanical |  |  |  | W-WW |  |  | 1000 | 0 |  | 0 |  | IMG_0477 |  |  |  | OPERATING | 0 |  | 0 |  | 0 | good
AC | 5549 |  | KWPH | Chemical Entry Room Protective Floor Coating | 1984 | 1 | 5 | The asset was observed to be in very poor condition as it had failed. The coating to be applied in the intermediate term. | 6 |  |  |  |  | 00016088 |  | The asset had failed. | [16 empty] | 1000 | 0 |  | 0 |  | IMG_7062 | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | failed
SIC | 5239 | 00018060 | KWPH | Chemical Entry Room Temperature Switch | 1984 | 1 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 6 | Installtion year assumed to be 1984 |  |  |  | 00016088 | West Park Heights Res Control Room |  | M00076 | T631A1063 |  |  | Temperature |  |  | Area 3 Water Treatment |  | Instrumentation and Control | NOT AVAILABLE |  |  | W-WW |  |  | 1000 | 0 |  | 0 |  | IMG_4702 | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
ES | 5608 |  | KWPH | Chlorination Building Outdoor Lighting Fixture | 2002 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 12 | One (1) in total. Installation year assumed to be 2010. |  |  |  | 00016086 | [18 empty] | 1000 | 0 |  | 0 |  | IMG_4698 | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | good
SIC | 5213 | 00006918 | KWPH | Chlorine System Pressure Gauges | 2002 | 2 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 6 | Two (2) in total. |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room | Minor surface corrosion was observed. | M00924 | [6 empty] | Area 3 Water Treatment |  | Instrumentation and Control |  |  |  | W-WW |  |  | 1000 | 0 |  | 0 |  | IMG_1258 | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | minor surface corrosion
AC | 5548 |  | KWPH | Electrical Room Protective Floor Coating | 1984 | 1 | 5 | The asset was observed to be in very poor condition as it had failed. The coating to be applied in the intermediate term. | 6 |  |  |  |  | 00016090 |  | The asset had failed. | [16 empty] | 1000 | 0 |  | 0 |  | IMG_7056 | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | failed
SIC | 5611 |  | KWPH | Electrical Room Temperature Switch | 2014 | 1 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 11 |  |  |  |  | 00016090 | [12 empty] | NOT AVAILABLE | [5 empty] | 1000 | 0 |  | 0 |  | IMG_4771 | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | good
SIC | 5227 | 00017988 | KWPH | Valve Chamber Float Switch | 2002 | 2 | 3 | The asset was assumed to be in fair condition. Asset to be replaced in the intermediate term. | 6 |  |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber |  | M00061 | Not available |  |  | Level |  |  | Area 3 Water Treatment |  | Instrumentation and Control | NOT AVAILABLE |  |  | W-WW |  |  | 1000 | 0 |  | 0 |  | IMG_1403 | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0
BM | 5612 |  | KWPH | Valve Chamber Gooseneck Vent | 1984 | 1 | 2 | The asset was observed to be in good condition. The asset typically had a longer theoretical service life. It is to be replaced by the end of its estimated remaining service life. | 23 |  |  |  |  | 00016091 |  | Minor surface corrosion was observed. | [16 empty] | 1000 | 0 |  | 0 |  | IMG_1312 |  |  |  |  | 0 |  | 0 |  | 0 | minor surface corrosion
SIC | 5622 | 00017988 | KWPH | Valve Chamber Sump Pit Float Switch | 2002 | 2 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 6 |  |  |  |  | 00016091 | West Park Heights Res Valve/Meter Chamber | Metal stain on the surface. | M00061 | Not available |  |  | Level |  |  | Area 3 Water Treatment |  | Instrumentation and Control | NOT AVAILABLE |  |  | W-WW |  |  | 1000 | 0 |  | 0 |  | IMG_0609 | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
BM | 5192 | 00004254 | KWPH | Valve Chamber Unit heater | 2002 | 2 | 3 | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 6 | Heating System, Convection Heater, wall mount, by Ouellet |  |  |  | 00016091 | West Park Heights Res Control Room | Minor corrosion was observed. | M00037 | [6 empty] | Area 3 Water Treatment |  | Building Mechanical |  |  |  | W-WW |  |  | 1000 | 0 |  | 0 |  | IMG_0594 | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | Minor corrosion
AC | 5550 |  | KWPH | Chemical Room Ceiling Paint | 1984 | 1 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 6 |  |  |  |  | 00016089 | [18 empty] | 700 | 0 |  | 0 |  | IMG_7065 | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | good
HSS | 5242 | 00024557 | KWPH | Eyewash Station | 2014 | 3 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 8 |  |  |  |  | 00016089 | West Park Heights Res Chemical Storage Room |  | M00191 | [6 empty] | Area 3 Water Treatment |  | Health and Safety |  |  |  | W-WW |  |  | 600 | 0 |  | 0 |  | IMG_4725 | Keswick West Park Heights Reservoir Capital Project 1 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
AC | 5562 |  | KWPH | Chemical Entry Room Ceiling Paint | 1984 | 1 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 6 |  |  |  |  | 00016088 | [18 empty] | 500 | 0 |  | 0 |  | IMG_7062 | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | good
AC | 5563 |  | KWPH | Electrical Room Ceiling Paint | 1984 | 1 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 6 |  |  |  |  | 00016090 | [18 empty] | 500 | 0 |  | 0 |  | IMG_7055 | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | good
HSS | 5621 |  | KWPH | First Aid Kit | 2020 | 1 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 14 |  |  |  |  | 00016089 | [18 empty] | 500 | 0 |  | 0 |  | IMG_1280 | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | good
HSS | 5623 |  | KWPH | Fire Extinguisher | 2020 | 1 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 14 | Total of 1 |  |  |  | 00016086 | [18 empty] | 300 | 0 |  | 0 |  | img_1234 | Keswick West Park Heights Reservoir Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | good
HSS | 5245 | 00044422 | KWPH | Battery Acid Spill Containment Kit | 2020 | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 14 |  |  |  |  | 00006881 | West Park Heights Reservoir |  | M10266 | [6 empty] | Area 3 Water Treatment | W - Storage Reservoir | Health and Safety |  |  |  | W-WW |  |  | 100 | 0 |  | 0 |  | img_1297 | Keswick West Park Heights Reservoir Capital Project 2 |  |  | OPERATING | 0 |  | 0 |  | 0 | good
HSS | 5618 |  | KWPH | Chlorine Room Smoke Detector | 2014 | 1 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 8 |  |  |  |  | 00016089 | [18 empty] | 0 | 0 |  | 0 |  | IMG_1271 | Keswick West Park Heights Reservoir Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | good