## Sheet1
CategoryCode | facility | remainingESL | seqNum | COF | assetTag | assetName | RehabRepairCost | repCost | RehabRepairYear | rehabProjectName | observations | condition | rehabComment2 | RehabRepairCost2 | RehabRepairYear2 | installYear | defect1Input | Description | Process | building | inspectorName | LocationTag | LocationORIGINAL | manufacturer | TransmitterModel | TransducerModel | TransducerSerial | InstMeva | installationDate | InstType | ServiceArea | FacilityType | LifeCycleCategory | SerialNo | Parent | RotatingItem | Site | defect1 | defect2 | defect3 | rehabComment1 | rehabCost1 | photoName | repProjectName | rehab2ProjectName | Status | InspectionYear | rehabCost2 | defect2Input | defect3Input
SC | MAN | 44 | 5057 | 5 |  | Elevated Tank Steel Tank |  | 1300000 |  |  | The asset was observed to be in good condition. Elevated tank steel tank to be replaced at the end of remaining service life. | 2 |  | 0 |  | 2004 | minor corrosion |  |  |  |  | 790900018 | [15 empty] | Minor corrosion was observed. |  |  |  | 0 | IMG_4055 |  |  |  | 0 | 0
SC | MAN | 44 | 5056 | 4 |  | Elevated Tank Concrete Structure | 50000 | 900000 | 2030 | Mt Albert North ET Capital Project 2 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Elevated tank concrete structure to be replaced at the end of remaining service life. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 790900018 | [18 empty] | Provision for structural repairs every 10 years. | 0 | IMG_4103 |  |  |  | 0 | 0
SCS | MAN | 22 | 5073 | 3 |  | Elevated Tank Exterior Coating | 205000 | 780000 | 2026 | Mt Albert North ET Capital Project 1 | The asset was observed to be in fair condition. Exterior tank coating overcoating is recommended in five years. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 790900018 | [15 empty] | minor corrosion spots observed on the roof and shell of the elevated tank |  |  |  | 0 | IMG_4055 |  |  |  | 0 | 0
SCS | MAN |  | 5074 | 3 |  | Elevated Tank Interior Coating | 5000 | 450000 | 2023 | Mt Albert North ET Capital Project 1 | The asset was observed to be in good condition. Application of coating for the submarine floor hatch should be completed in the short term. | 3 |  | 0 |  | 2004 | good |  |  |  |  | 790900018 | [15 empty] | Minor spot corrosion and heavy mineral staining were observed. | The submarine floor hatch was hot dipped galvanised but not painted as it acted as a sacrificial anode. Now the zinc painted was gone so it should be painted. |  |  | 0 | IMG_4072 |  |  |  | 0 | 0
SW | MAN | 44 | 5009 | 4 |  | Elevated Tank Watermain |  | 71000 |  |  | The asset was assumed to be in fair condition. | 3 |  | 0 |  | 2004 |  | 300mm watermain, approximately 65m in length |  |  |  | 790900018 | [19 empty] | 0 |  |  |  |  | 0 | 0
SIC | MAN | 6 | 4988 | 4 | 00078461 | Elevated Tank NAC Panel |  | 60000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2004 | good | Network Access Closet Panel, Xmtetnl1 |  |  |  | 00017169 | Mt Alberta North ET Electrical Control Room | 1002018 | [8 empty] | Instrumentation and Control | 14E-088/MTETNL_NAC |  |  | W-WW |  |  |  |  | 0 | PXL_20201111_142225191 | Mt Albert North ET Capital Project 1 |  | OPERATING |  | 0
SC | MAN | 44 | 5064 | 3 |  | Elevated Tank Aluminum Upper Platform |  | 50000 |  |  | The asset was observed to be in good condition. Elevated tank aluminum platform to be replaced at the end of remaining service life. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 790900018 | [19 empty] | 0 | IMG_4103 |  |  |  | 0 | 0
SIC | MAN | 6 | 5035 | 4 | 00078460 | Elevated Tank MTETNL PAC Panel |  | 50000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 000000001 | [19 empty] | 0 | IMG_6352 | Mt Albert North ET Capital Project 1 |  |  | 0 | 0
PM | MAN | 44 | 5044 | 4 |  | Elevated Tank Overflow Line Piping |  | 47000 |  |  | The asset was observed to be in good condition. Replace the asset at the end of its service life. | 2 |  | 0 |  | 2004 | Good | Diameter: 300mm, Length(portion in elevated tank): 43 meters |  |  |  | 790900018 | [19 empty] | 0 | IMG_4103 |  |  |  | 0 | 0
PM | MAN | 44 | 5043 | 4 |  | Elevated Tank Outlet Line Piping |  | 43000 |  |  | The asset was observed to be in good condition. Replace the asset at the end of its service life. | 2 |  | 0 |  | 2004 | Good | Diameter: 300mm, Length(portion in elevated tank): 39 meters |  |  |  | 790900018 | [19 empty] | 0 | IMG_6298 |  |  |  | 0 | 0
SW | MAN | 19 | 5007 | 2 |  | Pavement | 30000 | 35000 | 2024 | Mt Albert North ET Capital Project 1 | The asset was observed to be in fair condition. Conduct pavement evaluation, and confirm if road resurfacing is sufficient or full reconstruction required. Extend the pavement to the site alternative exit point on Ridge Gate Cres. Pavement to be replaced | 3 |  | 0 |  | 2004 | Asphalt had cracking for entire length of driveway, with severe damage by elevated tank. | Asphalt pavement (incl. granular base) within site, from Ninth line entrance to elevated tank entrance. Approx. 450m2 |  |  |  | 790900018 | [15 empty] | Asphalt had cracking for entire length of driveway, with severe damage by elevated tank. | Damage of asphalt at entrance of site was observed. |  | Conduct pavement evaluation, and confirm if road resurfacing is sufficient or full reconstruction required. | 15000 | IMG_20201111_100101 | Mt Albert North ET Capital Project 2 |  |  | 0 | 0 | Damage of asphalt at entrance of site.
PM | MAN | 44 | 5042 | 4 |  | Elevated Tank Inlet Line Piping | 500 | 33000 | 2025 | Mt Albert North ET Capital Project 1 | The asset was observed to be in good condition. Replace the asset at the end of its service life. | 2 |  | 0 |  | 2004 | Good | Diameter: 300mm, Length(portion in elevated tank): 30 meters |  |  |  | 790900018 | [15 empty] | Minor surface corrosion was observed. |  |  |  | 0 | IMG_6273 |  |  |  | 0 | 0
SIC | MAN | 6 | 4989 | 4 | 00078458 | Elevated Tank Remote OIT Panel |  | 30000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2004 | good | MTENTL |  |  |  | 00017166 | Mt Alberta North ET Valve Room | M10189 | [8 empty] | Instrumentation and Control | KSA0868427 |  |  | W-WW |  |  |  |  | 0 | PXL_20201111_140549229 | Mt Albert North ET Capital Project 1 |  | OPERATING |  | 0
SC | MAN | 44 | 5063 | 4 |  | Elevated Tank Aluminum Ladder (Ground to Platform) | 15000 | 30000 | 2020 | Mt Albert North ET Capital Project 1 | The asset was observed to be in poor condition. Fall arrest system (TS rail) is required to be replaced immediately. | 4 |  | 0 |  | 2004 | good |  |  |  |  | 790900018 | [15 empty] | The Class Frontal-Fixed Rail Ladder (Class FRL) fall protection system was installed throughout, and it was no longer compliant to current CSA standards. |  |  |  | 0 | IMG_4103 |  |  |  | 0 | 0
SC | MAN | 44 | 5084 | 2 |  | Elevated Tank Inlet Pipe Support |  | 30000 |  |  | The asset was observed to be in good condition. Elevated tank inlet pipe support to be replaced at the end of remaining service life. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 790900018 | [19 empty] | 0 | IMG_4103 |  |  |  | 0 | 0
SC | MAN | 44 | 5085 | 2 |  | Elevated Tank Outlet Pipe Support |  | 30000 |  |  | The asset was observed to be in good condition. Elevated tank outlet pipe support to be replaced at the end of remaining service life. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 790900018 | [19 empty] | 0 | IMG_4103 |  |  |  | 0 | 0
SIC | MAN | 6 | 5026 | 3 |  | Elevated Tank Security System |  | 30000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 00017169 | [19 empty] | 0 | PXL_20201111_141948382 | Mt Albert North ET Capital Project 1 |  |  | 0 | 0
SC | MAN | 44 | 5121 | 3 |  | Valve Room Concrete Floor Slab | 3000 | 30000 | 2030 | Mt Albert North ET Capital Project 2 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. | 2 |  | 0 |  | 2004 | [5 empty] | 00017166 | [19 empty] | 0 | IMG_6253 |  |  |  | 0 | 0
SC | MAN | 44 | 5060 | 3 |  | Valve Room Masonry Blockwalls | 3000 | 30000 | 2030 | Mt Albert North ET Capital Project 2 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Valve room masonry blockwalls to be replaced at the end of remaining service life. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 00017166 | [18 empty] | Provision for structural repairs every 10 years. | 0 | IMG_4113 |  |  |  | 0 | 0
SW | MAN | 15 | 4999 | 2 |  | Chainlink Fence | 2000 | 25000 | 2024 | Mt Albert North ET Capital Project 1 | The asset was observed to be in fair condition. Re-attach barbed wire to top of fence. Install new mesh at location of damaged fence mesh. | 3 | Install new mesh at location of damaged fence mesh. |  |  | 2004 | Barbed wire was not attached to fence along west side of site for approximately 30m. | 1.8m high chainlink fence, with barbed wire on top. Approx. total length 180m |  |  |  | 790900018 | [15 empty] | Barbed wire was not attached to fence along west side of site for approximately 30m. | Fence mesh damaged at sw corner of site was observed. |  | Re-attach barbed wire to top of fence. | 1000 | IMG_20201111_102312 | Mt Albert North ET Capital Project 2 |  |  | 0 | 1000 | Fence mesh damaged at SW corner of site.
SC | MAN | 44 | 5069 | 3 |  | Elevated Tank Roof Guardrail | 15000 | 25000 |  | Mt Albert North ET Capital Project 1 | The asset was observed to be in good condition. It is recommended to conduct a full design review of the existing supporting structural for the telecommunication system to determine if any additional reinforcement is required. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 790900018 | [19 empty] | 0 | IMG_4087 |  |  |  | 0 | 0
SW | MAN | 25 | 5000 | 1 |  | Soft Drainage | 7000 | 25000 | 2024 | Mt Albert North ET Capital Project 1 | The asset was observed to be in poor condition. Regrade area around fire hydrant. Remove top soil and sod and place riprap at outlet of overflow pipe, ensure positive drainage towards property line and but away from adjacent property owner. | 4 | Remove top soil and sod and place riprap at outlet of overflow pipe, ensure positive drainage towards property line and but away from adjacent property owner. |  |  | 2004 | Low spots around fire hydrant | Soft surfaces throughout site, approximate area 1250m2. |  |  |  | 790900018 | [15 empty] | Low spots around fire hydrant was observed. | Damaged sod was observed at outlet of overflow pipe. |  | Regrade area around fire hydrant | 2500 | IMG_20201111_102456 |  |  |  | 0 | 7000 | Damaged sod at outlet of overflow pipe.
SC | MAN | 44 | 5065 | 4 |  | Elevated Tank Aluminum Ladder (Platform to Roof) | 10000 | 20000 | 2020 | Mt Albert North ET Capital Project 1 | The asset was observed to be in poor condition. Fall arrest system (TS rail) is required to be replaced immediately. | 4 |  | 0 |  | 2004 | Good | Platform to roof |  |  |  | 790900018 | [15 empty] | The Class Frontal-Fixed Rail Ladder (Class FRL) fall protection system was installed throughout, and it was no longer compliant to current CSA standards. |  |  |  | 0 | IMG_4095 |  |  |  | 0 | 0
SC | MAN | 44 | 5066 | 4 |  | Elevated Tank Aluminum Ladder (Roof to Tank) | 15000 | 20000 | 2020 | Mt Albert North ET Capital Project 1 | The asset was observed to be in poor condition. The ladder appear to be painted galvanised carbon steel type. Fall arrest system (TS rail) is required to be replaced immediately. Elevated tank ladder (roof to tank) to be replaced at the end of remaining | 4 |  | 0 |  | 2004 | poor | Roof to tank |  |  |  | 790900018 | [15 empty] | Rail slide was bent. The Class Frontal-Fixed Rail Ladder (Class FRL) fall protection system was installed throughout, and it was no longer compliant to current CSA standards. |  |  | Replace rail slide. | 0 | IMG_4072 |  |  |  | 0 | 0 | rail slide is bent
ES | MAN | 11 | 5020 | 2 |  | Elevated Tank Pedestal and Access Tube Lighting |  | 20000 |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. | 2 |  | 0 |  | 2004 | good | 8 fixtures in total |  |  |  | 00017166 | [19 empty] | 0 | PXL_20201111_140004696 | Mt Albert North ET Capital Project 2 |  |  | 0 | 0
SC | MAN | 44 | 5090 | 3 |  | Valve Room Composite Roof | 2000 | 20000 | 2030 | Mt Albert North ET Capital Project 2 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Valve room composite roof to be replaced at the end of remaining service life. | 2 |  | 0 |  | 2004 | Good |  |  |  |  | 00017166 | [15 empty] | Abandoned process equipment and other equipment was piled up on the roof. |  |  | Provision for structural repairs every 10 years. | 0 | IMG_4105 |  |  |  | 0 | 0
SW | MAN | 44 | 5010 | 2 |  | Sanitary Sewer | 15000 | 17500 | 2025 | Mt Albert North ET Capital Project 1 | The asset was assumed to be in fair condition. Sanitary service extension to Ridge Gate Crescent. | 3 |  | 0 |  | 2004 |  | 100mm sanitary sewer, approximately 22m in length |  |  |  | 790900018 | [19 empty] | 0 |  |  |  |  | 0 | 0
SC | MAN | 44 | 5091 | 3 |  | Electrical Control Room Composite Roof | 1000 | 15000 | 2030 | Mt Albert North ET Capital Project 2 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Electrical room composite roof to be replaced at the end of remaining service life. | 2 |  | 0 |  | 2004 | Good |  |  |  |  | 00017169 | [18 empty] | Provision for structural repairs every 10 years. | 0 | IMG_4106 |  |  |  | 0 | 0
SC | MAN | 44 | 5061 | 3 |  | Electrical Control Room Concrete Floor Slab | 1500 | 15000 | 2030 | Mt Albert North ET Capital Project 2 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 00017169 | [18 empty] | Provision for structural repairs every 10 years. | 0 | IMG_4126 |  |  |  | 0 | 0
SC | MAN | 44 | 5125 | 3 |  | Electrical Control Room Masonry Blockwalls | 1500 | 15000 | 2030 | Mt Albert North ET Capital Project 2 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Electrical room masonry blockwalls to be replaced at the end of remaining service life. | 2 |  | 0 |  | 2004 | [24 empty] | Provision for structural repairs every 10 years. | 0 | IMG_4108 |  |  |  | 0 | 0
ES | MAN | 11 | 5033 | 3 |  | Electrical Duct System and Conduit System |  | 15000 |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. | 2 |  | 0 |  | 2004 | good | Conduit system including conduit, and underground duct for electrical services |  |  |  | #N/A | Glenway RES Outside Sanitary Pumping Station | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  |  | 0 | IMG_4102 | Mt Albert North ET Capital Project 2 |  | W-WW | 2020 | 0
SIC | MAN | 6 | 4952 | 3 | 00017764 | Elevated Tank Outlet Piping Chlorine Analyzer |  | 15000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2004 | good | MTETNL_TWR_AIT1 Free Residual Chlorine Analyzer |  |  |  | 00017166 | Mt Alberta North ET Valve Room | M00482 | [8 empty] | Instrumentation and Control | 40300009396 |  |  | W-WW |  |  |  |  | 0 | PXL_20201111_140257952 | Mt Albert North ET Capital Project 1 |  | OPERATING |  | 0
SW | MAN | 44 | 5008 | 4 |  | Overflow Piping | 10000 | 15000 | 2024 | Mt Albert North ET Capital Project 1 | The asset was assumed to be in fair condition. Regrade area around pipe outlet to allow for above grade overflow outlet with grating on pipe. Place riprap at outlet. | 3 |  |  |  | 2004 |  | 300mm, length: 16.0m |  |  |  | 790900018 | [18 empty] | Regrade area around pipe outlet to allow for above grade overflow outlet with grating on pipe. Place riprap at outlet. | 10000 | IMG_20201111_100602 |  |  |  | 0
SIC | MAN | 6 | 4993 | 3 | 00041442 | Elevated Tank Level Indicating Transmitter |  | 12000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2004 | good | MTETNL_TWR_LIT1 |  |  |  | 790900018 | Mt Alberta North Elevated Tank | M00405 | [8 empty] | Instrumentation and Control | E904901509C |  |  | W-WW |  |  |  |  | 0 | PXL_20201111_140316939 | Mt Albert North ET Capital Project 1 |  | OPERATING |  | 0
PM | MAN | 12 | 4963 | 4 | 00024547 | Elevated Tank Outlet Line Flow Control Valve |  | 12000 |  |  | The asset was observed to be in fair condition. The Region recommended replacing the valve with a check valve. | 3 |  | 0 |  | 2004 | Good | 300 mm solenoid operated flow control valve, manufacturer: Singer Model S106 |  |  |  | 00017166 | Mt Alberta North ET Valve Room | M00818 | [8 empty] | Process Mechanical | 504-97 |  |  | W-WW | Minor surface corrosion was observed. |  |  | Resurface and repaint to protect against corrosion. | 0 | IMG_6313 | Mt Albert North ET Capital Project 2 |  | OPERATING |  | 0
ES | MAN | 11 | 4973 | 3 | 00024558 | Lighting Panel |  | 12000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2004 | good | Siemens Panel Board P1; 120/240V, 1PH, 30CCT, a 100A main breaker is included. |  |  |  | 00017169 | Mt Alberta North ET Electrical Control Room | M00125 | [8 empty] | Electrical System |  |  |  | W-WW |  |  |  |  | 0 | PXL_20201111_142000666 | Mt Albert North ET Capital Project 2 |  | OPERATING |  | 0
PM | MAN | 44 | 5041 | 4 |  | Elevated Tank Inlet/Outlet Line Piping | 1000 | 11000 | 2025 | Mt Albert North ET Capital Project 1 | The asset was observed to be in good condition. Replace the asset at the end of its service life. | 2 |  | 0 |  | 2004 | Good | Diameter: 300mm, Length(portion in elevated tank): 10 meters |  |  |  | 790900018 | [15 empty] | Minor surface corrosion was observed. |  |  |  | 0 | IMG_6280 |  |  |  | 0 | 0
SIC | MAN | 6 | 5022 | 2 | 00042848 | Elevated Tank Flow Transmitter |  | 10000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2004 | good | with two ultrasonic flow meters installed on inlet and outlet of the elevated tank pipe. |  |  |  | 00017166 | [19 empty] | 0 | PXL_20201111_140503354 | Mt Albert North ET Capital Project 1 |  |  | 0 | 0
ES | MAN | 44 | 5029 | 3 |  | Elevated Tank Grounding |  | 10000 |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 790900018 | [19 empty] | 0 | IMG_4100 |  |  |  | 0 | 0
SC | MAN | 44 | 5067 | 3 |  | Elevated Tank Roof Access Hatch |  | 10000 |  |  | The asset was observed to be in good condition. Elevated tank roof access hatch to be replaced at the end of remaining service life. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 790900018 | [19 empty] | 0 | IMG_4089 |  |  |  | 0 | 0
SC | MAN | 44 | 5068 | 3 |  | Elevated Tank Tank Access Hatch |  | 10000 |  |  | The asset was observed to be in good condition. Elevated tank tank access hatch to be replaced at the end of remaining service life. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 790900018 | [19 empty] | 0 | IMG_4088 |  |  |  | 0 | 0
SW | MAN | 44 | 4982 | 1 | 00032809 | Fire Hydrant | 1000 | 10000 | 2024 | Mt Albert North ET Capital Project 1 | The asset was observed to be in fair condition. Raise valve box to grade and regrade. | 3 |  | 0 |  | 2004 | Hydrant valve box settled (and ground around) by approximately 0.5m | Fire Hydrant and valve |  |  |  | 790900018 | Mt Alberta North Elevated Tank | M00100 | [8 empty] | Siteworks |  |  |  | W-WW | Hydrant valve box settled (and ground around) by approximately 0.5m. |  |  | Raise valve box to grade and regrade. | 1000 | IMG_20201111_094823 |  |  | OPERATING |  | 0
ES | MAN | 11 | 5028 | 3 | 00024561 | Inlet Piping Heat Tracing System |  | 10000 |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. | 2 |  | 0 |  | 2004 | good | Inlet Piping Heat Tracing System |  |  |  | 00017169 | [11 empty] | 15835 | [7 empty] | 0 | IMG_4103 | Mt Albert North ET Capital Project 2 |  |  | 0 | 0
SIC | MAN | 6 | 4953 | 3 | 00017760 | Network Antenna 1 |  | 10000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2004 | good | MTNTRAD103 Network Antenna & Cable |  |  |  | 790900018 | Mt Alberta North ET Valve Room | [9 empty] | SCADA |  |  |  | W-WW |  |  |  |  | 0 | IMG_4087 | Mt Albert North ET Capital Project 1 |  | OPERATING |  | 0
SIC | MAN | 6 | 4954 | 2 | 00017761 | Network Antenna 2 |  | 10000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2004 | good | MTNTRAD104 |  |  |  | 790900018 | Mt Alberta North ET Valve Room | [9 empty] | SCADA |  |  |  | W-WW |  |  |  |  | 0 | IMG_4084 | Mt Albert North ET Capital Project 1 |  | OPERATING |  | 0
ES | MAN | 11 | 5027 | 3 |  | Outlet Piping Heat Tracing System |  | 10000 |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. | 2 |  | 0 |  | 2004 | good | Outlet Piping Heat Tracing System |  |  |  | 00017169 | [11 empty] | 15837 | [7 empty] | 0 | IMG_4103 | Mt Albert North ET Capital Project 2 |  |  | 0 | 0
BM | MAN | 44 | 5037 | 2 |  | Plumbing and Drainage |  | 10000 |  |  | The asset was assumed to be in good condition based on its age. Asset to be replaced at the end of remaining service life. | 2 |  | 0 |  | 2004 | good | 100mm drainage piping for floor drain and future washroom. Piping is connected to 100mm sanitary main. Length(approximately): 20 meters |  |  |  | 790900018 | [19 empty] | 0 | IMG_4121 |  |  |  | 2019 | 0
SC | MAN | 44 | 5120 | 3 |  | Storage Room Concrete Floor Slab | 1000 | 10000 | 2030 | Mt Albert North ET Capital Project 2 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. | 2 |  | 0 |  | 2004 | [5 empty] | 000000001 | [19 empty] | 0 | IMG_6344 |  |  |  | 0 | 0
SC | MAN | 44 | 5062 | 3 |  | Storage Room Masonry Blockwalls | 1000 | 10000 | 2030 | Mt Albert North ET Capital Project 2 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Storage room masonry blockwalls to be replaced at the end of remaining service life. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 000000001 | [18 empty] | Provision for structural repairs every 10 years. | 0 | IMG_4123 |  |  |  | 0 | 0
SIC | MAN | 6 | 5025 | 3 | 00076067 | Elevated Tank Outlet Pipe Pressure Transmitter |  | 8500 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 00017166 | [19 empty] | 0 | PXL_20201111_140526897 | Mt Albert North ET Capital Project 1 |  |  | 0 | 0
SW | MAN | 44 | 5078 | 2 |  | Valve Chamber #1 Precast Concrete Structure |  | 8000 |  |  | The asset was observed to be in good condition. Asset to be replace at the end of its service life. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 790900018 | [19 empty] | 0 | IMG_4135 |  |  |  | 0 | 0
SW | MAN | 44 | 5079 | 2 |  | Valve Chamber #2 Precast Concrete Structure |  | 8000 |  |  | The asset was observed to be in good condition. Asset to be replace at the end of its service life. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 790900018 | [19 empty] | 0 | IMG_4137 |  |  |  | 0 | 0
SW | MAN | 44 | 5080 | 2 |  | Valve Chamber #3 Precast Concrete Structure |  | 8000 |  |  | The asset was observed to be in good condition. Asset to be replace at the end of its service life. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 790900018 | [19 empty] | 0 | IMG_4139 |  |  |  | 0 | 0
SC | MAN | 44 | 5058 | 3 |  | Foyer Aluminum Staircase |  | 6000 |  |  | The asset was observed to be in good condition. Foyer aluminum staircase to be replaced at the end of remaining service life. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 00017168 | [19 empty] | 0 | IMG_4107 |  |  |  | 0 | 0
ES | MAN | 11 | 5016 | 3 |  | Surge Protection Device |  | 6000 |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. | 2 |  | 0 |  | 2004 | good | Surge Protection Device, PTX 160, 120/240V, 30A |  |  |  | 00017169 | [19 empty] | 0 | PXL_20201111_142137604 | Mt Albert North ET Capital Project 2 |  |  | 0 | 0
ES | MAN | 11 | 5017 | 1 |  | Valve Room Lighting |  | 6000 |  |  | The asset was observed to be in good condition. The valve room lighting to be replaced with LED fixtures in next upgrade project. | 2 |  | 0 |  | 2004 | good | 2 linear fluorescent lighting fixtures,1 pendent mount, and 2 emergency lighting fixtures. |  |  |  | 00017166 | [20 empty] | PXL_20201111_140025870 | Mt Albert North ET Capital Project 2 |  |  | 0 | 0
AC | MAN | 6 | 5047 | 1 | 00024565 | Exterior Access Double Doors |  | 5500 |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of service life. | 3 |  | 0 |  | 2004 | corrosion at bottom of doors and door frame | double metal door |  |  |  | 00017168 | Mt Alberta North ET Foyer | [9 empty] | Architectural |  |  |  | W-WW | Corrosion was observed at bottom of door and door frame. | The doors swing inwards, based on OBC, the dow should be swing |  |  | 0 | IMG_4128 | Mt Albert North ET Capital Project 1 |  | OPERATING |  | 0
AC | MAN | 6 | 5050 | 1 | 00024562 | Valve Room Interior Double Doors |  | 5500 |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of service life. | 3 |  | 0 |  | 2004 | corrosion at bottom of door frame | double metal door |  |  |  | 00017166 | Mt Alberta North ET Valve Room | [9 empty] | Architectural |  |  |  | W-WW | Corrosion was observed at bottom of door frame. |  |  |  | 0 | IMG_4109 | Mt Albert North ET Capital Project 1 |  | OPERATING |  | 0
SIC | MAN | 6 | 4994 | 2 | 00078459 | Elevated Tank Remote OIT Panel Display and Computer |  | 5000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2004 | good | Advantech Computer |  |  |  | 00017166 | Mt Alberta North ET Valve Room | M10189 | [8 empty] | Instrumentation and Control | AFC1000532 |  |  | W-WW |  |  |  |  | 0 | PXL_20201111_140549229 | Mt Albert North ET Capital Project 1 |  | OPERATING |  | 0
PM | MAN | 24 | 4968 | 3 | 00024546 | Elevated Tank Inlet Line Check Valve | 500 | 5000 | 2025 | Mt Albert North ET Capital Project 1 | The asset was observed to be in fair condition. Resurface and repaint to protect against corrosion. Replace the asset at the end of its service life. | 3 |  | 0 |  | 2004 | Minor surface corrosion | 300mm check valve, manufacturer: Clow Kennedy |  |  |  | 00017166 | Mt Alberta North ET Valve Room | M00856 | [8 empty] | Process Mechanical |  |  |  | W-WW | Minor surface corrosion was observed. |  |  | Resurface and repaint to protect against corrosion. | 0 | IMG_6260 |  |  | OPERATING |  | 0
ES | MAN | 11 | 5030 | 3 |  | Elevated Tank Lightning Protection System |  | 5000 |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. | 2 |  | 0 |  | 2004 | good | 1 lightning air protection terminal |  |  |  | 790900018 | [19 empty] | 0 | IMG_4082 | Mt Albert North ET Capital Project 2 |  |  | 0 | 0
BM | MAN | 44 | 5036 | 1 |  | Elevated Tank Removable Louvred Vent |  | 5000 |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 790900018 | [19 empty] | 0 | IMG_4064 |  |  |  | 2019 | 0
PM | MAN | 24 | 5116 | 3 |  | Elevated Tank Roof Vent |  | 5000 |  |  | The asset was observed to be in fair condition. Replace the asset at the end of its service life. | 3 |  | 0 |  | 2004 | good |  |  |  |  | 790900018 | [15 empty] | Minor surface corrosion was observed. |  |  |  | 0 | 108_8562 |  |  |  | 0 | 0
SC | MAN | 44 | 5072 | 2 |  | Elevated Tank Submarine Floor Access Hatch |  | 5000 |  |  | The asset was observed to be in good condition. The cost for paint application is included under the asset Elevated Tank Interior Coating. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 790900018 | [15 empty] | The elevated tank side of the hatch was hot dipped galvanised but not painted, so it acted as a sacrificial anode. Now the zinc was gone so it should be painted. |  |  |  | 0 | IMG_4065 |  |  |  | 0 | 0
ES | MAN | 11 | 5015 | 3 | 00086712 | Generator Transfer Switch Panel |  | 5000 |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. | 2 |  | 0 |  | 2004 | good | Siemens Generator Transfer Switch Panel, EQ load centre, 120/240V, 30A |  |  |  | 00017169 | [19 empty] | 0 | PXL_20201111_141718982 | Mt Albert North ET Capital Project 2 |  |  | 0 | 0
ES | MAN | 11 | 4970 | 3 | 00024561 | Inlet Piping Heat Tracing Control Panel |  | 5000 |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. | 2 |  | 0 |  | 2004 | good | Heat Tracing and Monitoring Control Panel for inlet piping |  |  |  | 00017169 | Mt Alberta North ET Electrical Control Room | [9 empty] | Electrical System | 15835 |  |  | W-WW |  |  |  |  | 0 | PXL_20201111_141759008 | Mt Albert North ET Capital Project 2 |  | OPERATING |  | 0
SIC | MAN | 6 | 4991 | 3 | 00078396 | NAC Panel Network Ethernet Switch |  | 5000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2004 | good | inside Network Access Closet Panel |  |  |  | 00017169 | Mt Alberta North ET Electrical Control Room | M01002 | [8 empty] | Instrumentation and Control | FOC1847Z2E7 |  |  | W-WW |  |  |  |  | 0 | PXL_20201111_142225191 | Mt Albert North ET Capital Project 1 |  | OPERATING |  | 0
SIC | MAN | 6 | 4992 | 3 | 00078463 | NAC Panel Network Radio |  | 5000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2004 | good | Inside NAC Panel |  |  |  | 00017169 | Mt Alberta North ET Electrical Control Room | M00455 | [8 empty] | Instrumentation and Control | 0001966911 |  |  | W-WW |  |  |  |  | 0 | PXL_20201111_142225191 | Mt Albert North ET Capital Project 1 |  | OPERATING |  | 0
ES | MAN | 11 | 4961 | 3 | 00024560 | Outlet Piping Heat Tracing Control Panel |  | 5000 |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. | 2 |  | 0 |  | 2004 | good | Heat Tracing and Monitoring Control Panel for outlet piping |  |  |  | 00017169 | Mt Alberta North ET Electrical Control Room | [9 empty] | Electrical System | 15837 |  |  | W-WW |  |  |  |  | 0 | PXL_20201111_141847648 | Mt Albert North ET Capital Project 2 |  | OPERATING |  | 0
SIC | MAN | 6 | 4955 | 3 | 00017766 | Radio Modem |  | 5000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2004 | good | MTNTRAD101, Network, Radio Modem |  |  |  | 790900018 | Mt Alberta North ET Valve Room | M01018 | [8 empty] | SCADA | 1269550 |  |  | W-WW |  |  |  |  | 0 | IMG_4086 | Mt Albert North ET Capital Project 1 |  | OPERATING |  | 0
SC | MAN | 44 | 5092 | 3 |  | Storage Room Composite Roof | 1000 | 5000 | 2030 | Mt Albert North ET Capital Project 2 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Storage room composite roof to be replaced at the end of remaining service life. | 2 |  | 0 |  | 2004 | Good |  |  |  |  | 790900018 | [18 empty] | Provision for structural repairs every 10 years. | 0 | IMG_4104 |  |  |  | 0 | 0
HSS | MAN | 24 | 5070 | 4 |  | Elevated Tank Davit Socket Base (Platform Level) |  | 4000 |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 790900018 | [19 empty] | 0 | IMG_4101 |  |  |  | 0 | 0
HSS | MAN | 24 | 5071 | 4 |  | Elevated Tank Davit Socket Base (Roof Level) |  | 4000 |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 790900018 | [19 empty] | 0 | IMG_4093 |  |  |  | 0 | 0
AC | MAN | 6 | 5051 | 1 |  | Electrical Control Room Interior Door (Single) |  | 3500 |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of service life. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 00017169 | [19 empty] | 0 | IMG_4108 | Mt Albert North ET Capital Project 1 |  |  | 0 | 0
AC | MAN | 6 | 5046 | 1 | 00024566 | Valve Room Interior Single Door |  | 3500 |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of service life. | 3 |  | 0 |  | 2004 | corrosion at bottom of door frame | single metal door |  |  |  | 000000001 | Mt Alberta North ET Foyer | [9 empty] | Architectural |  |  |  | W-WW | Corrosion was observed at bottom of door frame. |  |  |  | 0 | IMG_4109 | Mt Albert North ET Capital Project 1 |  | OPERATING |  | 0
ES | MAN | 11 | 5032 | 3 |  | Elevated Tank Obstruction Lighting System |  | 3100 |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. | 2 |  | 0 |  | 2004 | good | Dual head lights |  |  |  | 790900018 | [19 empty] | 0 | IMG_4082 | Mt Albert North ET Capital Project 2 |  |  | 0 | 0
BM | MAN | 14 | 4981 | 2 | 00024559 | Electrical Control Room Electric Unit Heater |  | 3000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 2 |  | 0 |  | 2004 | Good | Electrical Control Room, forced air Heating System, Electric Unit Heater, by Stelpro; 3kW, 240/1/60; |  |  |  | 00017169 | Mt Alberta North ET Electrical Control Room | M00132 | [8 empty] | Building Mechanical | 40402 |  |  | W-WW |  |  |  |  | 0 | IMG_6361 | Mt Albert North ET Capital Project 2 |  | OPERATING |  | 0
HSS | MAN | 24 | 5088 | 4 |  | Elevated Tank Anchor Point (Roof Level) |  | 3000 |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 790900018 | [19 empty] | 0 | IMG_4091 |  |  |  | 0 | 0
SIC | MAN | 6 | 4990 | 3 | 00078462 | Elevated Tank Control Panel UPS |  | 3000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2004 | good | Inside of Elevated Tank MTETNL PAC Panel |  |  |  | 00017169 | Mt Alberta North ET Electrical Control Room | M10181 | [8 empty] | Instrumentation and Control | GH442A1091 |  |  | W-WW |  |  |  |  | 0 | IMG_6352 | Mt Albert North ET Capital Project 1 |  | OPERATING |  | 0
PM | MAN | 24 | 4962 | 3 | 00024535 | Elevated Tank Inlet Line Butterfly Valve 1 | 500 | 3000 | 2025 | Mt Albert North ET Capital Project 1 | The asset was observed to be in fair condition. Resurface and repaint to protect against corrosion. Replace the asset at the end of its service life. | 3 |  | 0 |  | 2004 | Minor surface corrosion | 300mm butterfly valve, manufacturer: Clow Kennedy |  |  |  | 00017166 | Mt Alberta North ET Valve Room | M00554 | [8 empty] | Process Mechanical |  |  |  | W-WW | Minor surface corrosion was observed. |  |  | Resurface and repaint to protect against corrosion. | 0 | IMG_6257 |  |  | OPERATING |  | 0
PM | MAN | 24 | 4969 | 3 | 00024534 | Elevated Tank Inlet Line Butterfly Valve 2 | 500 | 3000 | 2025 | Mt Albert North ET Capital Project 1 | The asset was observed to be in fair condition. Resurface and repaint to protect against corrosion. Replace the asset at the end of its service life. | 3 |  | 0 |  | 2004 | Minor surface corrosion | 300mm butterfly valve, manufacturer: Clow Kennedy |  |  |  | 00017166 | Mt Alberta North ET Valve Room | M00554 | [8 empty] | Process Mechanical |  |  |  | W-WW | Minor surface corrosion was observed. |  |  | Resurface and repaint to protect against corrosion. | 0 | IMG_6248 |  |  | OPERATING |  | 0
PM | MAN | 24 | 4983 | 3 | 00024541 | Elevated Tank Inlet/Outlet Line Butterfly Valve | 500 | 3000 | 2025 | Mt Albert North ET Capital Project 1 | The asset was observed to be in fair condition. Resurface and repaint to protect against corrosion. Replace the asset at the end of its service life. | 3 |  | 0 |  | 2004 | Minor surface corrosion | 300mm butterfly valve, manufacturer: Clow Kennedy |  |  |  | 00017166 | Mt Alberta North ET Valve Room | M00554 | [8 empty] | Process Mechanical |  |  |  | W-WW | Minor surface corrosion was observed. |  |  | Resurface and repaint to protect against corrosion. | 0 | IMG_6266 |  |  | OPERATING |  | 0
PM | MAN | 24 | 5013 | 3 |  | Elevated Tank Inlet/Outline Gate Valve 1 | 500 | 3000 | 2025 | Mt Albert North ET Capital Project 1 | The asset was observed to be in good condition. Resurface and repaint to protect against corrosion. Replace the asset at the end of its service life. | 2 |  | 0 |  | 2004 | Good | 300mm gate valve, installed in outdoor chamber |  |  |  | 790900018 | [15 empty] | Minor surface corrosion was observed due to environmental conditions. |  |  | Resurface and repaint to protect against corrosion. | 0 | IMG_6422 |  |  |  | 0 | 0
PM | MAN | 24 | 5011 | 3 |  | Elevated Tank Inlet/Outline Gate Valve 2 | 500 | 3000 | 2025 | Mt Albert North ET Capital Project 1 | The asset was observed to be in fair condition. Resurface and repaint to protect against corrosion. Replace the asset at the end of its service life. | 3 |  | 0 |  | 2004 | Good | 300mm gate valve, installed in outdoor chamber |  |  |  | 790900018 | [15 empty] | Minor surface corrosion was observed due to environmental conditions. |  |  | Resurface and repaint to protect against corrosion. | 0 | IMG_6408 |  |  |  | 0 | 0
PM | MAN | 24 | 5012 | 3 |  | Elevated Tank Inlet/Outline Gate Valve 3 | 500 | 3000 | 2025 | Mt Albert North ET Capital Project 1 | The asset was observed to be in good condition. Resurface and repaint to protect against corrosion. Replace the asset at the end of its service life. | 2 |  | 0 |  | 2004 | Good | 300mm gate valve, installed in outdoor chamber |  |  |  | 790900018 | [15 empty] | Minor surface corrosion was observed due to environmental conditions. |  |  | Resurface and repaint to protect against corrosion. | 0 | IMG_6385 |  |  |  | 0 | 0
SW | MAN | 15 | 4997 | 1 |  | Elevated Tank Ninth Line Access Gate |  | 3000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 2 |  | 0 |  | 2004 | Good. | 6.0m wide double gate located on Ninth Line |  |  |  | 790900018 | [19 empty] | 0 | IMG_20201111_094635 | Mt Albert North ET Capital Project 2 |  |  | 0 | 0
PM | MAN | 44 | 5045 | 3 |  | Elevated Tank Outlet Bypass Line Piping | 500 | 3000 | 2032 | Mt Albert North ET Capital Project 2 | The asset was observed to be in good condition. Remove the asset when flow control valve is installed. | 2 |  | 0 |  | 2004 | Good | Diameter: 150mm, Length(portion in elevated tank): 5 meters |  |  |  | 790900018 | [19 empty] | 0 | IMG_6253 |  |  |  | 0 | 0
PM | MAN | 24 | 4965 | 3 | 00024537 | Elevated Tank Outlet Line Butterfly Valve 1 | 500 | 3000 | 2025 | Mt Albert North ET Capital Project 1 | The asset was observed to be in fair condition. Resurface and repaint to protect against corrosion. Replace the asset at the end of its service life. | 3 |  | 0 |  | 2004 | minor surface corrosion | Outlet Control Isolation Butterfly valve, size: 300mm, manufacturer: Clow Kennedy |  |  |  | 00017166 | Mt Alberta North ET Valve Room | M00554 | [8 empty] | Process Mechanical |  |  |  | W-WW | Minor surface corrosion was observed. |  |  | Resurface and repaint to protect against corrosion. | 0 | IMG_6284 |  |  | OPERATING |  | 0
PM | MAN | 24 | 4975 | 3 | 00024538 | Elevated Tank Outlet Line Butterfly Valve 2 | 500 | 3000 | 2025 | Mt Albert North ET Capital Project 1 | The asset was observed to be in fair condition. Resurface and repaint to protect against corrosion. Replace the asset at the end of its service life. | 3 |  | 0 |  | 2004 | Minor surface corrosion | Outlet Control Isolation Butterfly valve, size: 300mm, manufacturer: Clow Kennedy |  |  |  | 00017166 | Mt Alberta North ET Valve Room | M00554 | [8 empty] | Process Mechanical |  |  |  | W-WW | Minor surface corrosion was observed. |  |  | Resurface and repaint to protect against corrosion. | 0 | IMG_6293 |  |  | OPERATING |  | 0
PM | MAN | 24 | 4977 | 3 | 00024540 | Elevated Tank Outlet Line Butterfly Valve 3 | 500 | 3000 | 2025 | Mt Albert North ET Capital Project 1 | The asset was observed to be in fair condition. Resurface and repaint to protect against corrosion. Replace the asset at the end of its service life. | 3 |  | 0 |  | 2004 | good | Outlet Control Isolation Butterfly valve, size: 300mm, manufacturer: Clow Kennedy |  |  |  | 00017166 | Mt Alberta North ET Valve Room | M00554 | [8 empty] | Process Mechanical |  |  |  | W-WW | Minor surface corrosion was observed. |  |  | Resurface and repaint to protect against corrosion. | 0 | IMG_6305 |  |  | OPERATING |  | 0
SW | MAN | 15 | 4998 | 1 |  | Elevated Tank Ridge Gate Cres Access Gate |  | 3000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 2 |  | 0 |  | 2004 | Good | 6.0m wide double gate for Ridge Gate crescent |  |  |  | 790900018 | [19 empty] | 0 | IMG_20201111_102248 | Mt Albert North ET Capital Project 2 |  |  | 0 | 0
SC | MAN | 44 | 5059 | 3 |  | Foyer Aluminum Guardrails |  | 3000 |  |  | The asset was observed to be in good condition. Foyer aluminum guardrails to be replaced at the end of remaining service life. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 00017168 | [19 empty] | 0 | IMG_4104 |  |  |  | 0 | 0
ES | MAN | 11 | 5014 | 1 |  | Foyer Lighting Fixtures |  | 3000 |  |  | The asset was observed to be in good condition. The incandescent lighting fixtures to be replaced with LED fixtures rated for wet locations in next upgrade. | 2 |  | 0 |  | 2004 | good | 5 lighting fixtures including 4 incandescent lighting fixtures and 1 emergency lighting fixture. |  |  |  | 790900018 | [20 empty] | PXL_20201111_140000689 | Mt Albert North ET Capital Project 2 |  |  | 0 | 0
BM | MAN | 25 | 4974 | 2 | 00024545 | Storage Room Electric Unit Heater |  | 3000 |  |  | The asset was observed to be in good condition. Storage room electric unit heater to be replaced at the end of remaining service life. | 2 |  | 0 |  | 2015 | good | PAC Room, Unit Heater, forced air Heating System, 5 kW; 240/1/60; by Outlet Model OAS05000T |  |  |  | 000000001 | Mt Alberta North ET Foyer | M00132 | [8 empty] | Building Mechanical | 40402 |  |  | W-WW |  |  |  |  | 0 | IMG_6348 |  |  | OPERATING |  | 0
BM | MAN | 26 | 4978 | 2 | 00024542 | Valve Room Electric Unit Heater |  | 3000 |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life | 2 |  | 0 |  | 2016 | good | Valve Room, Electric Unit Heater, forced air Heating System, 5 kW; 240/1/60; by Outlet Model OAS05000T |  |  |  | 00017166 | Mt Alberta North ET Valve Room | M00132 | [8 empty] | Building Mechanical |  |  |  | W-WW |  |  |  |  | 0 | IMG_6335 |  |  | OPERATING |  | 0
SC | MAN | 44 | 5086 | 4 |  | Elevated Tank Aluminum Ladder (Platform to Tank Bottom Hatch) | 1000 | 2500 | 2020 | Mt Albert North ET Capital Project 1 | The asset was observed to be in poor condition. Fall arrest system (TS rail) is required to be replaced immediately. | 4 |  | 0 |  | 2004 | Good | Platform to tank hatch |  |  |  | 790900018 | [15 empty] | The Class Frontal-Fixed Rail Ladder (Class FRL) fall protection system was installed throughout, and it was no longer compliant to current CSA standards. |  |  |  | 0 | IMG_4065 |  |  |  | 0 | 0
ES | MAN | 11 | 5021 | 1 |  | Outdoor Lighting |  | 2400 |  |  | The asset was observed to be in good condition. Asset to be replaced with LED fixtures in the next upgrade project. | 2 |  | 0 |  | 2004 | good | 2 fixtures |  |  |  | 790900018 | [20 empty] | PXL_20201111_134832486 | Mt Albert North ET Capital Project 2 |  |  | 0 | 0
HSS | MAN | 24 | 5087 | 4 |  | Elevated Tank Anchor Point (Platform Level) |  | 2000 |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 790900018 | [19 empty] | 0 | IMG_4066 |  |  |  | 0 | 0
PM | MAN | 24 | 4964 | 2 | 00024539 | Elevated Tank Outlet Bypass Line Butterfly Valve 1 | 500 | 2000 | 2032 | Mt Albert North ET Capital Project 2 | The asset was observed to be in good condition. Remove the asset when flow control valve is installed. | 2 |  | 0 |  | 2004 | Good | 150mm butterfly valve, manufacturer: Clow Kennedy |  |  |  | 00017166 | Mt Alberta North ET Valve Room | M00554 | [8 empty] | Process Mechanical |  |  |  | W-WW |  |  |  |  | 0 | IMG_6295 |  |  | OPERATING |  | 0
PM | MAN | 24 | 4966 | 2 | 00024536 | Elevated Tank Outlet Bypass Line Butterfly Valve 2 | 500 | 2000 | 2032 | Mt Albert North ET Capital Project 2 | The asset was observed to be in good condition. Remove the asset when flow control valve is installed. | 2 |  | 0 |  | 2004 | good | 150mm butterfly valve, manufacturer: Clow Kennedy |  |  |  | 00017166 | Mt Alberta North Elevated Tank | M00554 | [8 empty] | Process Mechanical |  |  |  | W-WW |  |  |  |  | 0 | IMG_6244 |  |  | OPERATING |  | 0
PM | MAN | 24 | 4967 | 2 | 00024544 | Elevated Tank Overflow Bypass Line Butterfly Valve | 500 | 2000 | 2025 | Mt Albert North ET Capital Project 1 | The asset was observed to be in fair condition. Resurface and repaint to protect against corrosion. Replace the asset at the end of its service life. | 3 |  | 0 |  | 2004 | Minor surface corrosion | 150mm butterfly valve, manufacturer: Clow Kennedy |  |  |  | 00017166 | Mt Alberta North ET Valve Room | M00554 | [8 empty] | Process Mechanical |  |  |  | W-WW | Minor surface corrosion was observed. |  |  | Resurface and repaint to protect against corrosion. | 0 | IMG_6280 |  |  | OPERATING |  | 0
ES | MAN | 11 | 4995 | 2 | 00080565 | Portable Generator |  | 2000 |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. | 2 |  | 0 |  | 2004 | good | Portable Gasoline Generator, Manufacturer: Comet |  |  |  | 790900018 | Mt Alberta North Elevated Tank | M00506 | [8 empty] | Electrical System | EAAJ 1069727 |  |  | W-WW |  |  |  |  | 0 | PXL_20201111_142703597 | Mt Albert North ET Capital Project 2 |  | OPERATING |  | 0
AC | MAN | 6 | 5052 | 1 |  | Valve Room Wall Paint |  | 2000 |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of service life. | 3 |  | 0 |  | 2004 | Minor peeled paint |  |  |  |  | 00017166 | [15 empty] | Minor peeled paint was observed. |  |  |  | 0 | IMG_4113 | Mt Albert North ET Capital Project 1 |  |  | 0 | 0
SW | MAN | 44 | 5081 | 2 |  | Valve Chamber #1 Access Ladder |  | 1500 |  |  | The asset was observed to be in good condition. Asset to be replace at the end of its service life. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 790900018 | [19 empty] | 0 | IMG_4135 |  |  |  | 0 | 0
SW | MAN | 44 | 5075 | 2 |  | Valve Chamber #1 Manhole Frame and Cover | 2000 | 1500 | 2024 | Mt Albert North ET Capital Project 1 | The asset was observed to be in good condition. Relocation of access hatch closer to the chamber side wall so that the ladder can be accessed. Installation of valve box on chamber roof. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 790900018 | [15 empty] | Safety issue: chamber ladder and chamber access hatch are not aligned. |  |  | Align chamber ladder with chamber access hatch. | 0 | IMG_4135 |  |  |  | 0 | 0
SW | MAN | 44 | 5082 | 2 |  | Valve Chamber #2 Access Ladder |  | 1500 |  |  | The asset was observed to be in good condition. Asset to be replace at the end of its service life. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 790900018 | [19 empty] | 0 | IMG_4137 |  |  |  | 0 | 0
SW | MAN | 44 | 5076 | 2 |  | Valve Chamber #2 Manhole Frame and Cover | 2000 | 1500 | 2024 | Mt Albert North ET Capital Project 1 | The asset was observed to be in good condition. Relocation of access hatch closer to the chamber side wall so that the ladder can be accessed. Installation of valve box on chamber roof. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 790900018 | [15 empty] | Safety issue: chamber ladder and chamber access hatch are not aligned. |  |  | Align chamber ladder with chamber access hatch. | 0 | IMG_4137 |  |  |  | 0 | 0
SW | MAN | 44 | 5083 | 2 |  | Valve Chamber #3 Access Ladder |  | 1500 |  |  | The asset was observed to be in good condition. Asset to be replace at the end of its service life. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 790900018 | [19 empty] | 0 | IMG_4139 |  |  |  | 0 | 0
SW | MAN | 44 | 5077 | 2 |  | Valve Chamber #3 Manhole Frame and Cover | 2000 | 1500 | 2024 | Mt Albert North ET Capital Project 1 | The asset was observed to be in good condition. Relocation of access hatch closer to the chamber side wall so that the ladder can be accessed. Installation of valve box on chamber roof. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 790900018 | [15 empty] | Safety issue: chamber ladder and chamber access hatch are not aligned. |  |  | Align chamber ladder with chamber access hatch. | 0 | IMG_4056 |  |  |  | 0 | 0
ES | MAN | 11 | 5019 | 1 |  | Electrical Control Room Lighting |  | 1000 |  |  | The asset was observed to be in good condition. Asset to be replaced with LED fixtures in next upgrade project. | 2 |  | 0 |  | 2004 | good | 1 linear fluorescent lighting fixture and 1 pendent mount |  |  |  | 00017166 | [20 empty] | PXL_20201111_141749310 | Mt Albert North ET Capital Project 2 |  |  | 0 | 0
AC | MAN | 6 | 5054 | 1 |  | Electrical Control Room Wall Paint |  | 1000 |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of service life. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 00017169 | [19 empty] | 0 | IMG_6363 | Mt Albert North ET Capital Project 1 |  |  | 0 | 0
AC | MAN | 6 | 5053 | 1 |  | Foyer Wall Paint |  | 1000 |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of service life. | 3 |  | 0 |  | 2004 | peeled paint at bottom |  |  |  |  | 00017168 | [15 empty] | Peeled paint at bottom was observed. |  |  |  | 0 | IMG_4107 | Mt Albert North ET Capital Project 1 |  |  | 0 | 0
HSS | MAN | 6 | 5039 | 2 |  | Smoke Detectors |  | 1000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  |  |  | 2004 | good | Smoke Detector (2) |  |  |  | 790900018 | [20 empty] | PXL_20201111_141747449 | Mt Albert North ET Capital Project 1 |  |  | 2019
BM | MAN | 14 | 4985 | 2 | 00078317 | Sump Pump |  | 1000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 2 |  | 0 |  | 2004 | good | Submersible centrifugal sump pump |  |  |  | 00017166 | Mt Alberta North ET Valve Room | [9 empty] | Process Mechanical |  |  |  | W-WW |  |  |  |  | 0 | IMG_6325 | Mt Albert North ET Capital Project 2 |  | OPERATING |  | 0
SIC | MAN | 6 | 4984 | 2 | 00078313 | Valve Room Low Temperature Switch |  | 1000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2004 | good | MTT2TSL101 |  |  |  | 00017166 | Mt Alberta North ET Valve Room | M00076 | [8 empty] | Instrumentation and Control |  |  |  | W-WW |  |  |  |  | 0 | PXL_20201111_140439546 | Mt Albert North ET Capital Project 1 |  | OPERATING |  | 0
HSS | MAN | 6 | 4956 | 2 | 00025415 | Chlorine Residual Kit |  | 700 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2004 | good | Hach II Pocket Colorimeter, Chlorine Residual Kit |  |  |  | 00017166 | Mt Alberta North ET Valve Room | M00482 | [8 empty] | Health and Safety | 05080C035745 |  |  | W-WW |  |  |  |  | 0 | PXL_20201111_140445688 | Mt Albert North ET Capital Project 1 |  | OPERATING |  | 0
HSS | MAN | 21 | 5038 | 2 | 00078315 | Portable Emergency Eyewash | 2000 | 600 | 2026 | Mt Albert North ET Capital Project 1 | The asset was observed to be in good condition. Asset to be replaced with a emergency eyewash system with water heater and electrical system. | 2 |  | 0 |  | 2004 | good | Portable type |  |  |  | 00017166 | [19 empty] | 0 | PXL_20201111_140206405 |  |  |  | 0 | 0
AC | MAN | 6 | 5055 | 1 |  | Storage Room Wall Paint |  | 500 |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of service life. | 2 |  | 0 |  | 2004 | good |  |  |  |  | 00017169 | [19 empty] | 0 | IMG_4123 | Mt Albert North ET Capital Project 1 |  |  | 0 | 0
HSS | MAN | 6 | 5040 | 1 |  | Fire Extinguisher |  | 300 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2004 | good | 1 Fire Extinguisher |  |  |  | 00017169 | [19 empty] | 0 | PXL_20201111_140246229 | Mt Albert North ET Capital Project 1 |  |  | 2019 | 0
BM | MAN | 26 | 4976 | 2 | 00024548 | Valve Room Dehumidifier |  | 300 |  |  | The asset was observed to be in good condition. Valve room dehumidifier to be replaced at the end of remaining service life. | 2 |  | 0 |  | 2016 | good | Dehumidifier, Air Handling System, by Noma; Installation year assumed to be 2016 |  |  |  | 00017166 | Mt Alberta North Elevated Tank | M00153 | [8 empty] | Building Mechanical |  |  |  | W-WW |  |  |  |  | 0 | IMG_6321 |  |  | OPERATING |  | 0