## Sheet1
CategoryCode | facility | remainingESL | seqNum | COF | assetTag | defect3Input | assetName | RehabRepairCost | repCost | RehabRepairYear | rehabProjectName | observations | condition | rehabComment2 | RehabRepairCost2 | RehabRepairYear2 | installYear | defect1Input | Description | Process | building | inspectorName | LocationTag | LocationORIGINAL | manufacturer | TransmitterModel | TransducerModel | TransducerSerial | InstMeva | installationDate | InstType | ServiceArea | FacilityType | LifeCycleCategory | SerialNo | Parent | RotatingItem | Site | defect1 | defect2 | defect3 | rehabComment1 | rehabCost1 | photoName | repProjectName | rehab2ProjectName | Status | InspectionYear | rehabCost2 | defect2Input
ES | NGR | 19 | 4691 | 3 | 00077373 | Common | Ammonia Feed Pump Panel | 0 | 4000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 2 |  | 0 |  | 2014 | good |  |  |  |  | 20369 | Glenway RES CFB Ammonia Room | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  |  | 0 | 20200520093012_IMG_2538 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
AC | NGR | 9 | 4797 | 1 |  | Common | Ammonia Room Access Door (Single) | 1000 | 3500 | 2023 | Newmarket Glenway Reservoirs Capital Project 1 | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 3 |  |  |  | 2014 | weathered paint |  |  |  |  | 00020369 | [15 empty] | Weathered paint was observed. |  |  |  |  | DSC07984 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0
BM | NGR | 24 | 4678 | 2 | 00077360 | Common | Ammonia Room Air Supply System LV-2 |  | 5000 |  |  | The asset was observed to be in good condition. Ammonia Room Air Supply System LV-2 to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Ammonia room 400x400mm supply air Louvre LV-2 with motorized damper (with Belimo actuator (120/1/60) spring return) |  |  |  | 00020369 | Glenway RES CFB Ammonia Room | M00405 | [6 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2448 |  |  | W-WW | 2020
SC | NGR | 54 | 4674 | 3 | 00077353 | Common | Ammonia Room Concrete Floor | 1000 | 8000 | 2030 | Newmarket Glenway Reservoir Capital Project 2 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Ammonia room concrete floor to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Ammonia room floor concrete slab |  |  |  | 00020369 | Glenway RES CFB Ammonia Room | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [8 empty] | W-WW | 2020
BM | NGR | 24 | 4680 | 2 | 00077362 | Common | Ammonia Room Electric Heating UH-5 |  | 2500 |  |  | The asset was observed to be in good condition. Ammonia Room Electric Heating UH-5 to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Ammonia room wall cabinet convection unit heater UH-5 with thermostat (3kw, 600/3/60) |  |  |  | 00020369 | Glenway RES CFB Ammonia Room | M00111 | [6 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2450 |  |  | W-WW | 2020
BM | NGR | 24 | 4679 | 2 | 00077361 | Common | Ammonia Room Exhaust System F-3 with MOD-3 |  | 10000 |  |  | The asset was observed to be in good condition. Ammonia Room Exhaust System F-3 to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Ammonia room direct drive in-line centrifugal exhaust fan F-3 (Twin city model DSI-080, 50 l/s, 60 Pa ESP, 1550 rpm; 120/1/60, 1/4 hp), 300x300 mm motorized damper mdd-3 c/w Belimo actuator (120/1/60) w/ spring return, 300x300 mm louver LV-3 |  |  |  | 00020369 | Glenway RES CFB Ammonia Room | M00405 | [6 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2469 |  |  | W-WW | 2020
AC | NGR | 9 | 4805 | 1 |  | Common | Ammonia Room Exterior Brick Veneer |  | 4000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  |  |  | 2014 | good |  |  |  |  | 00020369 | [20 empty] | DSC07946 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0
HSS | NGR | 9 | 4681 | 2 | 00077363 | Common | Ammonia Room Eyewash & Safety Shower |  | 2500 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  |  |  | 2014 | good | Ammonia room eyewash with safety shower |  |  |  | 00020369 | Glenway RES CFB Ammonia Room | M00074 | [6 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2479 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020
ES | NGR | 19 | 4878 | 2 |  | Common | Ammonia Room Lighting | 0 | 2400 |  |  | The asset was observed to be in good condition. It is recommended to replace the fixtures with LED type in the long term when the fixtures reach the end of their expected service life. | 2 |  | 0 |  | 2014 | good | 2 fluroscent fixtures |  |  |  | 00020369 | [19 empty] | 0 | 20200520093318_IMG_2558 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0 | 0 | to be replaced with LED in next upgrade
BM | NGR | 24 | 4872 | 2 |  | Common | Ammonia Room Louvre LV-3 |  | 1500 |  |  | The asset was observed to be in good condition. Ammonia Room Louvre LV-3 to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Fixed blade, size 300 x 300 x 100mm |  |  |  | 00020369 | Glenway RES CFB Ammonia Room | M00405 | [6 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | 12341 |  |  | W-WW | 2020
SC | NGR | 54 | 4585 | 4 |  | Common | Ammonia Room Masonry Blockwall | 1000 | 8000 | 2030 | Newmarket Glenway Reservoir Capital Project 2 | The asset was observed to be in good condition. Ammonia room masonry blockwall to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good |  |  |  |  | 00020369 | Glenway RES CFB Valve Chamber No. 1 (Existing) | [7 empty] | Area 2N Linear Water & Wells |  | Structural |  |  |  | OPERATING | [5 empty] | DSC07986 |  |  | W-WW | 2020
SIC | NGR | 9 | 4676 | 2 | 00077358 | Common | Ammonia Room Occupancy Sensor | 0 | 1000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2014 | good |  |  |  |  | 20369 | Glenway RES CFB Ammonia Room | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  |  | 0 |  | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
SC | NGR | 54 | 4675 | 4 | 00077355 | Common | Ammonia Room Precast Concrete Roof | 500 | 4000 | 2030 | Newmarket Glenway Reservoir Capital Project 2 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Ammonia room precast concrete roof to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Ammonia room concrete ceiling |  |  |  | 00020369 | Glenway RES CFB Ammonia Room | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | DSC07986 |  |  | W-WW | 2020
AC | NGR | 9 | 4796 | 1 |  | Common | Ammonia Room Protective Floor Coating |  | 8000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  |  |  | 2014 | good |  |  |  |  | 00020369 | [20 empty] | DSC07985 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0
AC | NGR | 9 | 4800 | 1 |  | Common | Ammonia Room Roofing System |  | 1000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  |  |  | 2014 | good |  |  |  |  | 00020369 | [20 empty] | DSC08388 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0
AC | NGR | 9 | 4795 | 1 |  | Common | Ammonia Room Wall and Ceiling Paint |  | 1500 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  |  |  | 2014 | good |  |  |  |  | 00020369 | [20 empty] | DSC07986 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0
SIC | NGR | 9 | 4689 | 2 | 00077371 | Common | Ammonia Storage Level Sensor | 0 | 1000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2014 | good |  |  |  |  | 20369 | Glenway RES CFB Ammonia Room | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  |  | 0 | IMG_2453 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
SIC | NGR | 9 | 4690 | 3 | 00077372 | Common | Ammonia Storage Level Transmitter | 0 | 3000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2014 | good |  |  |  |  | 20369 | Glenway RES CFB Ammonia Room |  | Prosonic S - FMU90 |  |  | Level |  |  | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  |  | 0 | 20200520092726_IMG_2521 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
SIC | NGR | 9 | 4688 | 3 | 00077370 | Common | Ammonia Storage Tank Leak Detector | 0 | 1000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2014 | good |  |  |  |  | 20369 | Glenway RES CFB Ammonia Room | M00125 | [6 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  |  | 0 | IMG_2453 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
PM | NGR | 14 | 4686 | 2 | 00077368 | Common | Ammonia Storage Tank |  | 3000 |  |  | The asset was observed to be in good condition. Ammonia storage tank to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good |  |  |  |  | 00020369 | Glenway RES CFB Ammonia Room |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2453 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020
PM | NGR | 14 | 4699 | 3 | 00077382 | Common | Ammonia Injection Points and Piping |  | 2000 |  |  | The asset was observed to be in good condition. Ammonia injection points and piping to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good |  |  |  |  | 00017315 | Glenway RES CFB Valve Chamber No. 1 (Existing) |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2666 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020
PM | NGR | 14 | 4885 | 2 |  | Common | Ammonia Tank Mixer | 0 | 1000 |  |  | The tank mixer was observed to be in good condition. Asset to be replace at the end of its estimated remaining service life. | 2 |  | 0 |  | 2014 | [5 empty] | 00017315 | [20 empty] | 20200520092948_IMG_2535 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0
SIC | NGR | 9 | 4692 | 3 | 00077374 | Common | Ammonia Tank Mixer Flow Switch | 0 | 500 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2014 | good |  |  |  |  | 20369 | Glenway RES CFB Ammonia Room | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  |  | 0 | 20200520093003_IMG_2537 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
BM | NGR | 24 | 4693 | 2 | 00077375 | Common | Backflow Preventer 1 |  | 2000 |  |  | The asset was observed to be in good condition. Backflow Preventer 1 to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Service water backflow preventer on wall (manufacturer: Watts,40 mm) |  |  |  | 00020369 | Glenway RES CFB Ammonia Room | M00145 | [6 empty] | Area 2N Linear Water & Wells |  |  | 02779 |  |  | OPERATING | [5 empty] | IMG_2485 |  |  | W-WW | 2020
BM | NGR | 24 | 4748 | 2 | 00077710 | Common | Backflow Preventer 2 |  | 1500 |  |  | The asset was observed to be in good condition. Backflow preventer 2 to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Service water backflow preventer on wall (manufacturer: Watts, 40 mm) |  |  |  | 00020369 | Glenway RES CFB Ammonia Room | M00145 | [6 empty] | Area 2N Linear Water & Wells |  |  | 010773 |  |  | OPERATING | [5 empty] | IMG_2485 |  |  | W-WW | 2020
SIC | NGR | 9 | 4726 | 3 | 00077412 | Common | Bi-Directional Magnetic Flowmeter | 0 | 12000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2014 | good | Size: 300mm, located below aluminum platform |  |  |  | 20368 | Glenway RES CFB Valve Chamber No. 1 (New) | M00405 | [6 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  |  | 0 |  | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
SW | NGR | 54 | 4594 | 1 | 00077259 | Common | Bollards | 3000 | 50000 | 2024 | Newmarket Glenway Reservoirs Capital Project 1 | The assets were observed to be in fair condition. Replace the deficient bollards with new ones. Asset to be replaced at the end of remaining service life. | 3 |  |  |  | 2014 | One of the bollards was heavily corroded. | 19 bollards |  |  |  | 00008891 | Glenway RES Outside Sanitary Pumping Station | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | Some bollards were heavily corroded. |  |  | Replace the deficient bollard with a new one. | 3000 | IMG_20200520_094307 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020
PM | NGR | 14 | 4684 | 2 | 00077366 | Common | Booster Ammonia Feed Pump 1 |  | 8000 |  |  | The asset was observed to be in good condition. Booster ammonia feed pump 1 to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Peristaltic Pump, manufacturer: Watson Marlow, model: 520u |  |  |  | 00020369 | Glenway RES CFB Ammonia Room |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2456 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020
PM | NGR | 14 | 4685 | 2 | 00077367 | Common | Booster Ammonia Feed Pump 2 |  | 8000 |  |  | The asset was observed to be in good condition. Booster ammonia feed pump 2 to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Peristaltic Pump, manufacturer: Watson Marlow, model: 520u |  |  |  | 00020369 | Glenway RES CFB Ammonia Room |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2456 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020
PM | NGR | 14 | 4723 | 3 | 00077409 | Common | Booster Chlorine Feed Injection Points and Piping |  | 2000 |  |  | The asset was observed to be in good condition. Booster chlorine feed injection points and piping to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good |  |  |  |  | 00017315 | Glenway RES CFB Valve Chamber No. 1 (New) |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2735 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020
PM | NGR | 14 | 4838 | 2 | 00077345 | Common | Booster Chlorine Feed Pump 1 |  | 10000 |  |  | The asset was observed to be in good condition. Booster chlorine feed pump 1 to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Peristaltic Pump, manufacturer: Watson Marlow, model: 520u |  |  |  | 00017314 |  |  | Done | [17 empty] | IMG_2529 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0
PM | NGR | 14 | 4667 | 2 | 00077346 | Common | Booster Chlorine Feed Pump 2 |  | 8000 |  |  | The asset was observed to be in good condition. Booster chlorine feed pump 2 to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Peristaltic Pump, manufacturer: Watson Marlow, model: 520u |  |  |  | 00017314 | Glenway RES CFB Chlorine Room |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2528 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020
BM | NGR | 24 | 4682 | 2 | 00077364 | Common | Chemical Feed Building Drainage System |  | 35000 |  |  | The asset was observed to be in good condition. The drainage system to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | [5 empty] | Glenway RES CFB Ammonia Room | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2503 |  |  | W-WW | 2020
SIC | NGR | 9 | 4728 | 1 | 00077414 | Common | Chemical System Pressure Gauges | 0 | 1500 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2014 | good | Pressure gauges for reformation chlorine feed system, booster chlorine feed system, booster ammonia feed system |  |  |  | 20368 | Glenway RES CFB Valve Chamber No. 1 (New) | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  |  | 0 | 20200520093124_IMG_2546 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
HSS | NGR | 9 | 4669 | 2 | 00077348 | Common | Chemical Spill Kit 1 |  | 100 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  |  |  | 2014 | good | Chemical spill kit |  |  |  | 00017314 | Glenway RES CFB Chlorine Room | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | DSC07975 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020
HSS | NGR | 9 | 4661 | 2 | 00077340 | Common | Chemical Spill Kit 2 |  | 100 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  |  |  | 2014 | good | Chemical spill kit |  |  |  | 00017314 | Glenway RES CFB Chlorine Room | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | dsc07977 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020
HSS | NGR | 9 | 4687 | 2 | 00077369 | Common | Chemical Spill Kit 3 |  | 100 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  |  |  | 2014 | good | Chemical spill kit 3 |  |  |  | 00020369 | Glenway RES CFB Ammonia Room | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | dsc07987 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020
SIC | NGR | 9 | 4750 | 3 | 00080172 | Common | Chloramine Analyzer | 0 | 15000 |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the long term. | 3 |  | 0 |  | 2016 |  | Analyzer monitors reservoir inlet and outlet water conditions via four sample points in Valve Chamber 3 and Valve Chamber 4 |  |  |  | 17315 | Glenway RES CFB Valve Chamber No. 1 (Existing) | M00482 | CL-17 |  |  | Chlorine |  |  | Area 2N Linear Water & Wells |  | Instrumentation and Control | 030700007657 |  |  | OPERATING |  |  |  |  | 0 |  | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
AC | NGR | 9 | 4791 | 1 |  | Common | Chlorine Room Access Door (Single) | 1000 | 3500 | 2025 | Newmarket Glenway Reservoirs Capital Project 1 | The asset was observed to be in fair condition. Repaint the door. Asset to be replaced in the intermediate term. | 3 |  |  |  | 2014 | weathered paint |  |  |  |  | 00017314 | [15 empty] | Weathered paint was observed. |  |  |  |  | DSC07972 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0
BM | NGR | 24 | 4654 | 2 | 00077332 | Common | Chlorine Room Air Supply System LV-1 |  | 5000 |  |  | The asset was observed to be in good condition. Chlorine Room Air Supply System LV-1 to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Chlorine room 400x400mm Louvre LV-1with motorized damper (with Belimo actuator (120/1/60) spring return) |  |  |  | 00017314 | Glenway RES CFB Chlorine Room | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2552 |  |  | W-WW | 2020
SC | NGR | 54 | 4584 | 4 | 00013086 | Common | Chlorine Room Concrete Blockwall | 1000 | 6000 | 2030 | Newmarket Glenway Reservoir Capital Project 2 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Chlorine room concrete blockwall to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good |  |  |  |  | 00017314 | Glenway RES CFB Chlorine Room | [7 empty] | Area 2N Linear Water & Wells |  | Structural |  |  |  | OPERATING | [5 empty] | DSC07976 |  |  | W-WW | 2020
SC | NGR | 54 | 4762 | 3 |  | Common | Chlorine Room Concrete Floor | 1000 | 8000 | 2030 | Newmarket Glenway Reservoir Capital Project 2 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Chlorine room concrete floor to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good |  |  |  |  | 00017314 | Glenway RES CFB Chlorine Room | [19 empty] | DSC07975 |  |  |  | 0
BM | NGR | 24 | 4655 | 2 | 00077333 | Common | Chlorine Room Electrical Heater UH-4 |  | 5000 |  |  | The asset was observed to be in good condition. Chlorine Room Electrical Heater UH-4 to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Chlorine room suspended fan forced heater UH-4 (5 kw, 600/3/60) |  |  |  | 00017314 | Glenway RES CFB Chlorine Room | M00111 | [6 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2517 |  |  | W-WW | 2020
BM | NGR | 24 | 4653 | 2 | 00086892 | Common | Chlorine Room Exhaust System F-2 |  | 5000 |  |  | The asset was observed to be in fair condition. Chlorine room exhaust system f-2 to be replaced at the end of remaining service life. | 3 |  |  |  | 2014 | The fan inlet is blocked by a storage tank; the inlet should be unblocked | Chlorine room direct-drive centrifugal exhaust fan F-2 (50 L/s at 100 Pa ESP, 1725 rpm; 120/1/60, 1/4 hp motor, by MK plastics model CNW 160) |  |  |  | 00017314 | Glenway RES CFB Chlorine Room | M00096 | [6 empty] | Area 2N Linear Water & Wells |  |  | C0177-1A |  |  | OPERATING | The fan inlet was blocked by a plastic tank at the time of the inspection. The inlet of the fan should be unblocked. |  |  |  |  | IMG_2509 |  |  | W-WW | 2020
AC | NGR | 9 | 4806 | 1 |  | Common | Chlorine Room Exterior Brick Veneer |  | 2000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  |  |  | 2014 | good |  |  |  |  | 00017314 | [20 empty] | DSC07946 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0
HSS | NGR | 9 | 4656 | 2 | 00077334 | Common | Chlorine Room Eyewash & Safety Shower |  | 2500 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  |  |  | 2014 | good | Chlorine room eyewash with safety shower |  |  |  | 00017314 | Glenway RES CFB Chlorine Room | M00074 | [6 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2520 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020
SIC | NGR | 9 | 4883 | 2 |  | Common | Chlorine Room High Temperature Switch | 0 | 500 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2014 | good |  |  |  |  | 20367 | [19 empty] | 0 | 20200520092820_IMG_2526 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0 | 0
AC | NGR | 9 | 4586 | 1 | 00013096 | Common | Chlorine Room Interior Window |  | 3000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  |  |  | 2014 | good | Interior aluminum window |  |  |  | 00017314 | Glenway RES Outside Sanitary Pumping Station | [7 empty] | Area 2N Linear Water & Wells |  | Architectural |  |  |  | OPERATING | [5 empty] | DSC07963 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020
ES | NGR | 19 | 4879 | 2 |  | Common | Chlorine Room Lighting | 0 | 2400 |  |  | The asset was observed to be in good condition. It is recommended to replace the fixtures with LED type in the long term when the fixtures reach the end of their expected service life. | 2 |  | 0 |  | 2014 | good | 2 fluroscent fixtures |  |  |  | 00017314 | [19 empty] | 0 | 20200520093927_IMG_2602 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0 | 0 | to be replaced with LED in next upgrade
SIC | NGR | 9 | 4754 | 2 | 00080984 | Common | Chlorine Room Low Temperature Switch | 0 | 500 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2014 | good |  |  |  |  | 17314 | Glenway RES CFB Chlorine Room | M00076 | T631A1063 | [5 empty] | Area 2N Linear Water & Wells |  | Instrumentation and Control |  |  |  | OPERATING |  |  |  |  | 0 | 20200520093855_IMG_2598 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
SC | NGR | 54 | 4761 | 3 |  | Common | Chlorine Room Precast Concrete Roof | 500 | 4000 | 2030 | Newmarket Glenway Reservoir Capital Project 2 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Chlorine room precast concrete roof to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good |  |  |  |  | 00017314 | Glenway RES CFB Chlorine Room | [19 empty] | DSC07976 |  |  |  | 0
AC | NGR | 9 | 4789 | 1 |  | Common | Chlorine Room Protective Floor Coating |  | 8000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  |  |  | 2014 | good |  |  |  |  | 00017314 | [20 empty] | DSC07975 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0
AC | NGR | 9 | 4801 | 1 |  | Common | Chlorine Room Roofing System |  | 1000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  |  |  | 2014 | good |  |  |  |  | 00017314 | [20 empty] | DSC08388 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0
AC | NGR | 9 | 4790 | 1 |  | Common | Chlorine Room Wall and Ceiling Paint |  | 1500 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  |  |  | 2014 | good |  |  |  |  | 00017314 | [20 empty] | DSC07976 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0
SIC | NGR | 9 | 4662 | 2 | 00077341 | Common | Chlorine Storage Tank 1 Leak Detector | 0 | 1000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2014 | good | Manufacturer: Siemens, model: Pointek CLS200 |  |  |  | 17314 | Glenway RES CFB Chlorine Room | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  |  | 0 | 20200520093732_IMG_2583 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
SIC | NGR | 9 | 4663 | 2 | 00077342 | Common | Chlorine Storage Tank 1 Level Sensor | 0 | 1000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2014 | good |  |  |  |  | 17314 | Glenway RES CFB Chlorine Room | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  |  | 0 | 20200520093744_IMG_2585 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
SIC | NGR | 9 | 4664 | 3 | 00077343 | Common | Chlorine Storage Tank 1 Level Transmitter | 0 | 3000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2014 | good | Manufacturer: Endress+Hauser, model: FMU90 |  |  |  | 17314 | Glenway RES CFB Chlorine Room | M00405 | Prosonic S - FMU90 |  |  | Level |  |  | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  |  | 0 | 20200520093645_IMG_2576 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
SIC | NGR | 9 | 4670 | 2 | 00086909 | Common | Chlorine Storage Tank 2 Leak Detector | 0 | 1000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2014 | good | Manufacturer: Siemens, model: Pointek CLS200 |  |  |  | 17314 | Glenway RES CFB Chlorine Room | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  |  | 0 | 20200520093554_IMG_2568 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
SIC | NGR | 9 | 4671 | 2 | 00077350 | Common | Chlorine Storage Tank 2 Level Sensor | 0 | 1000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2014 | good |  |  |  |  | 17314 | Glenway RES CFB Chlorine Room | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  |  | 0 | DSC07982 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
SIC | NGR | 9 | 4672 | 2 | 00077351 | Common | Chlorine Storage Tank 2 Level Transmitter | 0 | 3000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2014 | good |  |  |  |  | 17314 | Glenway RES CFB Chlorine Room |  | Prosonic S - FMU90 |  |  | Level |  |  | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  |  | 0 | 20200520093625_IMG_2573 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
SW | NGR | 25 | 4850 | 2 |  | Common | Driveway Entrance Pavement | 10000 | 30000 | 2022 | Newmarket Glenway Reservoirs Capital Project 1 | The asset was observed to be in fair condition. Regrade sodded and riprap area to ensure positive drainage away from driveway and reduce erosion. Remove and replace pavement structure as required. Asset to be replaced at the end of remaining service life | 3 |  |  |  | 2014 | Edge of pavement had washed out and damaged driveway. | Asphalt driveway between the two swing gates. |  |  |  | 00008891 | [15 empty] | Edge of pavement had washed out and damaged driveway. | Cracks were observed at various locations. |  | Regrade sodded and riprap area to ensure positive drainage away from driveway and reduce erosion. Remove and replace pavement structure as required. Repave areas exhibiting cracking | 5000 | IMG_20200520_100132 |  |  |  | 0 | 5000 | Cracks at various locations
ES | NGR | 19 | 4737 | 3 | 00077424 | Common | Electrical Duct System and Conduit System | 0 | 15000 |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the long term. | 3 |  | 0 |  | 2014 |  | Conduit system inculding underground electrical ductbanks, conduit, and underground electrical and communication pull boxe |  |  |  | 17316 | Glenway RES Outside Sanitary Pumping Station | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  |  | 0 |  | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
SC | NGR | 54 | 4628 | 3 | 00077299 | Common | Electrical Room Concrete Floor | 1000 | 8000 | 2030 | Newmarket Glenway Reservoir Capital Project 2 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Electrical room concrete floor to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Electrical room concrete floor slab |  |  |  | 00020367 | Glenway RES CFB Entry Room | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | DSC07969 |  |  | W-WW | 2020
BM | NGR | 24 | 4632 | 2 | 00077305 | Common | Electrical Room Electrical Heater UH-6 |  | 2500 |  |  | The asset was observed to be in good condition. Electrical Room Electrical Heater UH-6 to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Wall cabinet convection unit heater UH-6 with built-in thermostat (2kw; 600/3/60) |  |  |  | 00020367 | Glenway RES CFB Entry Room | M00111 | [6 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2578 |  |  | W-WW | 2020
BM | NGR | 24 | 4631 | 2 | 00077304 | Common | Electrical Room Exhaust Fan F-4 with LV-5 |  | 10000 |  |  | The asset was observed to be in good condition. Electrical Room Exhaust Fan F-4 and LV4 to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Electrical room ventilation system: direct drive centrifugal in-line exhaust fan F-4 (100 L/s at 60 Pa ESP, 120/1/60,1550 RPM), 300x300mm louvre LV-5; 300x300mm MDD-1 motorized damper c/w actuator |  |  |  | 00020367 | Glenway RES CFB Entry Room | M00405 | [6 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2593 |  |  | W-WW | 2020
ES | NGR | 19 | 4645 | 2 | 00077321 | Common | Electrical Room Exit Sign | 0 | 1500 |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 2 |  | 0 |  | 2014 | good | Electrical room emergency exit light |  |  |  | 00020367 | Glenway RES CFB Electrical Room | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  |  | 0 | 20200520094324_IMG_2626 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
ES | NGR | 19 | 4880 | 2 |  | Common | Electrical Room Exit Sign | 0 | 1500 |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the long term. | 3 |  | 0 |  | 2014 | [5 empty] | 00020367 | [19 empty] | 0 |  | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0 | 0
AC | NGR | 9 | 4807 | 1 |  | Common | Electrical Room Exterior Brick Veneer |  | 3000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  |  |  | 2014 | good |  |  |  |  | 00020367 | [20 empty] | DSC07946 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0
SIC | NGR | 9 | 4755 | 2 | 00080985 | Common | Electrical Room High Temperature Switch | 0 | 500 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2014 | good | Blds_tsh3_di, high alarm, temperature switch |  |  |  | 20367 | Glenway RES CFB Ammonia Room | M00076 | T631A1063 | [5 empty] | Area 2N Linear Water & Wells |  | Instrumentation and Control |  |  |  | OPERATING |  |  |  |  | 0 | 20200520094700_IMG_2654 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
ES | NGR | 19 | 4881 | 2 |  | Common | Electrical Room Lighting | 0 | 2400 |  |  | The asset was observed to be in good condition. It is recommended to replace the fixtures with LED type in the long term when the fixtures reach the end of their expected service life. | 2 |  | 0 |  | 2014 | good | 2 fluroscent fixtures |  |  |  | 20367 | [19 empty] | 0 | DSC07970 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0 | 0 | to be replaced with LED in next upgrade
BM | NGR | 24 | 4873 | 2 |  | Common | Electrical Room Louvre LV-4 |  | 1500 |  |  | The asset was observed to be in good condition. electrical room louvre lv-4 to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | 400x400x100 mm |  |  |  | 00020369 | Glenway RES CFB Ammonia Room | M00405 | [6 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | 12340 |  |  | W-WW | 2020
SIC | NGR | 9 | 4756 | 2 | 00080986 | Common | Electrical Room Low Temperature Switch | 0 | 500 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2014 | good | Blds_tsl3_di, low alarm, temperature switch |  |  |  | 20367 | Glenway RES CFB Ammonia Room | M00076 | T631A1063 | [5 empty] | Area 2N Linear Water & Wells |  | Instrumentation and Control |  |  |  | OPERATING |  |  |  |  | 0 | 20200520094656_IMG_2653 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
SC | NGR | 54 | 4763 | 4 |  | Common | Electrical Room Masonry Blockwall | 1000 | 8000 | 2030 | Newmarket Glenway Reservoir Capital Project 2 | The asset was observed to be in good condition. Electrical room masonry blockwall to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good |  |  |  |  | 00020367 | Glenway RES CFB Electrical Room | [19 empty] | DSC07969 |  |  |  | 0
SIC | NGR | 9 | 4630 | 2 | 00077303 | Common | Electrical Room Occupancy Sensor | 0 | 1000 |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the intermediate term. | 3 |  | 0 |  | 2014 | [5 empty] | 20370 | Glenway RES CFB Entry Room | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  |  | 0 |  | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
SC | NGR | 54 | 4629 | 4 | 00077301 | Common | Electrical Room Precast Concrete Roof | 1000 | 5000 | 2030 | Newmarket Glenway Reservoir Capital Project 2 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Electrical room precast concrete roof to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Electrical room concrete ceiling |  |  |  | 00020367 | Glenway RES CFB Entry Room | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | DSC07970 |  |  | W-WW | 2020
AC | NGR | 9 | 4802 | 1 |  | Common | Electrical Room Roofing System |  | 1000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  |  |  | 2014 | good |  |  |  |  | 00020367 | [20 empty] | DSC08388 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0
AC | NGR | 9 | 4794 | 1 |  | Common | Electrical Room Wall and Ceiling Paint |  | 1000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  |  |  | 2014 | good |  |  |  |  | 00020367 | [20 empty] | DSC07968 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0
AC | NGR | 9 | 4792 | 1 |  | Common | Entry Room Access Door (Single) | 1000 | 3500 | 2025 | Newmarket Glenway Reservoirs Capital Project 1 | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 3 |  |  |  | 2014 | weathered paint |  |  |  |  | 00020370 | [15 empty] | Weathered paint was observed. |  |  |  |  | DSC07956 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0
ES | NGR | 19 | 4634 | 2 | 00077307 | Common | Entry Room Exit Sign | 0 | 600 |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 2 |  | 0 |  | 2014 | good | Manufacturer: Beghelli |  |  |  | 00020370 | Glenway RES CFB Entry Room | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  |  | 0 | 20200520094236_IMG_2622 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
AC | NGR | 9 | 4808 | 1 |  | Common | Entry Room Exterior Brick Veneer |  | 1200 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  |  |  | 2014 | good |  |  |  |  | 00020370 | [20 empty] | DSC07946 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0
SC | NGR | 54 | 4647 | 3 | 00077323 | Common | Entry Room Interoir Aluminum Ladder |  | 1500 |  |  | The asset was observed to be in good condition. Entry room aluminum ladder to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good |  |  |  |  | 00020370 | Glenway RES CFB Electrical Room | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | DSC08019 |  |  | W-WW | 2020
ES | NGR | 19 | 4641 | 2 | 00077316 | Common | Entry Room Lighting | 0 | 2400 |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 2 |  | 0 |  | 2014 | good | Entry room 2 ceiling fixures (2x48'') |  |  |  | 00020370 | Glenway RES CFB Electrical Room | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  |  | 0 | 20200520094211_IMG_2617 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
SC | NGR | 54 | 4626 | 4 | 00077295 | Common | Entry Room Masonry Blockwall | 1000 | 6000 | 2030 | Newmarket Glenway Reservoir Capital Project 2 | The asset was observed to be in good condition. Entry room masonry blockwall to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good |  |  |  |  | 00020370 | Glenway RES CFB Entry Room | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | DSC07957 |  |  | W-WW | 2020
SC | NGR | 22 | 4581 | 2 | 00013081 | Common | Entry Room Monorail Hoist Beam |  | 4000 |  |  | The asset was observed to be in good condition. Entry room monorail hoist beam to be replaced at the end of remaining service life. | 2 |  |  |  | 1983 | good |  |  |  |  | 00020370 | Glenway RES CFB Entry Room | [7 empty] | Area 2N Linear Water & Wells |  | Structural |  |  |  | OPERATING | [5 empty] | DSC07966 |  |  | W-WW | 2020
SIC | NGR | 9 | 4642 | 2 | 00077317 | Common | Entry Room Occupancy Sensor | 0 | 1000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2014 | good |  |  |  |  | 20367 | Glenway RES CFB Electrical Room | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  |  | 0 | 20200520094236_IMG_2622 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
AC | NGR | 9 | 4803 | 1 |  | Common | Entry Room Roofing System |  | 500 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  |  |  | 2014 | good |  |  |  |  | 00020370 | [20 empty] | DSC08388 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0
SC | NGR | 54 | 4648 | 3 | 00077324 | Common | Entry Room Safety Chain |  | 300 |  |  | The asset was observed to be in good condition. Entry room safety chain to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Entry room access / egress safety chain |  |  |  | 00020370 | Glenway RES CFB Electrical Room | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | DSC07957 |  |  | W-WW | 2020
BM | NGR | 24 | 4644 | 2 | 00077320 | Common | Entry Room Unit Heater UH-1 |  | 2500 |  |  | The asset was observed to be in good condition. Entry Room Unit Heater UH-1 to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Chamber 1 entry room suspended fan-forced heater UH-1 (5 kw, 600/3/60), manufacturer: Ouellet |  |  |  | 00020370 | Glenway RES CFB Entry Room | M00111 | [6 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2557 |  |  | W-WW | 2020
AC | NGR | 9 | 4793 | 1 |  | Common | Entry Room Wall and Ceiling Paint |  | 1000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  |  |  | 2014 | good |  |  |  |  | 00020370 | [20 empty] | DSC07958 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0
ES | NGR | 19 | 4877 | 2 |  | Common | Exterior Lights | 0 | 4500 |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 2 |  | 0 |  | 2014 | good | 3 LED flood lights |  |  |  | 17316 | [19 empty] | 0 | 20200520092641_IMG_2517 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0 | 0
SW | NGR | 11 | 4857 | 2 |  | Common | External Fencing | 2000 | 25000 | 2025 | Newmarket Glenway Reservoirs Capital Project 1 | The asset was observed to be in fair condition. Repair areas as required. Asset to be replaced in the long term. | 3 |  |  |  | 1983 | broken horizontal bars or mesh | Chainlink mesh fence, approx. 330m in length |  |  |  | 00008891 | [15 empty] | Broken horizontal bars were observed. |  |  | Repair areas as required. | 2000 | IMG_20200520_095924 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0
SW | NGR | 14 | 4592 | 2 | 00077251 | Common | External Site Gate |  | 3000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 2 |  |  |  | 2014 | good | Double lockable, 1.2m high, 5m wide gate |  |  |  | 00017316 | Glenway RES Outside Sanitary Pumping Station | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_20200520_101342 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020
SW | NGR | 25 | 4848 | 2 |  | Common | External Site Grading | 2500 | 50000 | 2025 | Newmarket Glenway Reservoirs Capital Project 1 | The asset was observed to be in fair condition. Regrade area around swab recovery and ensure positive drainage. Asset to be replaced at the end of remaining service life. | 3 |  |  |  | 2014 | Low spots around swab recovery location | Site grading (between internal and external fences). |  |  |  | 00008891 | [15 empty] | Low spots around swab recovery location were observed. |  |  | Regrade area around swab recovery and ensure positive drainage. | 2500 | IMG_20200520_100015 |  |  |  | 0
SIC | NGR | 9 | 4646 | 3 | 00077322 | Common | Facility Security System | 0 | 30000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2014 | good |  |  |  |  | 20367 | Glenway RES CFB Electrical Room | M00076 | [6 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  |  | 0 | 20200520094354_IMG_2628 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
BM | NGR | 24 | 4608 | 2 | 00077275 | Common | Facility Service Water 50mm HDPE Piping 1 |  | 5000 |  |  | The asset was observed to be in good condition. Facility service water 50mm HDPE piping 1 to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Service water line to emergency showers |  |  |  | 00017312 | [8 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | dsc07979 |  |  | W-WW | 2020
BM | NGR | 24 | 4610 | 2 | 00077277 | Common | Facility Service Water 50mm HDPE Piping 2 |  | 5000 |  |  | The asset was observed to be in good condition. Facility service water 50mm HDPE piping 2 to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | 50mm HDPE water service line (to emergency shower) |  |  |  | 00017316 | [8 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | DSC07976 |  |  | W-WW | 2020
ES | NGR | 19 | 4637 | 4 | 00077310 | Common | GWR-A Distribution Panel | 0 | 20000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 2 |  | 0 |  | 2014 | good | Manufacturer: Eaton, power r-line, 600V, 250A, 24CCT |  |  |  | 00020367 | Glenway RES CFB Entry Room | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  |  | 0 | 20200520094720_IMG_2656 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
ES | NGR | 19 | 4636 | 3 | 00077309 | Common | GWR-B Lighting Panel | 0 | 10000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 2 |  | 0 |  | 2014 | good | Manufacturer: Eaton, Power-R-line 3A, 120V/208V, 100A, 30 cct |  |  |  | 00020367 | Glenway RES CFB Entry Room | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  |  | 0 | 20200520094746_IMG_2658 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
BM | NGR | 24 | 4683 | 2 | 00077365 | Common | Hot Water Tank WH-1 |  | 5000 |  |  | The asset was observed to be in good condition. Hot Water Tank WH-1 to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Ammonia room water heater tank (manufacturer: Rheem, 4.4 kw) |  |  |  | 00020369 | Glenway RES CFB Ammonia Room | M00763 | [6 empty] | Area 2N Linear Water & Wells |  |  | EG85C-9 |  |  | OPERATING | [5 empty] | IMG_2498 |  |  | W-WW | 2020
SW | NGR | 11 | 4856 | 2 |  | Common | Internal Site Fencing |  | 25000 |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 3 |  |  |  | 1983 | minor surface corrosion | Internal chainlink fencing with barbed wire at top. approx. 230m in length |  |  |  | 00008891 | [15 empty] | Minor surface corrosion was observed. |  |  |  |  | IMG_20200520_094505 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0
SW | NGR | 14 | 4593 | 2 | 00077252 | Common | Internal Site Gate |  | 5000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 2 |  |  |  | 2014 | good | Double lockable, 2.4m high and 4.5m wide gate |  |  |  | 00017316 | Glenway RES Outside Sanitary Pumping Station | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_20200520_093936 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020
SW | NGR | 25 | 4577 | 2 | 00013077 | Common | Internal Site Grading | 10000 | 40000 | 2024 | Newmarket Glenway Reservoirs Capital Project 1 | The asset was observed to be in fair condition. Regrade areas to ensure positive drainage. | 3 |  |  |  | 1983 | Sod had been damaged and exposed granular at few locations. | Site grading within internal site |  |  |  | 00008891 | Newmarket Glenway Reservoir 1 | [7 empty] | Area 2N Linear Water & Wells | W - Storage Reservoir | Siteworks |  |  |  | OPERATING | Sod had been damaged and exposed granular at few locations. | Low spots around yard hydrant causing tripping hazard. | Low spots around tank no.2 wall were noted. | Regrade areas to ensure positive drainage. | 10000 | IMG_20200520_095357 |  |  | W-WW | 2020 |  | Low spots around yard hydrant, causing tripping hazard.
PM | NGR | 24 | 4719 | 4 | 00077405 | Common | Main Header Line Altitude Valve |  | 22500 |  |  | The asset was observed to be in good condition. Main header line altitude valve to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Size: 400 mm, manufacturer: Cla-Val, RES_LCV 1 |  |  |  | 00017315 | Glenway RES CFB Valve Chamber No. 1 (New) |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2767 |  |  | W-WW | 2020
PM | NGR | 15 | 4571 | 4 | 00004455 | Common | Main Header Line Butterfly Valve 1 | 1000 | 4800 | 2025 | Newmarket Glenway Reservoirs Capital Project 1 | The asset was observed to be in fair condition. Repaint valve. | 3 |  |  |  | 1983 | Moderate surface corrosion | Main header butterfly valve with manual geared operator, size: 400mm, VC1_HV5 |  |  |  | 00017315 | Glenway RES CFB Valve Chamber No. 1 (Existing) | M00554 | Done | [5 empty] | Area 2N Linear Water & Wells |  | Process Mechanical |  |  |  | OPERATING | Moderate surface corrosion was observed. |  |  |  |  | IMG_2796 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020
PM | NGR | 24 | 4569 | 4 | 00004452 | Common | Main Header Line Butterfly Valve 2 | 1000 | 4800 | 2025 | Newmarket Glenway Reservoirs Capital Project 1 | The asset was observed to be in fair condition. Resurface and repaint valve. Main header line butterfly valve 2 to be replaced at the end of remaining service life. | 3 |  |  |  | 2014 | Paint Peeling | Size: 400mm, VC1_HV4 |  |  |  | 00017315 | Glenway RES CFB Valve Chamber No. 1 (Existing) | M00554 | Done | [5 empty] | Area 2N Linear Water & Wells |  | Process Mechanical |  |  |  | OPERATING | Paint peeling was observed. | Minor surface corrosion was observed. |  |  |  | IMG_2803 |  |  | W-WW | 2020 |  | Minor surface corrosion
PM | NGR | 24 | 4612 | 4 | 00077279 | Common | Main Header Line Butterfly Valve 3 (Valve Chamber 3) | 1000 | 4800 | 2025 | Newmarket Glenway Reservoirs Capital Project 1 | The asset was observed to be in fair condition.Valve cleaning, greasing, keeping the chamber dry to extend the valve life. Main header line butterfly valve 3 (valve chamber 3) to be replaced at the end of remaining service life. | 3 |  |  |  | 2014 | surface corrosion due to atmospheric conditions | Chamber 3 butterfly valve with manual geared operator (extension stem to the chamber roof slab), size: 400mm, VC3_HV3 |  |  |  | 00000000 | Glenway RES Outside Sanitary Pumping Station |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | Surface corrosion was observed. |  |  | Valve cleaning, greasing, keeping the chamber dry to extend the valve life. | 1000 | IMG_2888 |  |  | W-WW | 2020
PM | NGR | 24 | 4613 | 4 | 00077280 | Common | Main Header Line Butterfly Valve 4 |  | 4000 |  |  | The asset was assumed to be in fair condition. Main header line butterfly valve 4 to be replaced at the end of remaining service life. | 3 |  |  |  | 2014 |  | Butterfly valve (between magnetic flow meter and valve chamber 4), size: 350mm |  |  |  |  | Glenway RES Outside Sanitary Pumping Station |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [8 empty] | W-WW | 2020
PM | NGR | 15 | 4830 | 4 | 00086915 | Common | Main Header Line Check Valve | 1000 | 18000 | 2025 | Newmarket Glenway Reservoirs Capital Project 1 | The asset was observed to be in fair condition. Asset to be replaced in the short term. | 3 |  |  |  | 1983 | moderate surface corrosion | Size: 400mm, manufacturer: Kennedy, VC1_CV3 |  |  |  | 00017315 |  |  | Done | [12 empty] | Moderate surface corrosion was observed. |  |  |  |  | IMG_2674 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0
PM | NGR | 54 | 4727 | 5 | 00077413 | Common | Main Header Line Piping |  | 26500 |  |  | The asset was observed to be in fair condition. Main header line piping to be replaced at the end of remaining service life. | 3 |  |  |  | 2014 | Corrosion on small portion of pipe near the altitude valve | Main header 350mm, flanged and victaulic connections (located inside of the valve chamber), length: 20 meters |  |  |  | 00017315 | Glenway RES CFB Valve Chamber No. 1 (New) |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | Corrosion was observed on small portion of pipe near the altitude valve. |  |  |  |  | IMG_2747 |  |  | W-WW | 2020
PM | NGR | 24 | 4721 | 3 | 00077407 | Common | Main Header Line Reducer |  | 3000 |  |  | The asset was observed to be in good condition. Main header line reducer to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Reducer 350mm x 400mm, material: stainless steel |  |  |  | 00017315 | Glenway RES CFB Valve Chamber No. 1 (New) |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2726 |  |  | W-WW | 2020
PM | NGR | 24 | 4722 | 2 | 00077408 | Common | Main Header Line Static Mixer 1 |  | 8000 |  |  | The asset was observed to be in good condition. Main header line static mixer 1 to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Size: 350 mm, manufacturer: Westfall |  |  |  | 00017315 | Glenway RES CFB Valve Chamber No. 1 (New) |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2735 |  |  | W-WW | 2020
PM | NGR | 24 | 4700 | 2 | 00077383 | Common | Main Header Line Static Mixer 2 |  | 8000 |  |  | The asset was observed to be in fair condition. Main header line static mixer 2 to be replaced at the end of remaining service life. | 3 |  |  |  | 2014 | Minor surface corrosion | size: 400mm |  |  |  | 00017315 | Glenway RES CFB Valve Chamber No. 1 (Existing) |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | Minor surface corrosion was observed. |  |  |  |  | IMG_2801 |  |  | W-WW | 2020
ES | NGR | 19 | 4739 | 3 | 00077426 | Common | Main Power Pull Box | 0 | 1000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 2 |  | 0 |  | 2014 | good | Electrical pull box, power supply unit |  |  |  | 17316 | Glenway RES Outside Sanitary Pumping Station | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  |  | 0 | IMG_20200520_094250 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
SIC | NGR | 9 | 4638 | 3 | 00077312 | Common | Network Access Closet | 0 | 15000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2014 | good | Network access closet, network, computer |  |  |  | 20370 | Glenway RES CFB Entry Room | M00844 | [6 empty] | Area 2N Linear Water & Wells |  |  | 13E-034/XNMPSKC2 |  |  | OPERATING |  |  |  |  | 0 | 20200520094435_IMG_2635 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
SIC | NGR | 9 | 4639 | 4 | 00077313 | Common | PAC Control Panel | 0 | 60000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2014 | good |  |  |  |  | 20370 | Glenway RES CFB Entry Room | M00844 | [6 empty] | Area 2N Linear Water & Wells |  |  | 13E-034/NMTKKC-PAC |  |  | OPERATING |  |  |  |  | 0 | 20200520094500_IMG_2639 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
SIC | NGR | 9 | 4747 | 4 | 00077435 | Common | PAC Control Panel Chemical Controller | 0 | 5000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2014 | good | Pac chem panel - chemscan, chemical controller |  |  |  | 20370 | Glenway RES CFB Entry Room | M10249 | UV-2150/S | UV-2150/S |  |  |  |  | Area 2N Linear Water & Wells |  |  | 10012197 |  |  | OPERATING |  |  |  |  | 0 | 20200520094517_IMG_2643 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
SIC | NGR | 9 | 4640 | 3 | 00077314 | Common | PAC Control Panel Network Computer | 0 | 5000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2014 | good |  |  |  |  | 20370 | Glenway RES CFB Entry Room | M00844 | [6 empty] | Area 2N Linear Water & Wells |  |  | 13E-034/NMTKKC-CHEM |  |  | OPERATING |  |  |  |  | 0 | 20200520094500_IMG_2639 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
ES | NGR | 19 | 4742 | 3 | 00077429 | Common | Pump Station Control Panel | 0 | 12000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 2 |  | 0 |  | 2014 | good | Panel 100amp connection - kirby building, hydro service |  |  |  | 17316 | Glenway RES Outside Sanitary Pumping Station | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  |  | 0 | 20200520092522_IMG_2514 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
PM | NGR | 20 | 4720 | 3 | 00077406 | Common | Reformation Chlorine Feed Injection Points and Piping |  | 2000 |  |  | The asset was observed to be in good condition. Reformation chlorine feed injection points and piping to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good |  |  |  |  | 00017315 | Glenway RES CFB Valve Chamber No. 1 (New) |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2726 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020
PM | NGR | 20 | 4658 | 2 | 00077337 | Common | Reformation Chlorine Feed Pump 1 |  | 8000 |  |  | The asset was observed to be in good condition. Reformation chlorine feed pump 1 to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Peristaltic Pump, manufacturer: Watson Marlow, model: 520u |  |  |  | 00017314 | Glenway RES CFB Chlorine Room |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2541 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020
PM | NGR | 20 | 4659 | 2 | 00077338 | Common | Reformation Chlorine Feed Pump 2 |  | 8000 |  |  | The asset was observed to be in good condition. Reformation chlorine feed pump 2 to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Peristaltic Pump, manufacturer: Watson Marlow, model: 520u |  |  |  | 00017314 | Glenway RES CFB Chlorine Room |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2544 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020
SW | NGR | 54 | 4617 | 3 | 00077286 | Common | Sanitary Forcemain |  | 18900 |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | The visible portion of the pipe was observed to be in good condition. | diameter: 50mm, length: 100m, discharge from sanitary pumps to manhole near the sidewalk |  |  |  | 00017316 | Glenway RES Outside Sanitary Pumping Station |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | The visible portion of the pipe was observed to be in good condition. |  |  |  |  | IMG_2864 |  |  | W-WW | 2020
PM | NGR | 24 | 4618 | 2 | 00077287 | Common | Sanitary Pump 1 | 5000 | 15000 | 2032 | Newmarket Glenway Reservoir Capital Project 2 | The asset was assumed to be in fair condition.Pump inspection and pump testing are recommended. Sanitary pump 1 to be replaced at the end of remaining service life. | 3 |  |  |  | 2014 |  | Submersible centrifugal pump |  |  |  | 00017316 | Glenway RES Outside Sanitary Pumping Station |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  | Pump inspection and pump testing | 5000 | IMG_2864 |  |  | W-WW | 2020
PM | NGR | 24 | 4619 | 2 | 00077288 | Common | Sanitary Pump 2 | 5000 | 15000 | 2032 | Newmarket Glenway Reservoir Capital Project 2 | The asset was assumed to be in fair condition. Pump inspection and pump testing are recommended. Sanitary pump 2 to be replaced at the end of remaining service life. | 3 |  |  |  | 2014 |  | Submersible centrifugal pump |  |  |  | 00017316 | Glenway RES Outside Sanitary Pumping Station |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  | Pump inspection and pump testing | 5000 | IMG_2864 |  |  | W-WW | 2020
SW | NGR | 54 | 4766 | 2 |  | Common | Sanitary Pumping Station Access Ladder |  | 3000 |  |  | The asset was observed to be in good condition. Sanitary pumping station access ladder to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good |  |  |  |  | 00017316 | [20 empty] | DSC08042 |  |  |  | 0
SW | NGR | 54 | 4616 | 3 | 00077285 | Common | Sanitary Pumping Station Concrete Structure |  | 60000 |  |  | The asset was observed to be in good condition. Sanitary pumping station concrete structure to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good |  |  |  |  | 00017316 | Glenway RES Outside Sanitary Pumping Station | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | DSC08042 |  |  | W-WW | 2020
SIC | NGR | 9 | 4590 | 3 | 00028454 | Common | Sanitary Pumping Station High Level Float Switch | 0 | 1000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2014 | good | NMTKKC SUMP LSH1 |  |  |  | 17316 | Glenway RES CFB Valve Chamber No. 1 (Existing) | M00061 | ENM-10 |  |  | Level |  |  | Area 2N Linear Water & Wells |  | Instrumentation and Control |  |  |  | OPERATING |  |  |  |  | 0 | DSC08043 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
SW | NGR | 54 | 4764 | 2 | 00013079 | Common | Sanitary Pumping Station Manhole Cover and Frame |  | 2000 |  |  | The asset was observed to be in good condition. Sanitary pumping station manhole cover and frame to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good |  |  |  |  | 00017316 | [20 empty] | DSC08041 |  |  |  | 0
SW | NGR | 54 | 4765 | 2 |  | Common | Sanitary Pumping Station Pump Hatch |  | 5000 |  |  | The asset was observed to be in good condition. Sanitary pumping station pump hatch to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good |  |  |  |  | 00017316 | [20 empty] | DSC08041 |  |  |  | 0
SW | NGR | 54 | 4621 | 3 | 00077290 | Common | Sanitary Sewer Piping |  | 5700 |  |  | The asset was assumed to be in fair condition. Asset to be replaced at the end of remaining service life. | 3 |  |  |  | 2014 |  | 150mm sanitary sewer, piping c/w buried 150 gate valve; discharge from chemical building and chamber 1, length: approximately 10m |  |  |  | 00017316 | Glenway RES Outside Sanitary Pumping Station |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [8 empty] | W-WW | 2020
BM | NGR | 24 | 4724 | 1 | 00077410 | Common | Service Water Sample Tap 1 |  | 1000 |  |  | The asset was observed to be in good condition. Service Water Sample Tap 1 to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Sample taps on 350mm watermain pipe, material: stainless steel, welded construction, including isolation ball valves |  |  |  | 00020368 | Glenway RES CFB Valve Chamber No. 1 (New) | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2734 |  |  | W-WW | 2020
BM | NGR | 24 | 4725 | 1 | 00077411 | Common | Service Water Sample Tap 2 |  | 1000 |  |  | The asset was observed to be in good condition. Service Water Sample Tap 2 to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Sample taps on 350mm watermain pipe to tank 2, material: stainless steel, welded construction, including isolation ball valves |  |  |  | 00020368 | Glenway RES CFB Valve Chamber No. 1 (New) | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2747 |  |  | W-WW | 2020
SW | NGR | 13 | 4576 | 2 | 00013076 | Common | Signage |  | 1000 |  |  | The asset was observed to be in good condition. Asset to be replaced when the end of its service life. | 2 |  |  |  | 1983 | good | 2 Signboards |  |  |  | 00008891 | Newmarket Glenway Reservoir 1 | [7 empty] | Area 2N Linear Water & Wells | W - Storage Reservoir | Siteworks |  |  |  | OPERATING | [5 empty] | IMG_20200520_103445 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020
SW | NGR | 14 | 4849 | 2 |  | Common | Site Asphalt |  | 30000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 2 |  |  |  | 2014 | good | Asphalt within the site. |  |  |  | 00008891 | [20 empty] | IMG_20200520_095608 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0
SW | NGR | 54 | 4852 | 5 |  | Common | Site Watermain |  | 125000 |  |  | The asset was assumed to be in fair condition. Asset to be replaced at the end of remaining service life. | 3 |  |  |  | 2014 |  | Diameter various from 300mm to 400mm watermain, approx. length 75m. |  |  |  | 00008891 | [24 empty] | 0
ES | NGR | 19 | 4665 | 3 | 00077344 | Common | Sodium Hypoclorite Pump 1 Control Enclosure | 0 | 2000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 2 |  | 0 |  | 2014 | good | Control enclosure shared with sodium hypochlorite pump 2 |  |  |  | 17314 | Glenway RES CFB Chlorine Room | M00648 | [6 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  |  | 0 | 20200520093723_IMG_2582 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
ES | NGR | 19 | 4673 | 3 | 00077352 | Common | Sodium Hypoclorite Pump 2 Control Enclosure | 0 | 2000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 2 |  | 0 |  | 2014 | good | Control enclosure shared with sodium hypochlorite pump 1 |  |  |  | 00017314 | Glenway RES CFB Chlorine Room | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  |  | 0 | 20200520093700_IMG_2579 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
PM | NGR | 14 | 4660 | 2 | 00086906 | Common | Sodium Hypochlorite Tank 1 |  | 3000 |  |  | The asset was observed to be in good condition. Sodium hypochlorite tank 1 to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good |  |  |  |  | 00017314 | Glenway RES CFB Chlorine Room |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2540 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020
PM | NGR | 14 | 4668 | 2 | 00086907 | Common | Sodium Hypochlorite Tank 2 |  | 3000 |  |  | The asset was observed to be in good condition. Sodium hypochlorite tank 2 to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good |  |  |  |  | 00017314 | Glenway RES CFB Chlorine Room |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2525 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020
SW | NGR | 23 | 4876 | 3 |  | Common | Storm and Drain Piping |  | 130000 |  |  | The asset was assumed to be in fair condition. Asset to be replaced at the end of remaining service life. | 3 |  |  |  | 1983 |  | Diameter: 350mm, length (approximately): 100 meters | [28 empty] | 0
SW | NGR | 22 | 4869 | 2 |  | Common | Storm Manhole #1 Access Ladder |  | 2500 |  |  | The asset was assumed to be in fair condition. Storm manhole #1 access ladder to be replaced at the end of remaining service life. | 3 |  |  |  | 1983 | [5 empty] | 00008891 | [24 empty] | 0
SW | NGR | 22 | 4870 | 3 |  | Common | Storm Manhole #1 Concrete Structure |  | 20000 |  |  | The asset was assumed to be in fair condition. Storm manhole #1 concrete structure to be replaced at the end of remaining service life. | 3 |  |  |  | 1983 | [5 empty] | 00008891 | [24 empty] | 0
SW | NGR | 22 | 4871 | 2 |  | Common | Storm Manhole #1 Manhole Cover and Frame |  | 2000 |  |  | The asset was assumed to be in fair condition. Storm manhole #1 manhole cover and frame to be replaced at the end of remaining service life. | 3 |  |  |  | 1983 | [5 empty] | 00008891 | [24 empty] | 0
SW | NGR | 22 | 4866 | 2 |  | Common | Storm Manhole #2 Access Ladder |  | 2500 |  |  | The asset was assumed to be in fair condition. Storm manhole #2 access ladder to be replaced at the end of remaining service life. | 3 |  |  |  | 1983 | [5 empty] | 00008891 | [24 empty] | 0
SW | NGR | 22 | 4867 | 3 |  | Common | Storm Manhole #2 Concrete Structure |  | 20000 |  |  | The asset was assumed to be in fair condition. Storm manhole #2 concrete structure to be replaced at the end of remaining service life. | 3 |  |  |  | 1983 | [5 empty] | 00008891 | [24 empty] | 0
SW | NGR | 22 | 4868 | 2 |  | Common | Storm Manhole #2 Manhole Cover and Frame |  | 2000 |  |  | The asset was assumed to be in fair condition. Storm manhole #2 manhole cover and frame to be replaced at the end of remaining service life. | 3 |  |  |  | 1983 | [5 empty] | 00008891 | [24 empty] | 0
SW | NGR | 22 | 4784 | 2 |  | Common | Storm Manhole #3 Access Ladder |  | 2500 |  |  | The asset was observed to be in good condition. Storm manhole #3 access ladder to be replaced at the end of remaining service life. | 2 |  |  |  | 1983 | good |  |  |  |  | 00008891 | [20 empty] | DSC08054 |  |  |  | 0
SW | NGR | 22 | 4783 | 3 |  | Common | Storm Manhole #3 Concrete Structure |  | 20000 |  |  | The asset was observed to be in good condition. Storm manhole #3 concrete structure to be replaced at the end of remaining service life. | 2 |  |  |  | 1983 | good |  |  |  |  | 00008891 | [20 empty] | DSC08054 |  |  |  | 0
SW | NGR | 22 | 4785 | 2 |  | Common | Storm Manhole #3 Manhole Cover and Frame |  | 2000 |  |  | The asset was observed to be in good condition. Storm manhole #3 manhole cover and frame to be replaced at the end of remaining service life. | 2 |  |  |  | 1983 | good |  |  |  |  | 00008891 | [20 empty] | DSC08052 |  |  |  | 0
SW | NGR | 54 | 4609 | 2 | 00077276 | Common | Swab Recovery Isolation Piping |  | 50000 |  |  | The asset was assumed to be in fair condition. Asset to be replaced at the end of remaining service life. | 3 |  |  |  | 2014 |  | Swab recovery system including a 400mm gate valve |  |  |  | 00017316 | Glenway RES Outside Sanitary Pumping Station |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [8 empty] | W-WW | 2020
ES | NGR | 19 | 4859 | 4 | 00086897 | Common | Transformer T-1 | 0 | 16000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 2 |  | 0 |  | 2014 | good | Manufacturer: Rex Power, 600-120/208v, 30KVA |  |  |  | 20367 | [19 empty] | 0 | 20200520094630_IMG_2648 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0 | 0
SC | NGR | 54 | 4732 | 3 | 00077419 | Common | Valve Chamber #1 Access Platform |  | 5000 |  |  | The asset was observed to be in good condition. Valve chamber #1 access platform to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Chamber 1 exterior access platform and aluminum grating |  |  |  | 00020368 | Glenway RES CFB Valve Chamber No. 1 (New) | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | DSC07949 |  |  | W-WW | 2020
SC | NGR | 54 | 4718 | 3 | 00077404 | Common | Valve Chamber #1 Aluminum Handrail |  | 2500 |  |  | The asset was observed to be in good condition. Valve chamber #1 aluminum handrail to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good |  |  |  |  | 00020368 | Glenway RES CFB Valve Chamber No. 1 (New) | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | DSC08032 |  |  | W-WW | 2020
SC | NGR | 54 | 4715 | 3 | 00077401 | Common | Valve Chamber #1 Aluminum Ladder |  | 1500 |  |  | The asset was observed to be in good condition. Valve chamber #1 aluminum ladder to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Chamber 1 interoir aluminum ladder (safety post type) |  |  |  | 00020368 | Glenway RES CFB Valve Chamber No. 1 (New) | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | DSC08034 |  |  | W-WW | 2020
SC | NGR | 54 | 4716 | 3 | 00077402 | Common | Valve Chamber #1 Aluminum Platform |  | 10000 |  |  | The asset was observed to be in good condition. Valve chamber #1 aluminum platform to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Chamber 1 interior aluminum access platform |  |  |  | 00020368 | Glenway RES CFB Valve Chamber No. 1 (New) | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | DSC08032 |  |  | W-WW | 2020
SC | NGR | 54 | 4717 | 3 | 00077403 | Common | Valve Chamber #1 Aluminum Staircase |  | 10000 |  |  | The asset was observed to be in good condition. Valve chamber #1 aluminum staircase to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good |  |  |  |  | 00020368 | Glenway RES CFB Valve Chamber No. 1 (New) | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | DSC08032 |  |  | W-WW | 2020
SC | NGR | 22 | 4578 | 3 | 00013078 | Common | Valve Chamber #1 Concrete Floor | 2000 | 20000 | 2030 | Newmarket Glenway Reservoir Capital Project 2 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Valve chamber #1 concrete floor to be replaced at the end of remaining service life. | 2 |  |  |  | 1983 | good | Concrete floor slab |  |  |  | 00017315 | Glenway RES CFB Valve Chamber No. 1 (Existing) | [7 empty] | Area 2N Linear Water & Wells |  | Structural |  |  |  | OPERATING | [5 empty] | DSC08021 |  |  | W-WW | 2020
SC | NGR | 54 | 4708 | 3 | 00077391 | Common | Valve Chamber #1 Concrete Floor | 1000 | 12000 | 2030 | Newmarket Glenway Reservoir Capital Project 2 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Valve chamber #1 concrete floor to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Chamber 1 concrete floor slab |  |  |  | 00020368 | Glenway RES CFB Valve Chamber No. 1 (New) | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | DSC08035 |  |  | W-WW | 2020
SC | NGR | 22 | 4583 | 3 | 00013084 | Common | Valve Chamber #1 Concrete Pipe Supports | 1000 | 10000 | 2030 | Newmarket Glenway Reservoir Capital Project 2 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Valve chamber #1 concrete pipe supports to be replaced at the end of remaining service life. | 2 |  |  |  | 1983 | good |  |  |  |  | 00017315 | Glenway RES CFB Valve Chamber No. 1 (Existing) | [7 empty] | Area 2N Linear Water & Wells |  | Structural |  |  |  | OPERATING | [5 empty] | DSC08026 |  |  | W-WW | 2020
SC | NGR | 22 | 4760 | 4 | 00013082 | Common | Valve Chamber #1 Concrete Walls | 2000 | 50000 | 2030 | Newmarket Glenway Reservoir Capital Project 2 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Valve chamber #1 concrete walls to be replaced at the end of remaining service life. | 2 |  |  |  | 1983 | good | Basement concrete walls |  |  |  | 00017315 | Glenway RES CFB Valve Chamber No. 1 (Existing) | [7 empty] | Area 2N Linear Water & Wells |  | Structural |  |  |  | OPERATING | [5 empty] | DSC08025 |  |  | W-WW | 2020
SC | NGR | 54 | 4759 | 4 | 00013088 | Common | Valve Chamber #1 Concrete Walls | 3000 | 35000 | 2030 | Newmarket Glenway Reservoir Capital Project 2 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Valve chamber #1 concrete walls to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Chamber 1 internal concrete walls |  |  |  | 00020368 | Glenway RES CFB Valve Chamber No. 1 (New) | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | DSC08032 |  |  | W-WW | 2020
SC | NGR | 22 | 4580 | 3 | 00013080 | Common | Valve Chamber #1 Entry Room Access Hatches | 50000 | 3000 | 2024 | Newmarket Glenway Reservoirs Capital Project 1 | The assets were observed to be in good condition. Upgrade the hatches into a new stair for valve chamber access. | 2 |  |  |  | 1983 | good | 2 aluminum hatches |  |  |  | 00017315 | Glenway RES CFB Valve Chamber No. 1 (Existing) | [7 empty] | Area 2N Linear Water & Wells |  | Structural |  |  |  | OPERATING | [5 empty] | DSC07964 |  |  | W-WW | 2020
SC | NGR | 54 | 4734 | 3 | 00077421 | Common | Valve Chamber #1 Exterior Access Hatch |  | 3000 |  |  | The asset was observed to be in good condition. Valve chamber #1 exterior access hatch to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Single leaf roof access hatch |  |  |  | 00020368 | Glenway RES CFB Valve Chamber No. 1 (New) | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | DSC07951 |  |  | W-WW | 2020
SC | NGR | 54 | 4627 | 2 | 00077297 | Common | Valve Chamber #1 Exterior Concrete Sidewalk |  | 2000 |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Valve chamber #1 exterior concrete sidewalk to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good |  |  |  |  | 00020368 | Glenway RES CFB Valve Chamber No. 1 (New) | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | DSC07949 |  |  | W-WW | 2020
SC | NGR | 54 | 4733 | 3 | 00077420 | Common | Valve Chamber #1 Exterior Staircase |  | 2000 |  |  | The asset was observed to be in good condition. Valve chamber #1 exterior staircase to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Chamber 1 exterior aluminum stairs |  |  |  | 00020368 | Glenway RES CFB Valve Chamber No. 1 (New) | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | DSC07949 |  |  | W-WW | 2020
SC | NGR | 22 | 4582 | 2 | 00013082 | Common | Valve Chamber #1 Monorail Hoist Beam |  | 8000 |  |  | The asset was observed to be in good condition. Valve chamber #1 monorail hoist beam to be replaced at the end of remaining service life. | 2 |  |  |  | 1983 | good |  |  |  |  | 00017315 | Glenway RES CFB Valve Chamber No. 1 (Existing) | [7 empty] | Area 2N Linear Water & Wells |  | Structural |  |  |  | OPERATING | [5 empty] | DSC08025 |  |  | W-WW | 2020
SC | NGR | 54 | 4709 | 4 | 00077393 | Common | Valve Chamber #1 Precast Concrete Roof | 1000 | 11000 | 2030 | Newmarket Glenway Reservoir Capital Project 2 | The asset was observed to be in fair condition. Provisions for structural repairs. Valve chamber #1 precast concrete roof to be replaced at the end of remaining service life. | 3 |  |  |  | 2014 | corrosion at opening reinforcing steel | Chamber 1 concrete precast ceiling |  |  |  | 00020368 | Glenway RES CFB Valve Chamber No. 1 (New) | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | Corrosion was observed at the opening reinforcing steel. |  |  |  |  | DSC08033 |  |  | W-WW | 2020
SC | NGR | 54 | 4735 | 3 | 00077422 | Common | Valve Chamber #1 Pump Hatch |  | 5000 |  |  | The asset was observed to be in good condition. Valve chamber #1 pump hatch to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Double leaf roof access hatch |  |  |  | 00020368 | Glenway RES CFB Valve Chamber No. 1 (New) | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | DSC07952 |  |  | W-WW | 2020
AC | NGR | 9 | 4798 | 1 |  | Common | Valve Chamber #1 Wall and Ceiling Paint |  | 3000 |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 3 |  |  |  | 2014 | peeling paint behind roof drain pipe |  |  |  |  | 00017315 | [15 empty] | Peeling paint was observed behind the roof drain pipe. |  |  |  |  | DSC08025 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0
AC | NGR | 9 | 4799 | 1 |  | Common | Valve Chamber #1 Wall and Ceiling Paint |  | 2000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  |  |  | 2014 | good |  |  |  |  | 00020368 | [20 empty] | DSC08032 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0
SW | NGR | 54 | 4768 | 2 |  | Common | Valve Chamber #3 Access Ladder |  | 1500 |  |  | The asset was observed to be in good condition. Valve chamber #3 access ladder to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good |  |  |  |  | 00008891 | [20 empty] | DSC08046 |  |  |  | 0
SW | NGR | 54 | 4767 | 3 |  | Common | Valve Chamber #3 Concrete Structure |  | 30000 |  |  | The asset was observed to be in good condition. Valve chamber #3 concrete structure to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good |  |  |  |  | 00008891 | [20 empty] | DSC08046 |  |  |  | 0
SW | NGR | 54 | 4769 | 2 |  | Common | Valve Chamber #3 Manhole Cover and Frame |  | 3000 |  |  | The asset was observed to be in good condition. Valve chamber #3 manhole cover and frame to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good |  |  |  |  | 00008891 | [20 empty] | DSC08045 |  |  |  | 0
SW | NGR | 54 | 4771 | 2 |  | Common | Valve Chamber #4 Access Ladder |  | 1500 |  |  | The asset was observed to be in good condition. Valve chamber #4 access ladder to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good |  |  |  |  | 00008891 | [20 empty] | DSC08051 |  |  |  | 0
SW | NGR | 54 | 4772 | 3 |  | Common | Valve Chamber #4 Concrete Structure |  | 30000 |  |  | The asset was observed to be in good condition. Valve chamber #4 concrete structure to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good |  |  |  |  | 00008891 | [20 empty] | DSC08051 |  |  |  | 0
SW | NGR | 54 | 4770 | 2 |  | Common | Valve Chamber #4 Manhole Cover and Frame |  | 2000 |  |  | The asset was observed to be in good condition. Valve chamber #4 manhole cover and frame to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good |  |  |  |  | 00008891 | [20 empty] | DSC08047 |  |  |  | 0
BM | NGR | 24 | 4696 | 2 | 00077379 | Common | Valve Chamber 1 Electric Heater UH-2 |  | 5000 |  |  | The asset was observed to be in good condition. Valve Chamber 1 Electric Heater UH-2 to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Chamber 1 suspended fan forced heater UH-2 (7.5 kw, 600/3/60) |  |  |  | 00017315 | Glenway RES CFB Valve Chamber No. 1 (Existing) | M00111 | [6 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2826 |  |  | W-WW | 2020
BM | NGR | 24 | 4713 | 2 | 00086891 | Common | Valve Chamber 1 Ceiling Ventilation System MOD-2 |  | 3000 |  |  | The asset was observed to be in good condition. Valve chamber 1 ceiling ventilation system to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Chamber 1 ceiling Exhaust fan with motorized damper MDD-2 (Belimo actuator, 120/1/60) |  |  |  | 00020368 | Glenway RES CFB Valve Chamber No. 1 (New) | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2855 |  |  | W-WW | 2020
BM | NGR | 24 | 4712 | 2 | 00077398 | Common | Valve Chamber 1 Electric Heating UH-3 |  | 5000 |  |  | The asset was observed to be in good condition. Valve Chamber Electric Heating UH-3 to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Chamber 1 suspended fan forced heater UH-3 (7.5 kW, 600/3/60) |  |  |  | 00020368 | Glenway RES CFB Valve Chamber No. 1 (New) | M00111 | [6 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2722 |  |  | W-WW | 2020
BM | NGR | 24 | 4650 | 2 | 00077326 | Common | Valve Chamber 1 Entry Room Louvre LV-6 |  | 3000 |  |  | The asset was observed to be in good condition. Entry Room Air Supply System LV-6 to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Chamber 1 entry room 400x400mm louvre LV-6 with motorized damper (120/1/60 with spring return) |  |  |  | 00020370 | Glenway RES CFB Entry Room | M00405 | [6 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2580 |  |  | W-WW | 2020
BM | NGR | 24 | 4736 | 2 | 00077423 | Common | Valve Chamber 1 Exhaust Fan F-1 |  | 5000 |  |  | The asset was observed to be in good condition. Valve Chamber 1 Exhaust Fan F-1 to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | External centrifugal belt-drive exhaust stack F-1 (Twin city model BCRD, 320 l/s, 60 Pa ESP, 120/1/60, 1/4hp, 1725 rpm) |  |  |  | 00020368 | Glenway RES CFB Valve Chamber No. 1 (New) | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2427 |  |  | W-WW | 2020
HSS | NGR | 9 | 4697 | 2 | 00077380 | Common | Valve Chamber 1 Eyewash Station 1 |  | 1500 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  |  |  | 2014 | good | Chamber 1 eyewash |  |  |  | 00017315 | Glenway RES CFB Valve Chamber No. 1 (Existing) | M00074 | [6 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2813 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020
HSS | NGR | 9 | 4758 | 2 | 00080999 | Common | Valve Chamber 1 Eyewash Station 2 |  | 1500 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  |  |  | 2014 | good | Chamber 1 eyewash |  |  |  | 00017315 | Glenway RES CFB Valve Chamber No. 1 (Existing) | M00074 | [6 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2700 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020
ES | NGR | 19 | 4731 | 2 | 00077417 | Common | Valve Chamber 3 Heat Trace System | 0 | 5000 |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the long term. | 3 |  | 0 |  | 2014 |  | Heat trace system for heating pressure impulse and sample piping installed in Valve Chamber 3 |  |  |  | 20368 | Glenway RES CFB Valve Chamber No. 1 (New) | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  |  | 0 |  | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
ES | NGR | 19 | 4886 | 2 | 00077417 | Common | Valve Chamber 4 Heat Trace System | 0 | 5000 |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the long term. | 3 |  | 0 |  | 2014 |  | Heat trace system for heating pressure impulse and sample piping installed in Valve Chamber 4 |  |  |  | 20368 | [19 empty] | 0 |  | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0 | 0
SIC | NGR | 9 | 4753 | 3 | 00080175 | Common | Watermain Inlet Chlorine Analyzer | 0 | 15000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 2 |  | 0 |  | 2016 | good |  |  |  |  | 17315 | Glenway RES CFB Valve Chamber No. 1 (Existing) | M00482 | CL-17 |  |  | Chlorine |  |  | Area 2N Linear Water & Wells |  | Instrumentation and Control | 071100020407 |  |  | OPERATING |  |  |  |  | 0 | IMG_2807 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
SIC | NGR | 9 | 4751 | 3 | 00080173 | Common | Watermain Outlet Chlorine Analyzer | 0 | 15000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 2 |  | 0 |  | 2016 | good |  |  |  |  | 17315 | Glenway RES CFB Valve Chamber No. 1 (Existing) | M00482 | CL-17 |  |  | Level |  |  | Area 2N Linear Water & Wells |  | Instrumentation and Control | 030900008101 |  |  | OPERATING |  |  |  |  | 0 | IMG_2807 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
SIC | NGR | 9 | 4730 | 3 | 00077416 | Common | Watermain Pressure Transmitter | 0 | 3000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2014 | good |  |  |  |  | 20368 | Glenway RES CFB Valve Chamber No. 1 (New) | M00405 | PMC71-1F330/1A6 |  |  | Pressure |  |  | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  |  | 0 | DSC08034 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
SW | NGR | 54 | 4605 | 3 | 00077272 | Common | Yard Bypass Watermain Piping |  | 25000 |  |  | The asset was assumed to be in fair condition. Asset to be replaced at the end of remaining service life. | 3 |  |  |  | 2014 |  | Diameter: 350mm, length: 24m |  |  |  | 00017316 | Glenway RES Outside Sanitary Pumping Station |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [8 empty] | W-WW | 2020
SW | NGR | 25 | 4606 | 3 | 00077273 | Common | Yard Bypass Watermain Piping Gate Valve |  | 3000 |  |  | The asset was assumed to be in fair condition. Asset to be replaced at the end of remaining service life. | 3 |  |  |  | 2014 |  | size: 350mm |  |  |  | 00017316 | Glenway RES Outside Sanitary Pumping Station |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [8 empty] | W-WW | 2020
SW | NGR | 54 | 4607 | 1 | 00077274 | Common | Yard Hydrant |  | 5000 |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good |  |  |  |  | 00008891 | Glenway RES Outside Sanitary Pumping Station | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_20200520_094958 |  |  | W-WW | 2020