## Sheet1
CategoryCode | facility | remainingESL | seqNum | COF | assetTag | defect3Input | assetName | RehabRepairCost | repCost | RehabRepairYear | rehabProjectName | observations | condition | rehabComment2 | RehabRepairCost2 | RehabRepairYear2 | installYear | defect1Input | Description | Process | building | inspectorName | LocationTag | LocationORIGINAL | manufacturer | TransmitterModel | TransducerModel | TransducerSerial | InstMeva | installationDate | InstType | ServiceArea | FacilityType | LifeCycleCategory | SerialNo | Parent | RotatingItem | Site | defect1 | defect2 | defect3 | rehabComment1 | rehabCost1 | photoName | repProjectName | rehab2ProjectName | Status | InspectionYear | rehabCost2 | defect2Input
SW | NGR | 22 | 4776 | 2 |  | Reservoir 1 | Drain Chamber #1 Access Ladder |  | 2000 |  |  | The asset was observed to be in good condition. Drain chamber #1 access ladder to be replaced at the end of remaining service life. | 2 |  |  |  | 1983 | good |  |  |  |  | 00008891 | [20 empty] | DSC07995 |  |  |  | 0
SW | NGR | 22 | 4777 | 3 |  | Reservoir 1 | Drain Chamber #1 Concrete Structure |  | 60000 |  |  | The asset was observed to be in good condition. Drain chamber #1 concrete structure to be replaced at the end of remaining service life. | 2 |  |  |  | 1983 | good |  |  |  |  | 00008891 | [20 empty] | DSC07995 |  |  |  | 0
SW | NGR | 22 | 4775 | 2 |  | Reservoir 1 | Drain Chamber #1 Manhole Cover and Frame |  | 2000 |  |  | The asset was observed to be in good condition. Drain chamber #1 manhole cover and frame to be replaced at the end of remaining service life. | 2 |  |  |  | 1983 | good |  |  |  |  | 00008891 | [20 empty] | DSC07989 |  |  |  | 0
SIC | NGR | 9 | 4705 | 3 | 00077388 | Reservoir 1 | Reservoir 1 Level Transmitter | 0 | 5000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2014 | good |  |  |  |  | 17315 | Glenway RES CFB Valve Chamber No. 1 (Existing) |  | PMC71-1LK64/142 |  |  | Level |  |  | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  |  | 0 | DSC08023 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
SC | NGR | 22 | 4782 | 2 |  | Reservoir 1 | Tank 1 Access Ladder | 5000 | 10000 | 2020 | Newmarket Glenway Reservoirs Capital Project 1 | The asset was observed to be in good condition. Tank 1 access ladder to be replaced at the end of remaining service life. | 3 |  |  |  | 1983 | good |  |  |  |  | 00017312 | [15 empty] | Fall arrest system is not compliant to current CSA standards. |  |  |  |  | DSC08005 |  |  |  | 0
PM | NGR | 24 | 4698 | 2 | 00077381 | Reservoir 1 | Tank 1 Drain Line Gate Valve (Drain Chamber 1) |  | 3700 |  |  | The asset was assumed to be in fair condition. Tank 1 drain line gate valve (drain chamber 1) to be replaced at the end of remaining service life. | 3 |  |  |  | 2014 |  | size: 300mm |  |  |  | 00020368 | Newmarket Glenway Reservoir 1 |  | Done | [5 empty] | Area 2N Linear Water & Wells | W - Storage Reservoir |  |  |  |  | OPERATING | [8 empty] | W-WW | 2020
SW | NGR | 23 | 4863 | 3 |  | Reservoir 1 | Tank 1 Drain Line Piping |  | 11400 |  |  | The asset was assumed to be in fair condition. Asset to be replaced at the end of remaining service life. | 3 |  |  |  | 1983 |  | Diameter: 300mm, length (approximately):10 meters |  |  |  | 00017312 |  |  | Done | [21 empty] | 0
SCS | NGR | 22 | 4786 | 3 |  | Reservoir 1 | Tank 1 Exterior Coating | 170000 | 575000 | 2035 | Newmarket Glenway Reservoir Capital Project 2 | The asset was observed to be in fair condition in general. Overcoating is recommende in the long term. Tank 1 exterior coating to be replaced at the end of remaining service life. | 3 |  |  |  | 1983 | good |  |  |  |  | 00017312 | [15 empty] | The exterior coating consists of an epoxy / urethane type of system which is in good condition, with only mild Lichen and mildew growth on the shell which was washed off during the condition assessment. | The sheen level on the shell is good and there are only a few corrosion spots around the manways and bolt holes and where grounds keeping equipment had damaged it. | The roof has a somewhat lower sheen level, which is to be expected given the higher levels of ultraviolet exposure. A few small areas on the roof have some corrosion, around the vent base and some of the handrail posts. There are piles of pine needles bui |  |  | DSC08004 |  |  |  | 0
SC | NGR | 22 | 4844 | 3 |  | Reservoir 1 | Tank 1 Guardrail |  | 8000 |  |  | The asset was observed to be in good condition. Tank 1 guardrail to be replaced at the end of remaining service life. | 2 |  |  |  | 1983 | good |  |  |  |  | 00017312 | [20 empty] | DSC08382 |  |  |  | 0
PM | NGR | 15 | 4574 | 3 | 00004458 | Reservoir 1 | Tank 1 Inlet Line Bypass Gate Valve | 1000 | 3700 | 2025 | Newmarket Glenway Reservoirs Capital Project 1 | The asset was observed to be in fair condition. Repaint valve. | 3 |  |  |  | 1983 | Minor surface corrosion | Size: 300mm, VC1_HV8 |  |  |  | 00017315 | Glenway RES CFB Valve Chamber No. 1 (Existing) | M00554 | Done | [5 empty] | Area 2N Linear Water & Wells |  | Process Mechanical |  |  |  | OPERATING | Minor surface corrosion was observed. |  |  |  |  | IMG_2798 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020
PM | NGR | 15 | 4828 | 3 | 00086914 | Reservoir 1 | Tank 1 Inlet Line Check Valve | 1000 | 3400 | 2025 | Newmarket Glenway Reservoirs Capital Project 1 | The asset was observed to be in fair condition. Rsurface and repaint valve. | 3 |  |  |  | 1983 | surface corrosion | Size: 300mm, VC1_CV1 |  |  |  | 00017315 |  |  | Done | [12 empty] | Surface corrosion was observed. |  |  |  |  | IMG_2693 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0
PM | NGR | 15 | 4614 | 3 | 00077283 | Reservoir 1 | Tank 1 Inlet Line Gate Valve 1 |  | 3700 |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the short term. | 3 |  |  |  | 1983 |  | Buried gate valve, size: 300mm |  |  |  | 00017312 | Glenway RES Tank No. 1 |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [6 empty] | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020
PM | NGR | 15 | 4743 | 3 | 00077430 | Reservoir 1 | Tank 1 Inlet Line Gate Valve 2 | 1000 | 2700 | 2025 | Newmarket Glenway Reservoirs Capital Project 1 | The asset was observed to be in fair condition. Asset to be replaced in the short term. | 3 |  |  |  | 1983 | Minor surface corrosion | Size: 300mm, VC1_HV3 |  |  |  | 00017315 | Glenway RES Outside Sanitary Pumping Station |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | Minor surface corrosion was observed. |  |  |  |  | IMG_2807 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020
PM | NGR | 15 | 4568 | 3 | 00004451 | Reservoir 1 | Tank 1 Inlet Line Gate Valve 3 | 1000 | 3700 | 2025 | Newmarket Glenway Reservoirs Capital Project 1 | The asset was observed to be in fair condition. Repaint the valve. | 3 |  |  |  | 1983 | surface corrosion |  |  |  |  | 00017315 | Glenway RES CFB Valve Chamber No. 1 (Existing) | M00554 | Done | [5 empty] | Area 2N Linear Water & Wells |  | Process Mechanical |  |  |  | OPERATING | Surface corrosion was observed. |  |  |  |  | IMG_2682 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020
PM | NGR | 15 | 4572 | 3 | 00004456 | Reservoir 1 | Tank 1 Inlet Line Gate Valve 4 | 1000 | 3700 | 2025 | Newmarket Glenway Reservoirs Capital Project 1 | The asset was observed to be in fair condition. Repaint valve. | 3 |  |  |  | 1983 | Moderate surface corrosion | size: 300mm, VC_HV1 |  |  |  | 00017315 | Glenway RES CFB Valve Chamber No. 1 (Existing) | M00554 | Done | [5 empty] | Area 2N Linear Water & Wells |  | Process Mechanical |  |  |  | OPERATING | Moderate surface corrosion was observed. |  |  |  |  | IMG_2696 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020
SW | NGR | 54 | 4865 | 4 |  | Reservoir 1 | Tank 1 Inlet Line Piping |  | 56700 |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Diameter: 300mm, length(approximately): 50m, from main header to tank 1 |  |  |  | 00017312 |  |  | Done | [17 empty] | IMG_2859 |  |  |  | 0
SCS | NGR | 15 | 4787 | 3 |  | Reservoir 1 | Tank 1 Interior Coating |  | 750000 |  |  | The asset was observed to be in fair condition. Tank 1 interior coating to be replaced at the end of remaining service life. | 3 |  |  |  | 1983 | good |  |  |  |  | 00017312 | [15 empty] | The interior is lined with a 100% solids polyurethane which is in fair condition. Below the water line there are almost no areas of corrosion apart from some small mechanically damaged spots and hidden areas around the mixing system support brackets and o | Above the water line there are a number of corroded areas including the roof plate seams which are not welded or sealed, and the seams between the roof plates and the support/assembly members which are only stitch welded and thus create many areas for cre | These areas should be touched up before they become structural in nature. At the same time, the roof plates should be seam sealed with a urethane type of caulking, applied between the primer and the top coat. Either scaffolding or swing stages will need t |  |  | DSC08010 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0
ES | NGR | 19 | 4858 | 2 | 00077325 | Reservoir 1 | Tank 1 Mixer Control Panel | 0 | 8500 |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 2 |  | 0 |  | 2014 | good |  |  |  |  | 20370 | [19 empty] | 0 | 20200520094144_IMG_2613 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0 | 0
PM | NGR | 24 | 4744 | 3 | 00077431 | Reservoir 1 | Tank 1 Outlet Line Butterfly Valve (Valve Chamber 3) | 1000 | 4800 | 2025 | Newmarket Glenway Reservoirs Capital Project 1 | The asset was observed to be in fair condition. Valve cleaning and shaft greasing are recommended. Tank 1 outlet line butterfly valve (valve chamber 3) to be replaced at the end of remaining service life. | 3 |  |  |  | 2014 | moderate corrosion due to atmospheric condition | Chamber 3 butterfly valve with manual geared operator (extension stem to the chamber roof slab), size: 400mm, VC3_HV1 |  |  |  | 00000000 | Glenway RES Outside Sanitary Pumping Station |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | Moderate corrosion was observed. |  |  | valve cleaning and shaft greasing. | 1000 | IMG_2885 |  |  | W-WW | 2020
PM | NGR | 24 | 4611 | 3 | 00077278 | Reservoir 1 | Tank 1 Outlet Line Gate Valve |  | 5000 |  |  | The asset was assumed to be in fair condition. Tank 1 outlet line gate valve to be replaced at the end of remaining service life. | 3 |  |  |  | 2014 |  | Size: 300mm |  |  |  |  | Glenway RES Outside Sanitary Pumping Station |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [8 empty] | W-WW | 2020
SW | NGR | 54 | 4615 | 4 | 00077284 | Reservoir 1 | Tank 1 Outlet Piping |  | 22700 |  |  | The asset was assumed to be in fair condition. Asset to be replaced at the end of remaining service life. | 3 |  |  |  | 2014 |  | diameter: 400mm, length: 15 meters. |  |  |  | 00017312 | Glenway RES Tank No. 1 |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [8 empty] | W-WW | 2020
SC | NGR | 22 | 4780 | 3 |  | Reservoir 1 | Tank 1 Roof Hatch |  | 5000 |  |  | The asset was observed to be in good condition. Tank 1 roof hatch to be replaced at the end of remaining service life. | 2 |  |  |  | 1983 | good |  |  |  |  | 00017312 | [20 empty] | DSC08383 |  |  |  | 0
PM | NGR | 12 | 4781 | 2 |  | Reservoir 1 | Tank 1 Roof Vent |  | 6000 |  |  | The asset was observed to be in good condition. The roof vent screen was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  |  |  | 1983 | good | 16'' frost-proof S.S. vent/vacuum relief unit |  |  |  | 00017312 | [20 empty] | 106_1729 | Newmarket Glenway Reservoir Capital Project 2 |  |  | 0
SC | NGR | 22 | 4779 | 3 |  | Reservoir 1 | Tank 1 Side Access Hatch |  | 5000 |  |  | The asset was observed to be in good condition. Tank 1 side access hatch to be replaced at the end of remaining service life. | 2 |  |  |  | 1983 | good |  |  |  |  | 00017312 | [20 empty] | DSC07994 |  |  |  | 0
SC | NGR | 22 | 4778 | 5 |  | Reservoir 1 | Tank 1 Steel Tank | 20000 | 1500000 | 2030 | Newmarket Glenway Reservoir Capital Project 2 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Tank 1 steel tank to be replaced at the end of remaining service life. | 2 |  |  |  | 1983 | good |  |  |  |  | 00017312 | [20 empty] | DSC08005 |  |  |  | 0
PM | NGR | 24 | 4887 | 3 |  | Reservoir 1 | Tank 1 Submersible Tank Mixer |  | 8000 |  |  | The asset was observed to be in good condition. | 3 |  |  |  | 2014 |  | Mixer attached to a stainless steel retrieval chain | [23 empty] | 0 | DSCN4372 |  |  |  | 0 | 0