## Sheet1
CategoryCode | facility | remainingESL | seqNum | COF | assetTag | defect3Input | assetName | RehabRepairCost | repCost | RehabRepairYear | rehabProjectName | observations | condition | rehabComment2 | RehabRepairCost2 | RehabRepairYear2 | installYear | defect1Input | Description | Process | building | inspectorName | LocationTag | LocationORIGINAL | manufacturer | TransmitterModel | TransducerModel | TransducerSerial | InstMeva | installationDate | InstType | ServiceArea | FacilityType | LifeCycleCategory | SerialNo | Parent | RotatingItem | Site | defect1 | defect2 | defect3 | rehabComment1 | rehabCost1 | photoName | repProjectName | rehab2ProjectName | Status | InspectionYear | rehabCost2 | defect2Input
SW | NGR | 22 | 4842 | 2 |  | Reservoir 2 | Drain Chamber #2 Access Ladder |  | 1500 |  |  | The asset was observed to be in good condition. Drain chamber #2 access ladder to be replaced at the end of remaining service life. | 2 |  |  |  | 1983 | good |  |  |  |  | 00020364 | [20 empty] | DSC08355 |  |  |  | 0
SW | NGR | 54 | 4773 | 2 |  | Reservoir 2 | Drain Chamber #2 Concrete Structure |  | 10000 |  |  | The asset was observed to be in good condition. Drain chamber #2 concrete structure to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good |  |  |  |  | 00020364 | [20 empty] | DSC08355 |  |  |  | 0
SW | NGR | 54 | 4774 | 2 |  | Reservoir 2 | Drain Chamber #2 Grate and Frame |  | 2000 |  |  | The asset was observed to be in good condition. Drain chamber #2 grate and frame to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good |  |  |  |  | 00008891 | [20 empty] | DSC08353 |  |  |  | 0
SIC | NGR | 9 | 4706 | 3 | 00077389 | Reservoir 2 | Reservoir 2 Level Transmitter | 0 | 5000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 2 |  | 0 |  | 2014 | good |  |  |  |  | 17315 | Glenway RES CFB Valve Chamber No. 1 (Existing) | M00405 | PMC71-1LK64/142 |  |  | Level |  |  | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  |  | 0 | DSC08023 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
SC | NGR | 54 | 4597 | 4 | 00077262 | Reservoir 2 | Tank 2 Access Ladder | 5000 | 10000 | 2020 | Newmarket Glenway Reservoirs Capital Project 1 | The asset was observed to be in fair condition. Tank 2 access ladder to be replaced at the end of remaining service life. | 3 |  |  |  | 2014 | Fall arrest system is not compliant to current CSA standards | Aluminum ladder |  |  |  | 00020365 | Glenway RES Tank No. 2 Roof | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | Fall arrest system is not compliant to current CSA standards. |  |  |  |  | DSC08352 |  |  | W-WW | 2020
SC | NGR | 54 | 4595 | 5 | 00077260 | Reservoir 2 | Tank 2 Concrete Tank | 40000 | 2000000 | 2030 | Newmarket Glenway Reservoir Capital Project 2 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Tank 2 concrete tank to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good |  |  |  |  | 00020364 | Glenway RES Tank No. 2 | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | DSC08352 |  |  | W-WW | 2020
PM | NGR | 24 | 4864 | 2 | 00077381 | Reservoir 2 | Tank 2 Drain Line Gate Valve |  | 3700 |  |  | The asset was assumed to be in fair condition. Tank 2 drain line gate valve to be replaced at the end of remaining service life. | 3 |  |  |  | 2014 |  | Size: 300mm gate valve (underground) |  |  |  |  | Newmarket Glenway Reservoir 1 |  | Done | [5 empty] | Area 2N Linear Water & Wells | W - Storage Reservoir |  |  |  |  | OPERATING | [8 empty] | W-WW | 2020
SW | NGR | 54 | 4601 | 3 | 00077267 | Reservoir 2 | Tank 2 Drain Line Piping |  | 17000 |  |  | The asset was assumed to be in fair condition. Asset to be replaced at the end of remaining service life. | 3 |  |  |  | 2014 |  | Diameter: 300mm, length: 15 meters |  |  |  | 00020364 | Glenway RES Tank No. 2 |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [8 empty] | W-WW | 2020
PM | NGR | 24 | 4598 | 2 | 00077264 | Reservoir 2 | Tank 2 Exhaust Stack |  | 10000 |  |  | The asset was observed to be in good condition. The screen of the exhaust stack was observed to be in good condition. The Tank 2 exhaust stack to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Tank 2 ventilation system: exhaust stack |  |  |  | 00020364 | Glenway RES Tank No. 2 Roof | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING |  |  |  | Insect screen cleaning and repair if found damaged; checking the flange anchorage system and gaskets and upgrading them if needed. | 3000 | 106_2722 |  |  | W-WW | 2020
SCS | NGR | 16 | 5163 | 1 |  | Reservoir 2 | Tank 2 Exterior Coating |  | 194000 |  |  | The asset was observed to be in good condition. Replace the asset at the end of the service life. | 2 |  |  |  | 2014 |  | exterior of the tank consists of a shotcrete textured protective layer finished in acrylic elastomeric finish. |  |  |  | 00020364 | [19 empty] | 0 | DSC08361 | Newmarket Glenway Reservoirs Capital Project 2 |  |  | 0 | 0
SC | NGR | 54 | 4843 | 3 |  | Reservoir 2 | Tank 2 Guardrail |  | 8000 |  |  | The asset was observed to be in good condition. Tank 2 guardrail to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good |  |  |  |  | 00020365 | [20 empty] | DSC08359 |  |  |  | 0
SC | NGR | 54 | 4845 | 3 |  | Reservoir 2 | Tank 2 Horizontal Lifeline |  | 2500 |  |  | The asset was observed to be in good condition. Tank 2 horizontal lifeline to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good |  |  |  |  | 00020365 | [20 empty] | DSC08385 |  |  |  | 0
PM | NGR | 24 | 4701 | 3 | 00077384 | Reservoir 2 | Tank 2 Inlet Line Bypass Gate Valve |  | 3700 |  |  | The asset was observed to be in good condition. Tank 2 inlet line bypass gate valve to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Size: 300mm |  |  |  | 00017315 | Newmarket Glenway Reservoir 1 |  | Done | [5 empty] | Area 2N Linear Water & Wells | W - Storage Reservoir |  |  |  |  | OPERATING | [5 empty] | IMG_2791 |  |  | W-WW | 2020
PM | NGR | 24 | 4827 | 3 | 00080991 | Reservoir 2 | Tank 2 Inlet Line Check Valve |  | 3400 |  |  | The asset was observed to be in good condition. Tank 2 inlet line check valve to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | size: 300mm, manufacturer: Cla-Val |  |  |  | 00020368 |  |  | Done | [17 empty] | IMG_2782 |  |  |  | 0
PM | NGR | 24 | 4702 | 3 | 00077385 | Reservoir 2 | Tank 2 Inlet Line Gate Valve 1 |  | 3700 |  |  | The asset was observed to be in good condition. Tank 2 inlet line gate valve 1 to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Size: 300 mm, manufacturer: Clow Valve Co. |  |  |  | 00017315 | Newmarket Glenway Reservoir 1 |  | Done | [5 empty] | Area 2N Linear Water & Wells | W - Storage Reservoir |  |  |  |  | OPERATING | [5 empty] | IMG_2773 |  |  | W-WW | 2020
PM | NGR | 24 | 4703 | 3 | 00077386 | Reservoir 2 | Tank 2 Inlet Line Gate Valve 2 |  | 3700 |  |  | The asset was observed to be in good condition. Tank 2 inlet line gate valve 2 to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Size: 300 mm, manufacturer: Clow Valve Co. |  |  |  | 00017315 | Newmarket Glenway Reservoir 1 |  | Done | [5 empty] | Area 2N Linear Water & Wells | W - Storage Reservoir |  |  |  |  | OPERATING | [5 empty] | IMG_2772 |  |  | W-WW | 2020
PM | NGR | 24 | 4746 | 3 | 00077433 | Reservoir 2 | Tank 2 Inlet Line Gate Valve 3 |  | 2700 |  |  | The asset was assumed to be in fair condition. Tank 2 inlet line gate valve to be replaced at the end of remaining service life. | 3 |  |  |  | 2014 |  | Size: 300mm |  |  |  | 00017316 | Glenway RES Outside Sanitary Pumping Station |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [8 empty] | W-WW | 2020
SW | NGR | 54 | 4704 | 4 | 00077387 | Reservoir 2 | Tank 2 Inlet Line Piping |  | 60000 |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Diameter: 350mm, length: 45m |  |  |  | 00017315 | Glenway RES CFB Valve Chamber No. 1 (Existing) |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_2791 |  |  | W-WW | 2020
SC | NGR | 4 | 4846 | 3 |  | Reservoir 2 | Tank 2 Interior Access Ladder |  | 5000 |  |  | The asset was observed to be in fair condition. Tank 2 interior access ladder to be replaced with stainless steel or FRP type of ladder. | 3 |  |  |  | 2014 | good |  |  |  |  | 00020364 | [15 empty] | The aluminum ladder was heavily oxidized. |  |  |  |  | DSC08424 | Newmarket Glenway Reservoirs Capital Project 1 |  |  | 0
ES | NGR | 19 | 4649 | 2 | 00077325 | Reservoir 2 | Tank 2 Mixer Control Panel | 0 | 8500 |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 2 |  | 0 |  | 2014 | good |  |  |  |  | 20370 | Glenway RES CFB Entry Room | M10304 | [6 empty] | Area 2N Linear Water & Wells |  | Electrical |  |  |  | OPERATING |  |  |  |  | 0 | 20200520094046_IMG_2611 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020 | 0
PM | NGR | 24 | 4745 | 3 | 00077432 | Reservoir 2 | Tank 2 Outlet Line Butterfly Valve (Valve Chamber 3) | 1000 | 4800 | 2025 | Newmarket Glenway Reservoirs Capital Project 1 | The asset was observed to be in fair condition. Valve cleaning and shaft greasing are recommended. Tank 2 outlet line butterfly valve (valve chamber 3) to be replaced at the end of remaining service life. | 3 |  |  |  | 2014 | moderate corrosion due to atmospheric condition | Chamber 3 butterfly valve with manual geared operator (extension stem to the chamber roof slab), size: 400mm, VC3_HV2 |  |  |  | 00000000 | Glenway RES Outside Sanitary Pumping Station |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | Moderate corrosion was observed. |  |  | valve cleaning and shaft greasing. | 1000 | IMG_2892 |  |  | W-WW | 2020
PM | NGR | 24 | 4861 | 3 |  | Reservoir 2 | Tank 2 Outlet Line Gate Valve |  | 5000 |  |  | The asset was assumed to be in fair condition. Tank 2 outlet line gate valve to be replaced at the end of remaining service life. | 3 |  |  |  | 2014 |  | Size: 400mm gate valve (underground) |  |  |  |  | Glenway RES Outside Sanitary Pumping Station |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [8 empty] | W-WW | 2020
SW | NGR | 54 | 4603 | 4 | 00077270 | Reservoir 2 | Tank 2 Outlet Line Piping |  | 22700 |  |  | The asset was assumed to be in fair condition. Asset to be replaced at the end of remaining service life. | 3 |  |  |  | 2014 |  | Diameter: 400 mm length: 15 meters |  |  |  | 00017316 | Glenway RES Outside Sanitary Pumping Station |  | Done | [5 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [8 empty] | W-WW | 2020
SC | NGR | 54 | 4600 | 4 | 00077266 | Reservoir 2 | Tank 2 Overflow Concrete Encasement | 2000 | 20000 | 2030 | Newmarket Glenway Reservoir Capital Project 2 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Tank 2 overflow concrete encasement to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Overflow pipe concrete support |  |  |  | 00020364 | Glenway RES Tank No. 2 | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | DSC08415 |  |  | W-WW | 2020
SW | NGR | 14 | 4623 | 2 | 00077292 | Reservoir 2 | Tank 2 Overflow Rip Rap Stone |  | 15000 |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 2 |  |  |  | 2014 | Good | Rip rap stone overflow channel |  |  |  | 00017316 | Glenway RES Outside Sanitary Pumping Station | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | IMG_20200520_094824 | Newmarket Glenway Reservoir Capital Project 2 |  | W-WW | 2020
SC | NGR | 54 | 4599 | 3 | 00077265 | Reservoir 2 | Tank 2 Roof Hatch |  | 5000 |  |  | The asset was observed to be in good condition. Tank 2 roof hatch to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good | Dome hatch |  |  |  | 00020365 | Glenway RES Tank No. 2 Roof | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | DSC08358 |  |  | W-WW | 2020
SC | NGR | 54 | 4596 | 3 | 00077261 | Reservoir 2 | Tank 2 Side Access Hatch |  | 5000 |  |  | The asset was observed to be in good condition. Tank 2 side access hatch to be replaced at the end of remaining service life. | 2 |  |  |  | 2014 | good |  |  |  |  | 00020364 | Glenway RES Tank No. 2 | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | [5 empty] | DSC08352 |  |  | W-WW | 2020
PM | NGR | 24 | 4884 | 3 |  | Reservoir 2 | Tank 2 Submersible Tank Mixer |  | 8000 |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. | 3 |  |  |  | 2014 |  | Mixer attached to a stainless steel retrieval chain |  |  |  | 00020364 | [15 empty] | Surface corrosion was observed. |  |  |  | 0 | DSC08393 |  |  |  | 0 | 0