## Sheet1
CategoryCode | assetTag | seqNum | facility | remainingESL | assetName | repCost | condition | observations | RehabRepairCost | COF | RehabRepairYear | rehabComment2 | RehabRepairCost2 | RehabRepairYear2 | installYear | defect1Input | rehabProjectName | Description | Process | building | inspectorName | LocationTag | LocationORIGINAL | manufacturer | TransmitterModel | TransducerModel | TransducerSerial | InstMeva | installationDate | InstType | ServiceArea | FacilityType | LifeCycleCategory | SerialNo | Parent | RotatingItem | Site | defect1 | defect2 | defect3 | rehabComment1 | rehabCost1 | photoName | repProjectName | rehab2ProjectName | Status | InspectionYear | rehabCost2 | defect2Input | defect3Input
SC |  | 4540 | NNE | 22 | Elevated Tank Steel Tank | 1224000 | 3 | The asset was observed to be in fair condition based on its age. Elevated tank steel tank to be replaced at the end of remaining service life. | 0 | 5 |  |  | 0 |  | 1972 | fair |  | Capacity: 2272 cubic meters. |  |  |  | 00017330 | [15 empty] | The inside roof plate seams were observed to be welded or sealed. |  |  |  | 0 | IMG_20200401_101104 |  |  |  | 0 | 0
SCS |  | 4558 | NNE | 19 | Elevated Tank Exterior Coating | 1100000 | 3 | The asset was observed to be in fair condition. Removal and replacement of the exterior coating is recommended in 16 - 20 years. | 0 | 3 |  |  | 0 |  | 2002 | good |  | External overcoating of the tank belly area and touchup of coating were performed in 2016 |  |  |  | 00017330 | [15 empty] | The exterior coating was sound; however, many touch-ups were observed. | Sheen level above catwalk was minimal. |  |  | 0 | IMG_20200401_101104 | Newmarket NE ET Capital Project 2 |  |  | 0 | 0
SCS |  | 4559 | NNE | 19 | Elevated Tank Interior Coating | 350000 | 3 | The asset was observed to be in fair condition. Elevated tank interior coating to be replaced in 16 - 20 years. | 0 | 3 |  |  | 0 |  | 2002 | good |  | Internal touchup of a thin film epoxy lining was performed in 2016 |  |  |  | 00017330 | [15 empty] | Lining was fairly sound below HWL. Crevice corrosion of roof plate seams were observed. |  |  |  | 0 | (195) | Newmarket NE ET Capital Project 2 |  |  | 0 | 0
PM |  | 4817 | NNE | 12 | Elevated Tank Inlet/Outlet Header | 255000 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 | 5 |  |  | 0 |  | 1972 | Minor corrosion was observed on the visible portion of the pipe. |  | Material: d.i, approximate length: 225meter, diameter: 300mm |  |  |  | 00009236 | [15 empty] | Minor corrosion was observed on the visible portion of the pipe. |  |  |  | 0 | IMG_1774 | Newmarket NE ET Capital Project 2 |  |  | 0 | 0
SW |  | 4505 | NNE | 12 | 300mm watermain | 153000 | 3 | The asset was assumed to be in fair condition. Asset to be replaced in the long term. | 0 | 5 |  |  | 0 |  | 1972 |  |  | 300mm cast iron watermain that connects elevated tank to network. approx. 180m in length. |  |  |  | 00009236 | [19 empty] | 0 |  | Newmarket NE ET Capital Project 2 |  |  | 0 | 0
SC | 00014421 | 4473 | NNE | 22 | Elevated Tank Tank Support Legs | 1300000 | 2 | The asset was observed to be in good condition. Elevated tank tank support legs to be replaced at the end of remaining service life. | 0 | 4 |  |  | 0 |  | 1972 | fair |  | Support legs of the elevated tower, other structural component, |  |  |  | 00017328 | Newmarket NE ET Tank Base | [7 empty] | Area 2N Linear Water & Wells |  | Structural |  |  |  | OPERATING |  |  |  |  | 0 | IMG_20200401_101104 |  |  | W-WW | 2020 | 0
SIC | 00084311 | 4511 | NNE | 11 | PLC Panel | 81600 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 | 4 |  |  | 0 |  | 2016 | good |  | Plc panel, summa engineering ltd.,nmetdd_pac, 14e-088, nema 12, installation year assumed to be 2016 |  |  |  | 00017331 | [19 empty] | 0 | IMG_2673 | Newmarket NE ET Capital Project 2 |  |  | 0 | 0
SW |  | 4502 | NNE | 6 | Asphalt Driveway (shared) | 66300 | 3 | The asset was observed to be in fair to poor condition. Asset to be repaved in the intermediate term. | 0 | 2 |  |  | 0 |  | 1972 | Poor condition. |  | Asphalt driveway where adjacent commercial properties also use driveway for deliveries. |  |  |  | 00009236 | [15 empty] | Major cracks and pot holes were observed in several locations. |  |  |  | 0 | IMG_20200401_100711 | Newmarket NE ET Capital Project 1 |  |  | 0 | 0 | Major cracks and pot holes in several locations.
SC | 00014415 | 4469 | NNE | 22 | Concrete Valve Chamber | 60000 | 3 | The asset was observed to be in fair condition. Structural repairs are recommended in 1 - 5 years. Concrete valve chamber to be replaced at the end of remaining service life. | 15000 | 3 | 2022 |  | 15000 | 2032 | 1972 | exposed rebar | Newmarket NE ET Capital Project 1 | Chamber, floor slab |  |  |  | 00017331 | Newmarket NE ET Valve Room | [7 empty] | Area 2N Linear Water & Wells |  | Structural |  |  |  | OPERATING | Exposed rebar was observed. |  |  |  | 0 | (139) |  | Newmarket NE ET Capital Project 2 | W-WW | 2020 | 0
SW |  | 4504 | NNE | 25 | Driveway Grading | 51000 | 3 | The asset was observed to be in fair condition. Remove and replace the gabion baskets or install new retaining wall. Regrade area between gabion baskets and driveway. | 20000 | 2 | 2024 |  | 0 |  | 1972 | Majority of gabion baskets were damaged allowing the stones to exit. | Newmarket NE ET Capital Project 1 | Grading on the west side of driveway entrance including gabion baskets/retaining wall, approximately: 50 meters |  |  |  | 00009236 | [15 empty] | Majority of gabion baskets are damaged allowing the stones to spill out. | The granular and sod between gabion baskets and driveway has settled in some sections which has caused a portion of the guard rail to start leaning. |  | Remove and replace the gabion baskets or install new retaining wall. Regrade area between gabion baskets and driveway. | 20000 | IMG_20200401_101502 |  |  |  | 0 | 0 | The granular and sod between gabion baskets and driveway had settled in some sections which has made a portion of the guard rail to start leaning.
SC |  | 4541 | NNE | 22 | Elevated Tank Catwalk | 51000 | 2 | The asset was observed to be in good condition. Elevated tank catwalk to be replaced at the end of remaining service life. | 0 | 4 |  |  | 0 |  | 1972 | good |  | Catwalk around the elevator tank |  |  |  | 00017328 | [15 empty] | Minor mechanical abrasion was observed |  |  |  | 0 | (234) |  |  |  | 0 | 0
SC |  | 4875 | NNE | 22 | Elevated Tank Roof Guardrail | 50000 | 3 | The asset was observed to be in fair condition. Weld repair of the roof guardrail upright is recommended in 1 - 5 years. | 2000 | 3 | 2022 |  | 0 | 0 | 1972 |  | Newmarket NE ET Capital Project 1 | Roof Guardrail | [19 empty] | One of the roof guardrail uprights (sockets) was observed to be split. |  |  |  | 0 | (267) |  |  |  | 0 | 0
SC |  | 4833 | NNE | 22 | Elevated Tank Base to Catwalk Ladder | 40800 | 4 | The asset was observed to be in poor condition. The fail arrest system was not compliant to current CSA standard. Replacement of the fall arrest system is recommended immediately. The ladder to be replaced at the end of remaining service life. | 5000 | 2 | 2020 |  | 0 |  | 1972 | minor surface corrosion | Newmarket NE ET Capital Project 1 |  |  |  |  | 00017328 | [15 empty] | Minor surface corrosion was observed. | The fail arrest system was not compliant to current CSA standard. |  |  | 0 | (314) |  |  |  | 0 | 0 | Peeling paint
SC |  | 4564 | NNE | 36 | Elevated Tank Cathodic Protection System | 40800 | 2 | The asset was observed to be in good condition. Elevated tank cathodic protection system to be replaced at the end of remaining service life. | 0 | 3 |  |  | 0 |  | 2016 | good |  | Two (2) cathodic protection device |  |  |  | 00017328 | [19 empty] | 0 | IMG_2131 |  |  |  | 0 | 0
SC |  | 4542 | NNE | 22 | Elevated Tank Wet Riser Internal Ladder | 40800 | 3 | The asset was observed to be in fair condition. The fail arrest system was not compliant to current CSA standard. Replace the fail arrest system immediately. Elevated tank wet riser internal ladder to be replaced at the end of remaining service life. | 5000 | 2 | 2020 |  | 0 |  | 1972 | moderate corrosion | Newmarket NE ET Capital Project 1 |  |  |  |  | 00017328 | [15 empty] | Moinr corrosion was observed. | The fail arrest system was not compliant to current CSA standard. |  |  | 0 | (202) |  |  |  | 0 | 0
PM | 00004562 | 4458 | NNE | 11 | Elevated Tank Inlet/Outlet Header Altitude Valve | 35700 | 3 | The asset was observed to be in fair condition based on its age. The valve was well maintained. Asset to be replaced in the long term. | 0 | 4 |  |  | 0 |  | 1972 | fair |  | Main line, 300 dia valve, control, cla-val, valve repainted in 2016 |  |  |  | 00017331 | Newmarket NE ET Valve Room | M00038 | [6 empty] | Area 2N Linear Water & Wells |  | Process Mechanical | W01644 |  |  | OPERATING |  |  |  |  | 0 | IMG_1779 | Newmarket NE ET Capital Project 2 |  | W-WW | 2020 | 0 | well maintained
SW |  | 4500 | NNE | 8 | Asphalt Parking Lot | 30600 | 3 | The asset was observed to be in fair condition. Asset to be repaved in the intermediate term. | 0 | 2 |  |  | 0 |  | 2002 | Minor cracks in pavement |  | Asphalt within site and driveway. |  |  |  | 00009236 | [15 empty] | Minor cracks in pavement were observed. |  |  |  | 0 | IMG_20200401_100203 | Newmarket NE ET Capital Project 1 |  |  | 0 | 0
PM |  | 4818 | NNE | 12 | Elevated Tank Overflow Piping | 30600 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 | 4 |  |  | 0 |  | 1972 | good |  | Diameter: 200mm, length: 40 meters, from elevated tank to overflow catch basin |  |  |  | 00009236 | [19 empty] | 0 | IMG_20200401_102522 | Newmarket NE ET Capital Project 2 |  |  | 0 | 0
SW |  | 4508 | NNE | 25 | Sanitary Manhole and DICBs | 30600 | 3 | The asset was observed to be in fair condition. | 0 | 2 |  |  | 0 |  | 1972 | The catchbasin cover was heavily corroded. Paint peeling was also observed. |  | One (1) sanitary manhole and two (2) dicbs on site. |  |  |  | 00009236 | [15 empty] | The catchbasin cover was heavily corroded. | Paint peeling was observed. |  |  | 0 | IMG_2959 |  |  |  | 0 | 0
SC | 00014420 | 4472 | NNE | 42 | Valve House Metal Prefab Structure | 30600 | 3 | The asset was observed to be in fair condition. Valve house metal prefab structure to be replaced at the end of remaining service life. | 0 | 3 |  |  | 0 |  | 2002 | corrosion on hardware |  | Steel enclosure/housing for entrance to , other structural component, |  |  |  | 00017331 | Newmarket NE ET Valve Room | [7 empty] | Area 2N Linear Water & Wells |  | Structural |  |  |  | OPERATING | Corrosion was observed on hardware. |  |  |  | 0 | IMG_20200401_101216 |  |  | W-WW | 2020 | 0
SW | 00014410 | 4847 | NNE | 15 | Perimeter Fence | 28000 | 3 | The site fencing was observed to be in fair condition. Remove overgrowth on fence as required. Asset to be replaced in the long term | 5000 | 1 | 2026 |  | 0 |  | 1972 | Good | Newmarket NE ET Capital Project 1 | Chainlink fence around perimeter, length: 200 meters |  |  |  | 00017331 | [15 empty] | Surface corrosion and overgrowth on fence was observed. |  |  |  | 0 | IMG_20200401_094004 | Newmarket NE ET Capital Project 2 |  |  | 0 | 0
SW | 00014414 | 4468 | NNE | 25 | Site Grading | 25500 | 3 | The asset was observed to be in fair condition. Regrade areas with low spots and holes throughout the site, and re-sod. Ensure areas around DCIBs have positive drainage towards DCIBs. | 6000 | 1 | 2024 |  | 0 |  | 1972 | Multiple locations around site where there are low spots and holes which cause tripping hazards. | Newmarket NE ET Capital Project 1 | Grass condition and drainage of site |  |  |  | 00009236 | Newmarket Northeast Elevated Tank | [7 empty] | Area 2N Linear Water & Wells | W - Storage Elevated Tank | Siteworks |  |  |  | OPERATING | Multiple locations around the site had low spots and rodent holes which can cause tripping hazards. | The low spots around Wellhouse No.14 can cause poor drainage away from building. | Tire marks along the edge of the asphalt by the facility parking area was noted. | Regrade areas with low spots and holes throughout the site, and re-sod. Ensure areas around DCIBs have positive drainage towards DCIBs. | 5000 | IMG_20200401_094041 |  |  | W-WW | 2020 | 0 | Low spots around Well No. 14 building wall causing poor drainage away from building. | Tire marks along edge of asphalt by parking area.
SC |  | 4547 | NNE | 22 | Wellhouse 14 Concrete Blockwall | 25500 | 3 | The asset was observed to be in fair condition based on age. The wellhouse is currently being decommissioned, replacement and/or rehabilitation of the asset are no longer required, and they are not included in the capital project. |  | 4 |  |  |  |  | 1972 | fair |  | Original construction |  |  |  | 00000000 | [19 empty] | 0 | IMG_2075 |  |  |  | 0 | 0
PM |  | 4819 | NNE | 12 | Elevated Tank Drain Piping | 23000 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 | 4 |  |  | 0 |  | 1972 | good |  | Diameter: 200mm, length: 30 meters, from elevated tank to sanitary maintenance hole |  |  |  | 00009236 | [19 empty] | 0 | IMG_1724 | Newmarket NE ET Capital Project 2 |  |  | 0 | 0
ES |  | 4841 | NNE | 7 | Electrical Conduit System | 20400 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 | 3 |  |  | 0 |  | 2002 | good |  | Installation year assumed to be 2002 |  |  |  | 00009236 | [19 empty] | 0 | (367) | Newmarket NE ET Capital Project 1 |  |  | 0 | 0
SC |  | 4832 | NNE | 22 | Elevated Tank Catwalk Bolted Manhole | 20400 | 2 | The asset was observed to be in good condition. Elevated tank catwalk bolted manhole to be replaced at the end of remaining service life. | 0 | 2 |  |  | 0 |  | 1972 | good | [5 empty] | 00017328 | [19 empty] | 0 | (255) |  |  |  | 0 | 0
AC |  | 4553 | NNE | 6 | Wellhouse 14 Metal Cladding | 16400 | 3 | The asset was observed to be in fair condition based in its age. The wellhouse is currently being decommissioned, replacement and/or rehabilitation of the asset are no longer required, and they are not included in the capital project. | 0 | 1 |  |  | 0 |  | 1972 | fair |  | Original construction |  |  |  | 00017331 | [19 empty] | 0 | IMG_20200401_102449 |  |  |  | 0 | 0
SW |  | 4506 | NNE | 12 | Sewers | 16000 | 3 | The asset was assumed to be in fair condition. Asset to be replaced in the long term. | 0 | 3 |  |  | 0 |  | 1972 |  |  | 200mm cast iron drain that convey storm water and elevated tank overflow out of site. approx. 200m in length. 150mm drain from well 14 building, approx. 13m in length. |  |  |  | 00009236 | [19 empty] | 0 |  | Newmarket NE ET Capital Project 2 |  |  | 0 | 0
SW |  | 4501 | NNE | 6 | Concrete Curb | 15300 | 4 | The asset was observed to be in poor condition. Asset to be replaced in the intermediate term. | 0 | 1 |  |  | 0 |  | 1972 | damaged on few sections |  | Concrete curb along driveway. |  |  |  | 00009236 | [15 empty] | Moderate damage of few sections were observed. | Multiple locations with cracks were observed. |  |  | 0 | IMG_20200401_100223 | Newmarket NE ET Capital Project 1 |  |  | 0 | 0 | Multiple locations with cracks
SC |  | 4834 | NNE | 22 | Elevated Tank Catwalk to Roof Ladder | 15300 | 4 | The asset was observed to be in poor condition. The fail arrest system was not compliant to current CSA standard. Replacement of the fall arrest system is recommended in immediately. Elevated tank catwalk to roof ladder to be replaced at the end of remai | 2000 | 4 | 2020 |  | 0 |  | 1972 | minor surface corrosion | Newmarket NE ET Capital Project 1 |  |  |  |  | 00017328 | [15 empty] | Minor surface corrosion and paint peeling were observed. | The fail arrest system was not compliant to current CSA standard. |  |  | 0 | (266) |  |  |  | 0 | 0 | Peeling paint
SC |  | 4544 | NNE | 22 | Wellhouse 14 Concrete Strip Footing | 15300 | 3 | The asset was observed to be in fair condition based on its age. The wellhouse is currently being decommissioned, replacement and/or rehabilitation of the asset are no longer required, and they are not included in the capital project. |  | 3 |  |  |  |  | 1972 | fair |  | Original construction |  |  |  | 00017331 | [19 empty] | 0 | (94) |  |  |  | 0 | 0
SIC | 00082890 | 4495 | NNE | 11 | Antenna NMETDD | 10200 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 | 1 |  |  | 0 |  | 2016 | good |  | Nmetdd antenna, network, antenna & cable, outdoor |  |  |  | 00017330 | Newmarket NE ET Water Tank Roof | M10316 | [6 empty] | Area 2N Linear Water & Wells |  | Instrumentation and Control | LPJ3842710 |  |  | OPERATING |  |  |  |  | 0 | (371) | Newmarket NE ET Capital Project 2 |  | W-WW | 2020 | 0
SIC | 00025197 | 4480 | NNE | 11 | Antenna Telus 1 | 10200 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 | 1 |  |  | 0 |  | 2016 | good |  | Antenna, telus 1, cellular , cellular, installation year assumed to be 2016 |  |  |  | 00009236 | Newmarket Northeast Elevated Tank | [7 empty] | Area 2N Linear Water & Wells | W - Storage Elevated Tank | Antenna |  |  |  | OPERATING |  |  |  |  | 0 | (368) | Newmarket NE ET Capital Project 2 |  | W-WW | 2020 | 0
SIC | 00025198 | 4481 | NNE | 11 | Antenna Telus 10 | 10200 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 | 1 |  |  | 0 |  | 2016 | good |  | Antenna, telus 10, pcs, pcs, installation year assumed to be 2016 |  |  |  | 00009236 | Newmarket Northeast Elevated Tank | [7 empty] | Area 2N Linear Water & Wells | W - Storage Elevated Tank | Antenna |  |  |  | OPERATING |  |  |  |  | 0 | (368) | Newmarket NE ET Capital Project 2 |  | W-WW | 2020 | 0
SIC | 00025201 | 4484 | NNE | 11 | Antenna Telus 11 | 10200 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 | 1 |  |  | 0 |  | 2016 | good |  | Antenna, telus 11, pcs, pcs, installation year assumed to be 2016 |  |  |  | 00009236 | Newmarket Northeast Elevated Tank | [7 empty] | Area 2N Linear Water & Wells | W - Storage Elevated Tank | Antenna |  |  |  | OPERATING |  |  |  |  | 0 | (370) | Newmarket NE ET Capital Project 2 |  | W-WW | 2020 | 0
SIC | 00025203 | 4486 | NNE | 11 | Antenna Telus 12 | 10200 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 | 1 |  |  | 0 |  | 2016 | good |  | Antenna, telus 12, pcs, pcs, installation year assumed to be 2016 |  |  |  | 00009236 | Newmarket Northeast Elevated Tank | [7 empty] | Area 2N Linear Water & Wells | W - Storage Elevated Tank | Antenna |  |  |  | OPERATING |  |  |  |  | 0 | (370) | Newmarket NE ET Capital Project 2 |  | W-WW | 2020 | 0
SIC | 00025208 | 4491 | NNE | 11 | Antenna Telus 13 | 10200 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 | 1 |  |  | 0 |  | 2016 | good |  | Antenna, telus 13, pcs, pcs, installation year assumed to be 2016 |  |  |  | 00009236 | Newmarket Northeast Elevated Tank | [7 empty] | Area 2N Linear Water & Wells | W - Storage Elevated Tank | Antenna |  |  |  | OPERATING |  |  |  |  | 0 | (208) | Newmarket NE ET Capital Project 2 |  | W-WW | 2020 | 0
SIC | 00025199 | 4482 | NNE | 11 | Antenna Telus 2 | 10200 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 | 1 |  |  | 0 |  | 2016 | good |  | Antenna, telus 2, cellular , cellular, installation year assumed to be 2016 |  |  |  | 00009236 | Newmarket Northeast Elevated Tank | [7 empty] | Area 2N Linear Water & Wells | W - Storage Elevated Tank | Antenna |  |  |  | OPERATING |  |  |  |  | 0 | (369) | Newmarket NE ET Capital Project 2 |  | W-WW | 2020 | 0
SIC | 00025200 | 4483 | NNE | 11 | Antenna Telus 3 | 10200 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 | 1 |  |  | 0 |  | 2016 | good |  | Antenna, telus 3, cellular , cellular, installation year assumed to be 2016 |  |  |  | 00009236 | Newmarket Northeast Elevated Tank | [7 empty] | Area 2N Linear Water & Wells | W - Storage Elevated Tank | Antenna |  |  |  | OPERATING |  |  |  |  | 0 | (369) | Newmarket NE ET Capital Project 2 |  | W-WW | 2020 | 0
SIC | 00025205 | 4488 | NNE | 11 | Antenna Telus 4 | 10200 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 | 1 |  |  | 0 |  | 2016 | good |  | Antenna, telus 4, cellular , cellular, installation year assumed to be 2016 |  |  |  | 00009236 | Newmarket Northeast Elevated Tank | [7 empty] | Area 2N Linear Water & Wells | W - Storage Elevated Tank | Antenna |  |  |  | OPERATING |  |  |  |  | 0 | (371) | Newmarket NE ET Capital Project 2 |  | W-WW | 2020 | 0
SIC | 00025206 | 4489 | NNE | 11 | Antenna Telus 5 | 10200 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 | 1 |  |  | 0 |  | 2016 | good |  | Antenna, telus 5, cellular , cellular, installation year assumed to be 2016 |  |  |  | 00009236 | Newmarket Northeast Elevated Tank | [7 empty] | Area 2N Linear Water & Wells | W - Storage Elevated Tank | Antenna |  |  |  | OPERATING |  |  |  |  | 0 | (371) | Newmarket NE ET Capital Project 2 |  | W-WW | 2020 | 0
SIC | 00025207 | 4490 | NNE | 11 | Antenna Telus 6 | 10200 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 | 1 |  |  | 0 |  | 2016 | good |  | Antenna, telus 6, cellular , cellular, installation year assumed to be 2016 |  |  |  | 00009236 | Newmarket Northeast Elevated Tank | [7 empty] | Area 2N Linear Water & Wells | W - Storage Elevated Tank | Antenna |  |  |  | OPERATING |  |  |  |  | 0 | (208) | Newmarket NE ET Capital Project 2 |  | W-WW | 2020 | 0
SIC | 00025192 | 4479 | NNE | 11 | Antenna Telus 7 | 10200 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 | 1 |  |  | 0 |  | 2016 | good |  | Antenna, telus 7, wireless, microwave dish, installation year assumed to be 2016 |  |  |  | 00009236 | Newmarket Northeast Elevated Tank | [7 empty] | Area 2N Linear Water & Wells | W - Storage Elevated Tank | Antenna |  |  |  | OPERATING |  |  |  |  | 0 | (368) | Newmarket NE ET Capital Project 2 |  | W-WW | 2020 | 0
SIC | 00025202 | 4485 | NNE | 11 | Antenna Telus 8 | 10200 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 | 1 |  |  | 0 |  | 2016 | good |  | Antenna, telus 8, pcs, pcs, installation year assumed to be 2016 |  |  |  | 00009236 | Newmarket Northeast Elevated Tank | [7 empty] | Area 2N Linear Water & Wells | W - Storage Elevated Tank | Antenna |  |  |  | OPERATING |  |  |  |  | 0 | (370) | Newmarket NE ET Capital Project 2 |  | W-WW | 2020 | 0
SIC | 00025204 | 4487 | NNE | 11 | Antenna Telus 9 | 10200 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 | 1 |  |  | 0 |  | 2016 | good |  | Antenna, telus 9, pcs, pcs, installation year assumed to be 2016 |  |  |  | 00009236 | Newmarket Northeast Elevated Tank | [7 empty] | Area 2N Linear Water & Wells | W - Storage Elevated Tank | Antenna |  |  |  | OPERATING |  |  |  |  | 0 | (371) | Newmarket NE ET Capital Project 2 |  | W-WW | 2020 | 0
SIC | 00025209 | 4492 | NNE | 11 | Antenna York Region 14 | 10200 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 | 1 |  |  | 0 |  | 2016 | good |  | Antenna, york region 14, traffic, 4-bay dipole |  |  |  | 00009236 | Newmarket Northeast Elevated Tank | [7 empty] | Area 2N Linear Water & Wells | W - Storage Elevated Tank | Antenna |  |  |  | OPERATING |  |  |  |  | 0 | (218) | Newmarket NE ET Capital Project 2 |  | W-WW | 2020 | 0
SC |  | 4831 | NNE | 22 | Elevated Tank Access Tube Bottom Bolted Manhole | 10200 | 3 | The asset was observed to be in fair condition. Elevated tank access tube bottom bolted manhole to be replaced at the end of remaining service life. | 0 | 3 |  |  | 0 |  | 1972 | surface corrosion | [5 empty] | 00017328 | [15 empty] | Surface corrosion was observed. |  |  |  | 0 | (349) |  |  |  | 0 | 0
SIC | 00084315 | 4518 | NNE | 4 | Elevated Tank Inlet/Outlet Header Flow Transmitter | 10200 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the short term. | 0 | 3 |  |  | 0 |  | 2002 | Minor corrosion on flow sensors installed in the valve chamber. |  | Flow meter, endress+hauser, prosonic flow 93, l308f416000 |  |  |  | 00017331 | [15 empty] | Minor corrosion was observed on flow sensors installed in the valve chamber. |  |  |  | 0 | IMG_2759 | Newmarket NE ET Capital Project 1 |  |  | 0 | 0
SW |  | 4503 | NNE | 6 | Guard Rail | 10200 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 | 1 |  |  | 0 |  | 1972 | Several sections were rusted. |  | Guard rail along driveway, approximately 62 meters long |  |  |  | 00009236 | [15 empty] | Several sections were rusted | Portion of guard rail was leaning to the west. |  |  | 0 | IMG_20200401_100341 | Newmarket NE ET Capital Project 1 |  |  | 0 | 0 | Portion of guard rail was leaning to the west.
SC | 00014426 | 4539 | NNE | 42 | Wellhouse 14 Concrete Blockwall | 10200 | 3 | The asset was observed to be in fair condition. The wellhouse is currently being decommissioned, replacement and/or rehabilitation of the asset are no longer required, and they are not included in the capital project. |  | 4 |  |  | 0 |  | 2002 | covered by metal cladding |  | Ammonia room expansion |  |  |  | 0000000 | [15 empty] | The wall was covered by metal cladding, therefore the condition was assumed to be fair. |  |  |  | 0 | IMG_20200401_102224 |  |  |  | 0 | 0 | fair
SC |  | 4543 | NNE | 42 | Wellhouse 14 Concrete Strip Footing | 10200 | 2 | The asset was observed to be in good condition. The wellhouse is currently being decommissioned, replacement and/or rehabilitation of the asset are no longer required, and they are not included in the capital project. |  | 3 |  |  | 0 |  | 2002 | fair |  | Ammonia room expansion |  |  |  | 00017331 | [19 empty] | 0 | IMG_1713 |  |  |  | 0 | 0
SC |  | 4560 | NNE | 22 | Wellhouse 14 Roof | 10200 | 3 | The asset was observed to be in fair condition based on age. The wellhouse is currently being decommissioned, replacement and/or rehabilitation of the asset are no longer required, and they are not included in the capital project. | 0 | 3 |  |  | 0 |  | 1972 | covered by insulation |  | Original construction |  |  |  | 00017330 | [15 empty] | The roof was covered by insulation. |  |  |  | 0 | (93) |  |  |  | 0 | 0
SW |  | 4499 | NNE | 25 | Wellhouse No.14 Overflow System | 10200 | 3 | The asset was observed to be in fair condition. The wellhouse is currently being decommissioned, replacement and/or rehabilitation of the asset are no longer required, and they are not included in the capital project. |  | 2 |  |  | 0 |  | 1972 | Concrete pad is in good condition. |  | W14 overflow system located on west side of building including concrete pad and crushed concrete |  |  |  | 00009236 | [15 empty] | Crushed concrete and cement found at end of concrete pad. They appeared to be acting as rip rap to reduce erosion. |  |  | Remove crushed concrete and cement. Regrade area and place rip rap. | 3000 | IMG_20200401_094548 |  |  |  | 0 | 0 | Crushed concrete and cement found at end of concrete pad. Appears to be acting as rip rap to reduce erosion.
SW | 00032814 | 4494 | NNE | 12 | Fire Hydrant | 8200 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 | 2 |  |  | 0 |  | 1972 | Operability of the fire hydrant was unknown. |  | Fire hydrant at driveway |  |  |  | 00009236 | Newmarket Northeast Elevated Tank | M00100 | [6 empty] | Area 2N Linear Water & Wells | W - Storage Elevated Tank | Siteworks |  |  |  | OPERATING | Operability of the fire hydrant is unknown. | Large portions of fire hydrant have rusted. |  |  | 0 | IMG_20200401_100829 | Newmarket NE ET Capital Project 2 |  | W-WW | 2020 | 0 | Large portions of fire hydrant had rusted.
SW | 00014410 | 4466 | NNE | 15 | Front Entrance Double Gates | 7700 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 | 1 |  |  | 0 |  | 1972 | Good |  | Double gates at entrance |  |  |  | 00017331 | Newmarket NE ET Valve Room | [7 empty] | Area 2N Linear Water & Wells |  | Siteworks |  |  |  | OPERATING |  |  |  |  | 0 | IMG_20200401_094004 | Newmarket NE ET Capital Project 2 |  | W-WW | 2020 | 0
ES | 00007186 | 4465 | NNE | 6 | Distribution Panel | 7400 | 3 | The asset was observed to be in fair condition based on its age. Asset to be replaced in the short term. | 0 | 3 |  |  | 0 |  | 1972 | good |  | 24 circuit, panelboard; square d; ; n000424l100; 240v, 100a, 3ph; |  |  |  |  | Newmarket NE ET Valve Room | M00059 | [6 empty] | Area 2N Linear Water & Wells |  | Electrical System |  |  |  | OPERATING |  |  |  |  | 0 | IMG_2103 | Newmarket NE ET Capital Project 1 |  | W-WW | 2020 | 0
SIC | 00028450 | 4517 | NNE | 4 | Elevated Tank Inlet/Outlet Header Chlorine Analyzer | 7200 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the short term. | 0 | 3 |  |  | 0 |  | 2002 | obsolete |  | Influent free chlorine analyzer, hach, cl2, cl17, 020600005220 |  |  |  | 00017331 | [15 empty] | The asset is obsolete. | The analyzer was not in operation at the time of the inspection. |  |  | 0 | IMG_2738 | Newmarket NE ET Capital Project 1 |  |  | 0 | 0 | The analyzer was not in operation at the time of the inspection.
AC |  | 4554 | NNE | 6 | Wellhouse 14 Chlorine and Well House Roofing | 7200 | 3 | The asset was observed to be in fair condition based on its age. The wellhouse is currently being decommissioned, replacement and/or rehabilitation of the asset are no longer required, and they are not included in the capital project. | 0 | 1 |  |  | 0 |  | 1972 | fair |  | Original construction |  |  |  | 00017331 | [19 empty] | 0 | IMG_20200401_102449 |  |  |  | 0 | 0
AC |  | 4552 | NNE | 6 | Wellhouse 14 Metal Cladding | 7200 | 3 | The asset was observed to be in fair condition based on its age. The wellhouse is currently being decommissioned, replacement and/or rehabilitation of the asset are no longer required, and they are not included in the capital project. | 0 | 1 |  |  | 0 |  | 2002 | fair |  | Ammonia |  |  |  | 00017331 | [19 empty] | 0 | IMG_20200401_102516 |  |  |  | 0 | 0
PM |  | 4824 | NNE | 12 | Elevated Tank Frostproof Vent/Vacuum | 6200 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 | 3 |  |  | 0 |  | 2002 | minor surface corrosion |  | 16'' stainless steel forst proof, installation year assumed to be 2002 |  |  |  | 00009236 | [15 empty] | Minor surface corrosion was observed. |  |  |  | 0 | (278) | Newmarket NE ET Capital Project 2 |  |  | 0 | 0
SIC | 00084312 | 4512 | NNE | 11 | OIT Control Panel | 6200 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 | 2 |  |  | 0 |  | 2016 | good |  | Installation year assumed to be 2016 |  |  |  | 00017331 | [19 empty] | 0 | IMG_2683 | Newmarket NE ET Capital Project 2 |  |  | 0 | 0
AC |  | 4551 | NNE | 6 | Wellhouse 14 Ammonia Room Access Door (Double) | 5700 | 3 | The asset was observed to be in fair condition. The wellhouse is currently being decommissioned, replacement and/or rehabilitation of the asset are no longer required, and they are not included in the capital project. | 0 | 1 |  |  | 0 |  | 2002 | Weathered paint | [5 empty] | 00000000 | [15 empty] | Weathered paint was observed. |  |  |  | 0 | IMG_20200401_102338 |  |  |  | 0 | 0
AC |  | 4549 | NNE | 6 | Wellhouse 14 Well Pump Room Access Door (Double) | 5700 | 3 | The asset was observed to be in fair condition. The wellhouse is currently being decommissioned, replacement and/or rehabilitation of the asset are no longer required, and they are not included in the capital project. | 0 | 1 |  |  | 0 |  | 1972 | weathered paint |  | Original construction |  |  |  | 00000000 | [15 empty] | Weathered paint was observed. |  |  |  | 0 | IMG_20200401_102338 |  |  |  | 0 | 0
PM | 00004565 | 4461 | NNE | 11 | Elevated Tank Bypass Line Gate Valve | 5100 | 3 | The asset was observed to be in fair condition based on its age. The valve was well maintained. Asset to be replaced in the intermediate term. | 0 | 4 |  |  | 0 |  | 1972 | good |  | Bypass, valve, gate; 300 dia, nrs, by darling, valve repainted in 2016 |  |  |  | 00017331 | Newmarket NE ET Valve Room | [7 empty] | Area 2N Linear Water & Wells |  | Process Mechanical |  |  |  | OPERATING |  |  |  |  | 0 | IMG_1746 | Newmarket NE ET Capital Project 2 |  | W-WW | 2020 | 0 | well maintained
PM | 00004563 | 4459 | NNE | 11 | Elevated Tank Inlet/Outlet Header Gate Valve 1 | 5100 | 2 | The asset was observed to be in fair condition. The valve was well maintained. Asset to be replaced in the long term. | 0 | 4 |  |  | 0 |  | 1972 | Good |  | Main line, 300 dia valve, gate, manual, nrs, by darling, valve repainted in 2016 |  |  |  | 00017331 | Newmarket NE ET Valve Room | [7 empty] | Area 2N Linear Water & Wells |  | Process Mechanical |  |  |  | OPERATING | Minor surface corrosion was observed. |  |  |  | 0 | IMG_1731 | Newmarket NE ET Capital Project 2 |  | W-WW | 2020 | 0 | well maintained
PM | 00004564 | 4460 | NNE | 11 | Elevated Tank Inlet/Outlet Header Gate Valve 2 | 5100 | 3 | The asset was observed to be in fair condition based on its age. The valve was well maintained. Asset to be replaced in the long term. | 0 | 4 |  |  | 0 |  | 1972 | good |  | Main line, 300 dia valve, gate, manual, nrs, by darling, valve repainted in 2016 |  |  |  | 00017331 | Newmarket NE ET Valve Room | [7 empty] | Area 2N Linear Water & Wells |  | Process Mechanical |  |  |  | OPERATING |  |  |  |  | 0 | IMG_1753 | Newmarket NE ET Capital Project 2 |  | W-WW | 2020 | 0 | well maintained
PM | 00004564 | 4816 | NNE | 11 | Elevated Tank Inlet/Outlet Header Gate Valve 3 | 5100 | 3 | The asset was assumed to be in fair condition based on its age. Asset to be replaced in the long term. | 0 | 4 |  |  | 0 |  | 1972 |  |  | Main line, 300 dia valve, gate, manual, underground |  |  |  | 00017331 | [19 empty] | 0 |  | Newmarket NE ET Capital Project 2 |  |  | 0 | 0
ES |  | 4813 | NNE | 21 | Elevated Tank Obstruction Light Controller | 5100 | 2 | The asset was observed to be in good condition. The obsturction light is not required at the elevated tank based on NAV Canada. Remove the asset at the end of its service life. | 2000 | 3 | 2039 |  | 0 |  | 2012 | good | Newmarket NE ET Capital Project 2 |  |  |  |  | 00009236 | [19 empty] | 0 | IMG_2104 |  |  |  | 0 | 0
SC |  | 4835 | NNE | 56 | Elevated Tank Roof Access Hatch 1 | 5100 | 2 | The asset was observed to be in good condition. Elevated tank roof access hatch 1 to be replaced at the end of remaining service life. | 0 | 2 |  |  | 0 |  | 2016 | good |  | 30'' x 30'' aluminum hatch |  |  |  | 00017328 | [19 empty] | 0 | (299) |  |  |  | 0 | 0
SC |  | 4836 | NNE | 56 | Elevated Tank Roof Access Hatch 2 | 5100 | 2 | The asset was observed to be in good condition. Elevated tank roof access hatch 2 to be replaced at the end of remaining service life. | 0 | 2 |  |  | 0 |  | 2016 | good |  | Aluminum hatch with carbon steel mounting curb |  |  |  | 00017328 | [19 empty] | 0 | (301) |  |  |  | 0 | 0
SC |  | 4545 | NNE | 22 | Wellhouse 14 Concrete Floor Slab | 5100 | 3 | The asset was observed to be in fair condition based on its age. The wellhouse is currently being decommissioned, replacement and/or rehabilitation of the asset are no longer required, and they are not included in the capital project. |  | 3 |  |  | 0 |  | 1972 | fair |  | Original construction |  |  |  | 00017331 | [19 empty] | 0 | IMG_2827 |  |  |  | 0 | 0
SC |  | 4874 | NNE | 25 | Elevated Tank Wet Riser Internal Ladder Grab Rail | 5000 | 4 | The asset was observed to be in poor condition. Weld repair grab bar is recommended immediately. Replace the asset at the end of the remaining service life. | 2000 | 3 | 2020 |  | 0 | 0 | 1972 |  | Newmarket NE ET Capital Project 1 |  |  |  |  | 00009236 | [15 empty] | The grab rail was observed to be broken. |  |  |  | 0 | (203) |  |  |  | 0 | 0
SW |  | 4498 | NNE | 6 | Bollards | 4100 | 4 | The asset was observed to be in poor condition. Asset to be replaced in the intermediate term. | 0 | 2 |  |  | 0 |  | 1972 | The bollards were in poor condition as they were bended. |  | Two bollards adjacent to fire hydrant |  |  |  | 00009236 | [15 empty] | Bollards are bent. |  |  |  | 0 | IMG_20200401_100829 | Newmarket NE ET Capital Project 1 |  |  | 0 | 0
SC | 00014426 | 4475 | NNE | 42 | Wellhouse 14 Precast Roof Slab | 4100 | 3 | The asset was observed to be in fair condition. The wellhouse is currently being decommissioned, replacement and/or rehabilitation of the asset are no longer required, and they are not included in the capital project. | 0 | 3 |  |  | 0 |  | 2002 | fair |  | Ammonia room expansion |  |  |  | 00017331 | Newmarket NE ET Valve Room | [7 empty] | Area 2N Linear Water & Wells |  | Architectural |  |  |  | OPERATING |  |  |  |  | 0 | img_2077 |  |  | W-WW | 2020 | 0
ES |  | 4565 | NNE | 21 | Elevated Tank Obstruction Light | 4000 | 3 | The asset was observed to be in fair condition. York Region determined that the tank does not require obstruction lights according to NAV Canada. The lights to be removed at the end of their service life. | 2000 | 3 | 2039 |  | 0 |  | 2020 | one of the light was not working at the time of the inspection. | Newmarket NE ET Capital Project 2 | Dual head lights with control |  |  |  | 00017330 | [15 empty] | One of the light was not working at the time of the inspection. |  |  |  | 0 | (281) |  |  |  | 0 | 0
BM |  | 4497 | NNE | 25 | Valve House Sump Drain Line | 4000 | 3 | The asset was observed to be in fair condition. Inspection, flushing and cleaning of the pipe is recommended in the short term. The Region can install a sump pump in the sump pit in the long term if the drain line is frequently used. | 2000 | 2 | 2024 |  | 0 |  | 1972 | The sump pit had water at the time of the inspection, which indicated that the drain pipe was plugged. | Newmarket NE ET Capital Project 1 | Sump drain line connects the sump pit to the sanitary sewer, size unknown |  |  |  | 00017331 | [15 empty] | The sump pit had water at the time of the inspection, which indicated that the drain pipe was plugged. |  |  |  | 0 | IMG_1826 | Newmarket NE ET Capital Project 2 |  |  | 0 | 0 | If drain doesn't work after cleaning, a sump pump shall be installed. | Poor
AC |  | 4556 | NNE | 6 | Valve House Access Door (Single) | 3600 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 | 1 |  |  | 0 |  | 2002 | minor corrosion | [5 empty] | 00017331 | [15 empty] | Minor corrosion was observed. |  |  |  | 0 | IMG_20200401_101344 | Newmarket NE ET Capital Project 1 |  |  | 0 | 0
AC |  | 4550 | NNE | 6 | Wellhouse 14 Chlorine Room Access Door (Single) | 3600 | 3 | The asset was observed to be in fair condition. The wellhouse is currently being decommissioned, replacement and/or rehabilitation of the asset are no longer required, and they are not included in the capital project. | 0 | 1 |  |  | 0 |  | 1972 | Weathered paint |  | Original construction |  |  |  | 00000000 | [15 empty] | Weathered paint was observed. | Missing toe kick plate. |  |  | 0 | IMG_20200401_102139 |  |  |  | 0 | 0 | Missing toe kick plate
HSS |  | 4840 | NNE | 56 | Elevated Tank Catwalk Rescue Port Base | 3100 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 | 4 |  |  | 0 |  | 2016 | good | [5 empty] | 00009236 | [19 empty] | 0 | (307) |  |  |  | 0 | 0
PM | 00017010 | 4477 | NNE | 28 | Elevated Tank Drain Line Gate Valve | 3100 | 2 | The asset was observed to be in good condition. Elevated tank drain line gate valve to be replaced at the end of remaining service life. | 0 | 2 |  |  | 0 |  | 2018 | good |  | Drain, valve, gate; 200 dia, nrs, by avk |  |  |  | 00017331 | Newmarket NE ET Valve Room | [7 empty] | Area 2N Linear Water & Wells |  | Process Mechanical |  |  |  | OPERATING |  |  |  |  | 0 | IMG_1787 |  |  | W-WW | 2020 | 0
HSS |  | 4839 | NNE | 56 | Elevated Tank Tank Roof Rescue Port Base | 3100 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 | 4 |  |  | 0 |  | 2016 | Minor corrosion | [5 empty] | 00009236 | [15 empty] | Minor corrosion was observed. |  |  |  | 0 | (300) |  |  |  | 0 | 0
BM | 00024567 | 4463 | NNE | 9 | Valve House Exhaust Fan | 3100 | 4 | The asset was observed to be in poor condition. Asset to be replaced in the long term. | 0 | 1 |  |  | 0 |  | 2002 | good |  | Shed area, ventilation system, exhaust fan |  |  |  | 00009236 | Newmarket Northeast Elevated Tank | M00597 | [6 empty] | Area 2N Linear Water & Wells | W - Storage Elevated Tank | Building Mechanical |  |  |  | OPERATING | The valve house exhaust fan was unable to operate as a garbage bag was used to plug the empty gap within the backdraft damper. |  |  |  | 0 | IMG_1707 | Newmarket NE ET Capital Project 1 |  | W-WW | 2020 | 0
AC |  | 4555 | NNE | 6 | Wellhouse 14 Ammonia Room Roofing | 3100 | 3 | The asset was observed to be in fair condition based on its age. The wellhouse is currently being decommissioned, replacement and/or rehabilitation of the asset are no longer required, and they are not included in the capital project. | 0 | 1 |  |  | 0 |  | 2002 | fair |  | Ammonia |  |  |  | 00017331 | [19 empty] | 0 | IMG_20200401_102400 |  |  |  | 0 | 0
SC | 00014422 | 4474 | NNE | 42 | Wellhouse 14 Concrete Floor Slab | 3100 | 2 | The asset was observed to be in good condition. The wellhouse is currently being decommissioned, replacement and/or rehabilitation of the asset are no longer required, and they are not included in the capital project. |  | 3 |  |  | 0 |  | 2002 | good |  | Concrete pad under enclosure/housing for, other structural component, ammonia room expansion |  |  |  | 00017331 | Newmarket NE ET Valve Room | [7 empty] | Area 2N Linear Water & Wells |  | Structural |  |  |  | OPERATING |  |  |  |  | 0 | IMG_20200401_102400 |  |  | W-WW | 2020 | 0
SC |  | 4546 | NNE | 22 | Wellhouse 14 Roof Hatch | 3100 | 3 | The asset was observed to be in fair condition based on its age. The wellhouse is currently being decommissioned, replacement and/or rehabilitation of the asset are no longer required, and they are not included in the capital project. | 0 | 2 |  |  | 0 |  | 1972 | fair |  | Original construction |  |  |  | 00017331 | [19 empty] | 0 | MVIMG_20200401_102308 |  |  |  | 0 | 0
SIC | 00028453 | 4493 | NNE | 4 | Elevated Tank Level Transmitter | 2600 | 3 | The asset was observed to be in fair condition based on its age. Asset to be replaced in the short term. | 0 | 3 |  |  | 0 |  | 1972 | good |  | P914lit101, elevated tank, pressure transmitter, level |  |  |  | 00017331 | Newmarket NE ET Valve Room | M00816 | 250815B-220-212-000-000 |  |  | Level |  |  | Area 2N Linear Water & Wells |  | Instrumentation and Control | 95A-08362 |  |  | OPERATING |  |  |  |  | 0 | (107) | Newmarket NE ET Capital Project 1 |  | W-WW | 2020 | 0
ES | 00007182 | 4561 | NNE | 6 | Splitters | 2100 | 2 | The asset was observed to be in fair condition based on its age. Asset to be replaced in the short term. | 0 | 4 |  |  | 0 |  | 1972 | good |  | Splitter; union switch box co. ltd.; ;48125; 125a, 250/575v | [19 empty] | Missing arch flash label. |  |  |  | 0 | IMG_2099 | Newmarket NE ET Capital Project 1 |  |  | 0 | 0
BM | 00024496 | 4462 | NNE | 4 | Valve Chamber Baseboard Electrical Heater | 2000 | 4 | The asset was observed to be in poor condition. A fan-forced, wall-mounted heater is recommended to be installed. Asset to be replaced in the intermediate term. | 0 | 2 |  |  | 0 |  | 1972 | Moderate to severe corrosion due to atmospheric conditions |  | Heating system, baseboard convection heater |  |  |  | 00017331 | Newmarket NE ET Valve Room | M00037 | [6 empty] | Area 2N Linear Water & Wells |  | Building Mechanical |  |  |  | OPERATING | Moderate to severe corrosion due to atmospheric conditions was observed. |  |  |  | 0 | IMG_1762 | Newmarket NE ET Capital Project 1 |  | W-WW | 2020 | 0
ES | 00007178 | 4563 | NNE | 6 | Main Disconnect Switch | 1900 | 2 | The asset was observed to be in fair condition based on its age. Asset to be replaced in the short term. | 0 | 3 |  |  | 0 |  | 1972 | good |  | Main disconnect switch; federal pioneer; 200a, 600v | [19 empty] | Missing arch flash label. |  |  |  | 0 | IMG_2083 | Newmarket NE ET Capital Project 1 |  |  | 0 | 0
ES | 00007177 | 4562 | NNE | 6 | Breaker | 1800 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the short term. | 0 | 4 |  |  | 0 |  | 1972 | minor surface corrosion |  | Breaker; square d; ;fa 100-s; 100a, 600v | [19 empty] | Minor surface corrosion was observed. |  |  |  | 0 | IMG_2097 | Newmarket NE ET Capital Project 1 |  |  | 0 | 0
ES |  | 4566 | NNE | 6 | Valve House Lighting Fixtures | 1700 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 | 2 |  |  | 0 |  | 2002 | good |  | Two (2) fluorescent lights |  |  |  | 00017331 | [19 empty] | 0 | IMG_2111 | Newmarket NE ET Capital Project 1 |  |  | 0 | 0
SIC |  | 4837 | NNE | 0 | Valve Chamber Float | 1600 | 5 | The asset was observed to be in very poor condition. The asset to be reinstalled in the short term. | 0 | 2 |  |  | 0 |  | 1972 | The asset appeared to be missing. The wire for float was still in the valve chamber. | [5 empty] | 00017331 | [15 empty] | The asset appeared to be missing. The wire for float was still in the valve chamber. |  |  |  | 0 | IMG_1778 | Newmarket NE ET Capital Project 1 |  |  | 0 | 0
SC | 00014416 | 4470 | NNE | 22 | Valve House Aluminum Hatch | 1600 | 2 | The asset was observed to be in good condition. Installation of grab bars for safe access of the chamber and installation of removeable guardrails to protect workers from falls when the chamber hatch is opened are recommended. Valve house aluminum hatch t | 2000 | 2 | 2024 |  | 0 |  | 1972 | Good | Newmarket NE ET Capital Project 1 | Aluminum hatch |  |  |  | 00017331 | Newmarket NE ET Valve Room | [7 empty] | Area 2N Linear Water & Wells |  | Structural |  |  |  | OPERATING |  |  |  |  | 0 | IMG_20200401_101254 |  |  | W-WW | 2020 | 0
BM |  | 4496 | NNE | 11 | Valve Chamber Dehumidifier | 1100 | 3 | The asset was observed to be in fair condition. Relocate Valve house dehumidifier to be replaced at the end of remaining service life. | 0 | 1 |  |  | 0 |  | 2016 | no drain tubing to sump |  | Valve chamber dehumidifier |  |  |  | 00017331 | [15 empty] | No drain tubing to sump was observed. | The existing receptacle for the dehumidifier was corroded due to moist environment. |  |  | 0 | IMG_1827 |  |  |  | 0 | 0
SC | 00014417 | 4471 | NNE | 6 | Valve Chamber Ladder Rungs | 1100 | 3 | The asset was observed to be in fair condition based on its age. Valve chamber ladder rungs to be replaced at the end of remaining service life. | 0 | 3 |  |  | 0 |  | 1972 | fair |  | Steel bar step iron ladder, ladder, |  |  |  | 00017331 | Newmarket NE ET Valve Room | [7 empty] | Area 2N Linear Water & Wells |  | Structural |  |  |  | OPERATING | Rungs were observed to be too narrow. |  |  |  | 0 | IMG_20200401_101302 | Newmarket NE ET Capital Project 1 |  | W-WW | 2020 | 0
AC | 00014427 | 4476 | NNE | 6 | Valve House Interior Wood Paneling | 1100 | 3 | The asset was observed to be in fair condition based on its age. Asset to be replaced in the intermediate term. | 0 | 1 |  |  | 0 |  | 2002 | fair |  | Enclosure/housing interior timber liner , interior finish |  |  |  | 00017331 | Newmarket NE ET Valve Room | [7 empty] | Area 2N Linear Water & Wells |  | Architectural |  |  |  | OPERATING |  |  |  |  | 0 | IMG_20200401_101327 | Newmarket NE ET Capital Project 1 |  | W-WW | 2020 | 0
AC |  | 4557 | NNE | 6 | Wellhouse 14 Window | 1100 | 3 | The asset was observed to be in fair condition. The wellhouse is currently being decommissioned, replacement and/or rehabilitation of the asset are no longer required, and they are not included in the capital project. | 0 | 1 |  |  | 0 |  | 1972 | fair |  | Original construction |  |  |  | 00000000 | [15 empty] | Surface corrosion was observed on window frame. |  |  |  | 0 | IMG_20200401_102214 |  |  |  | 0 | 0
ES |  | 4812 | NNE | 4 | Valve Chamber Lighting Fixture | 600 | 5 | The asset was observed to be in very poor condition. Asset to be replaced in the short term. | 0 | 2 |  |  | 0 |  | 1972 | Dusty |  | One (1) lighting fixture |  |  |  | 00017331 | [15 empty] | The lighting fixture was not working. |  |  |  | 0 | IMG_1798 | Newmarket NE ET Capital Project 1 |  |  | 0 | 0 | not working
BM | 00024567 | 4567 | NNE | 6 | Valve House Backdraft Damper | 600 | 5 | The asset was observed to be in very poor condition. Asset to be replaced in 1 - 5 years | 0 | 1 |  |  | 0 |  | 2006 | Broken |  | Backdraft damper, size: unknown |  |  |  | 00009236 | [15 empty] | The asset was broken. |  |  |  | 0 | IMG_1694 | Newmarket NE ET Capital Project 1 |  |  | 0 | 0
BM |  | 4478 | NNE | 9 | Valve House Door Ventilation Louver | 600 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 | 1 |  |  | 0 |  | 2002 | good |  | Shed door louver |  |  |  | 00017331 | Newmarket NE ET Valve Room | M00111 | [6 empty] | Area 2N Linear Water & Wells |  | Building Mechanical |  |  |  | OPERATING | The ventilation louver was isolated by a cardboard from the inside of the door. |  |  |  | 0 | IMG_1701 | Newmarket NE ET Capital Project 1 |  | W-WW | 2020 | 0 | louver was isolated at the interior
BM |  | 4810 | NNE | 6 | Valve House Abandoned Sampling Line | 300 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 | 1 |  |  | 0 |  | 1972 | Abandoned. |  | Sampling line drains to sump pit in the valve chamber |  |  |  | 00017331 | [19 empty] | 0 | IMG_1736 | Newmarket NE ET Capital Project 1 |  |  | 0 | 0
HSS |  | 4815 | NNE | 6 | Chemical Spill Kit | 200 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 | 2 |  |  | 0 |  | 2016 | good | [5 empty] | 00017331 | [19 empty] | 0 | IMG_0956 | Newmarket NE ET Capital Project 1 |  |  | 0 | 0
HSS |  | 4814 | NNE | 6 | Fire Extinguisher | 200 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 | 1 |  |  | 0 |  | 2019 | good |  | Total of 1. |  |  |  | 00017331 | [19 empty] | 0 | IMG_9055 | Newmarket NE ET Capital Project 1 |  |  | 0 | 0
BM |  | 4811 | NNE | 4 | Valve House Portable Tower Heater | 200 | 2 | The asset was observed to be in good condition. Valve house tower heater to be replaced at the end of remaining service life. | 0 | 2 |  |  | 0 |  | 2002 | good |  | Portable tower heater, installation year assumed to be 2002 |  |  |  | 00017331 | [19 empty] | 0 | IMG_0000 | Newmarket NE ET Capital Project 1 |  |  | 0 | 0