## Sheet1
assetTag | seqNum | facility | assetName | Description | Process | building | inspectorName | LocationTag | LocationORIGINAL | CategoryCode | manufacturer | TransmitterModel | TransducerModel | TransducerSerial | InstMeva | installYear | installationDate | remainingESL | InstType | ServiceArea | FacilityType | LifeCycleCategory | SerialNo | Parent | RotatingItem | Site | condition | COF | defect1 | defect2 | defect3 | observations | RehabRepairCost | RehabRepairYear | RehabRepairCost2 | RehabRepairYear2 | repCost | photoName | repProjectName | rehabProjectName | rehab2ProjectName | Status | InspectionYear | rehabComment1 | rehabCost1 | rehabComment2 | rehabCost2 | defect1Input | defect2Input | defect3Input
| 5094 | S | Elevated Tank Steel Tank |  |  |  |  | 790900008 |  | SC | [5 empty] | 1984 |  | 22 | [8 empty] | 3 | 5 | The seams on the roof noted to be not welded. Severe surface corrosion to stiffeners and painters' rails were noted. | Minor to moderate pitting was observed throughout inside of the elevated tank. |  | The asset was observed to be in fair condition. It is recommended to supply and install drip rings at the cone to shell interface. Seal the weld roof plate radial seams. Repair pitting on the tank interior. | 100000 | 2025 | 0 |  | 1300000 | IMG_3889 |  | Sutton ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
| 5093 | S | Elevated Tank Concrete Structure |  |  |  |  | 790900008 |  | SC | [5 empty] | 1984 |  | 22 | [8 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 50000 | 2030 | 0 |  | 900000 | IMG_3845 |  | Sutton ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
| 5095 | S | Elevated Tank Exterior Coating |  |  |  |  | 790900008 |  | SCS | [5 empty] | 1984 |  | 12 | [8 empty] | 4 | 3 | Paint blistering and flakings were noted. | Minor surface corrosion was observed. | The Region reported that the exterior coating has a low-level lead detected. | The asset was observed to be in fair condition. Pressure wash and exterior overcoating with fluorourethane in the short term to extend the service life of the exterior coating. | 155000 | 2024 | 0 |  | 600000 | IMG_3864 | Sutton ET Capital Project 2 | Sutton ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | fair
| 5096 | S | Elevated Tank Interior Coating |  |  |  |  | 790900008 |  | SCS | [5 empty] | 1984 |  | 3 | [8 empty] | 4 | 3 | Corrosion was observed throughout above the water line. Pitting corrosion was observed below the water line. | Significant lining corrosion was noted at the irregular surfaces such as edges and welds. |  | The asset was observed to be in fair to poor condition. It is recommended to conduct interior lining removal and replacement in the short term. |  |  | 0 |  | 450000 | IMG_3889 | Sutton ET Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | poor
| 4943 | S | 300mm Watermain | 125m of 300mm watermain. Material unknown |  |  |  | 790900008 |  | SW | [5 empty] | 1984 |  | 24 | [8 empty] | 3 | 5 |  |  |  | The asset was assumed to be in fair condition. The operation reported that maintenance group replaced water service connection and the water distribution line isolation valves to not hold in the valve room. | 0 |  | 0 |  | 137000 | IMG_20201029_093855 |  |  |  |  | 0 |  | 0 |  | 0
| 4944 | S | 375mm Storm Sewer | 375mm storm sewer (tank drain/overflow), concrete pipe, approx. length is 120m |  |  |  | 790900008 |  | SW | [5 empty] | 1984 |  | 24 | [8 empty] | 3 | 3 |  |  |  | The asset was assumed to be in fair condition. | 0 |  | 0 |  | 120000 | [5 empty] | 0 |  | 0 |  | 0
00083320 | 4937 | S | Elevated Tank SUETDR Control Panel | PAC control panel, installation year assumed to be 2017 |  |  |  | 00016062 | Sutton ET Tank Base | SIC | M00844 |  |  |  |  | 2017 |  | 12 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control | 14E-088/SUETDR_PAC |  |  | W-WW | 2 | 4 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 80000 | PXL_20201029_134934038 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  | 0 |  | 0 | good
| 5097 | S | Elevated Tank Upper Aluminum Platform |  |  |  |  | 790900008 |  | SC | [5 empty] | 1984 |  | 22 | [8 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 50000 | IMG_3846 |  |  |  |  | 0 |  | 0 |  | 0 | good
| 5112 | S | Valve Chamber Precast Concrete Chamber |  |  |  |  | 790900008 |  | SW | [5 empty] | 2016 |  | 56 | [8 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. | 0 |  | 0 |  | 50000 | IMG_3913 |  |  |  |  | 0 |  | 0 |  | 0 | good
| 5139 | S | Elevated Tank Overflow Piping | Diameter: 300mm, approximate length: 40m |  |  |  | 790900008 |  | PM | [5 empty] | 1984 |  | 4 | [8 empty] | 3 | 4 | Moderate surface corrosion was observed. | Couplings installed on the pipe were rusted was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. | 500 | 2025 | 0 |  | 45000 | IMG_5634 | Sutton ET Capital Project 1 | Sutton ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Moderate surface corrosion | Couplings installed on the pipe were rusted.
| 5137 | S | Elevated Tank Inlet/Outlet Piping | Diameter: 300mm, approximate length: 35m |  |  |  | 790900008 |  | PM | [5 empty] | 1984 |  | 23 | [8 empty] | 3 | 5 | Minor surface corrosion was observed. | The inlet/outlet nozzle of the elevated tank inlet/outlet piping was opened at the elevated tank floor with no sediment stop. |  | The asset was observed to be in fair condition. Polish the piping in the valve room to remove surface rust. Supply and install sediment/silt stop for the pipe. Asset to be replaced at the end of its theoretical service life. | 2000 | 2025 | 0 |  | 40000 | IMG_5591 | Sutton ET Capital Project 1 | Sutton ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Very minor surface corrosion
| 4951 | S | Access Road | Access road from Dalton Road to site entrance. Approx. length of 90m and 4.0m wide |  |  |  | 790900008 |  | SW | [5 empty] | 1984 |  | 15 | [8 empty] | 3 | 1 | Tire ruts and low spots were observed at various locations. |  |  | The asset was observed to be in fair condition. Place and compact granular material as required at low spots and tire ruts. Asset to be replaced in the long term. | 7000 | 2024 | 0 |  | 30000 | IMG_20201029_093755 | Sutton ET Capital Project 2 | Sutton ET Capital Project 1 |  |  | 0 | Place and compact granular material as required at low spots and tire ruts. | 7000 |  | 0 | Tire ruts and low spots at various locations.
| 5129 | S | Electrical Conduit System | Conduit system including conduit for electrical services, installation year assumed to be 2010. |  |  |  |  | Glenway RES Outside Sanitary Pumping Station | ES | [5 empty] | 2010 |  | 15 |  | Area 2N Linear Water & Wells | [5 empty] | OPERATING | 2 | 3 | The conduit were mounted to the access tube ladder side rails, which may pose as a safety hazard as worker climbs the ladder. |  |  | The asset was observed to be in good condition. It is recommended to install a cable tray system and relocate cables from the access tube ladder rails. The asset to be replaced in the long term. | 8000 | 2024 | 0 |  | 30000 | IMG_3882 | Sutton ET Capital Project 2 | Sutton ET Capital Project 1 |  | W-WW | 2020 |  | 0 |  | 0 | good
| 5098 | S | Elevated Tank Aluminum Ladder (Ground to Platform) |  |  |  |  | 790900008 |  | SC | [5 empty] | 1984 |  | 0 | [8 empty] | 2 | 4 | The Class Frontal-Fixed Rail Ladder (Class FRL) fall protection system was installed throughout, and it was no longer compliant to current CSA standards. | Inside of the side rails of the ladder, it was measured to be 15''. It should be 16'' wide. |  | The asset was observed to be in good condition but presented code concerns. Replace the ladder with galvanized code compliant ladder system, galvanized support brackets and anchorage connectors, and CSA certified fall arrest system. |  |  | 0 |  | 30000 | IMG_3845 | Sutton ET Capital Project 1 | Sutton ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
| 5108 | S | Elevated Tank Inlet/Outlet Pipe Support |  |  |  |  | 790900008 |  | SC | [5 empty] | 1984 |  | 22 | [8 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 30000 | IMG_3845 |  |  |  |  | 0 |  | 0 |  | 0 | good
| 5109 | S | Elevated Tank Overflow Pipe Support |  |  |  |  | 790900008 |  | SC | [5 empty] | 1984 |  | 22 | [8 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 30000 | IMG_3845 |  |  |  |  | 0 |  | 0 |  | 0 | good
| 5115 | S | Elevated Tank Roof Guardrail |  |  |  |  | 790900008 |  | SC | [5 empty] | 1984 |  | 22 | [8 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. It is recommended to conduct a full design review of the existing supporting structural for the telecommunication system to determine if any additional reinforcement is required. Cost for potential roof rein | 45000 | 2024 | 0 |  | 30000 | IMG_3873 |  | Sutton ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
| 5146 | S | Access Tube Coating | Installation year assumed to be 1984 |  |  |  | 00016061 |  | SC | [5 empty] | 1984 |  | 18 | [8 empty] | 3 | 1 | Isolated corrosion was observed on edges and welds. | Surface corrosion at the bottom of the access tube. |  | The asset was observed to be in fair condition. Epoxy spot repair is recommended in the short term. Installation of condensation drip pan is required. | 18000 | 2024 | 0 |  | 25000 | IMG_3881 | Sutton ET Capital Project 2 | Sutton ET Capital Project 1 |  |  | 0 |  | 0 |  | 0
| 4939 | S | Chainlink Fence | 1.8m high, chainlink fence, with 3 barbed wires at top. Approx. 165m in length |  |  |  | 790900008 |  | SW | [5 empty] | 1984 |  | 15 | [8 empty] | 3 | 2 | Top barbed wire was cut, affecting approximately 10m in length. | Minor surface corrosion was observed throughout. |  | The asset was observed to be in fair condition.Re-install top barbed wire for section that is damaged. General trees and bushs maintenance around the perimeter of the site. Asset to be replaced in the intermediate term. | 2000 | 2024 | 0 |  | 25000 | IMG_20201029_091640 | Sutton ET Capital Project 2 | Sutton ET Capital Project 1 |  |  | 0 | Re-install top barbed wire for section that is damaged. | 500 |  | 0 | Top barbed wire was cut, affecting approximately 10m in length.
00083307 | 4934 | S | Elevated Tank Network Access Closet | installation year assumed to be 2010 |  |  |  | 00016061 | Sutton ET Valve Room | SIC | M00844 |  |  |  |  | 2010 |  | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control | 14E-088/SUETDR_NAC |  |  | W-WW | 2 | 4 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 25000 | PXL_20201029_134521784 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  | 0 |  | 0 | good
| 4940 | S | Asphalt Driveway | Paved surface on site, and driveway entrance. Approximately 250m2. |  |  |  | 790900008 |  | SW | [5 empty] | 1984 |  | 15 | [8 empty] | 3 | 1 | Asphalt around the concrete pad at the tank pedestal was settled and damaged. | Minor asphalt cracking along south edge of driveway entrance was observed. |  | The asset was observed to be in fair condition. Remove and replace asphalt and granular around pedestal entrance to ensure positive drainage away from entrance. Asset to be replaced in the intermediate term. | 5000 | 2024 | 0 |  | 20000 | IMG_20201029_092545 | Sutton ET Capital Project 2 | Sutton ET Capital Project 1 |  |  | 0 | Remove and replace asphalt and granulars around pedestal entrance to ensure positive drainage away from entrance. | 5000 |  | 0 | Asphalt around concrete pad at tank pedestal settled, and damaged. | Minor asphalt cracking along south edge of driveway entrance
| 5099 | S | Elevated Tank Aluminum Ladder (Platform to Roof) |  |  |  |  | 790900008 |  | SC | [5 empty] | 1984 |  | 0 | [8 empty] | 2 | 4 | The Class Frontal-Fixed Rail Ladder (Class FRL) fall protection system was installed throughout, and it was no longer compliant to current CSA standards. | Inside of the side rails of the ladder, it was measured to be 15''. It should be 16'' wide. |  | The asset was observed to be in good condition but presented code concerns. Replace the ladder with galvanized code compliant ladder system, galvanized support brackets and anchorage connectors, and CSA certified fall arrest system. |  |  | 0 |  | 20000 | IMG_3857 | Sutton ET Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | good
00006888 | 5127 | S | Inlet/Outlet Riser Heat Trace System |  |  |  |  | 00016061 |  | ES | [5 empty] | 2016 |  | 26 | [8 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. | 0 |  | 0 |  | 20000 | IMG_5575 |  |  |  |  | 0 |  | 0 |  | 0 | good
| 4946 | S | Storm Maintenance Hole No.3 | Located approximately 5m from elevated tank pedestal. Approximately 2.5m deep. |  |  |  | 790900008 |  | SW | [5 empty] | 1984 |  | 24 | [8 empty] | 3 | 2 | Maintenance hole was buried below pavement was observed. |  |  | The asset was observed to be in fair condition. Excavate around maintenance hole and raise frame/lid to grade. Reinstate asphalt pavement around lid, convert the manhole into a dechlorination chamber. | 15000 | 2024 | 0 |  | 17500 | IMG_20201029_095120 |  | Sutton ET Capital Project 1 |  |  | 0 | Excavate around maintenance hole and raise frame/lid to grade. Reinstate asphalt pavement around lid. | 2500 |  | 0 | Maintenance hole was buried below pavement.
| 5143 | S | Elevated Tank Access Tube Tank Bulkhead Access Door | size: 24'' x 18'' |  |  |  | 790900008 |  | SC | [5 empty] | 1984 |  | 22 | [8 empty] | 3 | 4 | Moderate surface corrosion was observed. |  |  | The asset was observed to be in fair condition. It is recommended to remove and cap the existing access tube tank access door. | 8000 | 2024 | 0 |  | 15000 | IMG_3859 |  | Sutton ET Capital Project 1 |  |  | 0 |  | 0 |  | 0
| 5100 | S | Elevated Tank Aluminum Ladder (Roof to Tank) |  |  |  |  | 790900008 |  | SC | [5 empty] | 1984 |  | 22 | [8 empty] | 5 | 4 | Severe corrosion was noted and the fail arrest system was out of alignment. | The Class Frontal-Fixed Rail Ladder (Class FRL) fall protection system was installed throughout, and it was no longer compliant to current CSA standards. |  | The asset was observed to be in very poor condition. Fall arrest system (TS rail) is required to be replaced immediately. All bolt sets require to be replaced. | 8000 | 2020 | 0 |  | 15000 | IMG_3889 |  | Sutton ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | failed
00017903 | 4910 | S | Elevated Tank Chlorine Analyzer |  |  |  |  | 00016061 | Sutton ET Valve Room | SIC | M00482 | CL17 |  |  | Chlorine | 1984 |  | 2 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control | 30600007459 |  |  | W-WW | 3 | 3 | The asset was outdated. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. | 0 |  | 0 |  | 15000 | PXL_20201029_133942071 | Sutton ET Capital Project 1 |  |  | OPERATING | 2020 |  | 0 |  | 0 | outdated
00084446 | 4897 | S | Lighting Panel A | Mannufacturer:Square D; ; serial number: 12398972110010001, 120/240V, 200A, 42CCT; old tag is 00006883. The panel was installed approximately in 2017. |  |  |  | 00016061 | Sutton ET Valve Room | ES | M00129 |  |  |  |  | 2017 |  | 20 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Electrical System | T3A |  |  | W-WW | 3 | 3 | Corrosion was observed on enclosure. | The enclosure was not NEMA 3R type. |  | The asset was observed to be in fair condition. Replace the enclosure with NEMA 3R type. Asset to be replaced at the end of remaining service life. | 4000 | 2024 | 0 |  | 15000 | PXL_20201029_134229876 | Sutton ET Capital Project 2 | Sutton ET Capital Project 1 |  | OPERATING | 2020 | Replace the enclosure with NEMA 3R type. | 4000 |  | 0 | corrosion on enclosure | The enclosure was not NEMA 3R type. | The enclosure to be replaced with NEMA 3R type
00012111 | 4903 | S | Site Drainage (soft surfaces) | Site drainage on site, including grassed areas. |  |  |  | 790900008 | Sutton Elevated Tank | SW | [5 empty] | 1984 |  | 25 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Siteworks |  |  |  | W-WW | 3 | 1 | Along edge of pavement, tire ruts damaged sod was observed. | Low spots at various locations around site. |  | The asset was observed to be in fair condition. Remove top soil and sod along edge of pavement, and replace with gravel shoulder. | 10000 | 2024 |  |  | 15000 | IMG_20201029_091412 |  | Sutton ET Capital Project 1 |  | OPERATING | 2020 | Remove top soil and sod along edge of pavement, and replace with gravel shoulder. | 7500 | Remove and replace sod at low spots of soft surface around site. | 2000 | Along edge of pavement, tire ruts damaged sod | Low spots at various locations around site, not draining storm water properly
| 4945 | S | Storm Maintenance Hole No.2 | Located at Dalton Road ROW, approximately 2.0m deep. |  |  |  | 790900008 |  | SW | [5 empty] | 1984 |  | 24 | [8 empty] | 3 | 2 | Damaged adjustment unit for maintenance hole frame. |  |  | The asset was observed to be in fair condition. Remove and replace adjustment unit for maintenance hole frame. | 1000 | 2024 | 0 |  | 15000 | IMG_20201029_094643 |  | Sutton ET Capital Project 1 |  |  | 0 | Remove and replace adjustment unit for maintenance hole frame. | 1000 |  | 0 | Damaged maintenance hole adjustment unit for frame.
| 5111 | S | Valve Room Concrete Roof |  |  |  |  | 00016061 |  | SC | [5 empty] | 1984 |  | 22 | [8 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 1000 | 2030 | 0 |  | 15000 | IMG_3905 |  | Sutton ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
| 4942 | S | 300mm Underground Watermain Valve | 300mm Water valve, in valve box (within Region property line, adjacent to Dalton Road) |  |  |  | 790900008 |  | PM | [5 empty] | 1984 |  | 24 | [8 empty] | 3 | 3 | Curb box could not be opened. |  |  | The asset was assumed to be in fair condition. | 0 |  | 0 |  | 10000 | IMG_20201029_093855 |  |  |  |  | 0 |  | 0 |  | 0 | Lid could not be opened
00025271 | 4914 | S | Bell Antenna 1 | Cellular Antenna, installation year assumed to be 2010 based on its physical condition |  |  |  | 790900008 | Sutton Elevated Tank | SIC | [5 empty] | 2010 |  | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Antenna |  |  |  | W-WW | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 10000 | IMG_3867 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  | 0 |  | 0 | Good
00025272 | 4915 | S | Bell Antenna 2 | Cellular Antenna, installation year assumed to be 2010 based on its physical condition |  |  |  | 790900008 | Sutton Elevated Tank | SIC | [5 empty] | 2010 |  | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Antenna |  |  |  | W-WW | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 10000 | IMG_3867 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  | 0 |  | 0 | Good
00025273 | 4916 | S | Bell Antenna 3 | Cellular Antenna, installation year assumed to be 2010 based on its physical condition |  |  |  | 790900008 | Sutton Elevated Tank | SIC | [5 empty] | 2010 |  | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Antenna |  |  |  | W-WW | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 10000 | IMG_3867 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  | 0 |  | 0 | Good
00025276 | 4919 | S | Bell Antenna 4 | Cellular Antenna, installation year assumed to be 2010 based on its physical condition |  |  |  | 790900008 | Sutton Elevated Tank | SIC | [5 empty] | 2010 |  | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Antenna |  |  |  | W-WW | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 10000 | IMG_3874 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  | 0 |  | 0 | Good
00083317 | 4935 | S | Elevated Tank Flow Transmitter | installation year assumed to be 2010 based on its physical condition |  |  |  | 00016061 | Sutton ET Valve Room | SIC | M00405 | 93WA4-18D3/0 | 93WA4 |  | Flow | 2010 |  | 5 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control | M1027302000 |  |  | W-WW | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 10000 | PXL_20201029_134330909 | Sutton ET Capital Project 1 |  |  | OPERATING | 2020 |  | 0 |  | 0 | good
| 5131 | S | Elevated Tank Grounding | installation year assumed to be 2010 |  |  |  | 790900018 |  | ES | [5 empty] | 2010 |  | 15 | [8 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 10000 | IMG_3844 | Sutton ET Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | good
| 5103 | S | Elevated Tank Roof Access Hatch (Access Tube to Tank Roof) |  |  |  |  | 790900008 |  | SC | [5 empty] | 1984 |  | 22 | [8 empty] | 3 | 2 | Moderate surface corrosion was noted on mounting curb. |  |  | The asset was observed to be in fair condition. Hatch lid to be replaced with aluminum. | 3500 | 2024 | 0 |  | 10000 | IMG_3883 | Sutton ET Capital Project 2 | Sutton ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
| 5149 | S | Elevated Tank Roof Access Hatch (Tank Roof to Tank Interior) |  |  |  |  | 790900008 |  | SC | [5 empty] | 1984 |  | 22 | [8 empty] | 3 | 2 | moderate surface corrosion was noted on mounting curb. | Padlock and hasp was noted to be missing. They are required to prevent unauthorized personnel from entering the tank. |  | The asset was observed to be in fair condition. Hatch lid to be replaced with aluminum. Install padlock and hasp. | 4000 | 2024 | 0 |  | 10000 | IMG_3883 |  | Sutton ET Capital Project 1 |  |  | 0 |  | 0 |  | 0
| 5150 | S | Elevated Tank Roof Hatch (for Vent) |  |  |  |  | 790900008 |  | SC | [5 empty] | 1984 |  | 22 | [8 empty] | 3 | 2 | Moderate surface corrosion was noted on mounting curb. |  |  | The asset was observed to be in fair condition. Hatch lid to be replaced with aluminum. | 3500 | 2024 | 0 |  | 10000 | IMG_3875 |  | Sutton ET Capital Project 1 |  |  | 0 |  | 0 |  | 0
00083219 | 4933 | S | Elevated Tank SUETDR OIT Panel | Advantech Monitor Panel, installation year assumed to be 2017 based on its physical condition |  |  |  | 00016062 | Sutton ET Tank Base | SIC | M10189 |  |  |  |  | 2017 |  | 12 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control | KSA1476816 |  |  | W-WW | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 10000 | PXL_20201029_134143670 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  | 0 |  | 0 | good
| 5102 | S | Elevated Tank Upper Platform Tank Bulkhead Access Door |  |  |  |  | 790900008 |  | SC | [5 empty] | 1984 |  | 4 | [8 empty] | 4 | 3 | Severe corrosion was noted on bolt sets and door flange. |  |  | The asset was observed to be in poor condition. It is recommended to upgrade the bulkhead access door to submarine style manway for easy access. | 0 |  | 0 |  | 10000 | IMG_3853 | Sutton ET Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | good
| 5140 | S | Elevated Tank Vent/Vacuum Relief Unit | Installation year assumed to be 1984. |  |  |  | 790900008 |  | PM | [5 empty] | 2012 |  | 21 | [8 empty] | 3 | 3 | Minor surface corrosion was observed on steel collar. |  |  | The asset was observed to be in fair condition. Surface prep and touch-up vent collar. The asset to be relocated away from the hatch. | 1000 | 2025 |  |  | 10000 | DSCN0182 |  | Sutton ET Capital Project 1 |  |  | 2019 | Surface prep and touch-up vent collar | 2000 |  |  | Minor surface corrosion on steel collar
00017900 | 4908 | S | Network Antenna 1 | Installation year assumed to be 2010 based on its physical condition |  |  |  | 00016061 | Sutton ET Valve Room | SIC | [5 empty] | 2010 |  | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | SCADA |  |  |  | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 10000 | PXL_20201029_133504866 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  | 0 |  | 0 | good
00017901 | 4909 | S | Network Antenna 2 | Installation year assumed to be 2010 based on its physical condition |  |  |  | 00016061 | Sutton ET Valve Room | SIC | [5 empty] | 2010 |  | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | SCADA |  |  |  | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 10000 | PXL_20201029_133504866 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  | 0 |  | 0 | good
00078380 | 4930 | S | Security System | Three panels in total, installation year assumed to be 2010 based on the physical condition |  |  |  | 00016061 | Sutton ET Valve Room | SIC | M00076 |  |  |  |  | 2010 |  | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Health and Safety |  |  |  | W-WW | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 10000 | PXL_20201029_134421959 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  | 0 |  | 0 | good
00025275 | 4918 | S | York Region Antenna 5 | UHF SCADA Yagi Antenna, installation year assumed to be 2010 based on the physical condition |  |  |  | 790900008 | Sutton Elevated Tank | SIC | [5 empty] | 2010 |  | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Antenna |  |  |  | W-WW | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 10000 | IMG_3869 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  | 0 |  | 0 | Good
00025274 | 4917 | S | York Region Antenna 6 | UHF Yagi Antenna, installation year assumed to be 2010 based on the physical condition |  |  |  | 790900008 | Sutton Elevated Tank | SIC | [5 empty] | 2010 |  | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Antenna |  |  |  | W-WW | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 10000 | IMG_3869 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  | 0 |  | 0 | Good
00025277 | 4920 | S | York Region Antenna 7 | UHF Whip Traffic Antenna, installation year assumed to be 2010 based on the physical condition |  |  |  | 790900008 | Sutton Elevated Tank | SIC | [5 empty] | 2010 |  | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Antenna |  |  |  | W-WW | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 10000 | IMG_3874 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  | 0 |  | 0 | Good
00025278 | 4921 | S | York Region Antenna 8 | UHF Whip Traffic Antenna, installation year assumed to be 2010 based on the physical condition |  |  |  | 790900008 | Sutton Elevated Tank | SIC | [5 empty] | 2010 |  | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Antenna |  |  |  | W-WW | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 10000 | IMG_3874 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  | 0 |  | 0 | Good
00025279 | 4922 | S | York Region Antenna 9 | UHF Whip Traffic Antenna, installation year assumed to be 2010 based on the physical condition |  |  |  | 790900008 | Sutton Elevated Tank | SIC | [5 empty] | 2010 |  | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Antenna |  |  |  | W-WW | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 10000 | IMG_3874 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  | 0 |  | 0 | Good
| 4950 | S | Elevated Tank Pedestal Lighting | 6 NEMA 4 fixtures, installation year assumed to be 2010. |  |  |  | 790900008 |  | ES | [5 empty] | 2010 |  | 9 | [8 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Replace the lighting fixtures with LED type in the next capital project. | 0 |  | 0 |  | 8000 | PXL_20201029_135009897 | Sutton ET Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | good
| 5110 | S | Valve Room Masonry Blockwall |  |  |  |  | 00016061 |  | SC | [5 empty] | 1984 |  | 22 | [8 empty] | 3 | 4 | Hairline cracking was observed at corner. |  |  | The asset was observed to be in fair condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 1000 | 2030 | 0 |  | 8000 | IMG_3903 |  | Sutton ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | hairline cracking at corner | fair
| 5138 | S | Elevated Tank Bypass Line Piping | Diameter: 150mm, approximate length: 10m |  |  |  | 790900008 |  | PM | [5 empty] | 1984 |  | 23 | [8 empty] | 3 | 3 | Moderate surface corrosion was observed. | Couplings installed on the pipe were rusted was observed. |  | The asset was observed to be in fair condition. Polish the piping in the valve room to remove surface rust. Asset to be replaced at the end of its theoretical service life | 500 | 2025 | 0 |  | 5500 | IMG_5642 | Sutton ET Capital Project 1 | Sutton ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Moderate surface corrosion | Couplings installed on the pipe were rusted.
00044398 | 5049 | S | Elevated Tank Exterior Access Double Doors | Exterior double metal door, installation year assumed to be 1984 |  |  |  | 790900008 | Sutton Elevated Tank | AC | [5 empty] | 1984 |  | 6 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Architectural |  |  |  | W-WW | 3 | 1 | Corrosion was observed at bottom of door frame. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. It is recommended to install access doors with weather stripping. | 0 |  | 0 |  | 5500 | IMG_3836 | Sutton ET Capital Project 1 |  |  | OPERATING | 2020 |  | 0 |  | 0 | corrosion at bottom of door frame
| 5128 | S | Aircraft Obstruction Lights | Two warning lights, bulbs replaced in 2016 |  |  |  | 790900008 |  | ES | [5 empty] | 2016 |  | 9 | [8 empty] | 3 | 3 | In 2015, Transport Canada performed an assessment of the necessity for obstruction lighting on the Sutton Elevated Tank. It confirmed that obstruction lighting or marking was not required at the facility. | Surface corrosion was observed. |  | The asset was observed to be in fair condition. Asset can be removed at the end of remaining service life. | 0 |  | 0 |  | 5000 | IMG_3873 | Sutton ET Capital Project 1 |  |  |  | 2019 |  | 0 |  | 0 | Good
| 5106 | S | Elevated Tank Davit Base Socket (Tank Roof) | A new cap was installed during the 2016 condition assessment |  |  |  | 790900008 |  | HSS | [5 empty] | 1984 |  | 24 | [8 empty] | 3 | 4 | Moderate surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Surface prep and paint dismount post in safety yellow colour are recommended in the next capital project. | 1000 | 2022 | 0 |  | 5000 | IMG_3879 |  | Sutton ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
| 5105 | S | Elevated Tank Dismount Post (Tank Roof) |  |  |  |  | 790900008 |  | HSS | [5 empty] | 1984 |  | 24 | [8 empty] | 3 | 4 | Moderate surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Surface prep and paint dismount post in safety yellow colour. | 1000 | 2022 | 0 |  | 5000 | IMG_3883 |  | Sutton ET Capital Project 1 |  |  | 0 | Surface prep and paint dismount post in safety yellow colour. | 2000 |  | 0 | Moderate surface corrosion
| 5130 | S | Elevated Tank Lightning Protection System | 1 lightning air protection terminal |  |  |  | 790900018 |  | ES | [5 empty] | 2004 |  | 5 | [8 empty] | 3 | 3 | Moderate corrosion was found on the lightning protection system magnetic cable brackets. |  |  | The asset was observed to be in fair condition. Remove lightning cables and magnets, ensure cables are bonded to the tank to provide lightning protection and tank grounding. | 0 |  | 0 |  | 5000 | IMG_3862 | Sutton ET Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | good
00017906 | 4913 | S | Elevated Tank Network Radio Modem 1 | likely installed in the Network Access Closet, installation year assumed to be 2010 |  |  |  | 00016061 | Sutton ET Valve Room | SIC | M01018 |  |  |  |  | 2010 |  | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | SCADA | 831070 |  |  | W-WW | 3 | 2 |  | Included in 00083307 was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 5000 |  | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  | 0 |  | 0 |  | included in 00083307
00017905 | 4912 | S | Elevated Tank Network Radio Modem 2 | likely installed in the Network Access Closet, installation year assumed to be 2010 |  |  |  | 00016061 | Sutton ET Valve Room | SIC | M01018 |  |  |  |  | 2010 |  | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | SCADA | 831046 |  |  | W-WW | 3 | 2 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 5000 |  | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  | 0 |  | 0
| 5126 | S | Elevated Tank Removable Louvred Vent |  |  |  |  | 790900008 |  | BM | [5 empty] | 1984 |  | 23 | [8 empty] | 3 | 1 | The louvred did not completed cover the opening. A 2'' gap was noted above the louvred. |  |  | The asset was observed to be in fair condition. Seal 2’’ opening for the louvred vent located at the elevated tank upper platform. Asset to be replaced in the intermediate term. | 1000 | 2024 | 0 |  | 5000 | IMG_3848 |  | Sutton ET Capital Project 1 |  |  | 2019 |  | 0 |  | 0 | good
| 5117 | S | Elevated Tank Tank Vent |  |  |  |  | 790900008 |  | SC | [5 empty] | 1984 |  | 22 | [8 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 5000 | IMG_3879 |  |  |  |  | 0 |  | 0 |  | 0 | good
00045975 | 4927 | S | Generator Transfer Panel | Manufacturer: Siemens, Model No.:EQG630D. Installation year assumed to be 1984. |  |  |  | 00016061 | Sutton ET Valve Room | ES | M00125 |  |  |  |  | 1984 |  | 4 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Electrical System | 12167-067 |  |  | W-WW | 3 | 3 | Minor corrosion was observed around the circuit breakers. | The panel appeared to be original. |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. | 0 |  | 0 |  | 5000 | PXL_20201029_134356166 | Sutton ET Capital Project 1 |  |  | OPERATING | 2020 |  | 0 |  | 0 | minor corrosion around the circuit breakers
00006888 | 4900 | S | Heat Trace Control Panel |  |  |  |  | 00016061 | Sutton ET Valve Room | ES | [5 empty] | 2016 |  | 26 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Electrical System |  |  |  | W-WW | 2 | 3 |  |  |  | The asset was observed to be in good condition. | 0 |  | 0 |  | 5000 | PXL_20201029_134021130 |  |  |  | OPERATING | 2020 |  | 0 |  | 0 | outdated
| 5003 | S | Watermain Extended Stem Gate Valve 1 | Diameter: 300mm |  |  |  | 790900008 |  | PM | [5 empty] | 2016 |  | 26 | [8 empty] | 3 | 3 | Minor corrosion on wrench nut was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 5000 | IMG_5482 |  |  |  |  | 0 |  | 0 |  | 0 | Minor corrosion on wrench nut
| 5004 | S | Watermain Extended Stem Gate Valve 2 | Diameter: 300mm |  |  |  | 790900008 |  | PM | [5 empty] | 2016 |  | 26 | [8 empty] | 3 | 3 | Minor corrosion on wrench nut was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 5000 | IMG_5489 |  |  |  |  | 0 |  | 0 |  | 0 | Minor corrosion on wrench nut
| 5005 | S | Watermain Extended Stem Gate Valve 2 | Diameter: 300mm |  |  |  | 790900008 |  | PM | [5 empty] | 2016 |  | 26 | [8 empty] | 3 | 3 | Minor corrosion on wrench nut was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 5000 | IMG_5485 |  |  |  |  | 0 |  | 0 |  | 0 | Minor corrosion on wrench nut
| 5101 | S | Elevated Tank Aluminum Ladder (Platform to Tank Floor Access Hatch) |  |  |  |  | 790900008 |  | SC | [5 empty] | 1984 |  | 22 | [8 empty] | 2 | 4 | The Class Frontal-Fixed Rail Ladder (Class FRL) fall protection system was installed throughout, and it was no longer compliant to current CSA standards. |  |  | The asset was observed to be in good condition but presented code concerns. Fall arrest system (TS rail) is required to be replaced immediately. | 1000 | 2020 | 0 |  | 4000 | IMG_3853 |  | Sutton ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
00006879 | 5048 | S | Valve Room Interior Single Door | Installation year assumed to be 1984 |  |  |  | 00016061 | Sutton ET Tank Base | AC | [5 empty] | 1984 |  | 6 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Architectural |  |  |  | W-WW | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 3500 | IMG_3903 | Sutton ET Capital Project 1 |  |  | OPERATING | 2020 |  | 0 |  | 0 | fair
| 5144 | S | Elevated Tank Anchor Point (Access Tube) |  |  |  |  | 790900008 |  | HSS | [5 empty] | 2007 |  | 4 | [8 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. It is recommended to remove the 'D' ring mounted on hatch collar and install new anchorage connector at hatch with vent mount. | 0 |  | 0 |  | 3000 | IMG_3880 | Sutton ET Capital Project 1 |  |  |  | 0 |  | 0 |  | 0
| 5107 | S | Elevated Tank Anchor Point (Platform Level) | Platform level |  |  |  | 790900008 |  | HSS | [5 empty] | 2007 |  | 8 | [8 empty] | 2 | 4 | Very minor surface corrosion was noted. |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 3000 | IMG_3850 | Sutton ET Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | good
00004219 | 4889 | S | Elevated Tank Inlet/Outlet Line Gate Valve | Diameter: 300mm, Manufacturer: McAvity |  |  |  | 00016061 | Sutton ET Valve Room | PM | M00100 |  |  |  |  | 1984 |  | 4 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Process Mechanical |  |  |  | W-WW | 3 | 3 | Leak in packing was observed. | Minor to moderate corrosion was observed on valve body. | Corrosion was noted on the bolts of the valve. | The asset was observed to be in fair condition. Asset to be replaced in the short term. | 0 |  | 0 |  | 3000 | IMG_5556 | Sutton ET Capital Project 1 |  |  | OPERATING | 2020 |  | 0 |  | 0 | Leak in packing | Minor to moderate corrosion on valve body
00017896 | 4905 | S | Elevated Tank Network UPS 1 | likely installed in the Network Access Closet, installation year assumed to be 2010 |  |  |  | 00016061 | Sutton ET Valve Room | SIC | M00183 |  |  |  |  | 2010 |  | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | SCADA | JB0241022055R |  |  | W-WW | 3 | 2 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 3000 |  | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  | 0 |  | 0
00052825 | 4928 | S | Elevated Tank Network UPS 2 | likely installed in the Network Access Closet, installation year assumed to be 2010 |  |  |  | 00016061 | Sutton ET Valve Room | SIC | M00728 |  |  |  |  | 2010 |  | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | SCADA | GF104A0100 |  |  | W-WW | 3 | 2 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 3000 |  | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  | 0 |  | 0
00081400 | 4932 | S | Elevated Tank SUETDR Control Panel Ethernet Switch | likely installed in SUETDR Control Panel, installation year assumed to be 2017 |  |  |  | 00016062 | Sutton ET Tank Base | SIC | M01002 |  |  |  |  | 2017 |  | 12 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control | FOC2004Z1FF |  |  | W-WW | 3 | 2 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 3000 |  | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  | 0 |  | 0
00083386 | 4938 | S | Elevated Tank SUETDR Control Panel UPS | likely installed in SUETDR Control Panel, installation year assumed to be 2017 |  |  |  | 00016062 | Sutton ET Tank Base | SIC | M10181 |  |  |  |  | 2017 |  | 12 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control | GK053A0127 |  |  | W-WW | 3 | 2 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 3000 | PXL_20201029_134934038 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  | 0 |  | 0
00012107 | 4902 | S | Site Gate | East, Gate, Double Lockable |  |  |  | 790900008 | Sutton Elevated Tank | SW | [5 empty] | 1984 |  | 15 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Siteworks |  |  |  | W-WW | 3 | 2 | Minor damage was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 3000 | IMG_20201029_092823 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  | 0 |  | 0 | Minor damage
| 5089 | S | Valve Room Wall and Ceiling Paint | Installation year assumed to be 1984 |  |  |  | 00016061 |  | AC | [5 empty] | 1984 |  | 6 | [8 empty] | 2 | 1 | Wall section above the electrical baseboard heater was not painted. |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 3000 | IMG_3905 | Sutton ET Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | good
| 4941 | S | Concrete Curb | Concrete curb at driveway entrances (both east and west). Approximately 20m in length |  |  |  | 790900008 |  | SW | [5 empty] | 1984 |  | 11 | [8 empty] | 3 | 1 | Minor damage and cracking on curb were observed. |  |  | The asset was observed to be in fair condition. | 0 |  | 0 |  | 2500 | IMG_20201029_092855 | Sutton ET Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | Minor damage and cracking on curb.
| 5114 | S | Valve Chamber Access Ladder |  |  |  |  | 790900008 |  | SW | [5 empty] | 2016 |  | 56 | [8 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. | 0 |  | 0 |  | 2500 | IMG_3913 |  |  |  |  | 0 |  | 0 |  | 0 | good
| 5152 | S | Elevated Tank Guardrail Ladder |  |  |  |  | 790900008 |  | SC | [5 empty] | 1984 |  | 22 | [8 empty] | 2 | 3 | The Class Frontal-Fixed Rail Ladder (Class FRL) fall protection system was installed throughout, and it was no longer compliant to current CSA standards. |  |  | The asset was observed to be in good condition but presented code concerns. Fall arrest system (TS rail) is required to be replaced immediately. | 1000 | 2020 | 0 |  | 2000 | IMG_3873 |  | Sutton ET Capital Project 1 |  |  | 0 |  | 0 |  | 0
00044946 | 4926 | S | Elevated Tank Pressure Transmitter | Installation year assumed to be 2010 based on its physical condition |  |  |  | 00016061 | Sutton ET Valve Room | SIC | M00405 | PMC71 |  |  |  | 2010 |  | 5 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control | F900091509C |  |  | W-WW | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2000 | PXL_20201029_134314017 | Sutton ET Capital Project 1 |  |  | OPERATING | 2020 |  | 0 |  | 0 | good
00077743 | 4929 | S | Portable Generator | Manufacturer: Honda, Model Name: EU3000, specs: 120V, 20A. Installation year assumed to be 2017 |  |  |  | 790900008 | Sutton Elevated Tank | ES | M00506 |  |  |  |  | 2017 |  | 22 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Building Mechanical | EAVJ-1144610 |  |  | W-WW | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 2000 | PXL_20201029_134627924 |  |  |  | OPERATING | 2020 |  | 0 |  | 0 | good
00035519 | 4924 | S | Sump Pump and Drain Piping | Submersible Sump Pump, by Mastercraft, 120/1/60, 1/3hp, capacity: 10.4 m3/h. The sump pump pumping connected to elevated tank overflow pipe |  |  |  | 00016061 | Sutton ET Valve Room | BM | [5 empty] | 1984 |  | 6 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Process Mechanical |  |  |  | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 2000 | IMG_5618 | Sutton ET Capital Project 1 |  |  | OPERATING | 2020 |  | 0 |  | 0 | good
| 4948 | S | Valve Room Lighting Fixtures | 2 NEMA 4 fixtures, installation year assumed to be 2010. |  |  |  | 00016061 |  | ES | [5 empty] | 2010 |  | 9 | [8 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Replace the lighting fixtures with LED type in the next capital project. | 0 |  | 0 |  | 2000 | PXL_20201029_134544370 | Sutton ET Capital Project 1 |  |  |  | 0 |  | 0 |  | 0 | good
00004221 | 4891 | S | Elevated Tank Bypass Line Check Valve | Diameter: 150mm, Manufacturer: McAvity |  |  |  | 00016061 | Sutton ET Valve Room | PM | M00100 |  |  |  |  | 1984 |  | 4 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Process Mechanical |  |  |  | W-WW | 3 | 3 | Minor to moderate surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. | 0 |  | 0 |  | 1500 | IMG_5651 | Sutton ET Capital Project 1 |  |  | OPERATING | 2020 |  | 0 |  | 0 | Minor to moderate surface corrosion
00004220 | 4890 | S | Elevated Tank Bypass Line Gate Valve 1 | Diameter: 150mm, Manufacturer: McAvity |  |  |  | 00016061 | Sutton ET Valve Room | PM | M00100 |  |  |  |  | 1984 |  | 4 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Process Mechanical |  |  |  | W-WW | 3 | 3 | Minor to moderate surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. | 0 |  | 0 |  | 1500 | IMG_5568 | Sutton ET Capital Project 1 |  |  | OPERATING | 2020 |  | 0 |  | 0 | Minor to moderate surface corrosion
00004222 | 4892 | S | Elevated Tank Bypass Line Gate Valve 2 | Diameter: 150mm, Manufacturer: McAvity |  |  |  | 00016061 | Sutton ET Valve Room | PM | M00100 |  |  |  |  | 1984 |  | 4 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Process Mechanical |  |  |  | W-WW | 3 | 3 | Minor surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. | 0 |  | 0 |  | 1500 | IMG_5557 | Sutton ET Capital Project 1 |  |  | OPERATING | 2020 |  | 0 |  | 0 | Minor surface corrosion
00004223 | 4893 | S | Elevated Tank Bypass Line Gate Valve 3 | Diameter: 150mm, Manufacturer: McAvity |  |  |  | 00016061 | Sutton ET Valve Room | PM | M00100 |  |  |  |  | 1984 |  | 4 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Process Mechanical |  |  |  | W-WW | 3 | 3 | Minor surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. | 0 |  | 0 |  | 1500 | IMG_5551 | Sutton ET Capital Project 1 |  |  | OPERATING | 2020 |  | 0 |  | 0 | Minor surface corrosion
00004224 | 4894 | S | Elevated Tank Bypass Line Gate Valve 4 | Diameter: 150mm, Manufacturer: McAvity |  |  |  | 00016061 | Sutton ET Valve Room | PM | M00100 |  |  |  |  | 1984 |  | 4 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Process Mechanical |  |  |  | W-WW | 3 | 3 | Minor surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the short term. | 0 |  | 0 |  | 1500 | IMG_5550 | Sutton ET Capital Project 1 |  |  | OPERATING | 2020 |  | 0 |  | 0 | Minor surface corrosion
00083318 | 4936 | S | Elevated Tank SUETDR OIT Panel CPU | installed in SUETDR OIT Panel, installation year assumed to be 2017 |  |  |  | 00016062 | Sutton ET Tank Base | SIC | M10189 |  |  |  |  | 2017 |  | 12 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control | ACG2001486 |  |  | W-WW | 3 | 2 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 1500 | PXL_20201029_134143670 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  | 0 |  | 0
| 5113 | S | Valve Chamber Manhole Frame and Cover |  |  |  |  | 790900008 |  | SW | [5 empty] | 2016 |  | 56 | [8 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. | 0 |  | 0 |  | 1500 | IMG_3911 |  |  |  |  | 0 |  | 0 |  | 0 | good
| 5142 | S | Elevated Tank Sample Line |  |  |  |  | 790900008 |  | BM | [5 empty] | 1984 |  | 23 | [8 empty] | 2 | 1 | The sample line drains directly to the sump pit. |  |  | The asset was observed to be in good condition. Install a sample sink and a new sink drain system in the next capital project. Asset to be replaced in the intermediate term. | 3000 | 2024 | 0 |  | 1000 | IMG_5583 |  | Sutton ET Capital Project 1 |  |  | 0 |  | 0 |  | 0
| 4947 | S | Outdoor Lighting Fixture | 1 LED flood light, installation year assumed to be 2010. |  |  |  | 790900008 |  | ES | [5 empty] | 2010 |  | 15 | [8 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 1000 | PXL_20201029_133518930 | Sutton ET Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | good
| 4949 | S | Valve Room Emergency Lighting | Emergency lighting with 1 battery unit and 1 remote head, a new battery was installed in July 2020. |  |  |  | 00016061 |  | ES | [5 empty] | 2010 |  | 15 | [8 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 1000 | PXL_20201029_133917415 | Sutton ET Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | good
00078381 | 4931 | S | Electric Baseboard Heater | Baseboard Convection Heater, 120/1/60, Manufacturer: Dimplex, installation year assumed to be 2016 |  |  |  | 00016061 | Sutton ET Valve Room | BM | M00366 |  |  |  |  | 2016 |  | 11 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Building Mechanical |  |  |  | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 500 | IMG_5647 | Sutton ET Capital Project 2 |  |  | OPERATING | 2020 |  | 0 |  | 0 | good
00006889 | 4901 | S | Elevated Tank Pressure Gauge |  |  |  |  | 00016061 | Sutton ET Valve Room | SIC | M00627 |  |  |  |  | 1984 |  | 6 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control |  |  |  | W-WW | 3 | 1 | Minor surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 500 | PXL_20201029_134817672 | Sutton ET Capital Project 1 |  |  | OPERATING | 2020 |  | 0 |  | 0 | Minor surface corrosion
00017897 | 4906 | S | Sump Pump Float Switch | installed in the sump pump pit, installation year assumed to be 2010 based on its physical condition. |  |  |  | 00016061 | Sutton ET Valve Room | SIC |  |  |  |  | Level | 2010 |  | 5 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control |  |  |  | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 500 | PXL_20201029_134846156 | Sutton ET Capital Project 1 |  |  | OPERATING | 2020 |  | 0 |  | 0 | good
00017898 | 4907 | S | Valve Room Low Temperature Alarm | Valve room low temperature alarm, installation year assumed to be 2010 based on its physical condition. |  |  |  | 00016061 | Sutton ET Valve Room | SIC | M00076 | T631A1063 |  |  | Temperature | 2010 |  | 5 |  | Area 3 Water Treatment | W - Storage Elevated Tank | Instrumentation and Control | NOT AVAILABLE |  |  | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 500 | PXL_20201029_134218182 | Sutton ET Capital Project 1 |  |  | OPERATING | 2020 |  | 0 |  | 0 | good
| 5155 | S | Valve Room Smoke Detector | The installation year assumed to be 2016 |  |  |  | 00019610 |  | HSS | [5 empty] | 2016 |  | 8 | [8 empty] | 2 | 1 |  |  |  | The smoke detector was observed to be in good condition. | 0 |  | 0 |  | 500 | PXL_20201029_134547192 | Sutton ET Capital Project 1 |  |  |  | 0 |  | 0 |  | 0
00044308 | 5001 | S | Portable Dehumidifier | Portable dehumidifier by Electrolux Home Products, Model CAD304NWL, 115/60/1; capacity 30 pints/day |  |  |  | 00016061 |  | BM | [5 empty] | 2016 |  | 11 | [8 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 300 | IMG_5623 | Sutton ET Capital Project 2 |  |  |  | 0 |  | 0 |  | 0 | good
| 5141 | S | Fire Extinguisher | The installation year assumed to be 2016 |  |  |  | 00019610 |  | HSS | [5 empty] | 2016 |  | 8 | [8 empty] | 2 | 1 |  |  |  | The fire extinguisher was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 100 | IMG_3907 | Sutton ET Capital Project 1 |  |  |  | 2019 |  | 0 |  | 0 | Missing