## Sheet1
assetTag | seqNum | facility | remainingESL | assetName | COF | CategoryCode | installYear | defect1Input | rehabProjectName | condition | Description | Process | building | inspectorName | LocationTag | LocationORIGINAL | manufacturer | TransmitterModel | TransducerModel | TransducerSerial | InstMeva | installationDate | InstType | ServiceArea | FacilityType | LifeCycleCategory | SerialNo | Parent | RotatingItem | Site | repCost | observations | defect1 | defect2 | defect3 | rehabComment1 | RehabRepairCost | RehabRepairYear | rehabComment2 | RehabRepairCost2 | RehabRepairYear2 | photoName
| 4999 | MAN | 15 | Chainlink Fence | 2 | SW | 2004 | Barbed wire was not attached to fence along west side of site for approximately 30m. | Mt Albert North ET Capital Project 1 | 3 | 1.8m high chainlink fence, with barbed wire on top. Approx. total length 180m |  |  |  | 790900018 | [15 empty] | 25000 | The asset was observed to be in fair condition. Re-attach barbed wire to top of fence. Install new mesh at location of damaged fence mesh. | Barbed wire was not attached to fence along west side of site for approximately 30m. | Fence mesh damaged at sw corner of site was observed. |  | Re-attach barbed wire to top of fence. | 2000 | 2024 | Install new mesh at location of damaged fence mesh. |  |  | IMG_20201111_102312
00025415 | 4956 | MAN | 6 | Chlorine Residual Kit | 2 | HSS | 2004 | good |  | 2 | Hach II Pocket Colorimeter, Chlorine Residual Kit |  |  |  | 00017166 | Mt Alberta North ET Valve Room | M00482 | [8 empty] | Health and Safety | 05080C035745 |  |  | W-WW | 700 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | [7 empty] | 0 |  | PXL_20201111_140445688
| 5091 | MAN | 44 | Electrical Control Room Composite Roof | 3 | SC | 2004 | Good | Mt Albert North ET Capital Project 2 | 2 |  |  |  |  | 00017169 | [15 empty] | 15000 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Electrical room composite roof to be replaced at the end of remaining service life. |  |  |  | Provision for structural repairs every 10 years. | 1000 | 2030 |  | 0 |  | IMG_4106
| 5061 | MAN | 44 | Electrical Control Room Concrete Floor Slab | 3 | SC | 2004 | good | Mt Albert North ET Capital Project 2 | 2 |  |  |  |  | 00017169 | [15 empty] | 15000 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. |  |  |  | Provision for structural repairs every 10 years. | 1500 | 2030 |  | 0 |  | IMG_4126
00024559 | 4981 | MAN | 14 | Electrical Control Room Electric Unit Heater | 2 | BM | 2004 | Good |  | 2 | Electrical Control Room, forced air Heating System, Electric Unit Heater, by Stelpro; 3kW, 240/1/60; |  |  |  | 00017169 | Mt Alberta North ET Electrical Control Room | M00132 | [8 empty] | Building Mechanical | 40402 |  |  | W-WW | 3000 | The asset was observed to be in good condition. Asset to be replaced in the long term. | [7 empty] | 0 |  | IMG_6361
| 5051 | MAN | 6 | Electrical Control Room Interior Door (Single) | 1 | AC | 2004 | good |  | 2 |  |  |  |  | 00017169 | [15 empty] | 3500 | The asset was observed to be in good condition. Asset to be replaced at the end of service life. | [7 empty] | 0 |  | IMG_4108
| 5019 | MAN | 11 | Electrical Control Room Lighting | 1 | ES | 2004 | good |  | 2 | 1 linear fluorescent lighting fixture and 1 pendent mount |  |  |  | 00017166 | [15 empty] | 1000 | The asset was observed to be in good condition. Asset to be replaced with LED fixtures in next upgrade project. | [7 empty] | 0 |  | PXL_20201111_141749310
| 5125 | MAN | 44 | Electrical Control Room Masonry Blockwalls | 3 | SC | 2004 |  | Mt Albert North ET Capital Project 2 | 2 | [20 empty] | 15000 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Electrical room masonry blockwalls to be replaced at the end of remaining service life. |  |  |  | Provision for structural repairs every 10 years. | 1500 | 2030 |  | 0 |  | IMG_4108
| 5054 | MAN | 6 | Electrical Control Room Wall Paint | 1 | AC | 2004 | good |  | 2 |  |  |  |  | 00017169 | [15 empty] | 1000 | The asset was observed to be in good condition. Asset to be replaced at the end of service life. | [7 empty] | 0 |  | IMG_6363
| 5033 | MAN | 11 | Electrical Duct System and Conduit System | 3 | ES | 2004 | good |  | 2 | Conduit system including conduit, and underground duct for electrical services |  |  |  | #N/A | Glenway RES Outside Sanitary Pumping Station | [7 empty] | Area 2N Linear Water & Wells | [5 empty] | OPERATING | 15000 | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. | [7 empty] | 0 |  | IMG_4102
00078458 | 4989 | MAN | 6 | Elevated Tank Remote OIT Panel | 4 | SIC | 2004 | good |  | 2 | MTENTL |  |  |  | 00017166 | Mt Alberta North ET Valve Room | M10189 | [8 empty] | Instrumentation and Control | KSA0868427 |  |  | W-WW | 30000 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | [7 empty] | 0 |  | PXL_20201111_140549229
00078459 | 4994 | MAN | 6 | Elevated Tank Remote OIT Panel Display and Computer | 2 | SIC | 2004 | good |  | 2 | Advantech Computer |  |  |  | 00017166 | Mt Alberta North ET Valve Room | M10189 | [8 empty] | Instrumentation and Control | AFC1000532 |  |  | W-WW | 5000 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | [7 empty] | 0 |  | PXL_20201111_140549229
| 5063 | MAN | 44 | Elevated Tank Aluminum Ladder (Ground to Platform) | 4 | SC | 2004 | good | Mt Albert North ET Capital Project 1 | 4 |  |  |  |  | 790900018 | [15 empty] | 30000 | The asset was observed to be in poor condition. Fall arrest system (TS rail) is required to be replaced immediately. | The Class Frontal-Fixed Rail Ladder (Class FRL) fall protection system was installed throughout, and it was no longer compliant to current CSA standards. |  |  |  | 15000 | 2020 |  | 0 |  | IMG_4103
| 5065 | MAN | 44 | Elevated Tank Aluminum Ladder (Platform to Roof) | 4 | SC | 2004 | Good | Mt Albert North ET Capital Project 1 | 4 | Platform to roof |  |  |  | 790900018 | [15 empty] | 20000 | The asset was observed to be in poor condition. Fall arrest system (TS rail) is required to be replaced immediately. | The Class Frontal-Fixed Rail Ladder (Class FRL) fall protection system was installed throughout, and it was no longer compliant to current CSA standards. |  |  |  | 10000 | 2020 |  | 0 |  | IMG_4095
| 5086 | MAN | 44 | Elevated Tank Aluminum Ladder (Platform to Tank Bottom Hatch) | 4 | SC | 2004 | Good | Mt Albert North ET Capital Project 1 | 4 | Platform to tank hatch |  |  |  | 790900018 | [15 empty] | 2500 | The asset was observed to be in poor condition. Fall arrest system (TS rail) is required to be replaced immediately. | The Class Frontal-Fixed Rail Ladder (Class FRL) fall protection system was installed throughout, and it was no longer compliant to current CSA standards. |  |  |  | 1000 | 2020 |  | 0 |  | IMG_4065
| 5066 | MAN | 44 | Elevated Tank Aluminum Ladder (Roof to Tank) | 4 | SC | 2004 | poor | Mt Albert North ET Capital Project 1 | 4 | Roof to tank |  |  |  | 790900018 | [15 empty] | 20000 | The asset was observed to be in poor condition. Fall arrest system (TS rail) is required to be replaced immediately. Touchup for the ladder is recommended. It should be replaced with stainless-steel 316L type for NSF approved coating. Elevated tank ladde | Rail slide was bent. The Class Frontal-Fixed Rail Ladder (Class FRL) fall protection system was installed throughout, and it was no longer compliant to current CSA standards. | The ladder appear to be painted galvanised carbon steel type. Minor metal staining was noted. |  | Replace rail slide. | 20000 | 2020 |  | 0 |  | IMG_4072
| 5064 | MAN | 44 | Elevated Tank Aluminum Upper Platform | 3 | SC | 2004 | good |  | 2 |  |  |  |  | 790900018 | [15 empty] | 50000 | The asset was observed to be in good condition. Elevated tank aluminum platform to be replaced at the end of remaining service life. | [7 empty] | 0 |  | IMG_4103
| 5087 | MAN | 24 | Elevated Tank Anchor Point (Platform Level) | 4 | HSS | 2004 | good |  | 2 |  |  |  |  | 790900018 | [15 empty] | 2000 | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. | [7 empty] | 0 |  | IMG_4066
| 5088 | MAN | 24 | Elevated Tank Anchor Point (Roof Level) | 4 | HSS | 2004 | good |  | 2 |  |  |  |  | 790900018 | [15 empty] | 3000 | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. | [7 empty] | 0 |  | IMG_4091
| 5056 | MAN | 44 | Elevated Tank Concrete Structure | 4 | SC | 2004 | good | Mt Albert North ET Capital Project 2 | 2 |  |  |  |  | 790900018 | [15 empty] | 900000 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Elevated tank concrete structure to be replaced at the end of remaining service life. |  |  |  | Provision for structural repairs every 10 years. | 50000 | 2030 |  | 0 |  | IMG_4103
00078462 | 4990 | MAN | 6 | Elevated Tank Control Panel UPS | 3 | SIC | 2004 | good |  | 2 | Inside of Elevated Tank MTETNL PAC Panel |  |  |  | 00017169 | Mt Alberta North ET Electrical Control Room | M10181 | [8 empty] | Instrumentation and Control | GH442A1091 |  |  | W-WW | 3000 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | [7 empty] | 0 |  | IMG_6352
| 5070 | MAN | 24 | Elevated Tank Davit Socket Base (Platform Level) | 4 | HSS | 2004 | good |  | 2 |  |  |  |  | 790900018 | [15 empty] | 4000 | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. | [7 empty] | 0 |  | IMG_4101
| 5071 | MAN | 24 | Elevated Tank Davit Socket Base (Roof Level) | 4 | HSS | 2004 | good |  | 2 |  |  |  |  | 790900018 | [15 empty] | 4000 | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. | [7 empty] | 0 |  | IMG_4093
| 5073 | MAN | 14 | Elevated Tank Exterior Coating | 3 | SCS | 2004 | good |  | 3 |  |  |  |  | 790900018 | [15 empty] | 780000 | The asset was observed to be in fair condition. Exterior tank cleaning, coating inspection, and touch-up should be carried out every five years. Fully replacement of coating is recommended in long term. | [7 empty] | 0 |  | IMG_4055
00042848 | 5022 | MAN | 6 | Elevated Tank Flow Transmitter | 2 | SIC | 2004 | good |  | 2 |  |  |  |  | 00017166 | [15 empty] | 10000 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | [7 empty] | 0 |  | PXL_20201111_140503354
| 5029 | MAN | 44 | Elevated Tank Grounding | 3 | ES | 2004 | good |  | 2 |  |  |  |  | 790900018 | [15 empty] | 10000 | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. | [7 empty] | 0 |  | IMG_4100
00024535 | 4962 | MAN | 24 | Elevated Tank Inlet Line Butterfly Valve 1 | 3 | PM | 2004 | Minor surface corrosion | Mt Albert North ET Capital Project 1 | 3 | 300mm butterfly valve, manufacturer: Clow Kennedy |  |  |  | 00017166 | Mt Alberta North ET Valve Room | M00554 | [8 empty] | Process Mechanical |  |  |  | W-WW | 3000 | The asset was observed to be in fair condition. Resurface and repaint to protect against corrosion. Replace the asset at the end of its service life. | Minor surface corrosion was observed. |  |  | Resurface and repaint to protect against corrosion. | 500 | 2025 |  | 0 |  | IMG_6257
00024534 | 4969 | MAN | 24 | Elevated Tank Inlet Line Butterfly Valve 2 | 3 | PM | 2004 | Minor surface corrosion | Mt Albert North ET Capital Project 1 | 3 | 300mm butterfly valve, manufacturer: Clow Kennedy |  |  |  | 00017166 | Mt Alberta North ET Valve Room | M00554 | [8 empty] | Process Mechanical |  |  |  | W-WW | 3000 | The asset was observed to be in fair condition. Resurface and repaint to protect against corrosion. Replace the asset at the end of its service life. | Minor surface corrosion was observed. |  |  | Resurface and repaint to protect against corrosion. | 500 | 2025 |  | 0 |  | IMG_6248
00024546 | 4968 | MAN | 24 | Elevated Tank Inlet Line Check Valve | 3 | PM | 2004 | Minor surface corrosion | Mt Albert North ET Capital Project 1 | 3 | 300mm check valve, manufacturer: Clow Kennedy |  |  |  | 00017166 | Mt Alberta North ET Valve Room | M00856 | [8 empty] | Process Mechanical |  |  |  | W-WW | 5000 | The asset was observed to be in fair condition. Resurface and repaint to protect against corrosion. Replace the asset at the end of its service life. | Minor surface corrosion was observed. |  |  | Resurface and repaint to protect against corrosion. | 500 | 2025 |  | 0 |  | IMG_6260
| 5042 | MAN | 44 | Elevated Tank Inlet Line Piping | 4 | PM | 2004 | Good | Mt Albert North ET Capital Project 1 | 2 | Diameter: 300mm, Length(portion in elevated tank): 30 meters |  |  |  | 790900018 | [15 empty] | 33000 | The asset was observed to be in good condition. Replace the asset at the end of its service life. | Minor surface corrosion was observed. |  |  |  | 500 | 2025 |  | 0 |  | IMG_6273
| 5084 | MAN | 44 | Elevated Tank Inlet Pipe Support | 2 | SC | 2004 | good |  | 2 |  |  |  |  | 790900018 | [15 empty] | 30000 | The asset was observed to be in good condition. Elevated tank inlet pipe support to be replaced at the end of remaining service life. | [7 empty] | 0 |  | IMG_4103
00024541 | 4983 | MAN | 24 | Elevated Tank Inlet/Outlet Line Butterfly Valve | 3 | PM | 2004 | Minor surface corrosion | Mt Albert North ET Capital Project 1 | 3 | 300mm butterfly valve, manufacturer: Clow Kennedy |  |  |  | 00017166 | Mt Alberta North ET Valve Room | M00554 | [8 empty] | Process Mechanical |  |  |  | W-WW | 3000 | The asset was observed to be in fair condition. Resurface and repaint to protect against corrosion. Replace the asset at the end of its service life. | Minor surface corrosion was observed. |  |  | Resurface and repaint to protect against corrosion. | 500 | 2025 |  | 0 |  | IMG_6266
| 5041 | MAN | 44 | Elevated Tank Inlet/Outlet Line Piping | 4 | PM | 2004 | Good | Mt Albert North ET Capital Project 1 | 2 | Diameter: 300mm, Length(portion in elevated tank): 10 meters |  |  |  | 790900018 | [15 empty] | 11000 | The asset was observed to be in good condition. Replace the asset at the end of its service life. | Minor surface corrosion was observed. |  |  |  | 1000 | 2025 |  | 0 |  | IMG_6280
| 5013 | MAN | 24 | Elevated Tank Inlet/Outline Gate Valve 1 | 3 | PM | 2004 | Good | Mt Albert North ET Capital Project 1 | 2 | 300mm gate valve, installed in outdoor chamber |  |  |  | 790900018 | [15 empty] | 3000 | The asset was observed to be in good condition. Resurface and repaint to protect against corrosion. Replace the asset at the end of its service life. | Minor surface corrosion was observed due to environmental conditions. |  |  | Resurface and repaint to protect against corrosion. | 500 | 2025 |  | 0 |  | IMG_6422
| 5011 | MAN | 24 | Elevated Tank Inlet/Outline Gate Valve 2 | 3 | PM | 2004 | Good | Mt Albert North ET Capital Project 1 | 3 | 300mm gate valve, installed in outdoor chamber |  |  |  | 790900018 | [15 empty] | 3000 | The asset was observed to be in fair condition. Resurface and repaint to protect against corrosion. Replace the asset at the end of its service life. | Minor surface corrosion was observed due to environmental conditions. |  |  | Resurface and repaint to protect against corrosion. | 500 | 2025 |  | 0 |  | IMG_6408
| 5012 | MAN | 24 | Elevated Tank Inlet/Outline Gate Valve 3 | 3 | PM | 2004 | Good | Mt Albert North ET Capital Project 1 | 2 | 300mm gate valve, installed in outdoor chamber |  |  |  | 790900018 | [15 empty] | 3000 | The asset was observed to be in good condition. Resurface and repaint to protect against corrosion. Replace the asset at the end of its service life. | Minor surface corrosion was observed due to environmental conditions. |  |  | Resurface and repaint to protect against corrosion. | 500 | 2025 |  | 0 |  | IMG_6385
| 5074 | MAN | 14 | Elevated Tank Interior Coating | 3 | SCS | 2004 | good | Mt Albert North ET Capital Project 1 | 3 |  |  |  |  | 790900018 | [15 empty] | 450000 | The asset was observed to be in fair condition. Application of missing interior coating should be completed in the short term. Full replacement of coating is recommended in long term. | Mineral staining was noted on the inside of the tank, below the water line. | The submarine hatch was hot dipped galvanised but not painted as it acted as a sacrificial anode. Now the zinc painted was gone so it should be painted. |  |  | 35000 | 2023 |  | 0 |  | IMG_4072
00041442 | 4993 | MAN | 6 | Elevated Tank Level Indicating Transmitter | 3 | SIC | 2004 | good |  | 2 | MTETNL_TWR_LIT1 |  |  |  | 790900018 | Mt Alberta North Elevated Tank | M00405 | [8 empty] | Instrumentation and Control | E904901509C |  |  | W-WW | 12000 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | [7 empty] | 0 |  | PXL_20201111_140316939
| 5030 | MAN | 11 | Elevated Tank Lightning Protection System | 3 | ES | 2004 | good |  | 2 | 1 lightning air protection terminal |  |  |  | 790900018 | [15 empty] | 5000 | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. | [7 empty] | 0 |  | IMG_4082
00078460 | 5035 | MAN | 6 | Elevated Tank MTETNL PAC Panel | 4 | SIC | 2004 | good |  | 2 |  |  |  |  | 00017169 | [15 empty] | 50000 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | [7 empty] | 0 |  | IMG_6352
00078461 | 4988 | MAN | 6 | Elevated Tank NAC Panel | 4 | SIC | 2004 | good |  | 2 | Network Access Closet Panel, Xmtetnl1 |  |  |  | 00017169 | Mt Alberta North ET Electrical Control Room | 1002018 | [8 empty] | Instrumentation and Control | 14E-088/MTETNL_NAC |  |  | W-WW | 60000 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | [7 empty] | 0 |  | PXL_20201111_142225191
| 4997 | MAN | 15 | Elevated Tank Ninth Line Access Gate | 1 | SW | 2004 | Good. |  | 2 | 6.0m wide double gate located on Ninth Line |  |  |  | 790900018 | [15 empty] | 3000 | The asset was observed to be in good condition. Asset to be replaced in the long term. | [7 empty] | 0 |  | IMG_20201111_094635
| 5032 | MAN | 11 | Elevated Tank Obstruction Lighting System | 3 | ES | 2004 | good |  | 2 | Dual head lights |  |  |  | 790900018 | [15 empty] | 3100 | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. | [7 empty] | 0 |  | IMG_4082
00024537 | 4965 | MAN | 24 | Elevated Tank Outlet Line Butterfly Valve 1 | 3 | PM | 2004 | minor surface corrosion | Mt Albert North ET Capital Project 1 | 3 | Outlet Control Isolation Butterfly valve, size: 300mm, manufacturer: Clow Kennedy |  |  |  | 00017166 | Mt Alberta North ET Valve Room | M00554 | [8 empty] | Process Mechanical |  |  |  | W-WW | 3000 | The asset was observed to be in fair condition. Resurface and repaint to protect against corrosion. Replace the asset at the end of its service life. | Minor surface corrosion was observed. |  |  | Resurface and repaint to protect against corrosion. | 500 | 2025 |  | 0 |  | IMG_6284
00024538 | 4975 | MAN | 24 | Elevated Tank Outlet Line Butterfly Valve 2 | 3 | PM | 2004 | Minor surface corrosion | Mt Albert North ET Capital Project 1 | 3 | Outlet Control Isolation Butterfly valve, size: 300mm, manufacturer: Clow Kennedy |  |  |  | 00017166 | Mt Alberta North ET Valve Room | M00554 | [8 empty] | Process Mechanical |  |  |  | W-WW | 3000 | The asset was observed to be in fair condition. Resurface and repaint to protect against corrosion. Replace the asset at the end of its service life. | Minor surface corrosion was observed. |  |  | Resurface and repaint to protect against corrosion. | 500 | 2025 |  | 0 |  | IMG_6293
00024540 | 4977 | MAN | 24 | Elevated Tank Outlet Line Butterfly Valve 3 | 3 | PM | 2004 | good | Mt Albert North ET Capital Project 1 | 3 | Outlet Control Isolation Butterfly valve, size: 300mm, manufacturer: Clow Kennedy |  |  |  | 00017166 | Mt Alberta North ET Valve Room | M00554 | [8 empty] | Process Mechanical |  |  |  | W-WW | 3000 | The asset was observed to be in fair condition. Resurface and repaint to protect against corrosion. Replace the asset at the end of its service life. | Minor surface corrosion was observed. |  |  | Resurface and repaint to protect against corrosion. | 500 | 2025 |  | 0 |  | IMG_6305
00024547 | 4963 | MAN | 24 | Elevated Tank Outlet Line Flow Control Valve | 4 | PM | 2004 | Good | Mt Albert North ET Capital Project 1 | 3 | 300 mm solenoid operated flow control valve, manufacturer: Singer Model S106 |  |  |  | 00017166 | Mt Alberta North ET Valve Room | M00818 | [8 empty] | Process Mechanical | 504-97 |  |  | W-WW | 12000 | The asset was observed to be in fair condition. Resurface and repaint to protect against corrosion. Replace the asset at the end of its service life. | Minor surface corrosion was observed. |  |  | Resurface and repaint to protect against corrosion. | 500 | 2025 |  | 0 |  | IMG_6313
| 5043 | MAN | 44 | Elevated Tank Outlet Line Piping | 4 | PM | 2004 | Good |  | 2 | Diameter: 300mm, Length(portion in elevated tank): 39 meters |  |  |  | 790900018 | [15 empty] | 43000 | The asset was observed to be in good condition. Replace the asset at the end of its service life. | [7 empty] | 0 |  | IMG_6298
00076067 | 5025 | MAN | 6 | Elevated Tank Outlet Pipe Pressure Transmitter | 3 | SIC | 2004 | good |  | 2 |  |  |  |  | 00017166 | [15 empty] | 8500 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | [7 empty] | 0 |  | PXL_20201111_140526897
| 5085 | MAN | 44 | Elevated Tank Outlet Pipe Support | 2 | SC | 2004 | good |  | 2 |  |  |  |  | 790900018 | [15 empty] | 30000 | The asset was observed to be in good condition. Elevated tank outlet pipe support to be replaced at the end of remaining service life. | [7 empty] | 0 |  | IMG_4103
00017764 | 4952 | MAN | 6 | Elevated Tank Outlet Piping Chlorine Analyzer | 3 | SIC | 2004 | good |  | 2 | MTETNL_TWR_AIT1 Free Residual Chlorine Analyzer |  |  |  | 00017166 | Mt Alberta North ET Valve Room | M00482 | [8 empty] | Instrumentation and Control | 40300009396 |  |  | W-WW | 15000 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | [7 empty] | 0 |  | PXL_20201111_140257952
00024539 | 4964 | MAN | 24 | Elevated Tank Overflow Bypass Line Butterfly Valve 1 | 2 | PM | 2004 | Good |  | 2 | 150mm butterfly valve, manufacturer: Clow Kennedy |  |  |  | 00017166 | Mt Alberta North ET Valve Room | M00554 | [8 empty] | Process Mechanical |  |  |  | W-WW | 2000 | The asset was observed to be in good condition. Replace the asset at the end of its service life. | [7 empty] | 0 |  | IMG_6295
00024536 | 4966 | MAN | 24 | Elevated Tank Overflow Bypass Line Butterfly Valve 2 | 2 | PM | 2004 | good |  | 2 | 150mm butterfly valve, manufacturer: Clow Kennedy |  |  |  | 00017166 | Mt Alberta North Elevated Tank | M00554 | [8 empty] | Process Mechanical |  |  |  | W-WW | 2000 | The asset was observed to be in good condition. Replace the asset at the end of its service life. | [7 empty] | 0 |  | IMG_6244
00024544 | 4967 | MAN | 24 | Elevated Tank Overflow Bypass Line Butterfly Valve 3 | 2 | PM | 2004 | Minor surface corrosion | Mt Albert North ET Capital Project 1 | 3 | 150mm butterfly valve, manufacturer: Clow Kennedy |  |  |  | 00017166 | Mt Alberta North ET Valve Room | M00554 | [8 empty] | Process Mechanical |  |  |  | W-WW | 2000 | The asset was observed to be in fair condition. Resurface and repaint to protect against corrosion. Replace the asset at the end of its service life. | Minor surface corrosion was observed. |  |  | Resurface and repaint to protect against corrosion. | 500 | 2025 |  | 0 |  | IMG_6280
| 5045 | MAN | 44 | Elevated Tank Overflow Bypass Line Piping | 3 | PM | 2004 | Good |  | 2 | Diameter: 150mm, Length(portion in elevated tank): 5 meters |  |  |  | 790900018 | [15 empty] | 3000 | The asset was observed to be in good condition. Replace the asset at the end of its service life. | [7 empty] | 0 |  | IMG_6253
| 5044 | MAN | 44 | Elevated Tank Overflow Line Piping | 4 | PM | 2004 | Good |  | 2 | Diameter: 300mm, Length(portion in elevated tank): 43 meters |  |  |  | 790900018 | [15 empty] | 47000 | The asset was observed to be in good condition. Replace the asset at the end of its service life. | [7 empty] | 0 |  | IMG_4103
| 5020 | MAN | 11 | Elevated Tank Pedestal and Access Tube Lighting | 2 | ES | 2004 | good |  | 2 | 8 fixtures in total |  |  |  | 00017166 | [15 empty] | 20000 | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. | [7 empty] | 0 |  | PXL_20201111_140004696
| 5036 | MAN | 44 | Elevated Tank Removable Louvred Vent | 1 | BM | 2004 | good |  | 2 |  |  |  |  | 790900018 | [15 empty] | 5000 | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | [7 empty] | 0 |  | IMG_4064
| 4998 | MAN | 15 | Elevated Tank Ridge Gate Cres Access Gate | 1 | SW | 2004 | Good |  | 2 | 6.0m wide double gate for Ridge Gate crescent |  |  |  | 790900018 | [15 empty] | 3000 | The asset was observed to be in good condition. Asset to be replaced in the long term. | [7 empty] | 0 |  | IMG_20201111_102248
| 5067 | MAN | 44 | Elevated Tank Roof Access Hatch | 3 | SC | 2004 | good |  | 2 |  |  |  |  | 790900018 | [15 empty] | 10000 | The asset was observed to be in good condition. Elevated tank roof access hatch to be replaced at the end of remaining service life. | [7 empty] | 0 |  | IMG_4089
| 5069 | MAN | 44 | Elevated Tank Roof Guardrail | 3 | SC | 2004 | good |  | 2 |  |  |  |  | 790900018 | [15 empty] | 25000 | The asset was observed to be in good condition. Elevated tank roof guardrail to be replaced at the end of remaining service life. | [7 empty] | 0 |  | IMG_4087
| 5116 | MAN | 24 | Elevated Tank Roof Vent | 3 | PM | 2004 | good |  | 2 |  |  |  |  | 790900018 | [15 empty] | 5000 | The asset was observed to be in good condition. Replace the asset at the end of its service life. | [7 empty] | 0 |  | IMG_4089
| 5026 | MAN | 6 | Elevated Tank Security System | 3 | SIC | 2004 | good |  | 2 |  |  |  |  | 00017169 | [15 empty] | 30000 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | [7 empty] | 0 |  | PXL_20201111_141948382
| 5057 | MAN | 44 | Elevated Tank Steel Tank | 5 | SC | 2004 | minor corrosion |  | 2 |  |  |  |  | 790900018 | [15 empty] | 1300000 | The asset was observed to be in good condition. Elevated tank steel tank to be replaced at the end of remaining service life. | Minor corrosion was observed. | [6 empty] | 0 |  | IMG_4055
| 5072 | MAN | 44 | Elevated Tank Submarine Floor Hatch | 2 | SC | 2004 | good | Mt Albert North ET Capital Project 1 | 2 |  |  |  |  | 790900018 | [15 empty] | 5000 | The asset was observed to be in good condition. It acted as a sacrifical anode; however the zinc paint is gone, it should be repainted. | The submarine hatch was hot dipped galvanised but not painted, so it acted as a sacrificial anode. Now the zinc was gone so it should be painted. |  |  |  | 3000 | 2023 |  | 0 |  | IMG_4065
| 5068 | MAN | 44 | Elevated Tank Tank Access Hatch | 3 | SC | 2004 | good |  | 2 |  |  |  |  | 790900018 | [15 empty] | 10000 | The asset was observed to be in good condition. Elevated tank tank access hatch to be replaced at the end of remaining service life. | [7 empty] | 0 |  | IMG_4088
| 5009 | MAN | 44 | Elevated Tank Watermain | 4 | SW | 2004 |  |  | 3 | 300mm watermain, approximately 65m in length |  |  |  | 790900018 | [15 empty] | 71000 | The asset was assumed to be in fair condition. | [7 empty] | 0
00024565 | 5047 | MAN | 6 | Exterior Access Double Doors | 1 | AC | 2004 | corrosion at bottom of doors and door frame |  | 3 | double metal door |  |  |  | 00017168 | Mt Alberta North ET Foyer | [9 empty] | Architectural |  |  |  | W-WW | 5500 | The asset was observed to be in fair condition. Asset to be replaced at the end of service life. | Corrosion was observed at bottom of door and door frame. | [6 empty] | 0 |  | IMG_4128
| 5040 | MAN | 6 | Fire Extinguisher | 1 | HSS | 2004 | good |  | 2 | 1 Fire Extinguisher |  |  |  | 00017169 | [15 empty] | 300 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | [7 empty] | 0 |  | PXL_20201111_140246229
00032809 | 4982 | MAN | 44 | Fire Hydrant | 1 | SW | 2004 | Hydrant valve box settled (and ground around) by approximately 0.5m | Mt Albert North ET Capital Project 1 | 3 | Fire Hydrant and valve |  |  |  | 790900018 | Mt Alberta North Elevated Tank | M00100 | [8 empty] | Siteworks |  |  |  | W-WW | 10000 | The asset was observed to be in fair condition. Raise valve box to grade and regrade. | Hydrant valve box settled (and ground around) by approximately 0.5m. |  |  | Raise valve box to grade and regrade. | 1000 | 2024 |  | 0 |  | IMG_20201111_094823
| 5059 | MAN | 44 | Foyer Aluminum Guardrails | 3 | SC | 2004 | good |  | 2 |  |  |  |  | 00017168 | [15 empty] | 3000 | The asset was observed to be in good condition. Foyer aluminum guardrails to be replaced at the end of remaining service life. | [7 empty] | 0 |  | IMG_4104
| 5058 | MAN | 44 | Foyer Aluminum Staircase | 3 | SC | 2004 | good |  | 2 |  |  |  |  | 00017168 | [15 empty] | 6000 | The asset was observed to be in good condition. Foyer aluminum staircase to be replaced at the end of remaining service life. | [7 empty] | 0 |  | IMG_4107
| 5014 | MAN | 11 | Foyer Lighting Fixtures | 1 | ES | 2004 | good |  | 2 | 5 lighting fixtures including 4 incandescent lighting fixtures and 1 emergency lighting fixture. |  |  |  | 790900018 | [15 empty] | 3000 | The asset was observed to be in good condition. The incandescent lighting fixtures to be replaced with LED fixtures rated for wet locations in next upgrade. | [7 empty] | 0 |  | PXL_20201111_140000689
| 5053 | MAN | 6 | Foyer Wall Paint | 1 | AC | 2004 | peeled paint at bottom |  | 3 |  |  |  |  | 00017168 | [15 empty] | 1000 | The asset was observed to be in fair condition. Asset to be replaced at the end of service life. | Peeled paint at bottom was observed. | [6 empty] | 0 |  | IMG_4107
00086712 | 5015 | MAN | 11 | Generator Transfer Switch Panel | 3 | ES | 2004 | good |  | 2 | Siemens Generator Transfer Switch Panel, EQ load centre, 120/240V, 30A |  |  |  | 00017169 | [15 empty] | 5000 | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. | [7 empty] | 0 |  | PXL_20201111_141718982
00024561 | 4970 | MAN | 11 | Inlet Piping Heat Tracing Control Panel | 3 | ES | 2004 | good |  | 2 | Heat Tracing and Monitoring Control Panel for inlet piping |  |  |  | 00017169 | Mt Alberta North ET Electrical Control Room | [9 empty] | Electrical System | 15835 |  |  | W-WW | 5000 | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. | [7 empty] | 0 |  | PXL_20201111_141759008
00024561 | 5028 | MAN | 11 | Inlet Piping Heat Tracing System | 3 | ES | 2004 | good |  | 2 | Inlet Piping Heat Tracing System |  |  |  | 00017169 | [11 empty] | 15835 |  |  |  | 10000 | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. | [7 empty] | 0 |  | IMG_4103
00024558 | 4973 | MAN | 11 | Lighting Panel | 3 | ES | 2004 | good |  | 2 | Siemens Panel Board P1; 120/240V, 1PH, 30CCT, a 100A main breaker is included. |  |  |  | 00017169 | Mt Alberta North ET Electrical Control Room | M00125 | [8 empty] | Electrical System |  |  |  | W-WW | 12000 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | [7 empty] | 0 |  | PXL_20201111_142000666
00078396 | 4991 | MAN | 6 | NAC Panel Network Ethernet Switch | 3 | SIC | 2004 | good |  | 2 | inside Network Access Closet Panel |  |  |  | 00017169 | Mt Alberta North ET Electrical Control Room | M01002 | [8 empty] | Instrumentation and Control | FOC1847Z2E7 |  |  | W-WW | 5000 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | [7 empty] | 0 |  | PXL_20201111_142225191
00078463 | 4992 | MAN | 6 | NAC Panel Network Radio | 3 | SIC | 2004 | good |  | 2 | Inside NAC Panel |  |  |  | 00017169 | Mt Alberta North ET Electrical Control Room | M00455 | [8 empty] | Instrumentation and Control | 0001966911 |  |  | W-WW | 5000 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | [7 empty] | 0 |  | PXL_20201111_142225191
00017760 | 4953 | MAN | 6 | Network Antenna 1 | 3 | SIC | 2004 | good |  | 2 | MTNTRAD103 Network Antenna & Cable |  |  |  | 790900018 | Mt Alberta North ET Valve Room | [9 empty] | SCADA |  |  |  | W-WW | 10000 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | [7 empty] | 0 |  | IMG_4087
00017761 | 4954 | MAN | 6 | Network Antenna 2 | 2 | SIC | 2004 | good |  | 2 | MTNTRAD104 |  |  |  | 790900018 | Mt Alberta North ET Valve Room | [9 empty] | SCADA |  |  |  | W-WW | 10000 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | [7 empty] | 0 |  | IMG_4084
| 5021 | MAN | 11 | Outdoor Lighting | 1 | ES | 2004 | good |  | 2 | 2 fixtures |  |  |  | 790900018 | [15 empty] | 2400 | The asset was observed to be in good condition. Asset to be replaced with LED fixtures in the next upgrade project. | [7 empty] | 0 |  | PXL_20201111_134832486
00024560 | 4961 | MAN | 11 | Outlet Piping Heat Tracing Control Panel | 3 | ES | 2004 | good |  | 2 | Heat Tracing and Monitoring Control Panel for outlet piping |  |  |  | 00017169 | Mt Alberta North ET Electrical Control Room | [9 empty] | Electrical System | 15837 |  |  | W-WW | 5000 | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. | [7 empty] | 0 |  | PXL_20201111_141847648
| 5027 | MAN | 11 | Outlet Piping Heat Tracing System | 3 | ES | 2004 | good |  | 2 | Outlet Piping Heat Tracing System |  |  |  | 00017169 | [11 empty] | 15837 |  |  |  | 10000 | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. | [7 empty] | 0 |  | IMG_4103
| 5008 | MAN | 44 | Overflow Piping | 4 | SW | 2004 |  | Mt Albert North ET Capital Project 1 | 3 | 300mm, length: 16.0m |  |  |  | 790900018 | [15 empty] | 15000 | The asset was assumed to be in fair condition. Regrade area around pipe outlet to allow for above grade overflow outlet with grating on pipe. Place riprap at outlet. |  |  |  | Regrade area around pipe outlet to allow for above grade overflow outlet with grating on pipe. Place riprap at outlet. | 10000 | 2024 |  |  |  | IMG_20201111_100602
| 5007 | MAN | 19 | Pavement | 2 | SW | 2004 | Asphalt had cracking for entire length of driveway, with severe damage by elevated tank. | Mt Albert North ET Capital Project 1 | 3 | Asphalt pavement (incl. granular base) within site, from Ninth line entrance to elevated tank entrance. Approx. 450m2 |  |  |  | 790900018 | [15 empty] | 35000 | The asset was observed to be in fair condition. Conduct pavement evaluation, and confirm if road resurfacing is sufficient or full reconstruction required. Pavement to be replaced at the end of remaining service life. | Asphalt had cracking for entire length of driveway, with severe damage by elevated tank. | Damage of asphalt at entrance of site was observed. |  | Conduct pavement evaluation, and confirm if road resurfacing is sufficient or full reconstruction required. | 15000 | 2024 |  | 0 |  | IMG_20201111_100101
| 5037 | MAN | 44 | Plumbing and Drainage | 2 | BM | 2004 | good |  | 2 | 100mm drainage piping for floor drain and future washroom. Piping is connected to 100mm sanitary main. Length(approximately): 20 meters |  |  |  | 790900018 | [15 empty] | 10000 | The asset was assumed to be in good condition based on its age. Asset to be replaced at the end of remaining service life. | [7 empty] | 0 |  | IMG_4121
00078315 | 5038 | MAN | 6 | Portable Emergency Eyewash | 2 | HSS | 2004 | good |  | 2 | Portable type |  |  |  | 00017166 | [15 empty] | 600 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | [7 empty] | 0 |  | PXL_20201111_140206405
00080565 | 4995 | MAN | 11 | Portable Generator | 2 | ES | 2004 | good |  | 2 | Portable Gasoline Generator, Manufacturer: Comet |  |  |  | 790900018 | Mt Alberta North Elevated Tank | M00506 | [8 empty] | Electrical System | EAAJ 1069727 |  |  | W-WW | 2000 | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. | [7 empty] | 0 |  | PXL_20201111_142703597
00017766 | 4955 | MAN | 6 | Radio Modem | 3 | SIC | 2004 | good |  | 2 | MTNTRAD101, Network, Radio Modem |  |  |  | 790900018 | Mt Alberta North ET Valve Room | M01018 | [8 empty] | SCADA | 1269550 |  |  | W-WW | 5000 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | [7 empty] | 0 |  | IMG_4086
| 5010 | MAN | 44 | Sanitary Sewer | 2 | SW | 2004 |  |  | 3 | 100mm sanitary sewer, approximately 22m in length |  |  |  | 790900018 | [15 empty] | 17500 | The asset was assumed to be in fair condition. | [7 empty] | 0
| 5039 | MAN | 6 | Smoke Detectors | 2 | HSS | 2004 | good |  | 2 | Smoke Detector (2) |  |  |  | 790900018 | [15 empty] | 1000 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | [9 empty] | PXL_20201111_141747449
| 5000 | MAN | 25 | Soft Drainage | 1 | SW | 2004 | Low spots around fire hydrant | Mt Albert North ET Capital Project 1 | 4 | Soft surfaces throughout site, approximate area 1250m2. |  |  |  | 790900018 | [15 empty] | 25000 | The asset was observed to be in poor condition. Regrade area around fire hydrant. Remove top soil and sod and place riprap at outlet of overflow pipe, ensure positive drainage towards property line and but away from adjacent property owner. | Low spots around fire hydrant was observed. | Damaged sod was observed at outlet of overflow pipe. |  | Regrade area around fire hydrant | 7000 | 2024 | Remove top soil and sod and place riprap at outlet of overflow pipe, ensure positive drainage towards property line and but away from adjacent property owner. |  |  | IMG_20201111_102456
| 5092 | MAN | 44 | Storage Room Composite Roof | 3 | SC | 2004 | Good | Mt Albert North ET Capital Project 2 | 2 |  |  |  |  | 790900018 | [15 empty] | 5000 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Storage room composite roof to be replaced at the end of remaining service life. |  |  |  | Provision for structural repairs every 10 years. | 1000 | 2030 |  | 0 |  | IMG_4104
| 5120 | MAN | 44 | Storage Room Concrete Floor Slab | 3 | SC | 2004 |  | Mt Albert North ET Capital Project 2 | 2 |  |  |  |  | 000000001 | [15 empty] | 10000 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. |  |  |  |  | 1000 | 2030 |  | 0 |  | IMG_6344
00024545 | 4974 | MAN | 25 | Storage Room Electric Unit Heater | 2 | BM | 2015 | good |  | 2 | PAC Room, Unit Heater, forced air Heating System, 5 kW; 240/1/60; by Outlet Model OAS05000T |  |  |  | 000000001 | Mt Alberta North ET Foyer | M00132 | [8 empty] | Building Mechanical | 40402 |  |  | W-WW | 3000 | The asset was observed to be in good condition. Storage room electric unit heater to be replaced at the end of remaining service life. | [7 empty] | 0 |  | IMG_6348
| 5062 | MAN | 44 | Storage Room Masonry Blockwalls | 3 | SC | 2004 | good | Mt Albert North ET Capital Project 2 | 2 |  |  |  |  | 000000001 | [15 empty] | 10000 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Storage room masonry blockwalls to be replaced at the end of remaining service life. |  |  |  | Provision for structural repairs every 10 years. | 1000 | 2030 |  | 0 |  | IMG_4123
| 5055 | MAN | 6 | Storage Room Wall Paint | 1 | AC | 2004 | good |  | 2 |  |  |  |  | 00017169 | [15 empty] | 500 | The asset was observed to be in good condition. Asset to be replaced at the end of service life. | [7 empty] | 0 |  | IMG_4123
00078317 | 4985 | MAN | 14 | Sump Pump | 2 | BM | 2004 | good |  | 2 | Submersible centrifugal sump pump |  |  |  | 00017166 | Mt Alberta North ET Valve Room | [9 empty] | Process Mechanical |  |  |  | W-WW | 1000 | The asset was observed to be in good condition. Asset to be replaced in the long term. | [7 empty] | 0 |  | IMG_6325
| 5016 | MAN | 11 | Surge Protection Device | 3 | ES | 2004 | good |  | 2 | Surge Protection Device, PTX 160, 120/240V, 30A |  |  |  | 00017169 | [15 empty] | 6000 | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. | [7 empty] | 0 |  | PXL_20201111_142137604
| 5081 | MAN | 44 | Valve Chamber #1 Access Ladder | 2 | SW | 2004 | good |  | 2 |  |  |  |  | 790900018 | [15 empty] | 1500 | The asset was observed to be in good condition. Asset to be replace at the end of its service life. | [7 empty] | 0 |  | IMG_4135
| 5075 | MAN | 44 | Valve Chamber #1 Manhole Frame and Cover | 2 | SW | 2004 | good | Mt Albert North ET Capital Project 1 | 2 |  |  |  |  | 790900018 | [15 empty] | 1500 | The asset was observed to be in good condition. Align chamber ladder with chamber access hatch. Asset to be replaced at the end of the service life. | Safety issue: chamber ladder and chamber access hatch are not aligned. |  |  | Align chamber ladder with chamber access hatch. | 1000 | 2024 |  | 0 |  | IMG_4056
| 5078 | MAN | 44 | Valve Chamber #1 Precast Concrete Structure | 2 | SW | 2004 | good |  | 2 |  |  |  |  | 790900018 | [15 empty] | 8000 | The asset was observed to be in good condition. Asset to be replace at the end of its service life. | [7 empty] | 0 |  | IMG_4135
| 5082 | MAN | 44 | Valve Chamber #2 Access Ladder | 2 | SW | 2004 | good |  | 2 |  |  |  |  | 790900018 | [15 empty] | 1500 | The asset was observed to be in good condition. Asset to be replace at the end of its service life. | [7 empty] | 0 |  | IMG_4137
| 5076 | MAN | 44 | Valve Chamber #2 Manhole Frame and Cover | 2 | SW | 2004 | good | Mt Albert North ET Capital Project 1 | 2 |  |  |  |  | 790900018 | [15 empty] | 1500 | The asset was observed to be in good condition. Align chamber ladder with chamber access hatch. Asset to be replaced at the end of the service life. | Safety issue: chamber ladder and chamber access hatch are not aligned. |  |  | Align chamber ladder with chamber access hatch. | 1000 | 2024 |  | 0 |  | IMG_4056
| 5079 | MAN | 44 | Valve Chamber #2 Precast Concrete Structure | 2 | SW | 2004 | good |  | 2 |  |  |  |  | 790900018 | [15 empty] | 8000 | The asset was observed to be in good condition. Asset to be replace at the end of its service life. | [7 empty] | 0 |  | IMG_4137
| 5083 | MAN | 44 | Valve Chamber #3 Access Ladder | 2 | SW | 2004 | good |  | 2 |  |  |  |  | 790900018 | [15 empty] | 1500 | The asset was observed to be in good condition. Asset to be replace at the end of its service life. | [7 empty] | 0 |  | IMG_4139
| 5077 | MAN | 44 | Valve Chamber #3 Manhole Frame and Cover | 2 | SW | 2004 | good | Mt Albert North ET Capital Project 1 | 2 |  |  |  |  | 790900018 | [15 empty] | 1500 | The asset was observed to be in good condition. Align chamber ladder with chamber access hatch. Asset to be replaced at the end of the service life. | Safety issue: chamber ladder and chamber access hatch are not aligned. |  |  | Align chamber ladder with chamber access hatch. | 1000 | 2024 |  | 0 |  | IMG_4056
| 5080 | MAN | 44 | Valve Chamber #3 Precast Concrete Structure | 2 | SW | 2004 | good |  | 2 |  |  |  |  | 790900018 | [15 empty] | 8000 | The asset was observed to be in good condition. Asset to be replace at the end of its service life. | [7 empty] | 0 |  | IMG_4139
| 5090 | MAN | 44 | Valve Room Composite Roof | 3 | SC | 2004 | Good | Mt Albert North ET Capital Project 2 | 2 |  |  |  |  | 00017166 | [15 empty] | 20000 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Valve room composite roof to be replaced at the end of remaining service life. | Abandoned process equipment and other equipment was piled up on the roof. |  |  | Provision for structural repairs every 10 years. | 2000 | 2030 |  | 0 |  | IMG_4105
| 5121 | MAN | 44 | Valve Room Concrete Floor Slab | 3 | SC | 2004 |  | Mt Albert North ET Capital Project 2 | 2 |  |  |  |  | 00017166 | [15 empty] | 30000 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. |  |  |  |  | 3000 | 2030 |  | 0 |  | IMG_6253
00024548 | 4976 | MAN | 26 | Valve Room Dehumidifier | 2 | BM | 2016 | good |  | 2 | Dehumidifier, Air Handling System, by Noma; Installation year assumed to be 2016 |  |  |  | 00017166 | Mt Alberta North Elevated Tank | M00153 | [8 empty] | Building Mechanical |  |  |  | W-WW | 300 | The asset was observed to be in good condition. Valve room dehumidifier to be replaced at the end of remaining service life. | [7 empty] | 0 |  | IMG_6321
00024542 | 4978 | MAN | 26 | Valve Room Electric Unit Heater | 2 | BM | 2016 | good |  | 2 | Valve Room, Electric Unit Heater, forced air Heating System, 5 kW; 240/1/60; by Outlet Model OAS05000T |  |  |  | 00017166 | Mt Alberta North ET Valve Room | M00132 | [8 empty] | Building Mechanical |  |  |  | W-WW | 3000 | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life | [7 empty] | 0 |  | IMG_6335
00024562 | 5050 | MAN | 6 | Valve Room Interioir Double Doors | 1 | AC | 2004 | corrosion at bottom of door frame |  | 3 | double metal door |  |  |  | 00017166 | Mt Alberta North ET Valve Room | [9 empty] | Architectural |  |  |  | W-WW | 5500 | The asset was observed to be in fair condition. Asset to be replaced at the end of service life. | Corrosion was observed at bottom of door frame. | [6 empty] | 0 |  | IMG_4109
00024566 | 5046 | MAN | 6 | Valve Room Interior Single Door | 1 | AC | 2004 | corrosion at bottom of door frame |  | 3 | single metal door |  |  |  | 000000001 | Mt Alberta North ET Foyer | [9 empty] | Architectural |  |  |  | W-WW | 3500 | The asset was observed to be in fair condition. Asset to be replaced at the end of service life. | Corrosion was observed at bottom of door frame. | [6 empty] | 0 |  | IMG_4109
| 5017 | MAN | 11 | Valve Room Lighting | 1 | ES | 2004 | good |  | 2 | 2 linear fluorescent lighting fixtures,1 pendent mount, and 2 emergency lighting fixtures. |  |  |  | 00017166 | [15 empty] | 6000 | The asset was observed to be in good condition. The valve room lighting to be replaced with LED fixtures in next upgrade project. | [7 empty] | 0 |  | PXL_20201111_140025870
00078313 | 4984 | MAN | 6 | Valve Room Low Temperature Switch | 2 | SIC | 2004 | good |  | 2 | MTT2TSL101 |  |  |  | 00017166 | Mt Alberta North ET Valve Room | M00076 | [8 empty] | Instrumentation and Control |  |  |  | W-WW | 1000 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | [7 empty] | 0 |  | PXL_20201111_140439546
| 5060 | MAN | 44 | Valve Room Masonry Blockwalls | 3 | SC | 2004 | good | Mt Albert North ET Capital Project 2 | 2 |  |  |  |  | 00017166 | [15 empty] | 30000 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Valve room masonry blockwalls to be replaced at the end of remaining service life. |  |  |  | Provision for structural repairs every 10 years. | 3000 | 2030 |  | 0 |  | IMG_4113
| 5052 | MAN | 6 | Valve Room Wall Paint | 1 | AC | 2004 | Minor peeled paint |  | 3 |  |  |  |  | 00017166 | [15 empty] | 2000 | The asset was observed to be in fair condition. Asset to be replaced at the end of service life. | Minor peeled paint was observed. | [6 empty] | 0 |  | IMG_4113