## input_data
Stage | var_full_name | var_name | parameter | variable_explanation
Stage_1 | Report Year | ry | Delin 1 | The year that report is written
Stage_1 | Facility Name | fn | Delin 2 | Name of the facility
Stage_1 | Report Date | rd | Delin 3
Stage_1 | Inspection Date | id | Delin 4
Stage_1 | Facility Address | fa | Delin 5
AC Weighted Service Life | ac_wsl |  | Table 5-1
BM Weighted Service Life | bm_wsl |  | Table 5-1
ES Weighted Service Life | es_wsl |  | Table 5-1
HSS Weighted Service Life | hss_wsl |  | Table 5-1
#REF! | pm_wsl |  | Table 5-1
#REF! | sc_wsl |  | Table 5-1
#REF! | scs_wsl |  | Table 5-1
#REF! | sic_wsl |  | Table 5-1
#REF! | sw_wsl |  | Table 5-1 & ES

## Stage_2
var_full_name | var_name | parameter | variable_explanation | LIFE CYCLE CATEGORY | AVERAGE WEIGHTED ESTIMATED REMAINING SERVICE LIFE (YEARS) | THEORETICAL SERVICE LIFE (YEARS)* | AVERAGE WEIGHTED CONDITION RATING | AVERAGE WEIGHTED cof | AVERAGE WEIGHTED Risk Score | TOTAL REPLACEMENT VALUE ({{ ry }} $)
AC Weighted Service Life | acwsl | 15 | Table 5-1 | Architectural Components (AC) | {{ ac_wsl }}
BM Weighted Service Life | bm_wsl | 30 | Table 5-1 | Building Mechanical (BM) | {{ bm_wsl }}
ES Weighted Service Life | es_wsl | 25 | Table 5-1 | Electrical Systems (ES) | {{ es_wsl }}
HSS Weighted Service Life | hss_wsl | 15 | Table 5-1 | Health and Safety Systems (HSS) | {{ hss_wsl }}
PM Weighted Service Life | pm_wsl | 30 | Table 5-1 | Process Mechanical (PM) | {{ pm_wsl }}
SC Weighted Service Life | sc_wsl | 60 | Table 5-1 | Structural Components (SC) | {{ sc_wsl }}
SCS Weighted Service Life | scs_wsl | 15 | Table 5-1 | Structural Coating System | {{ scs_wsl }}
SIC Weighted Service Life | sic_wsl | 15 | Table 5-1 | SCADA/ Instrumentation/ Control (SIC) | {{ sic_wsl }}
SW Weighted Service Life | sw_wsl | 20 | Table 5-1 & ES | Site Works (SW) | {{ sw_wsl }}
TOTAL

## Table5-1
LIFE CYCLE CATEGORY | AVERAGE WEIGHTED ESTIMATED REMAINING SERVICE LIFE (YEARS) | THEORETICAL SERVICE LIFE (YEARS)* | AVERAGE WEIGHTED CONDITION RATING | AVERAGE WEIGHTED cof | AVERAGE WEIGHTED Risk Score | TOTAL REPLACEMENT VALUE ({{ ry }} $)
Architectural Components (AC) | 15 | 15 | 2.2 | 1 | 2.2 | 42000
Building Mechanical (BM) | 30 | 30 | 2 | 2 | 3.9 | 82000
Electrical Systems (ES) | 25 | 25 | 2.2 | 2.8 | 6.1 | 328500
Health and Safety Systems (HSS) | 15 | 15 | 2 | 3.7 | 7.4 | 10650
Process Mechanical (PM) | 30 | 30 | 2.4 | 3.6 | 8.3 | 333600
Structural Components (SC) | 60 | 60 | 2.2 | 3.8 | 8.1 | 2310500
Structural Coating System | 15 | 25 | 2 | 3 | 6.1 | 1042500
SCADA/ Instrumentation/ Control (SIC) | 15 | 15 | 2.1 | 3.3 | 6.9 | 201000
Site Works (SW) | 20 | 20 | 2.9 | 2.5 | 7.2 | 753600
TOTAL | 0 |  | 2.3 | 3.3 | 7.3 | 5104350

## Raw_Data
assetTag | seqNum | facility | Description | Process | building | inspectorName | LocationTag | LocationORIGINAL | assetName | CategoryCode | manufacturer | TransmitterModel | TransducerModel | TransducerSerial | InstMeva | installYear | installationDate | remainingESL | InstType | ServiceArea | FacilityType | LifeCycleCategory | SerialNo | Parent | RotatingItem | Site | condition | COF | defect1 | defect2 | defect3 | observations | RehabRepairCost | RehabRepairYear | RehabRepairCost2 | RehabRepairYear2 | repCost | photoName | repProjectName | rehabProjectName | rehab2ProjectName | Status | InspectionYear | rehabComment1 | rehabCost1 | rehabComment2 | rehabCost2 | defect1Input | defect2Input | defect3Input
00046041 | 3889 | NN | TWR_HTR-1, Heating System, Unit Heater, capacity: 5kW |  |  |  | 00019632 | Nobleton North ET Valve Room | Valve Room Unit Heater TWR-HTR1 | BM | M00111 |  |  |  |  | 2012 |  | 23 |  | Area 4 Water Treatment |  | Building Mechanical |  |  |  | W-WW | 2 | 2 |  |  |  | The valve room unit heater TWR-HTR1 was observed to be in good condition. Valve room unit heater TWR-HTR1 to be replaced at the end of remaining service life. |  |  |  |  | 7500 | IMG_0492 |  |  |  | OPERATING | 2019 |  |  |  |  | Good
00047975 | 3890 | NN | Unit Heater, Switch, Local Disconnect, max fuse 15A |  |  |  | 00019632 | Nobleton North ET Valve Room | Unit Heater Disconnect Switch | ES | M10181 |  |  |  |  | 2012 |  | 18 |  | Area 4 Water Treatment |  | Building Mechanical |  |  |  | W-WW | 2 | 2 |  |  |  | The unit heater disconnect switch was observed to be in good condition. Asset to be replaced in the long term. |  |  |  |  | 1500 | IMG_0498 | Nobleton North ET Capital Project 2 |  |  | OPERATING | 2019 |  |  |  |  | good
00047980 | 3891 | NN | HTRC2-CP,Outlet, Heating System, Heat Tracing |  |  |  | 00019632 | Nobleton North ET Valve Room | Outlet Header Heat Tracing System | ES | [5 empty] | 2012 |  | 18 |  | Area 4 Water Treatment |  | Building Mechanical | 26093 |  |  | W-WW | 3 | 3 |  |  |  | The outlet header heat tracing system was assumed to be in fair condition. Asset to be replaced in the long term. |  |  |  |  | 10000 |  | Nobleton North ET Capital Project 2 |  |  | OPERATING | 2019
00047981 | 3892 | NN | EFAN1, Ventilation System, Exhaust Fan |  |  |  | 00019632 | Nobleton North ET Valve Room | Valve Room Exhaust Fan EF-1 | BM | M00069 |  |  |  |  | 2012 |  | 23 |  | Area 4 Water Treatment |  | Building Mechanical |  |  |  | W-WW | 2 | 2 |  |  |  | The valve room exhaust fan EF-1 was observed to be in good condition. Valve room exhaust fan EF-1 to be replaced at the end of remaining service life. |  |  |  |  | 5000 | IMG_0487 |  |  |  | OPERATING | 2019 |  |  |  |  | Good
00047988 | 3900 | NN | UTL_HUM, Air Handling System, Dehumidifier, manu: Dectron, model: DA2-007-03, serial: 2011080112, electrical rating: 230V, 1 ph, 60Hz |  |  |  | 00019632 | Nobleton North ET Valve Room | Valve Room Dehumidifier | BM | M00353 |  |  |  |  | 2012 |  | 23 |  | Area 4 Water Treatment |  | Building Mechanical | B2011080112 |  |  | W-WW | 2 | 2 |  |  |  | The valve room dehumidifier was observed to be in good condition. Valve room dehumidifier to be replaced at the end of remaining service life. |  |  |  |  | 10000 | IMG_0489 |  |  |  | OPERATING | 2019 |  |  |  |  | Good
00047989 | 3901 | NN | Intake, Motor Actuated, LVR-1, Ventilation System, Louvre, 500mm x 500mm |  |  |  | 00019632 | Nobleton North ET Valve Room | Valve Room Motorized Intake Louver LVR_1 | BM | M00069 |  |  |  |  | 2012 |  | 23 |  | Area 4 Water Treatment |  | Building Mechanical |  |  |  | W-WW | 2 | 2 |  |  |  | The valve room motorized intake louver LVR_1 was observed to be in good condition. Valve room motorized intake louver LVR_1 to be replaced at the end of remaining service life. |  |  |  |  | 3000 | IMG_0396_ |  |  |  | OPERATING | 2019 |  |  |  |  | Good
00048003 | 3902 | NN | EFAN2, Ventilation System, Exhaust Fan, L/s: 181, RPM: 1050. |  |  |  | 00019609 | Nobleton North ET Chlorine Room | Chlorine Room Exhaust Fan EF-2 | BM | M00069 |  |  |  |  | 2012 |  | 23 |  | Area 4 Water Treatment |  | Building Mechanical |  |  |  | W-WW | 2 | 2 |  |  |  | The chlorine room exhaust fan EF-2 was observed to be in good condition. Chlorine room exhaust fan EF-2 to be replaced at the end of remaining service life. |  |  |  |  | 5000 | IMG_0471 |  |  |  | OPERATING | 2019 |  |  |  |  | Good
00048004 | 3903 | NN | Exhaust Fan 2, Ventilation System, Thermostat |  |  |  | 00019609 | Nobleton North ET Chlorine Room | Chlorine Room Exhaust Fan Thermostat | SIC | M00076 |  |  |  |  | 2012 |  | 8 |  | Area 4 Water Treatment |  | Building Mechanical | T631A 1006 |  |  | W-WW | 2 | 2 |  |  |  | The chlorine room exhaust fan thermostat was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | 1000 | IMG_0468 | Nobleton North ET Capital Project 1 |  |  | OPERATING | 2019 |  |  |  |  | good
00048006 | 3904 | NN | TWR_HTR2, Heating System, Unit Heater, 3kw |  |  |  | 00019609 | Nobleton North ET Chlorine Room | Chlorine Room Unit Heater TWR_HTR2 | BM | M00111 |  |  |  |  | 2012 |  | 23 |  | Area 4 Water Treatment |  | Building Mechanical |  |  |  | W-WW | 2 | 2 |  |  |  | The chlorine room unit heater TWR_HTR2 was observed to be in good condition. Chlorine room unit heater TWR_HTR2 to be replaced at the end of remaining service life. |  |  |  |  | 7500 | IMG_0473 |  |  |  | OPERATING | 2019 |  |  |  |  | Good
00048007 | 3905 | NN | Intake, Motor Actuated, LVR-2, Ventilation System, Louvre, 500x500mm |  |  |  | 00019609 | Nobleton North ET Chlorine Room | Chlorine Room Ventilation Louvre LVR_2 | BM | M00069 |  |  |  |  | 2012 |  | 23 |  | Area 4 Water Treatment |  | Building Mechanical |  |  |  | W-WW | 2 | 2 |  |  |  | The chlorine room ventilation louvre LVR_2 was observed to be in good condition. Chlorine room ventilation louvre LVR_2 to be replaced at the end of remaining service life. |  |  |  |  | 3000 | IMG_0476 |  |  |  | OPERATING | 2019 |  |  |  |  | Good
00048027 | 3906 | NN | Intake, LVR-3, Ventilation System, Louvre |  |  |  | 00019633 | Nobleton North ET Upper Service Platform | Mezzanine Ventilation Louvre LVR_3 | BM | M00069 |  |  |  |  | 2012 |  | 23 |  | Area 4 Water Treatment |  | Building Mechanical |  |  |  | W-WW | 2 | 1 |  |  |  | The mezzanine ventilation louvre LVR_3 was observed to be in good condition. Mezzanine ventilation louvre LVR_3 to be replaced at the end of remaining service life. |  |  |  |  | 3000 | IMG_0506 |  |  |  | OPERATING | 2019 |  |  |  |  | good
00046042 | 3927 | NN | Distribution Transformer, Disconnect Switch, 600V, 60A, 3ph |  |  |  | 00019610 | Nobleton North ET Atrium | Transformer Disconnect Switch | ES | M10181 |  |  |  |  | 2012 |  | 18 |  | Area 4 Water Treatment |  | Electrical Systems |  |  |  | W-WW | 2 | 3 |  |  |  | The transformer disconnect switch was observed to be in good condition. Asset to be replaced in the long term. |  |  |  |  | 1500 | IMG_1453 | Nobleton North ET Capital Project 2 |  |  | OPERATING | 2019 |  |  |  |  | good
00046044 | 3928 | NN | Generator Manual Transfer switch/Load Center, 120V/240V |  |  |  | 00019610 | Nobleton North ET Atrium | SCADA and Network Panel Generator Manual Transfer Switch | ES | M00125 |  |  |  |  | 2012 |  | 18 |  | Area 4 Water Treatment |  | Electrical Systems |  |  |  | W-WW | 2 | 4 |  |  |  | The Scada and network panel generator manual transfer switch was observed to be in good condition. Asset to be replaced in the long term. |  |  |  |  | 2000 | IMG_1336 | Nobleton North ET Capital Project 2 |  |  | OPERATING | 2019 |  |  |  |  | good
00047966 | 3929 | NN | Obstruction Light Controller, Lighting, HID, 120V, 10A |  |  |  | 00019610 | Nobleton North ET Atrium | Obstruction Light Controller | ES | [5 empty] | 2012 |  | 18 |  | Area 4 Water Treatment |  | Electrical Systems |  |  |  | W-WW | 2 | 3 |  |  |  | The obstruction light controller was observed to be in good condition. Asset to be replaced in the long term. |  |  |  |  | 5000 | IMG_1331 | Nobleton North ET Capital Project 2 |  |  | OPERATING | 2019 |  |  |  |  | good
| 3930 | NN | HTRC1-CP, Inlet, Heating System, Heat Tracing |  |  |  | 00019632 | Nobleton North ET Valve Room | Inlet Header Heat Trace Panel | ES | [5 empty] | 2012 |  | 18 |  | Area 4 Water Treatment |  | Electrical Systems | 26092 |  |  | W-WW | 2 | 3 |  |  |  | The inlet header heat trace panel was observed to be in good condition. Asset to be replaced in the long term. |  |  |  |  | 13000 | IMG_1358 | Nobleton North ET Capital Project 2 |  |  | OPERATING | 2019 |  |  |  |  | good
00047973 | 3931 | NN | LP A, Control Panel, Lighting, Weatherproof, 120/208V, 225A, 3ph, 4w |  |  |  | 00019632 | Nobleton North ET Valve Room | Lighting Panel LP-A | ES | M00044 |  |  |  |  | 2012 |  | 18 |  | Area 4 Water Treatment |  | Electrical Systems |  |  |  | W-WW | 2 | 3 |  |  |  | The Lighting Panel LP-A was observed to be in good condition. Asset to be replaced in the long term. |  |  |  |  | 15000 | IMG_1405 | Nobleton North ET Capital Project 2 |  |  | OPERATING | 2019 |  |  |  |  | good
00047974 | 3932 | NN | Transformer, Distribution, 45KVA, 600-120/208V, class 1, Div 2 rated |  |  |  | 00019632 | Nobleton North ET Valve Room | Distribution Transformer | ES | [5 empty] | 2012 |  | 18 |  | Area 4 Water Treatment |  | Electrical Systems | 911ENCL4 |  |  | W-WW | 2 | 4 |  |  |  | The distribution transformer was observed to be in good condition. Asset to be replaced in the long term. |  |  |  |  | 27000 | IMG_1410 | Nobleton North ET Capital Project 2 |  |  | OPERATING | 2019 |  |  |  |  | good
00047976 | 3933 | NN | TVSS, Surge Protection, 600V, 30A, 3ph |  |  |  | 00019632 | Nobleton North ET Valve Room | Surge Protection Device | ES | [5 empty] | 2012 |  | 18 |  | Area 4 Water Treatment |  | Electrical Systems |  |  |  | W-WW | 2 | 4 |  |  |  | The surge protection device was observed to be in good condition. Asset to be replaced in the long term. |  |  |  |  | 2500 | IMG_1447 | Nobleton North ET Capital Project 2 |  |  | OPERATING | 2019 |  |  |  |  | good
00047977 | 3934 | NN | Digital Energy Meter, Metering, 600V, 3ph, 4W |  |  |  | 00019632 | Nobleton North ET Valve Room | Digital Power Meter | ES | M10139 |  |  |  |  | 2012 |  | 18 |  | Area 4 Water Treatment |  | Electrical Systems | 12-12-01-0011 |  |  | W-WW | 2 | 2 |  |  |  | The digital power meter was observed to be in good condition. Asset to be replaced in the long term. |  |  |  |  | 3500 | IMG_1441 | Nobleton North ET Capital Project 2 |  |  | OPERATING | 2019 |  |  |  |  | good
00047978 | 3935 | NN | Main Service Disconnect Switch, 600V, 100A, 3ph |  |  |  | 00019632 | Nobleton North ET Valve Room | Main Disconnect Switch | ES | [5 empty] | 2012 |  | 18 |  | Area 4 Water Treatment |  | Electrical Systems |  |  |  | W-WW | 2 | 3 |  |  |  | The main disconnect switch was observed to be in good condition. Asset to be replaced in the long term. |  |  |  |  | 1500 | IMG_1460 | Nobleton North ET Capital Project 2 |  |  | OPERATING | 2019 |  |  |  |  | good
00046885 | 3946 | NN | Health and Safety Compliance Systems, Spill Containment, Chemical Spill Kit |  |  |  | 00019632 | Nobleton North ET Valve Room | Chemical Spill Kit | HSS | M10095 |  |  |  |  | 2012 |  | 8 |  | Area 4 Water Treatment |  | Health and Safety System |  |  |  | W-WW | 2 | 2 |  |  |  | The chemical spill kit was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | 100 | IMG_0441 | Nobleton North ET Capital Project 1 |  |  | OPERATING | 2019 |  |  |  |  | good
00047965 | 3947 | NN | Security Panel Node 2, Security System |  |  |  | 00019610 | Nobleton North ET Atrium | Security Panel | SIC | [5 empty] | 2012 |  | 8 |  | Area 4 Water Treatment |  | Health and Safety System |  |  |  | W-WW | 2 | 3 |  |  |  | The security panel was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | 5000 | IMG_0430 | Nobleton North ET Capital Project 1 |  |  | OPERATING | 2019 |  |  |  |  | Good
00047967 | 3948 | NN | Alarm Relay Panel, Security System |  |  |  | 00019632 | Nobleton North ET Valve Room | Alarm Relay Panel | SIC | [5 empty] | 2012 |  | 8 |  | Area 4 Water Treatment |  | Health and Safety System |  |  |  | W-WW | 2 | 3 |  |  |  | The alarm relay panel was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | 3000 | IMG_0455 | Nobleton North ET Capital Project 1 |  |  | OPERATING | 2019 |  |  |  |  | Good
00047968 | 3949 | NN | Alarm Dialer, Auto Dialer |  |  |  | 00019632 | Nobleton North ET Valve Room | Alarm Dialer | SIC | M00455 |  |  |  |  | 2012 |  | 8 |  | Area 4 Water Treatment |  | Health and Safety System | GCQUSA-31771-AL-T |  |  | W-WW | 2 | 3 |  |  |  | The alarm dialer was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | 5000 | IMG_0431 | Nobleton North ET Capital Project 1 |  |  | OPERATING | 2019 |  |  |  |  | Good
00047969 | 3950 | NN | Europlex 3GS Controller, Security System |  |  |  | 00019632 | Nobleton North ET Valve Room | Access Security Panel | SIC | M01094 |  |  |  |  | 2012 |  | 8 |  | Area 4 Water Treatment |  | Health and Safety System |  |  |  | W-WW | 2 | 3 |  |  |  | The access security panel was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | 10000 | IMG_0465 | Nobleton North ET Capital Project 1 |  |  | OPERATING | 2019 |  |  |  |  | Good
00051734 | 3951 | NN | Health and Safety Compliance Systems, Hach Pocket Colorimeter II, Chlorine Residual Kit |  |  |  | 790900200 | Nobleton North Elevated Tank | Chlorine Residual Kit | HSS | M00482 |  |  |  |  | 2012 |  | 8 |  | Area 4 Water Treatment | W - Storage Elevated Tank | Health and Safety System | 13110E234722 |  |  | W-WW | 2 | 2 |  |  |  | The chlorine residual kit was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | 650 | IMG_0461 | Nobleton North ET Capital Project 1 |  |  | OPERATING | 2019 |  |  |  |  | good
00078342 | 3952 | NN | Health and Safety Compliance Systems, Tank, Portable, Tank, eyewash, Fendall Porta Stream II |  |  |  | 00019632 | Nobleton North ET Valve Room | Emergency Eyewash | HSS | M10242 |  |  |  |  | 2012 |  | 8 |  | Area 4 Water Treatment |  | Health and Safety System |  |  |  | W-WW | 2 | 2 |  |  |  | The emergency eyewash was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | 600 | IMG_0445 | Nobleton North ET Capital Project 1 |  |  | OPERATING | 2019 |  |  |  |  | good
00047991 | 3956 | NN | Inlet, Piping, Expansion Joint |  |  |  | 00019632 | Nobleton North ET Valve Room | Elevated Tank Inlet Header Expansion Joint | PM | [5 empty] | 2012 |  | 23 |  | Area 4 Water Treatment |  | Process Mechanical |  |  |  | W-WW | 2 | 3 |  |  |  | The elevated tank inlet header expansion joint was observed to be in good condition. Elevated tank inlet header expansion joint to be replaced at the end of remaining service life. |  |  |  |  | 1400 | 20191126_093538 |  |  |  | OPERATING | 2019 |  |  |  |  | Good
00047992 | 3957 | NN | Inlet, TWR_VALT1, Valve, Altitude |  |  |  | 00019632 | Nobleton North ET Valve Room | Elevated Tank Inlet Header Altitude Valve TWR_VALT1 | PM | M00038 |  |  |  |  | 2012 |  | 23 |  | Area 4 Water Treatment |  | Process Mechanical | 27467425F |  |  | W-WW | 3 | 3 | Corroded bolts and washers were observed. | Corroded ball valve levers were observed. |  | The elevated tank inlet header altitude valve twr_valt1 was observed to be in fair condition. Elevated tank inlet header altitude valve twr_valt1 to be replaced at the end of remaining service life. | 500 | 2025 |  |  | 16000 | 20191126_093234 |  | Nobleton North ET Capital Project 1 |  | OPERATING | 2019 |  |  |  |  | Corroded bolts and washers | Corroded ball valve levers
00047993 | 3958 | NN | Inlet, BV-1, Valve, Butterfly, 300mm |  |  |  | 00019632 | Nobleton North ET Valve Room | Elevated Tank Inlet Header Butterfly Valve BV-1 | PM | M00114 |  |  |  |  | 2012 |  | 23 |  | Area 4 Water Treatment |  | Process Mechanical | 1436990-1-4 MS |  |  | W-WW | 3 | 3 | Surficial corrosion was observed. | Corrosion was observed at face with gasket. |  | The elevated tank inlet header butterfly valve bv-1 was observed to be in fair condition. Elevated tank inlet header butterfly valve bv-1 to be replaced at the end of remaining service life. | 500 | 2025 |  |  | 4000 | 20191126_092817 |  | Nobleton North ET Capital Project 1 |  | OPERATING | 2019 |  |  |  |  | Surficial corrosion | Corrosion at face with gasket
00047994 | 3959 | NN | Air Release, Valve, Gate, 100mm |  |  |  | 00019632 | Nobleton North ET Valve Room | Elevated Tank Inlet/Outlet Header Air Release Isolation Gate Valve | PM | M00671 |  |  |  |  | 2012 |  | 23 |  | Area 4 Water Treatment |  | Process Mechanical | 09505479 |  |  | W-WW | 2 | 2 |  |  |  | The elevated tank inlet/outlet header air release isolation gate valve was observed to be in good condition. Elevated tank inlet/outlet header air release isolation gate valve to be replaced at the end of remaining service life. |  |  |  |  | 1100 | 20191126_093429 |  |  |  | OPERATING | 2019 |  |  |  |  | Good
00047995 | 3960 | NN | Valve, Air Release, 100 mm |  |  |  | 00019632 | Nobleton North ET Valve Room | Elevated Tank Inlet/Outlet Header Air Release Valve | PM | [5 empty] | 2012 |  | 23 |  | Area 4 Water Treatment |  | Process Mechanical | 124889 |  |  | W-WW | 2 | 3 |  |  |  | The elevated tank inlet/outlet header air release valve was observed to be in good condition. Elevated tank inlet/outlet header air release valve to be replaced at the end of remaining service life. |  |  |  |  | 4000 | 20191126_092651 |  |  |  | OPERATING | 2019 |  |  |  |  | Good
00047996 | 3961 | NN | Outlet, BV-3, Valve, Butterfly, 300mm |  |  |  | 00019632 | Nobleton North ET Valve Room | Elevated Tank Outlet Header Valve Butterfly BV-3 | PM | M00114 |  |  |  |  | 2012 |  | 23 |  | Area 4 Water Treatment |  | Process Mechanical | 1436990-1-1 WS |  |  | W-WW | 3 | 3 | Minor surficial corrosion. | Corrosion was observed at the gasket face. |  | The elevated tank outlet header valve butterfly bv-3 was observed to be in fair condition. Elevated tank outlet header valve butterfly bv-3 to be replaced at the end of remaining service life. | 500 | 2025 |  |  | 4000 | 20191126_091421 |  | Nobleton North ET Capital Project 1 |  | OPERATING | 2019 |  |  |  |  | Minor surficial corrosion | corrosion at the gasket face
00047997 | 3962 | NN | Drain, BV-4, Valve, Butterfly, 300mm |  |  |  | 00019632 | Nobleton North ET Valve Room | Elevated Tank Drain Line Butterfly Valve BV-4 | PM | [5 empty] | 2012 |  | 23 |  | Area 4 Water Treatment |  | Process Mechanical | 1436990-1-2 WS |  |  | W-WW | 2 | 3 |  |  |  | The elevated tank drain line butterfly valve bv-4 was observed to be in good condition. Elevated tank drain line butterfly valve bv-4 to be replaced at the end of remaining service life. |  |  |  |  | 4000 | 20191126_091644 |  |  |  | OPERATING | 2019 |  |  |  |  | Good
00047998 | 3963 | NN | Outlet, CK-1, Valve, Check, 300mm |  |  |  | 00019632 | Nobleton North ET Valve Room | Elevated Tank Outlet Header Check Valve CK-1 | PM | M00856 |  |  |  |  | 2012 |  | 23 |  | Area 4 Water Treatment |  | Process Mechanical |  |  |  | W-WW | 3 | 3 | Corroded washers were observed. |  |  | The elevated tank outlet header check valve ck-1 was observed to be in fair condition. Elevated tank outlet header check valve ck-1 to be replaced at the end of remaining service life. |  |  |  |  | 4600 | 20191126_092418 |  |  |  | OPERATING | 2019 |  |  |  |  | Corroded washers
00047999 | 3964 | NN | Outlet, Flex Connection, Piping, Expansion Joint |  |  |  | 00019632 | Nobleton North ET Valve Room | Elevated Tank Outlet Header Expansion Joint | PM | M10130 |  |  |  |  | 2012 |  | 23 |  | Area 4 Water Treatment |  | Process Mechanical |  |  |  | W-WW | 2 | 3 |  |  |  | The elevated tank outlet header expansion joint was observed to be in good condition. Elevated tank outlet header expansion joint to be replaced at the end of remaining service life. |  |  |  |  | 1400 | 20191126_092535 |  |  |  | OPERATING | 2019 |  |  |  |  | good
00048023 | 3965 | NN | Outlet, Isolation, BV-5, Valve, Butterfly, 300mm |  |  |  | 00019611 | Nobleton North ET Mezzanine | Elevated Tank Outlet Header Butterfly Valve BV-5 | PM | M00114 |  |  |  |  | 2012 |  | 23 |  | Area 4 Water Treatment |  | Process Mechanical |  |  |  | W-WW | 3 | 3 | Not accessible as within aluminum jacket. |  |  | The elevated tank outlet header butterfly valve bv-5 was assumed to be in fair condition. Elevated tank outlet header butterfly valve bv-5 to be replaced at the end of remaining service life. |  |  |  |  | 4000 | 20191126_094412 |  |  |  | OPERATING | 2019 |  |  |  |  | Not accessible as within aluminum jacket
00048025 | 3966 | NN | Inlet, Isolation, BV-2, Valve, Butterfly, 300mm |  |  |  | 00019611 | Nobleton North ET Mezzanine | Elevated Tank Inlet Header Butterfly Valve BV-2 | PM | M00114 |  |  |  |  | 2012 |  | 23 |  | Area 4 Water Treatment |  | Process Mechanical |  |  |  | W-WW | 3 | 3 | Not accessible as within aluminum jacket. |  |  | The elevated tank inlet header butterfly valve bv-2 was assumed to be in fair condition. Elevated tank inlet header butterfly valve bv-2 to be replaced at the end of remaining service life. |  |  |  |  | 3100 | 20191126_094301 |  |  |  | OPERATING | 2019 |  |  |  |  | Not accessible as within aluminum jacket
00047971 | 3985 | NN | Network Core Closet, Network |  |  |  | 00019632 | Nobleton North ET Valve Room | Network Core Closet | SIC | M00505 |  |  |  |  | 2012 |  | 8 |  | Area 4 Water Treatment |  | SCADA/ Instrumentation/ Control | 10-408 |  |  | W-WW | 2 | 3 |  |  |  | The network core closet was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | 15000 | IMG_0513 | Nobleton North ET Capital Project 1 |  |  | OPERATING | 2019 |  |  |  |  | Good
00047972 | 3986 | NN | NBET27, Control Panel, PLC |  |  |  | 00019632 | Nobleton North ET Valve Room | PAC Panel | SIC | [5 empty] | 2012 |  | 8 |  | Area 4 Water Treatment |  | SCADA/ Instrumentation/ Control | 10-408 |  |  | W-WW | 2 | 4 |  |  |  | The pac panel was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | 60000 | IMG_0504 | Nobleton North ET Capital Project 1 |  |  | OPERATING | 2019 |  |  |  |  | Good
00047979 | 3987 | NN | TWR-TSL1, Low Temperature Switch, Temperature |  |  |  | 00019632 | Nobleton North ET Valve Room | Valve Room Low Temperature Switch | SIC | M00076 |  |  |  | Temperature | 2012 |  | 8 |  | Area 4 Water Treatment |  | SCADA/ Instrumentation/ Control | T631B 1005 |  |  | W-WW | 2 | 2 |  |  |  | The valve room low temperature switch was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | 1000 | IMG_0483 | Nobleton North ET Capital Project 1 |  |  | OPERATING | 2019 |  |  |  |  | Good
00047982 | 3988 | NN | NBET27_TWR_PIT1, Header Pressure, Pressure Transmitter, Level |  |  |  | 00019632 | Nobleton North ET Valve Room | Elevated Tank Pressure Transmitter PIT1 | SIC | M00125 | Sitrans P D-76181 |  |  | Level | 2012 |  | 8 |  | Area 4 Water Treatment |  | SCADA/ Instrumentation/ Control | 7MF4033-1OA10-1NC6-Z |  |  | W-WW | 2 | 3 |  |  |  | The elevated tank pressure transmitter pit1 was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | 2500 | IMG_0516 | Nobleton North ET Capital Project 1 |  |  | OPERATING | 2019 |  |  |  |  | Good
00047983 | 3989 | NN | NBET27_TWR_PIT2, Tower, Pressure Transmitter, Level |  |  |  | 00019632 | Nobleton North ET Valve Room | Elevated Tank Pressure Transmitter PIT2 | SIC | M00125 | Sitrans P D-76181 |  |  | Level | 2012 |  | 8 |  | Area 4 Water Treatment |  | SCADA/ Instrumentation/ Control | 7MF4033-1EA10-1NC6-Z |  |  | W-WW | 2 | 3 |  |  |  | The elevated tank pressure transmitter pit2 was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | 2500 | IMG_0520 | Nobleton North ET Capital Project 1 |  |  | OPERATING | 2019 |  |  |  |  | Good
00047984 | 3990 | NN | Analyzer, Depolox 5, Analyzer, Multi-Parameter, Transmitter Model No.: MFC AAD4447, Analyzer, Wallace & Tiernan MICRO/2000 |  |  |  | 00019632 | Nobleton North ET Valve Room | Elevated Tank Outlet Header Multi-Parameter Analyzer | SIC | M00125 | EM101 |  |  | Chlorine | 2012 |  | 8 |  | Area 4 Water Treatment |  | SCADA/ Instrumentation/ Control | BT 90132-02 |  |  | W-WW | 2 | 4 |  |  |  | The elevated tank outlet header multi-parameter analyzer was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | 20000 | IMG_0531 | Nobleton North ET Capital Project 1 |  |  | OPERATING | 2019 |  |  |  |  | Good
00047985 | 3991 | NN | NBET27_TWR_FIT1, Inlet Flow, Flowmeter, Flow |  |  |  | 00019632 | Nobleton North ET Valve Room | Elevated Tank Inlet Header Ultrasonic Flowmeter | SIC | M00405 |  |  |  | Flow | 2012 |  | 8 |  | Area 4 Water Treatment |  | SCADA/ Instrumentation/ Control | E802A816000 |  |  | W-WW | 2 | 3 |  |  |  | The elevated tank inlet header ultrasonic flowmeter was observed to be in good condition. Replace the flow transmitter with a magnetic flowmeter. Asset to be replaced in the intermediate term. |  |  |  |  | 9000 | IMG_0495 | Nobleton North ET Capital Project 1 |  |  | OPERATING | 2019 | Replace the flow transmitter with a magnetic flowmeter. |  |  |  | Good
00047986 | 3992 | NN | NBET27_TWR_FIT2, Outlet Flow, Flowmeter, Flow |  |  |  | 00019632 | Nobleton North ET Valve Room | Elevated Tank Outlet Header Ultrasonic Flowmeter | SIC | M00405 |  |  |  | Flow | 2012 |  | 8 |  | Area 4 Water Treatment |  | SCADA/ Instrumentation/ Control | E802A916000 |  |  | W-WW | 2 | 3 |  |  |  | The elevated tank outlet header ultrasonic flowmeter was observed to be in good condition. Replace the flow transmitter with a magnetic flowmeter. Asset to be replaced in the intermediate term. |  |  |  |  | 9000 | IMG_0498 | Nobleton North ET Capital Project 1 |  |  | OPERATING | 2019 | Replace the flow transmitter with a magnetic flowmeter. |  |  |  | Good
00047987 | 3993 | NN | EFAN1, Temperature Switch |  |  |  | 00019632 | Nobleton North ET Valve Room | Valve Room EFAN1 Low Temperature Switch | SIC | M00076 |  |  |  |  | 2012 |  | 8 |  | Area 4 Water Treatment |  | SCADA/ Instrumentation/ Control | T631A 1154 |  |  | W-WW | 2 | 2 |  |  |  | The valve room efan1 low temperature switch was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | 1000 | IMG_0486 | Nobleton North ET Capital Project 1 |  |  | OPERATING | 2019 |  |  |  |  | Good
00048005 | 3994 | NN | TWR-TSL2, TWR-TSL2, Temperature Switch, Temperature |  |  |  | 00019609 | Nobleton North ET Chlorine Room | Chlorine Room Low Temperature Switch | SIC | M00076 |  |  |  | Temperature | 2012 |  | 8 |  | Area 4 Water Treatment |  | SCADA/ Instrumentation/ Control | T631B 1005 |  |  | W-WW | 2 | 2 |  |  |  | The chlorine room low temperature switch was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | 1000 | IMG_0556 | Nobleton North ET Capital Project 1 |  |  | OPERATING | 2019 |  |  |  |  | Good
00048022 | 3995 | NN | Outlet, TWR-FE2, Flow Meter, Mag Meter |  |  |  | 00019611 | Nobleton North ET Mezzanine | Elevated Tank Outlet Header Magnetic Flowmeter | SIC | M00405 |  |  |  |  | 2012 |  | 8 |  | Area 4 Water Treatment |  | SCADA/ Instrumentation/ Control |  |  |  | W-WW | 2 | 3 | Dust was observed. |  |  | The elevated tank outlet header magnetic flowmeter was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | 9000 | IMG_0586 | Nobleton North ET Capital Project 1 |  |  | OPERATING | 2019 |  |  |  |  | Dust
00048024 | 3996 | NN | Inlet, TWR-FE1, Flow Meter, Mag Meter, 300mm |  |  |  | 00019611 | Nobleton North ET Mezzanine | Elevated Tank Inlet Header Magnetic Flowmeter | SIC | M00405 |  |  |  |  | 2012 |  | 8 |  | Area 4 Water Treatment |  | SCADA/ Instrumentation/ Control |  |  |  | W-WW | 2 | 3 | Dust was observed. |  |  | The elevated tank inlet header magnetic flowmeter was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | 9000 | IMG_0568 | Nobleton North ET Capital Project 1 |  |  | OPERATING | 2019 |  |  |  |  | Dust
00048031 | 3997 | NN | OMNI, Access, Network, Antenna & Cable |  |  |  | 00019634 | Nobleton North ET Tank Roof | OMNI Antenna & Cable | SIC | [5 empty] | 2012 |  | 8 |  | Area 4 Water Treatment |  | SCADA/ Instrumentation/ Control | SC488-SF3SNF |  |  | W-WW | 2 | 3 |  |  |  | The omni antenna & cable was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | 7000 | DSC06648 | Nobleton North ET Capital Project 1 |  |  | OPERATING | 2019 |  |  |  |  | Good
00048032 | 3998 | NN | YAGI, Remote, Network, Antenna & Cable |  |  |  | 00019634 | Nobleton North ET Tank Roof | YAGI Antenna & Cable | SIC | [5 empty] | 2012 |  | 8 |  | Area 4 Water Treatment |  | SCADA/ Instrumentation/ Control | RY-9008 |  |  | W-WW | 2 | 2 |  |  |  | The yagi antenna & cable was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | 7000 | DSC06638 | Nobleton North ET Capital Project 1 |  |  | OPERATING | 2019 |  |  |  |  | Good
00048033 | 3999 | NN | ICP-01, Network, Ethernet Switch |  |  |  | 00019632 | Nobleton North ET Valve Room | PAC Panel Ethernet Switch | SIC | [5 empty] | 2012 |  | 8 |  | Area 4 Water Treatment |  | SCADA/ Instrumentation/ Control | ICP-01 |  |  | W-WW | 3 | 2 |  |  |  | The pac panel ethernet switch was assumed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | 3000 |  | Nobleton North ET Capital Project 1 |  |  | OPERATING | 2019
00048034 | 4000 | NN | PAC, CompactLogix, RPU, PLC |  |  |  | 00019632 | Nobleton North ET Valve Room | PAC Panel PLC | SIC | M00005 |  |  |  |  | 2012 |  | 8 |  | Area 4 Water Treatment |  | SCADA/ Instrumentation/ Control |  |  |  | W-WW | 3 | 2 |  |  |  | The pac panel plc was assumed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | 3000 |  | Nobleton North ET Capital Project 1 |  |  | OPERATING | 2019
00048035 | 4001 | NN | Network Core Closet, Network, Radio Modem |  |  |  | 00019632 | Nobleton North ET Valve Room | Network Core Closet Radio Modem | SIC | M00455 |  |  |  |  | 2012 |  | 8 |  | Area 4 Water Treatment |  | SCADA/ Instrumentation/ Control |  |  |  | W-WW | 3 | 3 |  |  |  | The network core closet radio modem was assumed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | 15000 |  | Nobleton North ET Capital Project 1 |  |  | OPERATING | 2019
00052861 | 4002 | NN | UPS, Dry, Main PAC Panel |  |  |  | 00019632 | Nobleton North ET Valve Room | PAC Panel UPS | SIC | M00728 |  |  |  |  | 2012 |  | 8 |  | Area 4 Water Treatment |  | SCADA/ Instrumentation/ Control | GE324A1503 |  |  | W-WW | 3 | 2 |  |  |  | The pac panel ups was assumed to be in fair condition. Asset to be replaced in the intermediate term. |  |  |  |  | 3000 |  | Nobleton North ET Capital Project 1 |  |  | OPERATING | 2019
00046022 | 4020 | NN | Emergency Overflow Outfall, Site Drainage, Dry Pond, including sewers |  |  |  | 790900200 | Nobleton North Elevated Tank | Overflow System (Dry Pond) | SW | [5 empty] | 2007 |  | 48 |  | Area 4 Water Treatment | W - Storage Elevated Tank | Site Works |  |  |  | W-WW | 3 | 3 | Settled headwall was observed. |  |  | The overflow system (dry pond) was observed to be in fair condition. There were no needs required. Re-inspect outlet was recommended in 3-5 years. Asset to be replaced at the end of estimated service life. | 0 |  |  |  | 75000 | IMG_20191126_094623 |  |  |  | OPERATING | 2019 | There were no needs required. Re-inspect outlet was recommended in 3-5 years. | 0 |  |  | Settled headwall and outlet pipe
00047954 | 4021 | NN | Gate, Double Lockable |  |  |  | 790900200 | Nobleton North Elevated Tank | Swing Gate to Entrance | SW | [5 empty] | 2012 |  | 19 |  | Area 4 Water Treatment | W - Storage Elevated Tank | Site Works |  |  |  | W-WW | 3 | 1 | Broken gate mesh was observed. | Peeling fence paint was observed. |  | The swing gate to entrance was observed to be in fair condition. Remove and replace gate mesh. Asset to be replaced in the long term. | 1000 | 2025 |  |  | 5000 | IMG_20191126_092649 | Nobleton North ET Capital Project 2 | Nobleton North ET Capital Project 1 |  | OPERATING | 2019 | Remove and replace gate mesh. | 1000 |  |  | Broken gate mesh | Peeling fence paint
00047958 | 4022 | NN | Signboard |  |  |  | 790900200 | Nobleton North Elevated Tank | (Missing) Signboard | SW | [9 empty] | Area 4 Water Treatment | W - Storage Elevated Tank | Site Works |  |  |  | W-WW | [15 empty] | OPERATING | 2019
00047959 | 4026 | NN | Ladder Interior, Aluminum With Fall Arrest Rail, floor to mezzanine roof |  |  |  | 00019610 | Nobleton North ET Atrium | Mezzanine Roof Ladder | SCC | [5 empty] | 2012 |  | 53 |  | Area 4 Water Treatment |  | Structural Components |  |  |  | W-WW | 2 | 4 | Fall arrest system is required to be replaced. |  |  | The Mezzanine Roof Ladder was observed to be in good condition. Ladder fall arrest system should be replaced immediately. | 500 | 2019 |  |  | 2500 | DSC06593 |  |  |  | OPERATING | 2019 |  |  |  |  | Good
00048000 | 4027 | NN | Outlet, Pipe Support |  |  |  | 00019632 | Nobleton North ET Valve Room | Valve Room Pipe Supports (Outlet) | SCC | [5 empty] | 2012 |  | 53 |  | Area 4 Water Treatment |  | Structural Components |  |  |  | W-WW | 2 | 3 |  |  |  | The valve room pipe supports (outlet) was observed to be in good condition. Valve room pipe supports (outlet) to be replaced at the end of remaining service life. |  |  |  |  | 1000000 | DSC06690 |  |  |  | OPERATING | 2019 |  |  |  |  | Good
00048002 | 4029 | NN | Inlet, Pipe Support |  |  |  | 00019632 | Nobleton North ET Valve Room | Valve Room Pipe Supports (Inlet) | SCC | [5 empty] | 2012 |  | 53 |  | Area 4 Water Treatment |  | Structural Components | YR STD W-148 |  |  | W-WW | 2 | 3 |  |  |  | The valve room pipe supports (inlet) was observed to be in good condition. Valve room pipe supports (inlet) to be replaced at the end of remaining service life. |  |  |  |  | 10000 | DSC06692 |  |  |  | OPERATING | 2019 |  |  |  |  | Good
00048026 | 4030 | NN | Ladder Interior, Aluminum With Fall Arrest Rail, mezzanine to platform |  |  |  | 00019611 | Nobleton North ET Mezzanine | Mezzanine Ladder | SCC | [5 empty] | 2012 |  | 53 |  | Area 4 Water Treatment |  | Structural Components |  |  |  | W-WW | 2 | 4 | Fall arrest system (TS rail) is required to be replaced immediately. |  |  | The mezzanine ladder was observed to be in good condition. Fall arrest system (TS rail) is required to be replaced immediately. Mezzanine ladder to be replaced at the end of remaining service life. | 5000 | 2019 |  |  | 30000 | DSC06610 |  |  |  | OPERATING | 2019 |  |  |  |  | Good
00048030 | 4031 | NN | Floor Slab, Concrete |  |  |  | 00019610 | Nobleton North Elevated Tank | Atrium Concrete Floor Slab | SC | [5 empty] | 2012 |  | 53 |  | Area 4 Water Treatment | W - Storage Elevated Tank | Structural Components |  |  |  | W-WW | 2 | 3 |  |  |  | The atrium concrete floor slab was observed to be in good condition. Provision for structural repairs every 10 years. Atrium concrete floor slab to be replaced at the end of remaining service life. | 2000 | 2029 |  |  | 13000 | DSC06608 |  | Nobleton North ET Capital Project 2 |  | OPERATING | 2019 |  |  |  |  | Good
| 4197 | NN | Smoke Detector (1) |  |  |  | 00019632 |  | Smoke Detector | HSS | [5 empty] | 2012 |  | 8 | [8 empty] | 2 | 2 |  |  |  | The smoke detector was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 200 | IMG_0481 | Nobleton North ET Capital Project 1 |  |  |  | 2019 |  | 0 |  | 0 | good
| 4199 | NN | Fire Extinguisher (1) |  |  |  | 00019610 |  | Fire Extinguisher | HSS | [5 empty] | 2012 |  | 8 | [8 empty] | 2 | 1 |  |  |  | The fire extinguisher was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 100 | IMG_0449 | Nobleton North ET Capital Project 1 |  |  |  | 2019 |  | 0 |  | 0 | good
| 4208 | NN |  |  |  |  | 790900200 |  | Elevated Tank Exterior Coating | SC | [5 empty] | 2012 |  | 21 | [8 empty] | 2 | 3 |  |  |  | The elevated tank exterior cone, shell, roof, and access tube coatings were observed to be in good condition. Exterior tank cleaning, coating inspection, and touch-up should be carried out every five years. Overcoating of the access tube (dry side) is rec | 10000 | 2026 | 0 |  | 520000 | DSC06556 |  | Nobleton North ET Capital Project 1 |  |  | 2019 |  | 0 |  | 0 | Good
| 4209 | NN |  |  |  |  | 790900200 |  | Elevated Tank Interior Coating | SC | [5 empty] | 2011 |  | 21 | [8 empty] | 3 | 3 | Localized delamination of coating was observed. | The Stainless Steel Mixing System, Overflow Pipe and elevated tank bottom access hatch lid were not coated. | Minor mineral staining were observed throughout. | The elevated tank interior coating including the coatings for access tub, floor, cone, shell, and ceiling was observed to be in fair condition. Coating inspection and interior lining touch-up should be carried out every five years for the interior coating | 40000 | 2023 | 0 |  | 350000 | DSC06672 |  | Nobleton North ET Capital Project 1 |  |  | 2019 |  | 0 |  | 0 | Localized delamination of coating
| 4210 | NN |  |  |  |  | 00019610 |  | Atrium Access Door (Double) | AC | [5 empty] | 2011 |  | 12 | [8 empty] | 3 | 1 | Bubbled/missing paint was observed at bottom. | Corrosion on hardware was observed. |  | The atrium access door (double) was observed to be in fair condition. Door should be repainted in the short term and long term. | 2500 | 2023 | 2500 |  | 5500 | DSC06584 | Nobleton North ET Capital Project 2 | Nobleton North ET Capital Project 1 |  |  | 2019 |  | 0 |  | 0 | Bubbled/missing paint at bottom | Corrosion on hardware
| 4211 | NN |  |  |  |  | 00019632 |  | Valve Room Access Door (Double) | AC | [5 empty] | 2011 |  | 12 | [8 empty] | 2 | 1 |  |  |  | The valve room access door (double) was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 5500 | DSC06601 | Nobleton North ET Capital Project 2 |  |  |  | 2019 |  | 0 |  | 0 | good
| 4212 | NN |  |  |  |  | 00019609 |  | Chlorine Room Access Door (Single) | AC | [5 empty] | 2011 |  | 12 | [8 empty] | 3 | 1 | Peeling/missing paint was observed. | Corrosion on hardware was observed. |  | The chlorine room access door (single) was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 3500 | DSC06562 | Nobleton North ET Capital Project 2 |  |  |  | 2019 |  | 0 |  | 0 | Peeling/missing paint | Corrosion on hardware
| 4213 | NN |  |  |  |  | 00019609 |  | Chlorine Room Window | AC | [5 empty] | 2011 |  | 12 | [8 empty] | 2 | 1 |  |  |  | The chlorine room window was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 1500 | DSC06573 | Nobleton North ET Capital Project 2 |  |  |  | 2019 |  | 0 |  | 0 | Good
| 4214 | NN |  |  |  |  | 00019610 |  | Atrium Floor Coating | AC | [5 empty] | 2011 |  | 12 | [8 empty] | 2 | 1 |  |  |  | The atrium floor coating was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 2000 | DSC06608 | Nobleton North ET Capital Project 2 |  |  |  | 2019 |  | 0 |  | 0 | Good
| 4215 | NN |  |  |  |  | 00019632 |  | Valve Room Floor Coating | AC | [5 empty] | 2011 |  | 12 | [8 empty] | 2 | 1 |  |  |  | The valve room floor coating was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 4000 | DSC06690 | Nobleton North ET Capital Project 2 |  |  |  | 2019 |  | 0 |  | 0 | Good
| 4216 | NN |  |  |  |  | 00019610 |  | Atrium Wall Paint | AC | [5 empty] | 2011 |  | 12 | [8 empty] | 2 | 1 |  |  |  | The atrium wall paint was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 3000 | DSC06608 | Nobleton North ET Capital Project 2 |  |  |  | 2019 |  | 0 |  | 0 | Good
| 4217 | NN |  |  |  |  | 00019632 |  | Valve Room Wall Paint | AC | [5 empty] | 2011 |  | 12 | [8 empty] | 2 | 1 |  |  |  | The valve room wall paint was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 10000 | DSC06690 | Nobleton North ET Capital Project 2 |  |  |  | 2019 |  | 0 |  | 0 | Good
| 4227 | NN | Ladder Interior, Aluminum With Fall Arrest Rail, platform to roof |  |  |  | 790900200 |  | Elevated Tank Ladder (Platform to Roof) | SC | [5 empty] | 2012 |  | 53 | [8 empty] | 2 | 4 | Fall arrest system (TS rail) is required to be replaced immediately. |  |  | The elevated tank ladder (platform to roof) was observed to be in good condition. Fall arrest system (TS rail) is required to be replaced immediately. Elevated tank ladder (platform to roof) to be replaced at the end of remaining service life. | 5000 | 2019 |  |  | 10000 | DSC06682 |  |  |  |  | 2019 |  |  |  |  | Good
| 4228 | NN | Ladder Interior, Aluminum With Fall Arrest Rail, platform to tank |  |  |  | 790900200 |  | Elevated Tank Ladder (Platform to Tank) | SC | [5 empty] | 2012 |  | 53 | [8 empty] | 2 | 4 | Fall arrest system (TS rail) is required to be replaced immediately. | 'D' Ring on dry side was observed to be missing. |  | The elevated tank ladder (platform to tank) was observed to be in good condition. Replacement of fall arrest system and installation of D ring are recommended to be conducted immediately. Elevated tank ladder (platform to tank) to be replaced at the end | 1800 | 2019 |  |  | 1500 | DSC06621 |  |  |  |  | 2019 |  |  |  |  | Good
| 4229 | NN | Ladder Interior, Aluminum With Fall Arrest Rail, roof to tank |  |  |  | 790900200 |  | Elevated Tank Ladder (Roof to Tank Interior) | SC | [5 empty] | 2012 |  | 53 | [8 empty] | 2 | 3 | Fall arrest system (TS rail) is required to be replaced immediately. |  |  | The elevated tank ladder (roof to tank) was observed to be in good condition. Fall arrest system (TS rail) is required to be replaced immediately. Elevated tank ladder (roof to tank) to be replaced at the end of remaining service life. | 500 | 2019 |  |  | 10000 | DSC06661 |  |  |  |  | 2019 |  |  |  |  | Good
00048030 | 4230 | NN | Floor Slab, Concrete |  |  |  | 00019609 |  | Chlorine Room Concrete Floor Slab | SC | [5 empty] | 2012 |  | 53 | [8 empty] | 2 | 3 |  |  |  | The chlorine room concrete floor slab was observed to be in good condition. Provision for structural repairs every 10 years. Chlorine room concrete floor slab to be replaced at the end of remaining service life. | 2000 | 2029 |  |  | 13000 | DSC06564 |  | Nobleton North ET Capital Project 2 |  |  | 2019 |  |  |  |  | Good
00048030 | 4231 | NN | Floor Slab, Concrete |  |  |  | 00019632 |  | Valve Room Concrete Floor Slab | SC | [5 empty] | 2012 |  | 53 | [8 empty] | 2 | 3 |  |  |  | The valve room concrete floor slab was observed to be in good condition. Provision for structural repairs every 10 years. Valve room concrete floor slab to be replaced at the end of remaining service life. | 4000 | 2029 |  |  | 30000 | DSC06690 |  | Nobleton North ET Capital Project 2 |  |  | 2019 |  |  |  |  | Good
| 4233 | NN |  |  |  |  | 00019632 |  | Valve Room Masonry Block Wall | SC | [5 empty] | 2012 |  | 53 | [8 empty] | 2 | 4 |  |  |  | The valve room masonry block wall was observed to be in good condition. Provision for structural repairs every 10 years. Valve room masonry block wall to be replaced at the end of remaining service life. | 4000 | 2029 |  |  | 30000 | DSC06690 |  | Nobleton North ET Capital Project 2 |  |  | 2019 |  |  |  |  | Good
| 4234 | NN |  |  |  |  | 00019610 |  | Atrium Masonry Block Wall | SC | [5 empty] | 2012 |  | 53 | [8 empty] | 2 | 4 |  |  |  | The atrium masonry block wall was observed to be in good condition. Provision for structural repairs every 10 years. Atrium masonry block wall to be replaced at the end of remaining service life. | 2000 | 2029 |  |  | 10000 | DSC06608 |  | Nobleton North ET Capital Project 2 |  |  | 2019 |  |  |  |  | Good
| 4235 | NN |  |  |  |  | 00019609 |  | Chlorine Room Masonry Block Wall | SC | [5 empty] | 2012 |  | 53 | [8 empty] | 2 | 4 |  |  |  | The chlorine room masonry block wall was observed to be in good condition. Provision for structural repairs every 10 years. Chlorine room masonry block wall to be replaced at the end of remaining service life. | 2000 | 2029 |  |  | 10000 | DSC06565 |  | Nobleton North ET Capital Project 2 |  |  | 2019 |  |  |  |  | Good
| 4236 | NN |  |  |  |  | 00019632 |  | Valve Room Concrete Roof Slab | SC | [5 empty] | 2012 |  | 53 | [8 empty] | 2 | 3 |  |  |  | The valve room concrete roof slab was observed to be in good condition. Provision for structural repairs every 10 years. Valve room concrete roof slab to be replaced at the end of remaining service life. | 3000 | 2029 |  |  | 17000 | DSC06691 |  | Nobleton North ET Capital Project 2 |  |  | 2019 |  |  |  |  | Good
| 4237 | NN |  |  |  |  | 00019609 |  | Chlorine Room Concrete Roof Slab | SC | [5 empty] | 2012 |  | 53 | [8 empty] | 2 | 3 | There was a small piece of cladding and insulation missing at the landing. |  |  | The chlorine room concrete roof slab was observed to be in good condition. Replace missing cladding. Provision for structural repairs every 10 years. Chlorine room concrete roof slab to be replaced at the end of remaining service life. | 200 | 2022 | 1500 | 2029 | 8000 | DSC06565 |  | Nobleton North ET Capital Project 1 | Nobleton North ET Capital Project 2 |  | 2019 |  |  |  |  | Good
| 4238 | NN |  |  |  |  | 790900200 |  | Elevated Tank Platform | SC | [5 empty] | 2012 |  | 53 | [8 empty] | 2 | 4 |  |  |  | The elevated tank platform was observed to be in good condition. Elevated tank platform to be replaced at the end of remaining service life. |  |  |  |  | 50000 | DSC06612 |  |  |  |  | 2019 |  |  |  |  | Good
| 4239 | NN |  |  |  |  | 790900200 |  | Elevated Tank Concrete Foundation | SC | [5 empty] | 2012 |  | 53 | [8 empty] | 2 | 4 |  |  |  | The elevated tank concrete foundation was observed to be in good condition. Provision for structural repairs every 10 years. Elevated tank concrete foundation to be replaced at the end of remaining service life. | 12000 | 2029 |  |  | 150000 | DSC06608 |  | Nobleton North ET Capital Project 2 |  |  | 2019 |  |  |  |  | Good
| 4240 | NN |  |  |  |  | 790900200 |  | Elevated Tank Concrete Roof | SC | [5 empty] | 2012 |  | 53 | [8 empty] | 2 | 4 |  |  |  | The elevated tank concrete roof was observed to be in good condition. Provision for structural repairs every 10 years. Elevated tank concrete roof to be replaced at the end of remaining service life. | 6000 | 2029 |  |  | 80000 | DSC06612 |  | Nobleton North ET Capital Project 2 |  |  | 2019 |  |  |  |  | Good
| 4241 | NN |  |  |  |  | 790900200 |  | Elevated Tank Concrete Pedestal | SC | [5 empty] | 2012 |  | 53 | [8 empty] | 2 | 4 |  |  |  | The elevated tank concrete wall was observed to be in good condition. Provision for structural repairs every 10 years. Elevated tank concrete wall to be replaced at the end of remaining service life. | 12000 | 2029 |  |  | 280000 | DSC06556 |  | Nobleton North ET Capital Project 2 |  |  | 2019 |  |  |  |  | Good
| 4242 | NN |  |  |  |  | 790900200 |  | Elevated Tank Steel Tank | SC | [5 empty] | 2012 |  | 53 | [8 empty] | 2 | 5 |  |  |  | The elevated tank steel tank was observed to be in good condition. Elevated tank steel tank to be replaced at the end of remaining service life. |  |  |  |  | 600000 | DSC06556 |  |  |  |  | 2019 |  |  |  |  | Good
| 4243 | NN | Tank Roof to Tank Interior |  |  |  | 790900200 |  | Elevated Tank Roof Hatch 2 (Tank Roof to Tank Interior) | SC | [5 empty] | 2012 |  | 53 | [8 empty] | 3 | 2 | Surface corrosion was observed. | Paint Peeling was observed. |  | The elevated tank roof hatch 2 was observed to be in good condition. Elevated tank roof hatch 2 to be replaced at the end of remaining service life. | 1500 | 2023 |  |  | 5000 | DSC06634 |  | Nobleton North ET Capital Project 1 |  |  | 2019 |  |  |  |  | Good
| 4244 | NN | Access Tube to Tank Roof |  |  |  | 790900200 |  | Elevated Tank Roof Hatch 1 (Access Tube to Tank Roof) | SC | [5 empty] | 2012 |  | 53 | [8 empty] | 2 | 2 |  |  |  | The elevated tank roof hatch 1 was observed to be in good condition. Elevated tank roof hatch 1 to be replaced at the end of remaining service life. |  |  |  |  | 5000 | DSC06634 |  |  |  |  | 2019 |  |  |  |  | Good
| 4250 | NN |  |  |  |  | 790900200 |  | Elevated Tank Tank Hatch (Access from Upper Platform) | SC | [5 empty] | 2012 |  | 53 | [8 empty] | 3 | 2 |  |  |  | The elevated tank tank hatch was observed to be in fair condition. The tank hatch should be repainted on wet side. Elevated tank tank hatch to be replaced at the end of remaining service life. |  |  |  |  | 5000 | DSC06621 |  |  |  |  | 2019 |  |  |  |  | Good
00047980 | 4278 | NN | outlet Heat Tracing Panel |  |  |  | 00019632 |  | Outlet Header Heat Trace Panel | ES | [5 empty] | 2012 |  | 18 | [8 empty] | 2 | 3 |  |  |  | The outlet header heat trace panel was observed to be in good condition. Asset to be replaced in the long term. |  |  |  |  | 13000 | IMG_1466 | Nobleton North ET Capital Project 2 |  |  |  | 2019 |  |  |  |  | good
| 4279 | NN | Incoming power meter |  |  |  | 790900200 |  | Power Meter | ES | [5 empty] | 2012 |  | 18 | [8 empty] | 2 | 2 |  |  |  | The power meter was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 30000 | IMG_1301 | Nobleton North ET Capital Project 2 |  |  |  | 2019 |  | 0 |  | 0 | good
| 4280 | NN | weatherproof exit sign and battery unit emergency light |  |  |  | 00019609 |  | Chlorine Room Emergency Exit | ES | [5 empty] | 2012 |  | 18 | [8 empty] | 2 | 3 |  |  |  | The chlorine room emergency exit was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2500 | IMG_1311 | Nobleton North ET Capital Project 2 |  |  |  | 2019 |  | 0 |  | 0 | good
| 4281 | NN | total of 3 linear weather proof fluorescent light fixtures |  |  |  | 00019609 |  | Chlorine Room Lighting | ES | [5 empty] | 2012 |  | 18 | [8 empty] | 2 | 2 |  |  |  | The chlorine room lighting was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 4500 | IMG_1312 | Nobleton North ET Capital Project 2 |  |  |  | 2019 |  | 0 |  | 0 | good
| 4282 | NN | Exhaust Fan EFAN2 Control |  |  |  | 00019609 |  | Exhaust Fan EF2 Control | ES | [5 empty] | 2012 |  | 18 | [8 empty] | 2 | 2 |  |  |  | The exhaust fan ef2 control was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2000 | IMG_1314 | Nobleton North ET Capital Project 2 |  |  |  | 2019 |  | 0 |  | 0 | good
| 4284 | NN | weatherproof exit sign and battery unit emergency light |  |  |  | 00019610 |  | Atrium Emergency Exit | ES | [5 empty] | 2012 |  | 18 | [8 empty] | 2 | 3 |  |  |  | The atrium emergency exit was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2500 | IMG_1323 | Nobleton North ET Capital Project 2 |  |  |  | 2019 |  | 0 |  | 0 | good
| 4285 | NN | class 1, div 2, metal halide flood lights, total of 3 |  |  |  | 00019610 |  | Atrium Flood Lights | ES | [5 empty] | 2012 |  | 18 | [8 empty] | 2 | 3 |  |  |  | The atrium flood lights was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 7500 | IMG_1329 | Nobleton North ET Capital Project 2 |  |  |  | 2019 |  | 0 |  | 0 | good
| 4286 | NN | weatherproof exit sign with battery unit emergency light, 1 remote head |  |  |  | 00019632 |  | Valve Room Emergency Exit | ES | [5 empty] | 2012 |  | 18 | [8 empty] | 2 | 3 |  |  |  | The valve room emergency exit was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 3000 | IMG_1354 | Nobleton North ET Capital Project 2 |  |  |  | 2019 |  | 0 |  | 0 | good
| 4287 | NN | total of 6 linear weather proof fluorescent light fixtures |  |  |  | 00019632 |  | Valve Room Lighting | ES | [5 empty] | 2012 |  | 18 | [8 empty] | 2 | 2 |  |  |  | The valve room lighting was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 6000 | IMG_1388 | Nobleton North ET Capital Project 2 |  |  |  | 2019 |  | 0 |  | 0 | good
| 4289 | NN | Exhaust Fan EFAN1 Control |  |  |  | 00019609 |  | Exhaust Fan EF1 Control | ES | [5 empty] | 2012 |  | 18 | [8 empty] | 2 | 2 |  |  |  | The exhaust fan ef1 control was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2000 | IMG_1480 | Nobleton North ET Capital Project 2 |  |  |  | 2019 |  | 0 |  | 0 | good
| 4290 | NN | 2 weatherproof battery unit light and 4 remote heads |  |  |  | 790900200 |  | Pedestal Emergency Lighting | ES | [5 empty] | 2012 |  | 18 | [8 empty] | 2 | 3 |  |  |  | The pedestal emergency lighting was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 5000 | IMG_1485 | Nobleton North ET Capital Project 2 |  |  |  | 2019 |  | 0 |  | 0 | good
| 4291 | NN | class 1, div 2, metal halide flood lights, total of 6 |  |  |  | 00019611 |  | Mezzanine Lighting | ES | [5 empty] | 2012 |  | 18 | [8 empty] | 2 | 2 |  |  |  | The mezzanine lighting was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 15000 | IMG_0561 | Nobleton North ET Capital Project 2 |  |  |  | 2019 |  | 0 |  | 0 | good
| 4292 | NN | weatherproof battery unit light and 2 remote heads |  |  |  | 00019611 |  | ET Pedestal Emergency Lighting | ES | [5 empty] | 2012 |  | 18 | [8 empty] | 2 | 3 |  |  |  | The et pedestal emergency lighting was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 3000 | DSC06683 | Nobleton North ET Capital Project 2 |  |  |  | 2019 |  | 0 |  | 0 | good
| 4293 | NN | class 1, div 2, metal halide flood lights, total of 8 |  |  |  | 790900200 |  | ET Pedestal Lighting | ES | [5 empty] | 2012 |  | 18 | [8 empty] | 2 | 2 |  |  |  | The ET Pedestal Lighting was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 20000 | DSC06613 | Nobleton North ET Capital Project 2 |  |  |  | 2019 |  | 0 |  | 0 | good
| 4294 | NN | class 1, div 2, metal halide flood lights, total of 6 |  |  |  | 00019633 |  | Platform and Access Tube Lighting | ES | [5 empty] | 2012 |  | 18 | [8 empty] | 2 | 2 |  |  |  | The platform and access tube lighting was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 13000 | DSC06620 | Nobleton North ET Capital Project 2 |  |  |  | 2019 |  | 0 |  | 0 | good
| 4327 | NN | Soft surface areas around site |  |  |  | 790900200 |  | Site Grading | SW | [5 empty] | 2012 |  | 48 | [8 empty] | 3 | 1 | Damaged sod and exposed top soil were observed above septic bed. | Some areas by storm sewer outlet had settled, which had caused tripping hazards. |  | The site grading was observed to be in fair condition. Regrade and resod areas that have exposed soil. Asset to be replaced in the long term. | 25000 | 2025 | 0 |  | 140000 | IMG_20191126_091259 |  | Nobleton North ET Capital Project 1 |  |  | 2019 | Regrade and resod areas that have exposed soil. | 25000 |  | 0 | Damged sod and exposed top soil above septic bed | Some areas by storm sewer outlet had settled, which had caused tripping hazards.
| 4328 | NN | Chainlink fence with barbed wire on top, 530m |  |  |  | 790900200 |  | Site Fencing | SW | [5 empty] | 2012 |  | 19 | [8 empty] | 3 | 1 | Localized areas where fencing mesh was broken on the bottom. |  |  | The site fencing was observed to be in fair condition. Repair fence mesh as required. Asset to be replaced in the long term. | 1000 | 2025 | 0 |  | 70000 | IMG_20191126_095127 | Nobleton North ET Capital Project 2 | Nobleton North ET Capital Project 1 |  |  | 2019 | Repair fence mesh as required. | 1000 |  | 0 | Localized areas where fencing mesh was broken on the bottom.
| 4330 | NN | Asphalt driveway and parking area |  |  |  | 790900200 |  | Paved Areas | SW | [5 empty] | 2014 |  | 19 | [8 empty] | 3 | 2 | New asphalt around Freedom Mobile electrical station was damaged in a few locations. |  |  | The paved areas was observed to be in fair condition. Remove and replace asphalt road to the extents of the utility cut with asphalt. Asset to be replaced in the long term. | 15000 | 2025 | 0 |  | 130000 | IMG_20191126_091736 | Nobleton North ET Capital Project 2 | Nobleton North ET Capital Project 1 |  |  | 2019 | Remove and replace asphalt road to the extents of the utility cut with asphalt. | 15000 |  | 0 | New asphalt around Freedom Mobile electrical station was damaged in a few locations.
| 4331 | NN | Bollards in front of entrances and electrical station, 6 total. |  |  |  | 790900200 |  | Bollards | SW | [5 empty] | 2014 |  | 15 | [8 empty] | 2 | 2 |  |  |  | The bollards was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 6000 | IMG_20191126_095606 | Nobleton North ET Capital Project 2 |  |  |  | 2019 |  | 0 |  | 0 | good
| 4348 | NN |  |  |  |  | 00019609 |  | Chlorine Room Floor Coating | AC | [5 empty] | 2011 |  | 12 | [8 empty] | 2 | 1 |  |  |  | The chlorine room floor coating was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 2000 | DSC06564 | Nobleton North ET Capital Project 2 |  |  |  | 2019 |  | 0 |  | 0 | Good
| 4349 | NN |  |  |  |  | 00019609 |  | Chlorine Room Wall Paint | AC | [5 empty] | 2011 |  | 12 | [8 empty] | 2 | 1 |  |  |  | The chlorine room wall paint was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 5000 | DSC06564 | Nobleton North ET Capital Project 2 |  |  |  | 2019 |  | 0 |  | 0 | Good
| 4350 | NN |  |  |  |  | 790900200 |  | Elevated Tank Roof Guardrail | SC | [5 empty] | 2012 |  | 53 | [8 empty] | 2 | 3 |  |  |  | The elevated tank guardrail was observed to be in good condition. Elevated tank guardrail to be replaced at the end of remaining service life. |  |  |  |  | 15000 | DSC06640 |  |  |  |  | 2019 |  |  |  |  | Good
| 4351 | NN |  |  |  |  | 790900200 |  | Elevated Tank Antenna Structure | SC | [5 empty] | 2012 |  | 53 | [8 empty] | 2 | 3 | Fall arrest system (TS rail) is required to be replaced immediately. |  |  | The elevated tank antenna structure was observed to be in good condition. Elevated tank antenna structure to be replaced at the end of remaining service life. | 1200 | 2019 |  |  | 30000 | DSC06644 |  |  |  |  | 2019 |  |  |  |  | Good
| 4352 | NN |  |  |  |  | 790900200 |  | Elevated Tank Roof Davit Base | HSS | [5 empty] | 2012 |  | 18 | [8 empty] | 2 | 4 |  |  |  | The elevated tank roof davit base was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | 5000 | DSC06636 | Nobleton North ET Capital Project 2 |  |  |  | 2019 |  |  |  |  | Good
| 4353 | NN |  |  |  |  | 790900200 |  | Drain Manhole 1 Precast Concrete Structure | SW | [5 empty] | 2012 |  | 53 | [8 empty] | 3 | 3 |  |  |  | The drain manhole 1 precast concrete structure was assumed to be in fair condition. |  |  |  |  | 25000 | DSC06577 |  |  |  |  | 2019 |  |  |  |  | Good
| 4354 | NN |  |  |  |  | 790900200 |  | Drain Manhole 2 Precast Concrete Structure | SW | [5 empty] | 2012 |  | 53 | [8 empty] | 2 | 3 |  |  |  | The drain manhole 2 precast concrete structure was observed to be in good condition. |  |  |  |  | 10000 | DSC06685 |  |  |  |  | 2019 |  |  |  |  | Good
| 4355 | NN |  |  |  |  | 790900200 |  | Drain Manhole 1 Access Hatch | SW | [5 empty] | 2012 |  | 53 | [8 empty] | 2 | 2 |  |  |  | The drain manhole 1 access hatch was observed to be in good condition. |  |  |  |  | 5000 | DSC06577 |  |  |  |  | 2019 |  |  |  |  | Good
| 4356 | NN |  |  |  |  | 790900200 |  | Drain Manhole 2 Cover and Frame | SW | [5 empty] | 2012 |  | 53 | [8 empty] | 2 | 2 |  |  |  | The drain manhole 2 cover and frame was observed to be in good condition. Manhole #2 manhole cover and frame to be replaced at the end of remaining service life. |  |  |  |  | 3000 | DSC06684 |  |  |  |  | 2019 |  |  |  |  | Good
| 4357 | NN |  |  |  |  | 790900200 |  | Drain Manhole 3 Precast Concrete Structure | SW | [5 empty] | 2012 |  | 53 | [8 empty] | 2 | 3 |  |  |  | The drain chamber 3 precast concrete structure was observed to be in good condition. |  |  |  |  | 10000 | DSC06689 |  |  |  |  | 2019 |  |  |  |  | Good
| 4358 | NN |  |  |  |  | 790900200 |  | Drain Manhole 3 Cover and Frame | SW | [5 empty] | 2012 |  | 53 | [8 empty] | 2 | 2 |  |  |  | The drain chamber 3 manhole cover and frame was observed to be in good condition. Drain chamber manhole cover and frame to be replaced at the end of remaining service life. |  |  |  |  | 3000 | DSC06688 |  |  |  |  | 2019 |  |  |  |  | Good
| 4361 | NN |  |  |  |  | 790900200 |  | Electrical Chamber Precast Concrete Structure | SW | [5 empty] | 2012 |  | 53 | [8 empty] | 2 | 3 |  |  |  | The electrical chamber precast concrete structure was observed to be in good condition. |  |  |  |  | 10000 | DSC06687 |  |  |  |  | 2019 |  |  |  |  | Good
| 4362 | NN |  |  |  |  | 790900200 |  | Electrical Chamber Cover and Frame | SW | [5 empty] | 2012 |  | 53 | [8 empty] | 2 | 2 |  |  |  | The electrical chamber cover and frame was observed to be in good condition. Electrical chamber manhole cover and frame to be replaced at the end of remaining service life. |  |  |  |  | 3000 | DSC06686 |  |  |  |  | 2019 |  |  |  |  | Good
| 4395 | NN | Inlet Pipe, 300mm, length: 40 meters | [5 empty] | Elevated Tank Inlet Header | PM | [5 empty] | 2012 |  | 23 | [8 empty] | 2 | 4 |  |  |  | The elevated tank inlet header was observed to be in good condition. Elevated tank inlet header to be replaced at the end of remaining service life. | 0 |  | 0 |  | 60000 | 20191126_093841 |  |  |  |  | 2019 |  | 0 |  | 0 | Good
| 4396 | NN | Outlet Pipe, 300mm, length: 35 meters | [5 empty] | Elevated Tank Outlet Header | PM | [5 empty] | 2012 |  | 23 | [8 empty] | 2 | 4 |  |  |  | The elevated tank outlet header was observed to be in good condition. Elevated tank outlet header to be replaced at the end of remaining service life. | 0 |  | 0 |  | 60000 | 20191126_093936 |  |  |  |  | 2019 |  | 0 |  | 0 | Good
| 4397 | NN | Overflow Pipe, 300mm, length: 45 meters | [5 empty] | Elevated Tank Overflow and Drain Pipe | PM | [5 empty] | 2012 |  | 23 | [8 empty] | 2 | 4 |  |  |  | The elevated tank overflow and drain pipe was observed to be in good condition. Elevated tank overflow and drain pipe to be replaced at the end of remaining service life. | 0 |  | 0 |  | 70000 | 20191126_094004 |  |  |  |  | 2019 |  | 0 |  | 0 | good
| 4398 | NN | 300mm PVC Watermain, total length 190m. 400mm CPP Watermain, total length 10m |  |  |  | 790900200 |  | Yard Watermains | SW | [5 empty] | 2012 |  | 53 | [8 empty] | 3 | 4 |  |  |  | The yard watermains was assumed to be in fair condition. Asset to be replaced at the end of estimated remaining service life. | 0 |  | 0 |  | 220000 | [5 empty] | 2019 |  | 0 |  | 0
| 4399 | NN | Concrete Septic Tank (2.4x1.5x1.5m). 100mm perforated pipe, total length 50m. |  |  |  | 790900200 |  | Septic System | SW | [5 empty] | 2012 |  | 53 | [8 empty] | 3 | 2 |  |  |  | The septic system was assumed to be in fair condition. | 0 |  | 0 |  | 35000 | IMG_20191126_095520 |  |  |  |  | 2019 |  | 0 |  | 0
| 4412 | NN | Platform Removable Louver with Aluminum Cover, 900mm x 600mm |  |  |  | 00019633 |  | Platform Removable Louver with Aluminum Cover | BM | [5 empty] | 2012 |  | 23 | [8 empty] | 2 | 2 |  |  |  | The platform removable louver with aluminum cover was observed to be in good condition. Platform removable louver with aluminum cover to be replaced at the end of remaining service life. | 0 |  | 0 |  | 6000 | DSC06629 |  |  |  |  | 2019 |  | 0 |  | 0 | good
| 4413 | NN | Sample Sink |  |  |  | 00019632 |  | Sample Sink | BM | [5 empty] | 2012 |  | 23 | [8 empty] | 2 | 2 |  |  |  | The sample sink was observed to be in good condition. Sample sink to be replaced at the end of remaining service life. | 0 |  | 0 |  | 2000 | IMG_0443 |  |  |  |  | 2019 |  | 0 |  | 0 | Good
00047970 | 4414 | NN | HTRC1-CP, Inlet, Heating System, Heat Tracing |  |  |  | 00019632 |  | Inlet Header Heat Tracing System | ES | [5 empty] | 2012 |  | 18 |  |  |  |  | 26093 |  |  |  | 2 | 3 |  |  |  | The inlet header heat tracing system was observed to be in good condition. Asset to be replaced in the long term. |  |  |  |  | 10000 |  | Nobleton North ET Capital Project 2 |  |  |  | 2019 |  |  |  |  | good
| 4419 | NN | Two warning lights |  |  |  | 00019634 |  | Aircraft Obstruction Lights | ES | [5 empty] | 2012 |  | 18 | [8 empty] | 2 | 3 |  |  |  | The aircraft obstruction lights was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 1000 | DSC06680 | Nobleton North ET Capital Project 2 |  |  |  | 2019 |  | 0 |  | 0 | Good
| 4420 | NN | 1 LED Flood Light |  |  |  | 790900200 |  | Entrance Lighting | ES | [5 empty] | 2012 |  | 18 | [8 empty] | 2 | 2 |  |  |  | The entrance lighting was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 1000 | IMG_1320 | Nobleton North ET Capital Project 2 |  |  |  | 2019 |  | 0 |  | 0 | good
| 4424 | NN |  |  |  |  | 790900200 |  | Elevated Tank Mixing System | PM | [5 empty] | 2012 |  | 23 | [8 empty] | 3 | 3 |  |  |  | The elevated tank mixing system was assumed to be in fair condition. Elevated tank mixing system to be replaced at the end of remaining service life. | 0 |  | 0 |  | 85000 | [5 empty] | 2019 |  | 0 |  | 0
00047970 | 4426 | NN |  |  |  |  | 00019632 |  | Inlet Header Heat Trace System | ES | [5 empty] | 2012 |  | 18 |  |  |  |  | 26092 |  |  |  | 3 | 3 |  |  |  | The inlet header heat trace system was assumed to be in fair condition. Asset to be replaced in the long term. |  |  |  |  | 20000 |  | Nobleton North ET Capital Project 2 |  |  |  | 2019
00047980 | 4427 | NN |  |  |  |  | 00019632 |  | Outlet Header Heat Trace System | ES | [5 empty] | 2012 |  | 18 |  |  |  |  | 26092 |  |  |  | 3 | 3 |  |  |  | The outlet header heat trace system was assumed to be in fair condition. Asset to be replaced in the long term. |  |  |  |  | 20000 |  | Nobleton North ET Capital Project 2 |  |  |  | 2019
| 4430 | NN | Elevated Tank Grounding |  |  |  | 790900200 |  | Elevated Tank Grounding | ES | [5 empty] | 2012 |  | 18 | [8 empty] | 3 | 3 |  |  |  | The elevated tank grounding was assumed to be in fair condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 10000 |  | Nobleton North ET Capital Project 2 |  |  |  | 2019 |  | 0 |  | 0
| 4431 | NN | Elevated Tank Lightning Protection System |  |  |  | 790900200 |  | Elevated Tank Lightning Protection System | ES | [5 empty] | 2012 |  | 18 | [8 empty] | 2 | 3 | There were no Lightning Protection Air Terminals present. It should be installed due to the present of antennas. |  |  | The Elevated Tank Lightning Protection System was assumed to be in fair condition There were no lightning protection air terminals installed on the roof. It should be installed due to the present of antennas. | 1800 | 2021 | 0 |  | 5000 |  | Nobleton North ET Capital Project 2 | Nobleton North ET Capital Project 1 |  |  | 2019 |  | 0 |  | 0 | good
| 4432 | NN |  |  |  |  | 790900200 |  | Elevated Tank Frostproof Vent/Vacuum Relief Unit | PM | [5 empty] | 2012 |  | 23 | [8 empty] | 3 | 3 | The stainless steel frostproof vent/vacuum relief unit cannot be opened because it hits the antenna structure. It should be moved to outer edge of tank and replace hatch to tank interior. |  |  | The stainless steel frostproof vent/vacuum relief unit cannot be opened because it hits the antenna structure. It should be moved to outer edge of tank and replace hatch to tank interior. Asset to be replaced at the end of estimated remaining service life | 3500 | 2019 |  |  | 6000 | DSC06635 |  |  |  |  | 2019 |  | 0 |  | 0
| 4434 | NN | Mezzanine roof handrail |  |  |  | 00019611 |  | Mezzanine Roof Handrail | SC | [5 empty] | 2012 |  | 53 | [8 empty] | 2 | 2 |  |  |  | The Mezzanine Roof Handrail was observed to be in good condition. Replace the asset at the end of its remaining service life. | 0 | 0 | 0 | 0 | 8000 | DSC06593 |  |  |  |  | 2019 |  | 0 |  | 0
| 4435 | NN |  |  |  |  | 790900200 |  | Upper Platform Rescue Port Base | HSS | [5 empty] | 2012 |  | 18 | [8 empty] | 2 | 4 |  |  |  | The Upper Platform Rescue Port Base was observed to be in good condition. Asset to be replaced in the intermediate term. |  |  |  |  | 4000 | DSC06623 | Nobleton North ET Capital Project 2 |  |  |  | 2019 |  | 0 |  | 0
| 4437 | NN |  |  |  |  | 790900200 |  | Gin Wheel and Hoist Rope | SC | [5 empty] | 2012 |  | 4 | [8 empty] | 3 | 2 | The Gin Wheel rope was observed to be frayed and damaged. |  |  | The Gin Wheel and Hoist Rope was observed to be in poor condition. Replace the asset in 1-5 years. | 0 | 0 | 0 | 0 | 25000 | DSC06612 | Nobleton North ET Capital Project 1 |  |  |  | 2019 |  | 0 |  | 0
| 4438 | NN |  |  |  |  | 790900200 |  | Drain Manhole 3 Gate Valve | SW | [5 empty] | 2012 |  | 23 | [8 empty] | 2 | 2 | Dirty was observed on the surface of the valve. |  |  | The Drain Manhole 3 Gate Valve was observed to be in good condition. | 0 | 0 | 0 | 0 | 3600 | IMG_20191126_102917 |  |  |  |  | 2019 |  | 0 |  | 0
| 4444 | NN | Water sample tank, and plumbing and drainage assets within the facility. |  |  |  | 790900200 |  | Plumbing and Drainage | BM | [5 empty] | 2012 |  | 23 | [8 empty] | 2 | 2 |  |  |  | The Plumbing and Drainage were observed to be in good condition. | 0 | 0 | 0 | 0 | 30000 | IMG_0482 |  |  |  |  | 2019 |  | 0 |  | 0
| 4446 | NN | Electrical underground duct system and conduit system |  |  |  | 790900200 |  | Electrical Duct System and Conduit System | ES | [5 empty] | 2012 |  | 18 | [8 empty] | 2 | 3 |  |  |  | The Electrical Duct System and Conduit System were observed to be in good condition. Replace the system at the end of its estimated remaining service life. | 0 | 0 | 0 | 0 | 50000 | IMG_1486 | Nobleton North ET Capital Project 2 |  |  |  | 2019 |  | 0 |  | 0
| 4450 | NN | Elevated Tank Sacrificial Anode Cathodic Protection System |  |  |  | 00009403 |  | Elevated Tank Sacrificial Anode Cathodic Protection System | SC | [5 empty] | 2012 |  | 25 | [8 empty] | 3 | 3 |  |  |  | The Elevated Tank Sacrificial Anode Cathodic system was assumed to be in fair condition. It is recommended to be installed in 1 - 5 years. Supply and install sacrificial anode is recommended every five years. | 0 | 0 | 0 | 0 | 30000 | [5 empty] | 2019 |  | 0 |  | 0
| 4456 | NN | Tideflex Check Valve, 300mm | [5 empty] | Elevated Tank Overflow Pipe Tideflex Check Valve | PM | [5 empty] | 2012 |  | 23 | [8 empty] | 3 | 3 |  |  |  | The elevated tank overflow pipe tide flex valve was assumed to be in fair condition. Elevated tank overflow pipe tide flex valve to be replaced at the end of remaining service life. | 0 |  | 0 |  | 5000 | [5 empty] | 2019 |  | 0 |  | 0
| 4457 | NN | [6 empty] | Elevated Tank Roof Vent Hatch | SC | [5 empty] | 2013 |  | 55 | [8 empty] | 2 | 2 |  |  |  | The elevated tank tank access hatch was observed to be in good condition. Elevated tank access hatch to be replaced at the end of remaining service life. |  |  |  |  | 5000 | DSC06635 |  |  |  |  | 2019 |  | 0 |  | 0