## Sheet1
seqNum | RehabRepairCost2 | RehabRepairYear2 | facility | Process | building | inspectorName | CategoryCode | assetTag | assetName | LocationORIGINAL | LocationTag | photoName | repCost | defect1 | defect2 | defect3 | Description | installationDate | installYear | remainingESL | InstType | InstMeva | ServiceArea | FacilityType | SerialNo | Parent | RotatingItem | Site | condition | COF | observations | RehabRepairCost | RehabRepairYear | repProjectName | rehabProjectName | rehab2ProjectName | manufacturer | LifeCycleCategory
2377 | 0 |  | PD6 |  |  |  | AC |  | Valve House Ceiling Paint |  | 19041 | DSC00641 | 15000 | [5 empty] | 2006 | 7 | [8 empty] | 2 | 1 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1
2378 | 0 |  | PD6 |  |  |  | SC |  | Valve House Masonry Blockwalls |  | 25383 | DSC00630 | 12000 |  |  |  | Staircase and reservoir access |  | 2006 | 46 | [8 empty] | 2 | 4 | The asset was observed to be in good condition. Valve house masonry blockwalls to be replaced at the end of remaining service life. | 0
2379 | 0 |  | PD6 |  |  |  | SC |  | Valve House Precast Concrete Roof |  | 25383 | DSC00612 | 2000 |  |  |  | staircase |  | 2006 | 46 | [8 empty] | 2 | 3 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Valve house precast concrete roof to be replaced at the end of remaining service life. | 0 | 2030 |  | Stouffville PD6 Reservoir Capital Project 1
2380 | 0 |  | PD6 |  |  |  | SC |  | Valve House Aluminum Platform |  | 19041 |  | 1500 |  |  |  | in overflow |  | 2006 | 46 | [8 empty] | 2 | 2 | The asset was observed to be in good condition. Valve house aluminum platform to be replaced at the end of remaining service life. | 0
2381 | 0 |  | PD6 |  |  |  | SC |  | Rear Access House Concrete Floor |  | 19042 | IMG_2248 | 24000 | [5 empty] | 2006 | 46 | [8 empty] | 2 | 4 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Rear access house concrete floor to be replaced at the end of remaining service life. | 0 | 2030 |  | Stouffville PD6 Reservoir Capital Project 1
2382 | 0 |  | PD6 |  |  |  | HSS |  | Valve House First Extinguishers |  | 790900031 | IMG_2828 | 300 |  |  |  | Total of 3 |  | 2016 | 11 | [8 empty] | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2384 | 0 |  | PD6 |  |  |  | SW |  | Concrete Retaining Wall |  | 790900031 | DSC07813 | 50000 |  |  |  | 18m and 14.5m long |  | 2006 | 12 | [8 empty] | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2385 | 0 |  | PD6 |  |  |  | SW |  | Landscaping |  | 790900031 | DSC07845 | 750000 |  |  |  | approx 97250 sq m |  | 2006 | 12 | [8 empty] | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2386 | 0 |  | PD6 |  |  |  | SW |  | Reservoir Inflow Piping |  | 790900031 |  | 960000 |  |  |  | 1050mm diameter. Approx. 240m |  | 2006 | 12 | [8 empty] | 2 | 5 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2387 | 0 |  | PD6 |  |  |  | SW |  | Reservoir Outflow Piping |  | 790900031 |  | 960000 |  |  |  | 1050mm diameter. Approx. 240m |  | 2006 | 12 | [8 empty] | 2 | 5 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2388 | 0 |  | PD6 |  |  |  | SW |  | Geoweb Paver |  | 790900031 | DSC07858 | 20000 | Soil and sod had overgrown the geoweb paver was observed. |  |  | approx 1400 sq m |  | 2006 | 12 | [8 empty] | 3 | 1 | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2389 | 0 |  | PD6 |  |  |  | SW |  | Emergency Overflow Outfall and Site Drainage |  | 790900031 | DSC07767 | 100000 | [5 empty] | 2006 | 12 | [8 empty] | 2 | 4 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2390 | 0 |  | PD6 |  |  |  | SW |  | Facility Access Gate 1 |  | 790900031 | DSC07785 | 3500 | Bent at bottom was observed. |  |  | Entrance |  | 2006 | 12 | [8 empty] | 3 | 1 | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2391 | 0 |  | PD6 |  |  |  | SW |  | Site Chainlink Fencing |  | 790900031 | DSC07785 | 65000 | Bent/out of plumb post at rear access house was observed. |  |  | approx 400m |  | 2012 | 12 | [8 empty] | 4 | 1 | The asset was observed to be in poor condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2393 | 0 |  | PD6 |  |  |  | SW |  | Bollards |  | 790900031 | IMG_2862 | 1000 | [5 empty] | 2006 | 12 | [8 empty] | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2394 | 0 |  | PD6 |  |  |  | SW |  | Facility Access Gate 2 |  | 790900031 | DSC07802 | 3500 | [5 empty] | 2006 | 12 | [8 empty] | 2 | 1 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2395 | 0 |  | PD6 |  |  |  | BM |  | Motorized Damper MD-2 |  | 790900031 | IMG-2312 | 3000 |  |  |  | MD 2, Ventilation System, Damper c/w outdoor louver, main floor, north wall, 120VAC/1ph, Belimo actuator; powered from LP-A |  | 2006 | 16 | [8 empty] | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2396 | 0 |  | PD6 |  |  |  | BM |  | Motorized Damper MD-4 |  | 790900031 | IMG_2312 | 3000 |  |  |  | MD 4, Ventilation System, Damper c/w outdoor louver, main floor, west wall, 120VAC/1ph, Belimo actuator; powered from LP-A |  | 2006 | 16 | [8 empty] | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2397 | 0 |  | PD6 |  |  |  | BM | 00043525 | sump pump, P-2 |  | 790900031 | IMG_2043 | 3000 |  |  |  | sump pump, P-2; 120VAC/1ph, 4/10 hp; submersible, centrigugal, by Liberty Pumps model HT40-Series; powed from LP-A; |  | 2006 | 16 | [8 empty] | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2398 | 0 |  | PD6 |  |  |  | PM |  | Valve Local Disconnect Switch |  | 790900031 | IMG_2150 | 5000 |  |  |  | Actuator M200, Switch, Local Disconnect; by Siemens, 600 VAC, 3 poles, 30 Amps |  | 2006 | 16 | [8 empty] | 2 | 4 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2399 | 0 |  | PD6 |  |  |  | PM |  | Valve Local Disconnect Switch |  | 790900031 | IMG_2129 | 5000 |  |  |  | Actuator M400, Switch, Local Disconnect; by Siemens, 600 VAC, 3 poles, 30 Amps |  | 2006 | 16 | [8 empty] | 2 | 4 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2400 | 0 |  | PD6 |  |  |  | PM |  | Valve Local Disconnect Switch |  | 790900031 | IMG_2174 | 5000 |  |  |  | Actuator M600, Switch, Local Disconnect; by Siemens, 600 VAC, 3 poles, 30 Amps |  | 2006 | 16 | [8 empty] | 2 | 4 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2401 | 0 |  | PD6 |  |  |  | PM |  | Washdown Pump Local Disconnect Switch |  | 790900031 | IMG_2179 | 5000 |  |  |  | Actuator M700, Switch, Local Disconnect; by Siemens, 600 VAC, 3 poles,60 amps |  | 2006 | 16 | [8 empty] | 2 | 4 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2402 | 0 |  | PD6 |  |  |  | SIC |  | South Cell Level Transmitter, LIT-100 |  | 25383 | IMG_2247 | 12000 |  |  |  | ; MILTRONICS; MULTIRANGER 100; 031405199VX; 100-230V, 36VA (17W), CONTACT RATING: 5A @250VAC; 1 |  | 2006 | 7 | [8 empty] | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1
2403 | 0 |  | PD6 |  |  |  | SIC |  | North Cell Level Transmitter, LIT-200 |  | 25383 | IMG_2249 | 12000 |  |  |  | ; MILTRONICS; MULTIRANGER 100; 031405250VX; 100-230V, 36VA (17W), CONTACT RATING: 5A @250VAC; 1 |  | 2006 | 7 | [8 empty] | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1
2404 | 0 |  | PD6 |  |  |  | SIC | 00086987 | Control Panel |  | 25383 | IMG_2255 | 17000 |  |  |  | Network access closet; Haffman; ; ; 1 |  | 2006 | 7 | [8 empty] | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1
2406 | 0 |  | PD6 |  |  |  | SIC |  | Telephone Port |  | 25383 | IMG_2326 | 300 |  |  |  | Telephone; ; ; ; 1 |  | 2006 | 7 | [8 empty] | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1
2408 | 0 |  | PD6 |  |  |  | SIC |  | Valve Area Temperature Switch |  | 25384 | IMG_2348 | 500 |  |  |  | ; Honeywell; ; ; ;2 switches |  | 2006 | 7 | [8 empty] | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1
2410 | 0 |  | PD6 |  |  |  | SIC |  | Telephone Port |  | 25384 | IMG_2361 | 300 |  |  |  | Telephone; ; ; ; 1 |  | 2006 | 7 | [8 empty] | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1
2411 | 0 |  | PD6 |  |  |  | PM | 00002603 | M-100 Motorized Valve |  | 25384 | IMG_2366 | 10000 | Valve does not fully close. setpoints seems to be the problem was observed. |  |  | ; rotork; IQ; D120930106; 575V, 3ph, 0.69A, 0.19kW; 1 |  | 2006 | 16 | [8 empty] | 3 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2412 | 0 |  | PD6 |  |  |  | PM | 00026018 | M-600 Motorized Valve |  | 25384 | IMG_2406 | 10000 | Valve does not fully close. setpoints seems to be the problem was observed. |  |  | ; rotork; IQ; ; 575V, 3ph, 0.69A, 0.19kW; 1 |  | 2006 | 16 | [8 empty] | 3 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2413 | 0 |  | PD6 |  |  |  | PM | 00026015 | M-500 Motorized Valve |  | 25384 | IMG_2430 | 10000 | Valve does not fully close. setpoints seems to be the problem was observed. |  |  | ; rotork; IQ; D120930104; 575V, 3ph, 0.69A, 0.19kW; 1 |  | 2006 | 16 | [8 empty] | 3 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2414 | 0 |  | PD6 |  |  |  | PM | 00026009 | M-300 Motorized Valve |  | 25384 | IMG_2443 | 10000 | Valve does not fully close. setpoints seems to be the problem was observed. |  |  | ; rotork; IQ; D120930102; 575V, 3ph, 0.69A, 0.19kW; 1 |  | 2006 | 16 | [8 empty] | 3 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2415 | 0 |  | PD6 |  |  |  | PM | 00026012 | M-400 Motorized Valve |  | 25384 | IMG_2458 | 10000 | Valve does not fully close. setpoints seems to be the problem was observed. |  |  | ; rotork; IQ; D120930105; 575V, 3ph, 0.69A, 0.19kW; 1 |  | 2006 | 16 | [8 empty] | 3 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2416 | 0 |  | PD6 |  |  |  | PM | 00026006 | M-400 Motorized Valve |  | 25384 | IMG_2465 | 10000 | Valve does not fully close. setpoints seems to be the problem was observed. |  |  | ; rotork; IQ; D120930103; 575V, 3ph, 0.69A, 0.19kW; 1 |  | 2006 | 16 | [8 empty] | 3 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2418 | 0 |  | PD6 |  |  |  | SIC |  | Security Panels |  | 19042 | IMG_2494 | 20000 |  |  |  | security access control; Honeywell; ; ; ; 2 |  | 2019 | 14 | [8 empty] | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2424 | 0 |  | PD6 |  |  |  | ES |  | Welding Receptacle |  | 25383 | IMG_2186 | 9000 |  |  |  | Welding Receptacle; Appleton; Powertite; ;600V, 60A |  | 2006 | 11 | [8 empty] | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2425 | 0 |  | PD6 |  |  |  | ES |  | MCC Main Breaker |  | 25383 | IMG_2198 | 11900 |  |  |  | Main Breaker; Siemens; ; ; 600V, 200A; |  | 2006 | 11 | [8 empty] | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2426 | 0 |  | PD6 |  |  |  | ES |  | M-100 Valve Local DS |  | 25384 | IMG_2369 | 600 |  |  |  | M 100, local Switch, Disconnect; Siemens; ; ; 600V, 30A; |  | 2006 | 11 | [8 empty] | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2427 | 0 |  | PD6 |  |  |  | ES |  | M-500 Valve local DS |  | 25384 | IMG_2431 | 600 |  |  |  | M 500, Switch, local Disconnect; Siemens; ; ; 600V, 30A; |  | 2006 | 11 | [8 empty] | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2428 | 0 |  | PD6 |  |  |  | ES |  | M-300 Valve local DS |  | 25384 | IMG_2444 | 800 |  |  |  | M 300, Switch, local Disconnect; Siemens; ID361NF; ; 600V, 30A; |  | 2006 | 11 | [8 empty] | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2429 | 0 |  | PD6 |  |  |  | ES |  | LP-B Transformer |  | 19042 | IMG_2496 | 11000 |  |  |  | transformer; EVI; CDTC0010VHC6XXBB; 10KVA, 3ph, 600-120/208V; |  | 2006 | 11 | [8 empty] | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2430 | 0 |  | PD6 |  |  |  | ES |  | MCC Level Lighting |  | 25383 | IMG_2266 | 13200 | The lighting fixture was not led type. it should be replaced with led fixtures in the next upgrade was observed. |  |  | lighting; ; ; 22 linear flurescent fixtures |  | 2006 | 11 | [8 empty] | 3 | 2 | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2431 | 0 |  | PD6 |  |  |  | ES |  | Reservoir Exterior Lighting |  | 790900031 | IMG_2316 | 1500 | One of the fixture's sensor did not work and kept the light on during the day time was observed. |  |  | lighting; ; ; 2 LED flood lights with light sensor |  | 2006 | 11 | [8 empty] | 3 | 2 | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2432 | 0 |  | PD6 |  |  |  | ES |  | Valve Gallery Lighting |  | 25384 | IMG_2358 | 6000 | The lighting fixture was not led type. it should be replaced with led fixtures in the next upgrade was observed. |  |  | lighting; ; ; 10 linear flurescent fixtures |  | 2006 | 11 | [8 empty] | 3 | 2 | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2433 | 0 |  | PD6 |  |  |  | ES |  | East Hatch Building Exterior Light |  | 19042 | IMG_2492 | 750 | One of the fixture's sensor did not work and kept the light on during the day time was observed. |  |  | lighting; ; ; 1 LED flood lights with light sensor |  | 2006 | 11 | [8 empty] | 3 | 2 | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2434 | 0 |  | PD6 |  |  |  | ES |  | East Hatch Building Interior Light |  | 19042 |  | 600 | The lighting fixture was not led type. it should be replaced with led fixtures in the next upgrade was observed. |  |  | lighting; ; ; 1 linear flurescent fixtures |  | 2006 | 11 | [8 empty] | 3 | 2 | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2435 | 0 |  | PD6 |  |  |  | ES |  | MCC level Emergency Lighting |  | 25383 | IMG_2329 | 2400 |  |  |  | emeregency lighting; ; ; 3 exit signs and 1 remote head |  | 2006 | 11 | [8 empty] | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2334 | 0 |  | PD6 |  |  |  | SC |  | North Cell Aluminum Grating |  | 790900031 | DSC07706 | 500 | [5 empty] | 2006 | 46 | [8 empty] | 2 | 3 | The asset was observed to be in good condition. North cell aluminum grating to be replaced at the end of remaining service life. | 0
2335 | 0 |  | PD6 |  |  |  | SC |  | South Cell Aluminum Grating |  | 790900031 | IMG_2852 | 500 | [5 empty] | 2006 | 46 | [8 empty] | 2 | 2 | The asset was observed to be in good condition. South cell aluminum grating to be replaced at the end of remaining service life. | 0
2336 | 0 |  | PD6 |  |  |  | SC |  | South Cell Aluminum Ladder |  | 790900031 | IMG_2847 | 5000 | Corrosion was observed at ladder top. |  |  |  |  | 2006 | 46 | [8 empty] | 3 | 2 | The asset was observed to be in fair condition. South cell aluminum ladder to be replaced at the end of remaining service life. | 0
2337 | 0 | 2037 | PD6 |  |  |  | SC |  | South Cell Concrete Floor Slab |  | 790900031 | IMG_2848 | 3700000 | Hairline cracking with efflorescence deposits was observed. | Rust spots was observed. | Debonded expansion joint sealant was observed. |  |  | 2006 | 46 | [8 empty] | 3 | 5 | The asset was observed to be in fair condition. Provisions for structural repairs. South cell concrete floor slab to be replaced at the end of remaining service life. | 0 | 2022 |  | Stouffville PD6 Reservoir Capital Project 1 | Stouffville PD6 Reservoir Capital Project 2
2338 | 0 | 2037 | PD6 |  |  |  | SC |  | South Cell Concrete Walls |  | 790900031 | DSC07940 | 2700000 | Hairline cracking with efflorescence deposits was observed. | Rust spots was observed. | Active leaking was observed at expansion joints on dividing wall. |  |  | 2006 | 46 | [8 empty] | 3 | 5 | The asset was observed to be in fair condition. Provisions for structural repairs. South cell concrete walls to be replaced at the end of remaining service life. | 0 | 2022 |  | Stouffville PD6 Reservoir Capital Project 1 | Stouffville PD6 Reservoir Capital Project 2
2339 | 0 | 2037 | PD6 |  |  |  | SC |  | South Cell Concrete Columns |  | 790900031 | DSC07940 | 400000 | Rust spots was observed. | Corroded was observed exposed reinforcement. | Loss of cement was observed. |  |  | 2006 | 46 | [8 empty] | 3 | 5 | The asset was observed to be in fair condition. Provisions for structural repairs. South cell concrete columns to be replaced at the end of remaining service life. | 0 | 2022 |  | Stouffville PD6 Reservoir Capital Project 1 | Stouffville PD6 Reservoir Capital Project 2
2340 | 0 | 2037 | PD6 |  |  |  | SC |  | South Cell Concrete Roof |  | 790900031 | DSC07940 | 3600000 | Rust spots was observed. | Corroded was observed wire ties. | Exposed corroded reinforcement was observed. |  |  | 2006 | 46 | [8 empty] | 3 | 5 | The asset was observed to be in fair condition. Provisions for structural repairs. South cell concrete roof to be replaced at the end of remaining service life. | 0 | 2022 |  | Stouffville PD6 Reservoir Capital Project 1 | Stouffville PD6 Reservoir Capital Project 2
2341 | 0 | 2037 | PD6 |  |  |  | SC |  | South Cell Concrete Beams |  | 790900031 | IMG_2848 | 7000 | Corroded was observed wire ties. |  |  |  |  | 2006 | 46 | [8 empty] | 3 | 5 | The asset was observed to be in fair condition. Provisions for structural repairs. South cell concrete beams to be replaced at the end of remaining service life. | 0 | 2022 |  | Stouffville PD6 Reservoir Capital Project 1 | Stouffville PD6 Reservoir Capital Project 2
2342 | 0 | 2037 | PD6 |  |  |  | SC |  | North Cell Concrete Beams |  | 790900031 | DSC07735 | 7000 | Rust spots was observed. | Corroded was observed wire ties. |  |  |  | 2006 | 46 | [8 empty] | 3 | 5 | The asset was observed to be in fair condition. Provisions for structural repairs. North cell concrete beams to be replaced at the end of remaining service life. | 0 | 2022 |  | Stouffville PD6 Reservoir Capital Project 1 | Stouffville PD6 Reservoir Capital Project 2
2343 | 0 |  | PD6 |  |  |  | SC |  | Rear Access House Concrete Blockwalls |  | 19042 | IMG_2248 | 7500 | [5 empty] | 2006 | 46 | [8 empty] | 2 | 4 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Rear access house concrete blockwalls to be replaced at the end of remaining service life. | 0 | 2030 |  | Stouffville PD6 Reservoir Capital Project 1
2344 | 0 |  | PD6 |  |  |  | SC |  | Rear Access House Precast Concrete Roof |  | 19042 | IMG_2250 | 3000 | [5 empty] | 2006 | 46 | [8 empty] | 2 | 3 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Rear access house precast concrete roof to be replaced at the end of remaining service life. | 0 | 2030 |  | Stouffville PD6 Reservoir Capital Project 1
2345 | 0 |  | PD6 |  |  |  | SC |  | Rear Access House Wood Truss Roof |  | 19042 | IMG_2218 | 5000 | [5 empty] | 2006 | 46 | [8 empty] | 2 | 3 | The asset was observed to be in good condition. Rear access house wood truss roof to be replaced at the end of remaining service life. | 0
2346 | 0 |  | PD6 |  |  |  | SC |  | Rear Access House Aluminum Guardrails |  | 19042 | IMG_2247 | 1500 |  | Corrosion was observed on grab handles. |  |  |  | 2006 | 46 | [8 empty] | 2 | 2 | The asset was observed to be in good condition. Rear access house aluminum guardrails to be replaced at the end of remaining service life. | 0
2347 | 0 |  | PD6 |  |  |  | SC |  | Valve House Concrete Walls |  | 25383 | DSC00640 | 200000 | [5 empty] | 2006 | 46 | [8 empty] | 2 | 4 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Valve house concrete walls to be replaced at the end of remaining service life. | 0 | 2030 |  | Stouffville PD6 Reservoir Capital Project 1
2348 | 0 |  | PD6 |  |  |  | SC |  | Valve House Precast Concrete Roof |  | 19041 | DSC00641 | 50000 | [5 empty] | 2006 | 46 | [8 empty] | 2 | 4 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Valve house precast concrete roof to be replaced at the end of remaining service life. | 0 | 2030 |  | Stouffville PD6 Reservoir Capital Project 1
2349 | 0 |  | PD6 |  |  |  | SC |  | Valve House Wood Truss Roof |  | 19041 | IMG_2862 | 50000 | [5 empty] | 2006 | 46 | [8 empty] | 2 | 3 | The asset was observed to be in good condition. Valve house wood truss roof to be replaced at the end of remaining service life. | 0
2350 | 0 |  | PD6 |  |  |  | SC |  | Valve House Guardrails |  | 19041 | DSC00625 | 12000 | [5 empty] | 2006 | 46 | [8 empty] | 2 | 3 | The asset was observed to be in good condition. Valve house guardrails to be replaced at the end of remaining service life. | 0
2351 | 0 |  | PD6 |  |  |  | SC |  | Valve Gallery Concrete Floor Slab |  | 25384 | DSC00676 | 115000 | [5 empty] | 2006 | 46 | [8 empty] | 2 | 3 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Valve gallery concrete floor slab to be replaced at the end of remaining service life. | 0 | 2030 |  | Stouffville PD6 Reservoir Capital Project 1
2352 | 0 | 2037 | PD6 |  |  |  | SC |  | Valve Gallery Concrete Walls |  | 25384 | DSC00676 | 300000 | Cracking was observed with efflorescence on reservoir walls. |  |  |  |  | 2006 | 46 | [8 empty] | 3 | 4 | The asset was observed to be in fair condition. Provisions for structural repairs. Valve gallery concrete walls to be replaced at the end of remaining service life. | 0 | 2022 |  | Stouffville PD6 Reservoir Capital Project 1 | Stouffville PD6 Reservoir Capital Project 2
2353 | 0 |  | PD6 |  |  |  | SC |  | Valve Gallery Concrete Beams |  | 25384 | DSC00658 | 33000 | [5 empty] | 2006 | 46 | [8 empty] | 2 | 4 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Valve gallery concrete beams to be replaced at the end of remaining service life. | 0 | 2030 |  | Stouffville PD6 Reservoir Capital Project 1
2354 | 0 |  | PD6 |  |  |  | SC |  | Valve Gallery Aluminum Platform |  | 25384 | DSC00682 | 15000 | [5 empty] | 2006 | 46 | [8 empty] | 2 | 3 | The asset was observed to be in good condition. Valve gallery aluminum platform to be replaced at the end of remaining service life. | 0
2355 | 0 |  | PD6 |  |  |  | SC |  | Valve House Aluminum Hatch |  | 19041 | DSC00607 | 5000 |  |  |  | Overflow |  | 2006 | 46 | [8 empty] | 2 | 2 | The asset was observed to be in good condition. Valve house aluminum hatch to be replaced at the end of remaining service life. | 0
2356 | 0 |  | PD6 |  |  |  | AC |  | Rear Access House Access Door (Single) |  | 19042 | DSC07861 | 3500 | [5 empty] | 2006 | 7 | [8 empty] | 2 | 1 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1
2357 | 0 |  | PD6 |  |  |  | AC |  | Valve House Access Door (Single) |  | 19041 | DSC00629 | 5500 |  |  |  | To north cell |  | 2006 | 7 | [8 empty] | 2 | 1 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1
2358 | 0 |  | PD6 |  |  |  | AC |  | Valve House Access Door (Single) |  | 19041 | DSC00614 | 5500 |  |  |  | To south cell |  | 2006 | 7 | [8 empty] | 2 | 1 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1
2359 | 0 |  | PD6 |  |  |  | AC |  | Valve Gallery Wall and Ceiling Paint |  | 25384 | DSC00658 | 20000 | [5 empty] | 2006 | 7 | [8 empty] | 2 | 1 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1
2360 | 0 |  | PD6 |  |  |  | AC |  | Valve House Wall Paint |  | 25383 | DSC00641 | 15000 | [5 empty] | 2006 | 7 | [8 empty] | 2 | 1 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1
2361 | 0 |  | PD6 |  |  |  | AC |  | Rear Access House Wall and Ceiling Paint |  | 19042 | IMG_2247 | 2000 | [5 empty] | 2006 | 7 | [8 empty] | 2 | 1 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1
2362 | 0 |  | PD6 |  |  |  | AC |  | Rear Access House Exterior Brick Veneer |  | 19042 | DSC07860 | 8000 | [5 empty] | 2006 | 7 | [8 empty] | 2 | 1 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1
2363 | 0 |  | PD6 |  |  |  | AC |  | Rear Access House Metal Roofing |  | 19042 | DSC07860 | 3000 | [5 empty] | 2006 | 7 | [8 empty] | 2 | 1 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1
2364 | 0 |  | PD6 |  |  |  | AC |  | Access House Metal Roofing |  | 25383 | DSC07844 | 35000 | [5 empty] | 2006 | 7 | [8 empty] | 2 | 1 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1
2365 | 0 |  | PD6 |  |  |  | AC |  | Access House Exterior Brick Veneer |  | 25383 | DSC07844 | 65000 | [5 empty] | 2006 | 7 | [8 empty] | 2 | 1 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1
2366 | 0 |  | PD6 |  |  |  | AC |  | North Cell Stainless Door |  | 790900031 | DSC07714 | 10000 | Corrosion on hardware was observed. |  |  |  |  | 2006 | 7 | [8 empty] | 3 | 1 | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1
2367 | 0 |  | PD6 |  |  |  | AC |  | South Cell Stainless Door |  | 790900031 | DSC07939 | 10000 | Corrosion on hardware was observed. |  |  |  |  | 2006 | 7 | [8 empty] | 3 | 1 | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1
2368 | 0 |  | PD6 |  |  |  | SW |  | Drain Chamber Precast Concrete Structure |  | 790900031 | DSC07758 | 60000 |  |  |  | 2.4m diameter precast |  | 2006 | 12 | [8 empty] | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2371 | 0 |  | PD6 |  |  |  | SW |  | Drain Chamber Ladder |  | 790900031 | DSC07758 | 2500 | [5 empty] | 2006 | 12 | [8 empty] | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2372 | 0 |  | PD6 |  |  |  | SW |  | Drain Chamber Manhole Cover and Frame |  | 790900031 | DSC07757 | 3000 | [5 empty] | 2006 | 12 | [8 empty] | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2375 | 0 |  | PD6 |  |  |  | SW |  | Asphalt Access Road |  | 790900031 | DSC07804 | 215000 | Cracking was noted throughout was observed. |  |  | approx. 3050 sq m. |  | 2006 | 12 | [8 empty] | 3 | 2 | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2328 | 0 | 2037 | PD6 |  |  |  | SC |  | North Cell Concrete Floor Slab |  | 790900031 | DSC07720 | 3700000 | Hairline cracking with efflorescence deposits was observed. | Rust spots was observed. | Debonded expansion joints was observed. |  |  | 2006 | 46 | [8 empty] | 3 | 5 | The asset was observed to be in fair condition. Provisions for structural repairs. North cell concrete floor slab to be replaced at the end of remaining service life. | 0 | 2022 |  | Stouffville PD6 Reservoir Capital Project 1 | Stouffville PD6 Reservoir Capital Project 2
2329 | 0 | 2037 | PD6 |  |  |  | SC |  | North Cell Concrete Walls |  | 790900031 | DSC07720 | 2700000 | Hairline cracking with efflorescence deposits was observed. | Debonded expansion joints and active leaking at expansion joint at dividing wall was observed. | Bugholes was observed. |  |  | 2006 | 46 | [8 empty] | 3 | 4 | The asset was observed to be in fair condition. Provisions for structural repairs. North cell concrete walls to be replaced at the end of remaining service life. | 0 | 2022 |  | Stouffville PD6 Reservoir Capital Project 1 | Stouffville PD6 Reservoir Capital Project 2
2330 | 0 | 2037 | PD6 |  |  |  | SC |  | North Cell Concrete Columns |  | 790900031 | DSC07720 | 400000 | Rust spots was observed. | Loss of cement was observed. |  |  |  | 2006 | 46 | [8 empty] | 3 | 5 | The asset was observed to be in fair condition. Provisions for structural repairs. North cell concrete columns to be replaced at the end of remaining service life. | 0 | 2022 |  | Stouffville PD6 Reservoir Capital Project 1 | Stouffville PD6 Reservoir Capital Project 2
2331 | 0 | 2037 | PD6 |  |  |  | SC |  | North Cell Concrete Roof |  | 790900031 | DSC07720 | 3600000 | Rust spots was observed. | Corroded was observed wire ties. | Exposed corroded reinforcement was observed. |  |  | 2006 | 46 | [8 empty] | 3 | 5 | The asset was observed to be in fair condition. Provisions for structural repairs. North cell concrete roof to be replaced at the end of remaining service life. | 0 | 2022 |  | Stouffville PD6 Reservoir Capital Project 1 | Stouffville PD6 Reservoir Capital Project 2
2332 | 0 |  | PD6 |  |  |  | SC |  | North Cell Aluminum Ladder |  | 790900031 | DSC07734 | 5000 | Corrosion was observed at top. |  |  |  |  | 2006 | 46 | [8 empty] | 3 | 2 | The asset was observed to be in fair condition. North cell aluminum ladder to be replaced at the end of remaining service life. | 0
2150 | 0 |  | PD6 |  |  |  | SIC | 00018388 |  | Markham N PD6 RES MCC Level | 25383 |  | 5000 |  |  |  | MKNRPVW101, Network, OIT |  | 2006 | 7 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1 |  |  | M01026 | SCADA
2151 | 0 |  | PD6 |  |  |  | SIC | 00018394 | UPS | Markham N PD6 RES MCC Level | 25383 |  | 1000 |  |  |  | MKNRUPS101, Network, UPS |  | 2006 | 7 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1 |  |  | M00728 | SCADA
2152 | 0 |  | PD6 |  |  |  | SIC | 00018395 |  | Markham N PD6 RES MCC Level | 25383 |  | 2000 |  |  |  | MKNRRAD101, Network, Radio Modem |  | 2006 | 7 |  |  | East |  |  |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1 |  |  | M01018 | SCADA
2153 | 0 |  | PD6 |  |  |  | SIC | 00018396 | Network and Communication equipment | Markham N PD6 RES MCC Level | 25383 | IMG_2510 | 8000 |  |  |  | MKNRRAD102, Network, Antenna & Cable; ; Wilson; ; ; ;1 |  | 2006 | 7 |  |  | East |  |  |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1 |  |  |  | SCADA
2154 | 0 |  | PD6 |  |  |  | SIC | 00018397 |  | Markham N PD6 RES MCC Level | 25383 |  | 0 |  |  |  | MKNRRPU101, RPU, RPU Panel |  | 2006 | 2 |  |  | East |  |  |  |  | W-WW | 3 | 3 | The asset was assumed to be in fair condition. Asset to be replaced in the short term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1 |  |  | M00020 | SCADA
2155 | 0 |  | PD6 |  |  |  | SIC | 00018389 |  | Markham N PD6 RES Valve Gallery | 25384 |  | 1500 |  |  |  | MKNRTSH800, High Alarm, Temperature Switch, Temperature |  | 2006 | 7 |  |  | East |  | F5000979 |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1 |  |  | M00996 | Instrumentation and Control
2156 | 0 |  | PD6 |  |  |  | SIC | 00018390 | Chlorine Analyzer | Markham N PD6 RES Valve Gallery | 25384 | IMG_2373 | 15000 |  |  |  | MKNR_AIT1, Total Residual, Chlorine Analyzer, Chlorine; HACH; CL17 |  | 2006 | 7 |  |  | East |  | 060500015590 |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1 |  |  | M00482 | Instrumentation and Control
2157 | 0 |  | PD6 |  |  |  | SIC | 00018391 | High Level Floats | Markham N PD6 RES Valve Gallery | 790900031 | DSC07875 | 1000 |  |  |  | MKNRLSH101, High Level Alarm, Float Switch, Level; ; ; ; 2 |  | 2006 | 7 |  |  | East |  |  |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1 |  |  | M00061 | Instrumentation and Control
2158 | 0 |  | PD6 |  |  |  | SIC | 00018392 | Ultrasonic Level | Markham N PD6 RES MCC Level | 790900031 | DSC07877 | 7600 |  |  |  | MKNR_LIT1, Cell 1, Ultrasonic Level, Level; ; ; ; 1 |  | 2006 | 7 |  |  | East |  | 031405199VX |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1 |  |  | M00105 | Instrumentation and Control
2159 | 0 |  | PD6 |  |  |  | SIC | 00018393 | Cell 2 Ultrasonic Level sensor | Markham N PD6 RES MCC Level | 25383 | DSC07942 | 7600 |  |  |  | MKNR_LIT2, Cell 2, Ultrasonic Level, Level |  | 2006 | 7 |  |  | East |  | 031405250VX |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1 |  |  | M00105 | Instrumentation and Control
2160 | 0 |  | PD6 |  |  |  | ES | 00043542 | Monorail Switch | Markham N PD6 RES Valve Gallery | 25384 | IMG_2478 | 15000 |  |  |  | S 1, North Monorail Switch, Hoist Beam;Hammond; ; 575V, 3ph, 40hp |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00118
2161 | 0 |  | PD6 |  |  |  | ES | 00043543 | South Monorail Switch | Markham N PD6 RES Valve Gallery | 25384 | IMG_2474 | 15000 |  |  |  | S 2, South Monorail Switch, Hoist Beam; Hammond; ; 575V, 3ph, 40hp |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00118
2162 | 0 |  | PD6 |  |  |  | BM | 00043544 | Electrical Unit Heater, EH-4 | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2183 | 2500 | Good was observed condition. |  |  | EH 4, Heating System, Unit Heater, 7.5 kW, 575VAC/3ph, by Ouellet, located in basement, |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 3 | 2 | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00111
2163 | 0 |  | PD6 |  |  |  | SC | 00043546 | Rear Access House Davit Base (South) | Markham N PD6 RES East Hatch Building | 19042 | IMG_2235 | 3000 |  |  |  | South, Fall Arrest System, Davit Arm Base |  | 2006 | 46 |  |  | East |  |  |  |  | W-WW | 2 | 4 | The asset was observed to be in good condition. Rear access house davit base (south) to be replaced at the end of remaining service life. | 0 |  |  |  |  | M10152
2164 | 0 |  | PD6 |  |  |  | SC | 00043545 | Rear Access House Davit Arm | Markham N PD6 RES East Hatch Building | 19042 | IMG_2233 | 0 |  |  |  | Fall Arrest System, Davit Arm |  | 2009 | 49 |  |  | East |  | 12420657 |  |  | W-WW | 2 | 4 | The asset was observed to be in good condition. Rear access house davit arm to be replaced at the end of remaining service life. | 0 |  |  |  |  | M10152
2165 | 0 |  | PD6 |  |  |  | SC | 00043547 | Rear Access House Davit Base (North) | Markham N PD6 RES East Hatch Building | 19042 | IMG_2234 | 3000 |  |  |  | North, Fall Arrest System, Davit Arm Base |  | 2006 | 46 |  |  | East |  |  |  |  | W-WW | 2 | 4 | The asset was observed to be in good condition. Rear access house davit base (north) to be replaced at the end of remaining service life. | 0 |  |  |  |  | M10152
2166 | 0 |  | PD6 |  |  |  | ES | 00026045 | LP-B Panel | Markham N PD6 RES East Hatch Building | 19042 | IMG_2502 | 10300 | Panel was inside wooden cabinet. it needed to be replaced with nema 4x rated panel was observed. | Minor corrosion was observed. |  | LP B, Panel Board, Lighting Panel; Siemens; ; 120/208V; 125A, 36CCT; 1 |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 3 | 3 | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00317
2167 | 0 |  | PD6 |  |  |  | HSS | 00043524 | Valve House First Aid Kit | Markham N PD6 RES MCC Level | 25383 |  | 50 |  |  |  | First Aid Kit, First Aid Kit |  | 2006 | 2 |  |  | East |  |  |  |  | W-WW | 3 | 3 | The asset was assumed to be in fair condition. Asset to be replaced in the short term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1 |  |  | M10151
2168 | 0 |  | PD6 |  |  |  | ES | 00043528 |  | Markham N PD6 RES MCC Level | 25383 |  | 0 |  |  |  | Outside Timer, Lighting, Outside Timer |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 3 | 2 | The asset was assumed to be in fair condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00523
2169 | 0 |  | PD6 |  |  |  | AC | 00019069 | Valve House Access Door (Single) | Markham N PD6 RES MCC Level | 25383 | IMG_2862 | 3500 |  |  |  | Main Entrance, Door, Exterior Single Metal |  | 2006 | 7 |  |  | East |  |  |  |  | W-WW | 2 | 1 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1
2170 | 0 |  | PD6 |  |  |  | AC | 00019046 | Valve House Access Door (Single) | Markham N PD6 RES MCC Level | 25383 | DSC00630 | 3500 |  |  |  | Valve Gallery Stair Well, Door, Interior Single Metal With Window |  | 2006 | 7 |  |  | East |  |  |  |  | W-WW | 2 | 1 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1
2171 | 0 |  | PD6 |  |  |  | AC | 00019068 | Valve House Access Door (Single) | Markham N PD6 RES Pipe Gallery Stairwell | 19043 | IMG_2862 | 3500 |  |  |  | Access to Valve Gallery, Door, Exterior Single Metal |  | 2006 | 7 |  |  | East |  |  |  |  | W-WW | 2 | 1 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1
2172 | 0 |  | PD6 |  |  |  | PM | 00043498 | Gate Valve | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2092 | 2000 |  |  |  | Wash Down Inlet Isolation, Valve, Gate, 75mm DIA, DI construction, non-rising stem, manual, located in basement |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00145
2173 | 0 |  | PD6 |  |  |  | PM | 00043499 | Air Vacuum Release Valve | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2137 | 2500 |  |  |  | Watermain Crossover, Valve, Air-Vacuum Release; 25 mm DIA, Val-Matic model 201C; located in basement |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00926
2174 | 0 |  | PD6 |  |  |  | PM | 00043500 | Air Vacuum Release Valve | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2158 | 0 |  |  |  | North Watermain, Valve, Air-Vacuum Release, 25 mm DIA, Val-Matic model 201C; located in basement |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00926
2175 | 0 |  | PD6 |  |  |  | PM | 00043501 | Gate Valve | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2147 | 5000 |  |  |  | North Cell Drain, Valve, Gate; 300 mm DIA, DI construction, rising stem, by AVK; located in basement |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00210
2176 | 0 |  | PD6 |  |  |  | ES | 00043502 |  | Markham N PD6 RES MCC Level | 790900031 |  | 0 |  |  |  | Switch, Main Service |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 3 | 3 | The asset was assumed to be in fair condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2177 | 0 |  | PD6 |  |  |  | ES | 00043503 | Digital Meter | Markham N PD6 RES MCC Level | 25383 | IMG_2201 | 28500 |  |  |  | DMU Monitor, Switch, MCC Equipment Control; Siemens; Access 9330; ; ; digital |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2178 | 0 |  | PD6 |  |  |  | ES | 00043504 | EH-1 Breaker | Markham N PD6 RES MCC Level | 25383 | IMG_2203 | 900 |  |  |  | Unit Heater EH 1, Switch, MCC Disconnect; Siemens; ; ; 600V, 20A; |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2179 | 0 |  | PD6 |  |  |  | ES | 00043505 | EH-2 Breaker | Markham N PD6 RES MCC Level | 25383 | IMG_2203 | 800 |  |  |  | Unit Heater EH 2, Switch, MCC Disconnect; Siemens; ; ; 600V, 15A; |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2180 | 0 |  | PD6 |  |  |  | ES | 00043506 | EH-3 Breaker | Markham N PD6 RES MCC Level | 25383 | IMG_2205 | 800 |  |  |  | Unit Heater EH 3, Switch, MCC Disconnect; Siemens; ; ; 600V, 15A; |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2181 | 0 |  | PD6 |  |  |  | ES | 00043517 | EH-4 Breaker | Markham N PD6 RES MCC Level | 25383 | IMG_2222 | 800 |  |  |  | Unit Heater EH 4, Switch, MCC Disconnect; Siemens; ; ; 600V, 15A; |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2182 | 0 |  | PD6 |  |  |  | ES | 00043518 | EH-5 Breaker | Markham N PD6 RES MCC Level | 25383 | IMG_2222 | 800 |  |  |  | Unit Heater EH 5, Switch, MCC Disconnect; Siemens; ; ; 600V, 15A; |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2183 | 0 |  | PD6 |  |  |  | ES | 00043507 | Monorail M-1 Breaker | Markham N PD6 RES MCC Level | 25383 | IMG_2205 | 800 |  |  |  | Monorail Crane M 1, Switch, MCC Disconnect; Siemens; ; ; 600V, 15A; |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2184 | 0 |  | PD6 |  |  |  | ES | 00043508 | Monorail M-2 Breaker | Markham N PD6 RES MCC Level | 25383 | IMG_2209 | 800 |  |  |  | Monorail Crane M 2, Switch, MCC Disconnect; Siemens; ; ; 600V, 15A; |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2185 | 0 |  | PD6 |  |  |  | ES | 00043509 | M-100 Valve Breaker | Markham N PD6 RES MCC Level | 25383 | IMG_2209 | 800 |  |  |  | Rotork Actuator M 100, Switch, MCC Disconnect; Siemens; ; ; 600V, 15A; |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2186 | 0 |  | PD6 |  |  |  | ES | 00043510 | M-200 Valve Breaker | Markham N PD6 RES MCC Level | 25383 | IMG_2214 | 800 |  |  |  | Rotork Actuator M 200, Switch, MCC Disconnect; Siemens; ; ; 600V, 15A; |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2187 | 0 |  | PD6 |  |  |  | ES | 00043511 | M-300 Valve Breaker | Markham N PD6 RES MCC Level | 25383 | IMG_2214 | 800 |  |  |  | Rotork Actuator M 300, Switch, MCC Disconnect; Siemens; ; ; 600V, 15A; |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2188 | 0 |  | PD6 |  |  |  | ES | 00043512 | M-700 Valve Starter | Markham N PD6 RES MCC Level | 25383 | IMG_2217 | 6400 |  |  |  | Washdown Pump M 700, Switch, MCC Equipment Control; Siemens; ; ; 600V, size 2 starter; |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2189 | 0 |  | PD6 |  |  |  | ES | 00043513 | M-400 Valve Breaker | Markham N PD6 RES MCC Level | 25383 | IMG_2218 | 800 |  |  |  | Rotork Actuator M 400, Switch, MCC Disconnect; Siemens; ; ; 600V, 15A; |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2190 | 0 |  | PD6 |  |  |  | ES | 00043514 | M-500 Valve Breaker | Markham N PD6 RES MCC Level | 25383 | IMG_2218 | 800 |  |  |  | Rotork Actuator M 500, Switch, MCC Disconnect; Siemens; ; ; 600V, 15A; |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2191 | 0 |  | PD6 |  |  |  | ES | 00043515 | M-600 Valve Breaker | Markham N PD6 RES MCC Level | 25383 | IMG_2219 | 800 |  |  |  | Rotork Actuator M 600, Switch, MCC Disconnect; Siemens; ; ; 600V, 15A; |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2192 | 0 |  | PD6 |  |  |  | ES | 00043516 | Overhead Door Breaker | Markham N PD6 RES MCC Level | 25383 | IMG_2219 | 800 |  |  |  | Overhead Door, Switch, MCC Disconnect; ; ; 600V, 15A; |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2193 | 0 |  | PD6 |  |  |  | ES | 00043519 | Welding Receptacle Breaker | Markham N PD6 RES MCC Level | 25383 | IMG_2223 | 1200 |  |  |  | Welding Receptacles, Switch, MCC Disconnect; ; ; 600V, 30A; |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2194 | 0 |  | PD6 |  |  |  | ES | 00043520 | LP-A Transformer Breaker | Markham N PD6 RES MCC Level | 25383 | IMG_2223 | 800 |  |  |  | Transformer LP A, Switch, MCC Disconnect; ; ; 600V, 15A; |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2195 | 0 |  | PD6 |  |  |  | ES | 00043521 | Dehumidifier Transformer Breaker | Markham N PD6 RES MCC Level | 25383 | IMG_2225 | 900 |  |  |  | Transformer DHU 1, Switch, MCC Disconnect; ; ; 600V, 20A; |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2196 | 0 |  | PD6 |  |  |  | ES | 00043522 | LP-B Transformer Breaker | Markham N PD6 RES MCC Level | 25383 | IMG_2225 | 900 |  |  |  | Transformer LP B, Switch, MCC Disconnect; ; ; 600V, 15A; |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2197 | 0 |  | PD6 |  |  |  | HSS | 00043523 | Valve House Eye Wash Station | Markham N PD6 RES MCC Level | 25383 | DSC07815 | 600 |  |  |  | Health and Safety Compliance Systems, Tank, Portable, Eye Wash |  | 2006 | 7 |  |  | East |  |  |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1 |  |  | M00233 | Health and Safety
2198 | 0 |  | PD6 |  |  |  | PM | 00043525 | Sump Pump, P-2 | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2043 | 3000 |  |  |  | Sump pump, P-2; 120VAC/1ph, 4/10 hp; submersible, centrifugal, by Liberty Pumps model HT40-Series; powered from LP-A; located in basement |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2199 | 0 |  | PD6 |  |  |  | PM | 00043494 | Gate Valve | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2052 | 5000 |  |  |  | South Cell Drain, Valve, Gate; 300 mm DIA, DI construction, rising stem, by AVK; located in basement |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00210
2200 | 0 |  | PD6 |  |  |  | PM | 00043495 | Air Vacuum Release valve | Markham N PD6 RES MCC Level | 25383 | IMG_2027 | 0 |  |  |  | South Watermain, Valve, Vacuum Release; 25 mm DIA, Val-Matic model 201C; located in basement |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00926
2201 | 0 |  | PD6 |  |  |  | PM | 00026021 | Electrical Motor, reservoir washdown pump | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2082 | 8000 |  |  |  | Wash Down Pump, Electrical Motor, Induction; by Baldor Electric Co., 20 hp; 575VAC/3ph; 18.2 Amps; 3520 rpm; Class F , located in basement |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00015
2202 | 0 |  | PD6 |  |  |  | PM | 00043496 | Check Valve | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2097 | 2000 |  |  |  | Wash Down Outlet, Valve, Swing Flex Check; by Val Matci model 503A, 75 mm DIA, DI construction, |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00926
2203 | 0 |  | PD6 |  |  |  | PM | 00043497 | Gate Valve | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2097 | 2000 |  |  |  | Wash Down Outlet, Valve, Gate, 75 mm DIA; flanged, OS&Y; DI construction, manual; AVK |  | 2006 | 16 |  |  | East |  | 25-080-4602600429 |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00210
2204 | 0 |  | PD6 |  |  |  | ES | 00043526 | EM-2 Emergency Battery Unit Light | Markham N PD6 RES Pipe Gallery Stairwell | 19043 | IMG_2339 | 500 |  |  |  | EM 2, Lighting, Emergency |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00606
2205 | 0 |  | PD6 |  |  |  | ES | 00043530 | EM-3 Emergency Battery Unit Light | Markham N PD6 RES Mezzanine | 19041 | IMG_2311 | 500 |  |  |  | EM 3, Lighting, Emergency |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00606
2206 | 0 |  | PD6 |  |  |  | ES | 00043527 | EM-1 Emergency Battery Unit Light | Markham N PD6 RES MCC Level | 25383 | IMG_2257 | 500 |  |  |  | EM 1, Lighting, Emergency |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00606
2207 | 0 |  | PD6 |  |  |  | BM | 00043529 | Fire Extinguishers, HS-FE1, HS_FE2, HS_FE3 | Stouffville PD6 Reservoir | 790900031 | IMG_1971, IMG_2828, IMG_2826 | 500 |  |  |  | 3 Fire Extinguishers, Other Life Safety & Compliance, Kidde dry chemical |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2208 | 0 |  | PD6 |  |  |  | BM | 00026032 | Valve House Air Handling System | Markham N PD6 RES MCC Level | 790900031 | IMG_1933 | 35000 |  |  |  | DHU 1, Air Handling System, Dehumidifier, Bry- Air Model Mini PAC-350, 208VAC/3ph; main floor |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2209 | 0 |  | PD6 |  |  |  | ES | 00026033 | Dehumidifier Local DS | Markham N PD6 RES MCC Level | 25383 | IMG_2261 | 1000 |  |  |  | Dehumidifier DHU 1, Switch, Local Disconnect |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2210 | 0 |  | PD6 |  |  |  | ES | 00026034 | DHU-1 Transformer | Markham N PD6 RES MCC Level | 25383 | IMG_2263 | 11900 |  |  |  | 15 kVA, Dehumidifier DHU 1, Transformer, Power; MARCUS; ;600-120/208V |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00620
2211 | 0 |  | PD6 |  |  |  | SIC | 00026042 | Security Panel | Markham N PD6 RES MCC Level | 25383 | IMG_2244 | 7000 |  |  |  | Security System; Honeywell |  | 2006 | 7 |  |  | East |  |  |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1 |  |  | M01094
2212 | 0 |  | PD6 |  |  |  | ES | 00026043 | LP-A Panel | Markham N PD6 RES MCC Level | 25383 | IMG_2236 | 10300 |  |  |  | LP A, Panel Board, Lighting Panel; Siemens; 120/208V, 125A, 30CCT |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2213 | 0 |  | PD6 |  |  |  | SIC | 00026039 |  | Markham N PD6 RES MCC Level | 25383 |  | 0 |  |  |  | RPU, RPU Panel |  | 2006 | 2 |  |  | East |  |  |  |  | W-WW | 3 | 3 | The asset was assumed to be in fair condition. Asset to be replaced in the short term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1
2214 | 0 |  | PD6 |  |  |  | ES | 00026036 | MCC-1 | Markham N PD6 RES MCC Level | 25383 | IMG_2193 | 60000 |  |  |  | MCC 1, Motor Control Centre; Siemens; tiastar; 600V, 600A, 4 Columns |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2215 | 0 |  | PD6 |  |  |  | ES | 00026025 | EH-1 Local DS | Markham N PD6 RES MCC Level | 25383 | IMG_2229 | 600 |  |  |  | Unit Heater EH 1, Switch, Local Disconnect; 600V, 30A, non-fused |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2216 | 0 |  | PD6 |  |  |  | ES | 00026038 | Overhead Door local DS | Markham N PD6 RES MCC Level | 25383 | IMG_2184 | 600 |  |  |  | Overhead Door, Switch, Local Disconnect |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2217 | 0 |  | PD6 |  |  |  | ES | 00026026 | EH-2 local DS | Markham N PD6 RES MCC Level | 25383 | IMG_2181 | 600 |  |  |  | Unit Heater EH 2, Switch, Local Disconnect; 600V, 30A, non-fused |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2218 | 0 |  | PD6 |  |  |  | ES | 00026030 | EF-1 Exhaust Fan | Markham N PD6 RES MCC Level | 25383 | IMG_2178 | 4000 |  |  |  | EF 1, Ventilation System, Exhaust Fan;Baldor; L3403; 1/4hp, 120V |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00015
2219 | 0 |  | PD6 |  |  |  | AC | 00019077 | Valve House Access Door (Single) | Markham N PD6 RES Mezzanine | 19041 | DSC07842 | 3500 |  |  |  | North East, Door, Exterior Single Metal |  | 2006 | 7 |  |  | East |  |  |  |  | W-WW | 2 | 1 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1
2220 | 0 |  | PD6 |  |  |  | SC | 00019072 | North Cell Aluminum Hatch | Markham N PD6 RES Mezzanine | 19041 | DSC00627 | 5000 |  |  |  | North Cell, Hatch |  | 2006 | 46 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. North cell aluminum hatch to be replaced at the end of remaining service life. | 0
2221 | 0 |  | PD6 |  |  |  | SC | 00019071 | South Cell Aluminum Hatch | Markham N PD6 RES Mezzanine | 19041 | DSC00610 | 5000 |  |  |  | South Cell, Hatch |  | 2006 | 46 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. South cell aluminum hatch to be replaced at the end of remaining service life. | 0
2222 | 0 |  | PD6 |  |  |  | SC | 00019063 | Precast Concrete Hatch | Markham N PD6 RES MCC Level | 25383 | DSC00643 | 1500 |  |  |  | Concrete, Access To Valve Gallery, Hatch |  | 2006 | 46 |  |  | East |  |  |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Precast concrete hatch to be replaced at the end of remaining service life. | 0 | 2030 |  | Stouffville PD6 Reservoir Capital Project 1
2223 | 0 |  | PD6 |  |  |  | SC | 00019079 | Access House Concrete Staircase | Markham N PD6 RES MCC Level | 25383 | DSC07764 | 15000 |  |  |  | MCC Level to Mezzanine, Stair Interior, Concrete |  | 2006 | 46 |  |  | East |  |  |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Access house concrete staircase to be replaced at the end of remaining service life. | 0 | 2030 |  | Stouffville PD6 Reservoir Capital Project 1
2224 | 0 |  | PD6 |  |  |  | BM | 00026047 | Rear Access House Baseboard Heater | Markham N PD6 RES East Hatch Building | 790900031 | IMG_2230 | 1000 | Surface corrosion was observed. |  |  | North Side, Heating System, Baseboard Heater, Rear Access House, 1 kW |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 3 | 2 | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2225 | 0 |  | PD6 |  |  |  | BM | 00026048 | Baseboard electrical heater | Markham N PD6 RES East Hatch Building | 790900031 | IMG_2244 | 1000 | Surface corrosion was observed. |  |  | North Side, Heating System, Baseboard Heater, Rear Access House, 1 kW |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 3 | 2 | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2226 | 0 |  | PD6 |  |  |  | SC | 00019065 | North Cell Concrete Staircase | Markham N PD6 RES Mezzanine | 19041 | DSC07704 | 30000 |  |  |  | Access to North Cell, Stair Interior, Concrete |  | 2006 | 46 |  |  | East |  |  |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. North cell concrete staircase to be replaced at the end of remaining service life. | 0 | 2030 |  | Stouffville PD6 Reservoir Capital Project 1
2227 | 0 |  | PD6 |  |  |  | SC | 00019064 | South Cell Concrete Staircase | Markham N PD6 RES Mezzanine | 19041 | IMG_2859 | 30000 |  |  |  | Access to South Cell, Stair Interior, Concrete |  | 2006 | 46 |  |  | East |  |  |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. South cell concrete staircase to be replaced at the end of remaining service life. | 0 | 2030 |  | Stouffville PD6 Reservoir Capital Project 1
2228 | 0 |  | PD6 |  |  |  | SC | 00019058 | Valve Gallery Concrete Staircase | Markham N PD6 RES Pipe Gallery Stairwell | 19043 | DSC00646 | 20000 |  |  |  | Stair Interior, Concrete |  | 2006 | 46 |  |  | East |  |  |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Valve gallery concrete staircase to be replaced at the end of remaining service life. | 0 | 2030 |  | Stouffville PD6 Reservoir Capital Project 1
2229 | 0 |  | PD6 |  |  |  | BM | 00043548 | Motorized Damper, MD-3 | Markham N PD6 RES MCC Level | 790900031 | IMG_1927 | 0 |  |  |  | MD 3 Dehumidifier, Ventilation System, Damperc/w Belimo actuator |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2230 | 0 |  | PD6 |  |  |  | BM | 00026031 | Exhaust Fan, EF-2 | Markham N PD6 RES MCC Level | 790900031 | IMG_1903 | 5000 |  |  |  | EF 2, Ventilation System, Exhaust Fan,inline centrifugal, by Carnes model VIBK08L1A5CL93S G1, 115VAC /1ph; 0.25hp motor; powered from LP-A |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2231 | 0 |  | PD6 |  |  |  | ES | 00026023 | M-1 Disconnect Switch | Markham N PD6 RES MCC Level | 25383 | IMG_2295 | 600 |  |  |  | Monorail Crane M 1, Switch, Local Disconnect; siemens; ID361NF, 600V, 30A, nonfused |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2232 | 0 |  | PD6 |  |  |  | ES | 00026027 | EH-3 local DS | Markham N PD6 RES MCC Level | 25383 | IMG_2308 | 600 |  |  |  | Unit Heater EH 3, Switch, Local Disconnect; siemens; 600V, 30A, nonfused |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2233 | 0 |  | PD6 |  |  |  | ES | 00026035 | LP-A Transformer | Markham N PD6 RES MCC Level | 25383 | IMG_2232 | 11900 |  |  |  | LP A, Transformer, Distribution; EVI; COTC6615VHC5VHC6XXBB; 15KVA, 600-120/208V |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00357
2234 | 0 |  | PD6 |  |  |  | ES | 00026024 | M-2 local DS | Markham N PD6 RES Valve Gallery | 25384 | IMG_2343 | 600 |  |  |  | Monorail Crane M 2, Switch, Local Disconnect;Siemens; ID361NF; 600V, 30A, non-fused |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2235 | 0 |  | PD6 |  |  |  | ES | 00026028 | EH-4 local DS | Markham N PD6 RES Valve Gallery | 25384 | IMG_2345 | 600 |  |  |  | Unit Heater EH 4, Switch, Local Disconnect;Siemens; ID361NF; 600V, 30A, non-fused |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2236 | 0 |  | PD6 |  |  |  | PM | 00026004 | Valve Local Disconnect Switch | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2025 | 5000 |  |  |  | Actuator M 100, Switch, Local Disconnect; by Siemens, 600 VAC, 3 poles, 30 Amps |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 4 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2237 | 0 |  | PD6 |  |  |  | PM | 00026003 | Butterfly valve electric actuator | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2018 | 10000 |  |  |  | M 100, Actuator, Electric; by Rotork Type IQ12, 575VAC/3 ph/60 Hz; torque 81 Nm |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 4 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00120
2238 | 0 |  | PD6 |  |  |  | PM | 00026002 | Butterfly Valve | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2005 | 40000 |  |  |  | V 100, Valve, Butterfly,flanged, 1050 mm DIA, by Val Matic model 2042P1; Class #150B; electrical actuator; |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 4 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2239 | 0 |  | PD6 |  |  |  | ES | 00026029 | EH-5 Local DS | Markham N PD6 RES Valve Gallery | 25384 | IMG_2402 | 600 |  |  |  | Unit Heater EH 5, Switch, Local Disconnect;Siemens; ID361NF; 600V, 30A, non-fused |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2240 | 0 |  | PD6 |  |  |  | ES | 00026019 | M-600 local DS | Markham N PD6 RES Valve Gallery | 25384 | IMG_2416 | 600 |  |  |  | Actuator M 600, Switch, Local Disconnect;Siemens; ID361NF; 600V, 30A, non-fused |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2241 | 0 |  | PD6 |  |  |  | PM | 00026017 | Butterfly Valve | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2109 | 40000 |  |  |  | V 600, Valve, Butterfly, 1050 mm DIA, flanged, by Val Matic model 2042P1; Class #150B; electrical actuator; |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 4 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2242 | 0 |  | PD6 |  |  |  | PM | 00026018 | Electric Actuator for Butterfly Valve | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2109 | 10000 |  |  |  | M 600 , Actuator, Electric; by Rotork Type IQ12, 575VAC/3 ph/60 Hz; torque 81 Nm |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 4 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00120
2243 | 0 |  | PD6 |  |  |  | ES | 00026022 | Washdown Pump Local DS | Markham N PD6 RES Valve Gallery | 25384 | IMG_2419 | 1100 |  |  |  | Wash Down Pump, Switch, Local Disconnect;Siemens; ID362NF; 600V, 60A, non-fused |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2244 | 0 |  | PD6 |  |  |  | PM | 00026016 | Valve Local Disconnect Switch | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2104 | 5000 |  |  |  | Actuator M 500, Switch, Local Disconnect, by Siemens, 600 VAC, 3 poles, 30 Amps |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 4 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2245 | 0 |  | PD6 |  |  |  | PM | 00026015 | Butterfly Valve Electric Actuator | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2104 | 10000 |  |  |  | M 500, Actuator, Electric; by Rotork Type IQ12, 575VAC/3 ph/60 Hz; torque 81 Nm |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 4 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00120
2246 | 0 |  | PD6 |  |  |  | PM | 00026014 | Butterfly Valve | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2104 | 40000 |  |  |  | V 500, Valve, Butterfly, 1050 mm DIA, flanged, by Val Matic model 2042P1; Class #150B; electrical actuator; |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 4 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2247 | 0 |  | PD6 |  |  |  | PM | 00026010 | Valve Local Disconnect Switch | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2116 | 5000 |  |  |  | Actuator M300, Switch, Local Disconnect; by Siemens, 600 VAC, 3 poles, 30 Amps |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 4 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2248 | 0 |  | PD6 |  |  |  | PM | 00026008 | Butterfly Valve | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2120 | 40000 |  |  |  | V 300, Valve, Butterfly; 1050 mm DIA, flanged, by Val Matic model 2042P1; Class #150B; electrical actuator; |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 4 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2249 | 0 |  | PD6 |  |  |  | PM | 00026009 | Butterfly Valve Electric Actuator | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2114 | 10000 |  |  |  | M 300, Actuator, Electric; by Rotork Type IQ12, 575VAC/3 ph/60 Hz; torque 81 Nm |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 4 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00120
2250 | 0 |  | PD6 |  |  |  | PM | 00026011 | Butterfly Valve | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2130 | 40000 |  |  |  | V 400, Valve, Butterfly; 1050 mm DIA, flanged, by Val Matic model 2042P1; Class #150B; electrical actuator; |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 4 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2251 | 0 |  | PD6 |  |  |  | PM | 00026012 | Butterfly Valve Electric Actuator | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2130 | 10000 |  |  |  | M 400, Actuator, Electric; by Rotork Type IQ12, 575VAC/3 ph/60 Hz; torque 81 Nm |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 4 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00120
2252 | 0 |  | PD6 |  |  |  | ES | 00026013 | M-400 local DS | Markham N PD6 RES Valve Gallery | 25384 | IMG_2461 | 600 |  |  |  | Actuator M 400, Switch, Local Disconnect;Siemens; ID361NF; 600V, 30A, non-fused |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2253 | 0 |  | PD6 |  |  |  | ES | 00026007 | M-200 local DS | Markham N PD6 RES Valve Gallery | 25384 | IMG_2466 | 600 |  |  |  | Actuator M 200, Switch, Local Disconnect;Siemens; ID361NF; 600V, 30A, non-fused |  | 2006 | 11 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00125
2254 | 0 |  | PD6 |  |  |  | BM | 00043533 | Electric Heater, EH-2 | Markham N PD6 RES MCC Level | 790900031 | IMG_1913 | 2500 |  |  |  | EH 2, Heating System, Unit Heater 5 kW, 575VAC/3ph, by Ouellet, located on main floor |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00111
2255 | 0 |  | PD6 |  |  |  | AC | 00043534 | Valve House Overhead Door | Markham N PD6 RES MCC Level | 25383 | IMG_2862 | 8000 | Corrosion was observed at bottom of door frame. |  |  | Door, Rollup Overhead |  | 2006 | 7 |  |  | East |  |  |  |  | W-WW | 3 | 1 | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1 |  |  | M00328
2256 | 0 |  | PD6 |  |  |  | BM | 00043535 | Electric Heater, EH-1 | Markham N PD6 RES MCC Level | 790900031 | IMG_1920 | 3500 |  |  |  | EH 1, Heating System, Unit Heater 15kW, 575VAC/3ph, by Ouellet, located on main floor |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00111
2257 | 0 |  | PD6 |  |  |  | BM | 00043536 | Electric Heater, EH-3 | Markham N PD6 RES Mezzanine | 790900031 | IMG_1964 | 2500 |  |  |  | EH 3, Heating System, Unit Heater 5kW, 575VAC/3ph, by Ouellet, located on main floor, mezzanine |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00111
2258 | 0 |  | PD6 |  |  |  | SC | 00043537 | Valve House Monorail Hoist Beam | Markham N PD6 RES MCC Level | 25383 | DSC00605 | 10000 |  |  |  | M 1, Overhead, Elevator, Hoist |  | 2006 | 46 |  |  | East |  | 6982 |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Valve house monorail hoist beam to be replaced at the end of remaining service life. | 0 |  |  |  |  | M00091
2259 | 0 |  | PD6 |  |  |  | BM | 00043538 | Baseboard electrical heater, EH-6 | Markham N PD6 RES Pipe Gallery Stairwell | 790900031 | IMG_2198 | 1000 |  |  |  | EH 6, Heating System, Baseboard Heater, 1.25 kW, 120VAC/1ph, connected to LP-A, located on main floor in the stairwell to the basement; |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 1 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00111
2260 | 0 |  | PD6 |  |  |  | SC | 00043539 | Valve Gallery Monorail Hoist Beam | Markham N PD6 RES Valve Gallery | 25384 | DSC00659 | 40000 |  |  |  | M 2 Overhead, Elevator, Hoist |  | 2006 | 46 |  |  | East |  | 26771 |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Valve gallery monorail hoist beam to be replaced at the end of remaining service life. | 0 |  |  |  |  | M00091
2261 | 0 |  | PD6 |  |  |  | BM | 00043540 | Electric Heater, EH-5 | Markham N PD6 RES Valve Gallery | 790900031 | IMG_1988 | 2500 |  |  |  | EH 5, Heating System, Unit Heater, 7.5 kW, 575VAC/3ph, by Ouellet, located in basement, in the west-south corner |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00111
2262 | 0 |  | PD6 |  |  |  | PM | 00043541 | Reservoir washdown pump | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2082 | 10000 | Minor surface corrosion was observed. | Operation reported excessive noise and not sufficient pressure developed in the discharge was observed. | To be replaced with a new pump was observed. | Wash Down, Pump, End Suction Centrifugal; by Armstron model 2x1x10 4280 BF STD, 4.4 L/s at 82.4 m TDH, 14.91kW motor; 3600 rpm |  | 2006 | 16 |  |  | East |  | C523007 |  |  | W-WW | 3 | 2 | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00007
2263 | 0 |  | PD6 |  |  |  | PM | 00026006 | Butterfly Valve Electric Actuator | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2149 | 10000 |  |  |  | M 200, Actuator, Electric; by Rotork Type IQ12, 575VAC/3 ph/60 Hz; torque 81 Nm |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 4 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00120
2264 | 0 |  | PD6 |  |  |  | PM | 00026005 | Butterfly Valve | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2149 | 40000 |  |  |  | V 200, Valve, Butterfly; 1050 mm DIA, flanged, by Val Matic model 2042P1; Class #150B; electrical actuator; |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 4 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2265 | 0 |  | PD6 |  |  |  | SC | 00019059 | Valve House Concrete Floor Slab | Markham N PD6 RES MCC Level | 25383 | DSC00615 | 240000 |  |  |  | Floor Slab, Concrete |  | 2006 | 46 |  |  | East |  |  |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Valve house concrete floor slab to be replaced at the end of remaining service life. | 0 | 2030 |  | Stouffville PD6 Reservoir Capital Project 1 |  |  | Structural
2266 | 0 |  | PD6 |  |  |  | BM | 00043549 | Motorized Damper MD-1 | Markham N PD6 RES MCC Level | 790900031 | IMG_1959 | 3000 |  |  |  | MD 1, Ventilation System, Damper c/w outdoor louver, main floor, south wall, 120VAC/1ph, Belimo actuator; powered from LP-A |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2268 | 0 |  | PD6 |  |  |  | PM | 00019051 | Service Water Piping | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2174 | 2000 |  |  |  | Water Main, Piping, Service Water; 50-75 mm DIA, S.S., thermally insulated. |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2269 | 0 |  | PD6 |  |  |  | PM | 00019056 | Hose down water piping | Markham N PD6 RES Valve Gallery | 790900031 | IMG-2065 | 2000 |  |  |  | Hose Down Water, Piping, Insulated |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2270 | 0 |  | PD6 |  |  |  | PM | 00019055 | Washwater, Piping | Markham N PD6 RES Valve Gallery | 790900031 | IMG_1 | 5000 |  |  |  | Washwater, Piping, Discharge, in South Cell |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2271 | 0 |  | PD6 |  |  |  | PM | 00019054 | Over Flow Piping | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2056 | 20000 |  |  |  | Over Flow, Piping, 1050 mm DIA, all S.S., welded construction, |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 4 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2272 | 0 |  | PD6 |  |  |  | PM | 00019053 | Access Platform | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2065 | 15000 |  |  |  | Over Water Main Piping, Access Platform, Aluminum Grating |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2273 | 0 |  | PD6 |  |  |  | PM | 00019052 | Washwater, Piping, Suction | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2076 | 5000 |  |  |  | Washwater, Piping, Suction; all S.S. welded construction, 75 nmm DIA, flanged connection to valves, non-insulated |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2274 | 0 |  | PD6 |  |  |  | PM | 00019050 |  | Markham N PD6 RES Valve Gallery | 790900031 |  | 0 |  |  |  | Overflow, Piping, Insulated |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 3 | 3 | The asset was assumed to be in fair condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2275 | 0 |  | PD6 |  |  |  | PM | 00019049 | Sampling Piping | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2031 | 500 |  |  |  | Sample port, Piping, Stainless Steel, 10 mm DIA |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 4 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2276 | 0 |  | PD6 |  |  |  | PM | 00019048 |  | Markham N PD6 RES Valve Gallery | 790900031 |  | 0 |  |  |  | Piping, Chemical Tubing |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 3 | 3 | The asset was assumed to be in fair condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2277 | 0 |  | PD6 |  |  |  | PM | 00019047 |  | Markham N PD6 RES Valve Gallery | 790900031 |  | 0 |  |  |  | ABS Suction Pipe Discharge, Piping |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 3 | 4 | The asset was assumed to be in fair condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2278 | 0 |  | PD6 |  |  |  | AC | 00019045 | Valve Gallery Access Door (Single) | Markham N PD6 RES Valve Gallery | 25384 | DSC00651 | 3500 |  |  |  | Access, Door, Interior Single Metal With Window |  | 2006 | 7 |  |  | East |  |  |  |  | W-WW | 2 | 1 | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | Stouffville PD6 Reservoir Capital Project 1
2279 | 0 |  | PD6 |  |  |  | BM | 00019057 | Exhaust Fan, EF-1 | Markham N PD6 RES Valve Gallery | 790900031 | IMG_1898 | 6000 |  |  |  | Ducting, Ventilation System, Exhaust Fan EF-1, 120VAC/1ph, in-line centrifugal, powered from LP-A |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2
2280 | 0 |  | PD6 |  |  |  | HSS | 00077844 |  | Stouffville PD6 Reservoir | 790900031 |  | 0 |  |  |  | Health and Safety Compliance Systems, Spill Containment, Chemical Spill Kit |  | 2016 | 11 |  |  | East |  |  |  |  | W-WW | 3 | 3 | The asset was assumed to be in fair condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M10095 | Health and Safety
2281 | 0 |  | PD6 |  |  |  | SIC | 00086196 | Flow Transmitter | Markham N PD6 RES MCC Level | 25383 | IMG_2272 | 5000 |  |  |  | MKRSMR_RES_FIT1, Cell 1 Inlet/Outlet Line Clamp On Flow Transmitter, Flow Meter, Flow; Endress + Hausser; PROSONIC FLOW 93; P50AFC02000; 18VA, NEMA 4X;1 |  | 2019 | 14 |  |  | East |  | P50AFC02000 |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00405 | Instrumentation and Control
2282 | 0 |  | PD6 |  |  |  | SIC | 00086261 |  | Markham N PD6 RES MCC Level | 25383 | IMG_2288 | 0 |  |  |  | MKRSMR Advantech Monitor, OIT, Monitor, PAC Panel |  | 2019 | 14 |  |  | East |  | KSA1976795 |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M10189 | Instrumentation and Control
2283 | 0 |  | PD6 |  |  |  | SIC | 00086260 | MKRSMR Control Panel | Markham N PD6 RES MCC Level | 25383 | IMG_2286 | 100000 |  |  |  | MKRSMR PAC Panel, Control Panel, PAC Panel, Indoor; Summa; SIRSMR_PAC; 14E-088¦SIRSMR_PAC; 120V, 12A, Type 12; 1 |  | 2019 | 14 |  |  | East |  | 14E-088/MKRSMR_PAC |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00844 | Instrumentation and Control
2284 | 0 |  | PD6 |  |  |  | SIC | 00086263 |  | Markham N PD6 RES MCC Level | 25383 |  | 4000 |  |  |  | MKRSMR UPS, Uninterruptible Power Supply, PAC Tower UPS |  | 2019 | 14 |  |  | East |  | PC23K09B33 |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M10181 | Instrumentation and Control
2285 | 0 |  | PD6 |  |  |  | SIC | 00086197 | Flow Meter | Markham N PD6 RES MCC Level | 25383 | IMG_2276 | 5000 |  |  |  | MKRSMR_RES_FIT2, Cell 2 Inlet/Outlet Line clamp on Flow Transmitter, Flow Meter, Flow; Endress + Hausser; PROSONIC FLOW 93; P50AFC02000; 18VA, NEMA 4X;1 |  | 2019 | 14 |  |  | East |  | P50AFD02000 |  |  | W-WW | 2 | 3 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00405 | Instrumentation and Control
2286 | 0 |  | PD6 |  |  |  | SIC | 00086265 | Building Thermostat | Markham N PD6 RES MCC Level | 25383 | IMG_2280 | 1500 |  |  |  | MKVCSA_BLDS_TSH1, MCC Level High Temperature Switch, Temperature Switch, Temperature; Honeywell; |  | 2019 | 14 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00076 | Instrumentation and Control
2287 | 0 |  | PD6 |  |  |  | SIC | 00086264 | Building Thermostat | Markham N PD6 RES MCC Level | 25383 | IMG_2283 | 500 |  |  |  | MKVCSA_BLDS_TSL1, MCC Level Low Temperature Switch, Temperature Switch, Temperature; Honeywell |  | 2019 | 14 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00076 | Instrumentation and Control
2288 | 0 |  | PD6 |  |  |  | SIC | 00086268 | Valve Gallery Temp Switch | Markham N PD6 RES Valve Gallery | 25384 | IMG_2396 | 1500 |  |  |  | MKRSMR_BLDS_TSH2, Valve Gallery High Temperature Switch, Temperature Switch, Temperature; Honeywell |  | 2019 | 14 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00076 | Instrumentation and Control
2289 | 0 |  | PD6 |  |  |  | SIC | 00086267 | Valve Gallery Low Temp Switch | Markham N PD6 RES Valve Gallery | 25384 | IMG_2397 | 1500 |  |  |  | MKRSMR_BLDS_TSL2, Valve Gallery Low Temperature Switch, Temperature Switch, Temperature; Honeywell |  | 2019 | 14 |  |  | East |  |  |  |  | W-WW | 2 | 2 | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | Stouffville PD6 Reservoir Capital Project 2 |  |  | M00076 | Instrumentation and Control