## Sheet1
seqNum | facility | Process | building | inspectorName | assetTag | assetName | COF | Description | LocationTag | LocationORIGINAL | manufacturer | installationDate | installYear | remainingESL | InstType | InstMeva | ServiceArea | FacilityType | CategoryCode | LifeCycleCategory | SerialNo | Parent | RotatingItem | Site | condition | defect1 | defect2 | defect3 | observations | RehabRepairCost | RehabRepairYear | RehabRepairCost2 | RehabRepairYear2 | repCost | photoName | repProjectName | rehabProjectName | rehab2ProjectName
2574 | SRHR |  |  |  |  | 1200mm Diameter Interconnection Valve | 3 |  | 790900052 |  |  |  | 0 | [5 empty] | PM | [14 empty] | 100000
2573 | SRHR |  |  |  |  | 1200mm Diameter Interconnection Valve | 3 |  | 790900052 |  |  |  | 0 | [5 empty] | PM | [14 empty] | 100000
2576 | SRHR |  |  |  |  | 300mm Diameter Piping | 4 |  | 790900052 |  |  |  | 0 | [5 empty] | PM | [14 empty] | 70000
2575 | SRHR |  |  |  |  | 750mm Diameter Piping | 4 |  | 790900052 |  |  |  | 0 | [5 empty] | PM | [14 empty] | 100000
2465 | SRHR |  |  |  |  | Access House Access Door (Single) | 1 |  | 790900052 |  |  |  | 1978 | 0 |  |  |  |  | AC | [5 empty] | 0 | Paint failure on interior of door | Lead containing paint | fair | [5 empty] | 3500 | IMG_3983
2509 | SRHR |  |  |  |  | Access House Aluminum Checker Plate | 1 | [5 empty] | 1978 | 0 |  |  |  |  | SC | [5 empty] | 0 | good | [7 empty] | 1500 | IMG_3987
2481 | SRHR |  |  |  |  | Access House Aluminum Guardrails | 3 | [5 empty] | 1978 | 0 |  |  |  |  | SC | [5 empty] | 0 | good | [7 empty] | 1000 | IMG_3985
2480 | SRHR |  |  |  |  | Access House Concrete Roof | 3 | [5 empty] | 1978 | 0 |  |  |  |  | SC | [5 empty] | 0 | good | [7 empty] | 6000 | IMG_3985
2479 | SRHR |  |  |  |  | Access House Concrete Walls | 3 | [5 empty] | 1978 | 0 |  |  |  |  | SC | [5 empty] | 0 | hairline cracking on exterior | fair | [6 empty] | 23000 | IMG_3985
2561 | SRHR |  |  |  |  | Access House Emeregency Lighting | 1 | Emeregency Lighting; ; ; ; 1 battery unit | 790900052 |  |  |  | 1978 | 8 |  |  |  |  | ES | [5 empty] | 3 | the replacemnet unit to be mounted at lower (more accessible) height for maintenance |  |  | the replacemnet unit to be mounted at lower (more accessible) height for maintenance |  |  |  |  | 1000 | PXL_20201117_142633299
2467 | SRHR |  |  |  |  | Access House Exterior Wall Paint | 1 |  | 790900052 |  |  |  | 1978 | 0 |  |  |  |  | AC | [5 empty] | 0 | fair | localized missing paint | [6 empty] | 1500 | IMG_3982
2511 | SRHR |  |  |  |  | Access House FRP Grating | 1 | overflow |  |  |  |  | 1978 | 0 |  |  |  |  | SC | [5 empty] | 0 | good | [7 empty] | 2000 | IMG_3985
2560 | SRHR |  |  |  |  | Access House Lighting | 1 | Indoor Lighting; ; ; ; 2 fixtures | 790900052 |  |  |  | 1978 | 8 |  |  |  |  | ES | [5 empty] | 3 | 1 fixture was removed | to be replaced with LED fixtures in next upgrade | [6 empty] | 2000 | PXL_20201117_142608014
2468 | SRHR |  |  |  |  | Access House Roofing System | 3 |  | 790900052 |  |  |  | 1978 | 0 |  |  |  |  | AC | [5 empty] | 0 | good | [7 empty] | 2000 | IMG_3982
2466 | SRHR |  |  |  |  | Access House Wall and Ceiling Paint | 1 |  | 790900052 |  |  |  | 1978 | 0 |  |  |  |  | AC | [5 empty] | 0 | good | [7 empty] | 1500 | IMG_3985
2571 | SRHR |  |  |  |  | Alarm System Terminal Unit-A | 2 | Alarm System Terminal Unit-A | 790900052 |  |  |  | 1978 | 8 |  |  |  |  | SIC | [5 empty] | 3 | [8 empty] | 16000 | PXL_20201117_141216067
2562 | SRHR |  |  |  |  | Area Lighting | 1 | Area Lighting; ; ; ; 1 pole mount fixture | 790900052 |  |  |  | 2000 | 15 |  |  |  |  | ES | [5 empty] | 3 | [8 empty] | 10000 | PXL_20201117_143129250
2531 | SRHR |  |  |  |  | Asphalt Paving | 1 | approx. 500 sq m | 790900052 |  |  |  | 1978 | 0 |  |  |  |  | SW | [5 empty] | 0 | good | [7 empty] | 40000
2506 | SRHR |  |  |  |  | Cell 1 Access Ladder | 3 | access house |  |  |  |  | 1978 | 0 |  |  |  |  | SC | [5 empty] | 0 | good | missing anchor bolt at base plate at bottom | [6 empty] | 7500 | IMG_3990
2507 | SRHR |  |  |  |  | Cell 1 Access Ladder | 3 | Exterior hatch |  |  |  |  | 1978 | 0 |  |  |  |  | SC | [5 empty] | 0 | good | [7 empty] | 7500 | IMG_4011
2503 | SRHR |  |  |  |  | Cell 1 Aluminum Guardrail | 2 | [5 empty] | 1978 | 0 |  |  |  |  | SC | [5 empty] | 0 | good | [7 empty] | 3000 | IMG_4037
2451 | SRHR |  |  |  | 00002110 | Cell 1 and 3 Washdown Gate Valve | 3 | 100 DIA manual gate valve, flanged, manual chain operator, Class 125, by Seguro | 790900052 |  |  |  | 0 | 15 |  |  |  |  | PM | [5 empty] | 3 | Surface corrosion, minor | clean, repaint, check seals | [6 empty] | 5000 | IMG_6616
2446 | SRHR |  |  |  | 00082464 | Cell 1 Butterfly Valve | 4 | 750 DIA Butterfly Valve, flanged, by Val Matic, Model 2030XF; motorized, Auma Actuators; 575/3/60, 0.25 hp; Asset Tag #00082466 | 790900052 |  |  |  | 2014 | 25 |  |  |  |  | PM |  | M186430 |  |  |  | 2 | Good | [7 empty] | 75000 | IMG_6542
2445 | SRHR |  |  |  | 00082463 | Cell 1 Check Valve | 4 | 750 DIA Swing Flex Check Valve, flanged, by Val Matic, Model 530ABFX001, CWP 250 psi, c/w backflow actuator, NSF/ANSI 61 certified. | 790900052 |  |  |  |  | 25 |  |  |  |  | PM |  | M670550 |  |  |  | 2 | Good | [7 empty] | 65000 | IMG_6554
2459 | SRHR |  |  |  | 00047630 | Cell 1 Combination Air Valve | 2 | Combination Air Valve, 50 DIA, threaded, by A.R.I. model D-040-0, c/w 50 DIA isolation ball valve. | 790900052 |  |  |  | 0 | 20 |  |  |  |  | PM | [5 empty] | 2 | No defect | discharge pipe is missing | Install the discahrge pipe in the valve outlet extended to the floor | [5 empty] | 2500 | IMG_6519
2460 | SRHR |  |  |  | 00086943 | Cell 1 Combination Air Valve | 2 | Air Valve, 25 DIA, threaded, c/w 25 DIA isolation globe valve. | 790900052 |  |  |  | 0 | 20 |  |  |  |  | PM | [5 empty] | 2 | Valve is old | Replace the valve if it is still in operation; if not used, the valve shall be removed. | [6 empty] | 1800 | IMG_6517
2501 | SRHR |  |  |  |  | Cell 1 Concrete Columns | 5 | [5 empty] | 1978 | 0 |  |  |  |  | SC | [5 empty] | 0 | fair | Rust spots | Soft concrete and exposed aggregate on bottom half | [5 empty] | 400000 | IMG_4039
2499 | SRHR |  |  |  |  | Cell 1 Concrete Floor | 5 | [5 empty] | 1978 | 0 |  |  |  |  | SC | [5 empty] | 0 | fair | Previously repaired cracking, new hairline cracking and rust spots | [6 empty] | 1400000 | IMG_4037
2502 | SRHR |  |  |  |  | Cell 1 Concrete Roof | 5 | [5 empty] | 1978 | 0 |  |  |  |  | SC | [5 empty] | 0 | good | previously repaired cracking, new hairline cracking and rust spots primarily around the perimeter of the cell | [6 empty] | 1300000 | IMG_4039
2500 | SRHR |  |  |  |  | Cell 1 Concrete Walls | 5 | [5 empty] | 1978 | 0 |  |  |  |  | SC | [5 empty] | 0 | fair | Previously repaired cracking, new hairline cracking with efflorescence deposits and rust spots | Soft concrete and exposed aggregate on bottom half | [5 empty] | 1000000 | IMG_3990
2447 | SRHR |  |  |  | 00002104 | Cell 1 Drain Gate Valve | 4 | 300 DIA manual gate valve, flanged, Class 125, original installation, by Seguro | 790900052 |  |  |  | 0 | 10 |  |  |  |  | PM | [5 empty] | 3 | Surface corrosion, minor | Minor leak through the stem | replace the valve and drainage pipes | [5 empty] | 5000 | IMG_6562
2508 | SRHR |  |  |  |  | Cell 1 Equipment Hatch | 2 | Buried |  |  |  |  | 1978 | 0 |  |  |  |  | SC | [5 empty] | 0 | good | [7 empty] | 12000 | IMG_4011
2504 | SRHR |  |  |  |  | Cell 1 FRP Guardrail | 2 | [5 empty] | 1978 | 0 |  |  |  |  | SC | [5 empty] | 0 | good | [7 empty] | 3000 | IMG_4035
2505 | SRHR |  |  |  |  | Cell 1 FRP Ladder | 3 | [5 empty] | 1978 | 0 |  |  |  |  | SC | [5 empty] | 0 | good | [7 empty] | 2000 | IMG_4036
2522 | SRHR |  |  |  |  | Cell 1 Ladder Rungs | 2 | overflow |  |  |  |  | 1978 | 0 |  |  |  |  | SC | [5 empty] | 0 | good | [7 empty] | 1000 | IMG_4049
2566 | SRHR |  |  |  | 00028065 | Cell 1 Pressure Meter | 2 | pressure meter; Endress Hausser | 790900052 |  |  |  | 1978 | 8 |  |  |  |  | SIC | [5 empty] | 3 | [8 empty] | 8500 | PXL_20201117_140055101
2577 | SRHR |  |  |  |  | Cell 1 Washdown Piping |  | 100mm diameter | 790900052 |  |  |  | 0 | [5 empty] | PM | [14 empty] | 25000
2518 | SRHR |  |  |  |  | Cell 2 Access Ladder | 3 | equipment hatch |  |  |  |  | 1978 | 0 |  |  |  |  | SC | [5 empty] | 0 | fair | minor pitting | [6 empty] | 7500 | DSC00288
2517 | SRHR |  |  |  |  | Cell 2 Access Ladder | 3 | access house |  |  |  |  | 1978 | 0 |  |  |  |  | SC | [5 empty] | 0 | fair | missing anchor bolts noted | minor pitting | [5 empty] | 7500 | DSC00228
2520 | SRHR |  |  |  |  | Cell 2 Aluminum Guardrail | 2 | [5 empty] | 1978 | 0 |  |  |  |  | SC | [5 empty] | 0 | good | missing anchor bolt in 1 location | [6 empty] | 3000 | DSC00227
2443 | SRHR |  |  |  | 00002098 | Cell 2 Butterfly Valve | 4 | 750 DIA Butterfly Valve, flanged, by American-BFV Val Matic, Model 2030XF; motorized, Rotork Type 30A/48, output speed 21 rpm; motor rating 2 hp; 600/3/60; | 790900052 |  |  |  | 2014 | 25 |  |  |  |  | PM |  | M188430 |  |  |  | 1 | Good | [7 empty] | 75000 | DSC00209
2444 | SRHR |  |  |  | 00002097 | Cell 2 Check Valve | 4 | 750 DIA Check Valve, flanged, lever 750 DIA Check valve, flanged, lever-operated, manual | 790900052 |  |  |  |  | 5 |  |  |  |  | PM | [5 empty] | 3 | No visual defect, valve is old | valve replacement | [6 empty] | 65000 | IMG_6530
2515 | SRHR |  |  |  |  | Cell 2 Concrete Columns | 5 | [5 empty] | 1978 | 0 |  |  |  |  | SC | [5 empty] | 0 | fair | hairline cracking, previos patching, rust spots and exposed aggregates | [6 empty] | 400000 | DSC00295
2513 | SRHR |  |  |  |  | Cell 2 Concrete Floor Slab | 5 | [5 empty] | 1978 | 0 |  |  |  |  | SC | [5 empty] | 0 | fair | New hairline cracking, minor suface concrete spalling, previous patching and exposed aggregates | [6 empty] | 1400000 | DSC00290
2516 | SRHR |  |  |  |  | Cell 2 Concrete Roof | 5 | [5 empty] | 1978 | 0 |  |  |  |  | SC | [5 empty] | 0 | fair | new hairline cracking with efflorescence deposits, previoulsy repaired cracks and rust spots | [6 empty] | 1300000 | DSC00234
2514 | SRHR |  |  |  |  | Cell 2 Concrete Walls | 5 | [5 empty] | 1978 | 0 |  |  |  |  | SC | [5 empty] | 0 | fair | previously repaired cracking and new hairline cracking with efflorescence deposits | [6 empty] | 1000000 | DSC00290
2449 | SRHR |  |  |  | 00002103 | Cell 2 Drain Gate Valve | 4 | 300 DIA manual gate valve, flanged, Class 125, original installation, by Seguro | 790900052 |  |  |  | 0 | 10 |  |  |  |  | PM | [5 empty] | 3 | Surface corrosion, minor | some minor leak through the stem | replace the valve and drainage pipes | [5 empty] | 5000 | IMG_6565
2519 | SRHR |  |  |  |  | Cell 2 Equipment Hatch | 2 | exterior |  |  |  |  | 1978 | 0 |  |  |  |  | SC | [5 empty] | 0 | fair | [7 empty] | 12000 | IMG_4254
2521 | SRHR |  |  |  |  | Cell 2 Ladder Rungs | 2 | overflow |  |  |  |  | 1978 | 0 |  |  |  |  | SC | [5 empty] | 0 | good | [7 empty] | 1000 | DSC00307
2565 | SRHR |  |  |  | 00024780 | Cell 2 Pressure Meter | 2 | pressure meter; Endress Hausser | 790900052 |  |  |  | 1978 | 8 |  |  |  |  | SIC | [5 empty] | 3 | [8 empty] | 8500 | PXL_20201117_140017107
2450 | SRHR |  |  |  | 00002109 | Cell 2 Washdown Gate Valve | 3 | 100 DIA manual gate valve, flanged, manual chain operator, Class 125, by Seguro | 790900052 |  |  |  | 0 | 15 |  |  |  |  | PM | [5 empty] | 3 | Surface corrosion, minor | clean, repaint, check seals | [6 empty] | 5000 | IMG_6613
2578 | SRHR |  |  |  |  | Cell 2 Washdown Piping |  | 100mm diameter | 790900052 |  |  |  | 0 | [5 empty] | PM | [14 empty] | 25000
2491 | SRHR |  |  |  |  | Cell 3 Access Hatch | 2 | [5 empty] | 1996 | 0 |  |  |  |  | SC | [5 empty] | 0 | good | [7 empty] | 5000 | IMG_4253
2497 | SRHR |  |  |  |  | Cell 3 Aluminum Grating | 2 | Drain |  |  |  |  | 1996 | 0 |  |  |  |  | SC | [5 empty] | 0 | fair | corrosion noted on seat angle | [6 empty] | 500 | IMG_4226
2498 | SRHR |  |  |  |  | Cell 3 Aluminum Grating | 2 | Drain |  |  |  |  | 1996 | 0 |  |  |  |  | SC | [5 empty] | 0 | fair | corrosion noted on seat angle | [6 empty] | 500 | IMG_4226
2496 | SRHR |  |  |  |  | Cell 3 Aluminum Ladder | 3 | Equipment Hatch |  |  |  |  | 1996 | 0 |  |  |  |  | SC | [5 empty] | 0 | good | [7 empty] | 7500 | IMG_4202
2495 | SRHR |  |  |  |  | Cell 3 Aluminum Ladder | 3 | Vent House |  |  |  |  | 1996 | 0 |  |  |  |  | SC | [5 empty] | 0 | good | [7 empty] | 7500 | IMG_4190
2494 | SRHR |  |  |  |  | Cell 3 Aluminum Ladder | 3 | Access hatch |  |  |  |  | 1996 | 0 |  |  |  |  | SC | [5 empty] | 0 | good | [7 empty] | 7500 | IMG_4179
2489 | SRHR |  |  |  |  | Cell 3 Concrete Columns | 5 | [5 empty] | 1996 | 0 |  |  |  |  | SC | [5 empty] | 0 | fair | Rust spots noted throughout. A few columns exhibited a shifted rebar cage as concrete cover was found to be inconsistent | Approximately 30% of surface area exhibited exposed aggregate | [5 empty] | 1100000 | IMG_4238
2487 | SRHR |  |  |  |  | Cell 3 Concrete Floor Slab | 5 | [5 empty] | 1996 | 0 |  |  |  |  | SC | [5 empty] | 0 | fair | Previously repaired cracking noted throughout | New cracking with efflorescence deposits and rust spots | [5 empty] | 2000000 | IMG_4179
2490 | SRHR |  |  |  |  | Cell 3 Concrete Roof | 5 | [5 empty] | 1996 | 0 |  |  |  |  | SC | [5 empty] | 0 | Good | Cracking with efflorescence deposits noted primarily around the perimeter of the cell | [6 empty] | 3000000 | IMG_4237
2488 | SRHR |  |  |  |  | Cell 3 Concrete Walls | 5 | [5 empty] | 1996 | 0 |  |  |  |  | SC | [5 empty] | 0 | fair | Previously repaired cracking, new hairline cracking with efflorescence deposits, rust spots and concrete spalling at top of wall noted. | [6 empty] | 1100000 | IMG_4179
2448 | SRHR |  |  |  | 00002105 | Cell 3 Drain Gate Valve | 4 | 300 DIA manual gate valve, flanged, Class 125, original installation, by Seguro | 790900052 |  |  |  | 0 | 10 |  |  |  |  | PM | [5 empty] | 3 | Surface corrosion, minor | replace the valve and drainage pipes | [6 empty] | 5000 | IMG_6559
2492 | SRHR |  |  |  |  | Cell 3 Equipment Hatch | 3 | [5 empty] | 1996 | 0 |  |  |  |  | SC | [5 empty] | 0 | good | [7 empty] | 12000 | IMG_4249
2579 | SRHR |  |  |  |  | Cell 3 Washdown Piping |  | 100mm diameter | 790900052 |  |  |  | 0 | [5 empty] | PM | [14 empty] | 40000
2570 | SRHR |  |  |  |  | Communication Panel | 3 | communication panel | 790900052 |  |  |  | 1978 | 8 |  |  |  |  | SIC | [5 empty] | 3 | [8 empty] | 10000 | PXL_20201117_141157365
2582 | SRHR |  |  |  | 00014288 | Concrete Retaining Wall (North) | 3 |  | 790900052 |  |  |  | 2013 | 0 |  |  |  |  | SW | Siteworks |  |  |  |  | 0 | good | [7 empty] | 400000 | IMG_4266
2324 | SRHR |  |  |  | 00014288 | Concrete Retaining Wall (South) | 3 | 2 East Headwalls, Retaining Wall, Concrete | 790900052 |  |  | 1978-01-01 | 1978 | 0 |  |  |  |  | SW | Siteworks |  |  |  | W-WW | 0 | good | [7 empty] | 250000 | IMG_4275
2557 | SRHR |  |  |  | 00086924 | Distribution Transformer | 3 | Distribution Transformer; ; ; ; 600-120/240V, 5kVA | 790900052 |  |  |  | 1978 | 8 |  |  |  |  | ES | [5 empty] | 3 | [8 empty] | 8000 | PXL_20201117_141051752
2323 | SRHR |  |  |  | 00014284 | Facility Access Gate | 1 | Southeast, Gate, Single Lockable | 790900052 |  |  | 1978-01-01 | 1978 | 0 |  |  |  |  | SW | Siteworks |  |  |  | W-WW | 0 | [8 empty] | 3500
2564 | SRHR |  |  |  | 00026067 | Float | 2 | 1 Float | 790900052 |  |  |  | 1978 | 8 |  |  |  |  | SIC | [5 empty] | 3 | [8 empty] | 500 | PXL_20201117_135949317
2567 | SRHR |  |  |  |  | Flow Transmitter | 3 | Flow transmitter | 790900052 |  |  |  | 1978 | 8 |  |  |  |  | SIC | [5 empty] | 3 | to be installed on wall | [7 empty] | 5000 | PXL_20201117_140210585
2325 | SRHR |  |  |  | 00014289 | Landscaping | 1 | Graded Away From Structure, Site Drainage, approx 30625 sq m | 790900052 |  |  | 1978-01-01 | 1978 | 0 |  |  |  |  | SW | Siteworks |  |  |  | W-WW | 0 | good | [7 empty] | 300000
2563 | SRHR |  |  |  |  | Outdoor/Entrance Light | 1 | Outoddor/Entrance Light; ; ; ; 1 fixture | 790900052 |  |  |  | 2000 | 15 |  |  |  |  | ES | [5 empty] | 3 | to be replaced with LED fixture in next upgrade | [7 empty] | 1000 | PXL_20201117_142226839
2568 | SRHR |  |  |  | 00082458 | RHRSTR Control Panel | 3 | PLC | 790900052 |  |  |  | 2000 | 8 |  |  |  |  | SIC | [5 empty] | 3 | [8 empty] | 100000 | PXL_20201117_140617126
2572 | SRHR |  |  |  |  | RPU Panel | 3 | RPU | 790900052 |  |  |  | 1978 | 8 |  |  |  |  | SIC | [5 empty] | 3 | [8 empty] | 80000 | PXL_20201117_141240626
2527 | SRHR |  |  |  |  | Sanitary MH Ladder Rungs | 1 | [5 empty] | 1978 | 0 |  |  |  |  | SW | [5 empty] | 0 | good | [7 empty] | 1500 | IMG_4054
2529 | SRHR |  |  |  |  | Sanitary MH Manhole Frame and Cover | 1 | [5 empty] | 1978 | 0 |  |  |  |  | SW | [5 empty] | 0 | good | [7 empty] | 1500 | IMG_4053
2528 | SRHR |  |  |  |  | Sanitary MH Precast Concrete Structure | 2 | [5 empty] | 1978 | 0 |  |  |  |  | Sw | [5 empty] | 0 | good | [7 empty] | 15000 | IMG_4054
2530 | SRHR |  |  |  |  | Site Fencing | 2 | 700m | 790900052 |  |  |  | 1978 | 0 |  |  |  |  | SW | [5 empty] | 0 | fair | [7 empty] | 100000
2526 | SRHR |  |  |  |  | Storm MH Ladder Rungs | 1 | [5 empty] | 1978 | 0 |  |  |  |  | SW | [5 empty] | 0 | good | [7 empty] | 2500 | IMG_4050
2523 | SRHR |  |  |  |  | Storm MH Manhole Frame and Cover | 1 | [5 empty] | 1978 | 0 |  |  |  |  | SW | [5 empty] | 0 | good | [7 empty] | 1500 | IMG_4052
2524 | SRHR |  |  |  |  | Storm MH Precast Concrete Structure | 2 | [5 empty] | 1978 | 0 |  |  |  |  | SW | [5 empty] | 0 | good | [7 empty] | 30000 | IMG_4050
2461 | SRHR |  |  |  |  | Valve House Access Door (Double) | 1 |  | 790900052 |  |  |  | 1978 | 0 |  |  |  |  | AC | [5 empty] | 0 | Corrosion on bottom of door | Lead containing paint on exterior | fair | [5 empty] | 5500 | IMG_3962
2477 | SRHR |  |  |  |  | Valve House Aluminum Guardrail | 2 | [5 empty] | 1978 | 0 |  |  |  |  | SC | [5 empty] | 0 | good | [7 empty] | 1500 | IMG_3973
2478 | SRHR |  |  |  |  | Valve House Aluminum Staircase | 3 | [5 empty] | 1978 | 0 |  |  |  |  | SC | [5 empty] | 0 | good | [7 empty] | 25000 | IMG_3974
2441 | SRHR |  |  |  | 00024606 | Valve House Centrifugal Pump | 2 | Centrifugal Water Pump, by Diamond, Model 314071-01-1J04G, 0.5 hp, 115/1/60; 3450 rpm; c/w a 8L diaphragm tank; located on the main floor. | 790900052 |  |  |  | 2004 | 10 |  |  |  |  | BM | [5 empty] | 2 | good | [7 empty] | 5000 | IMG_6473
2473 | SRHR |  |  |  |  | Valve House Concrete Floor | 4 | Ground |  |  |  |  | 1978 | 0 |  |  |  |  | SC | [5 empty] | 0 | good | [7 empty] | 30000 | IMG_3969
2472 | SRHR |  |  |  |  | Valve House Concrete Floor | 4 | Basement |  |  |  |  | 1978 | 0 |  |  |  |  | SC | [5 empty] | 0 | good | [7 empty] | 40000 | IMG_3976
2474 | SRHR |  |  |  |  | Valve House Concrete Roof | 4 | [5 empty] | 1978 | 0 |  |  |  |  | SC | [5 empty] | 0 | good | [7 empty] | 22000 | IMG_3968
2475 | SRHR |  |  |  |  | Valve House Concrete Walls | 4 | [5 empty] | 1978 | 0 |  |  |  |  | SC | [5 empty] | 0 | damp hairline cracking in basement on walls adjacent to reservoir | fair | [6 empty] | 125000 | IMG_3977
2327 | SRHR |  |  |  | 00082457 | Valve House Dehumidifier | 2 | Dehumidifer, HVAC, desiccant type, by Munters Inc., Model HCD-600-EA-SF, 600 cfm at max 10" W.C. pressure; 575/3/60. Locate on the main floor. | 790900052 |  | 1004372 | 2015-03-13 | 2015 | 10 |  |  |  |  | BM | Instrumentation and Control | 4524 |  |  | W-WW | 2 | Reactivation air inlet and out let points shall have greater outdoor separation distance | Regular standard maintenance, including filter replacement on time. | [6 empty] | 50000 | IMG_6465
2556 | SRHR |  |  |  | 00086923 | Valve House Distribution Panel | 3 | Distribution Panel; ITE; ; ; 120/240V, 100A, 20 CCT | 790900052 |  |  |  | 1978 | 8 |  |  |  |  | ES | [5 empty] | 3 | [8 empty] | 7000 | PXL_20201117_140905118
2437 | SRHR |  |  |  | 00081046 | Valve House Electric Unit Heater | 3 | HVAC, fan-forced electric unit heater by Ouellet, Model OAS 020 36T, 2kW, 600/3/60, wall-mounted. Locate on the main floor. | 790900052 |  |  |  | 2017 | 15 |  |  |  |  | BM | [5 empty] | 2 | good | Dust cleaning of electrical elements | [6 empty] | 5000 | IMG_6459
2438 | SRHR |  |  |  | 00083274 | Valve House Electric Unit Heater | 3 | HVAC, fan-forced electric unit heater by Ouellet, Model OAS 030 36T, 3 kW, 600/3/60, wall-mounted. Locate on the main floor. | 790900052 |  |  |  | 2018 | 15 |  |  |  |  | BM | [5 empty] | 2 | good | Dust cleaning of electrical elements | [6 empty] | 5000 | IMG_6454
2439 | SRHR |  |  |  |  | Valve House Electric Unit Heater | 3 | HVAC, fan-forced electric unit heater by Dimplex, Model EUH 08 B84 CT Mod. C, 7.5 kW, 600/3/60, wall-mounted. Locate in the basement level. | 790900052 |  |  |  | 2010 | 15 |  |  |  |  | BM | [5 empty] | 2 | good | Dust cleaning of electrical elements | [6 empty] | 5000 | IMG_6583
2559 | SRHR |  |  |  |  | Valve House Emergency Lighting | 1 | Emergency Lighting; ; ; ; 1 battery unit and 1 remote head | 790900052 |  |  |  | 1978 | 8 |  |  |  |  | ES | [5 empty] | 3 | inadequate emergency lighting. | more fixtures to be added | [6 empty] | 2000 | PXL_20201117_140538344
2476 | SRHR |  |  |  |  | Valve House Equipment Hatch | 1 | [5 empty] | 1978 | 0 |  |  |  |  | SC | [5 empty] | 0 | good | missing safety grating or guardrail system for when hatch is open | [6 empty] | 7000 | IMG_3972
2558 | SRHR |  |  |  |  | Valve House Indoor Lighting | 1 | Indoor Lighting; ; ; ; 12 linear fixtures | 790900052 |  |  |  | 1978 | 8 |  |  |  |  | ES | [5 empty] | 3 | to be replaced with LED fixtures in next upgrade | [7 empty] | 12000 | PXL_20201117_135230268
2554 | SRHR |  |  |  |  | Valve House Main Breaker | 3 | Main breaker; Klockner Moeller; NZM 6 b-63; ; 600V, 33A | 790900052 |  |  |  | 1978 | 5 |  |  |  |  | ES | [5 empty] | 3 | Arc Flash study and labels to be reviewed in 2021. There has been multiple instances that a fault in resovior has caused the breaker in pumping sation switchgear to trip without triping the resoivor main breaker. Circuit Breaker coordination study must be | [7 empty] | 10000 | PXL_20201117_140737372
2553 | SRHR |  |  |  | 0006006 | Valve House MCC | 4 | MCC; Klockner Moeller; Series 200; ; 600V, 600A, 2 columns and 4 breakers | 790900052 |  |  |  | 1978 | 8 |  |  |  |  | ES | [5 empty] | 3 | no power meter | Arc Flash study and labels to be reviewed in 2021 | [6 empty] | 50000 | PXL_20201117_140713053
2442 | SRHR |  |  |  |  | Valve House Outdoor Louver | 2 | HVAC, outdoor louver, aluminium, 610x1220 mm; | 790900052 |  |  |  | 0 | 20 |  |  |  |  | BM | [5 empty] | 2 | good | [7 empty] | 2000 | IMG_6495
2464 | SRHR |  |  |  |  | Valve House Protective Floor Coating | 1 |  | 790900052 |  |  |  | 1978 | 0 |  |  |  |  | AC | [5 empty] | 0 | Failed | Low-level lead | [6 empty] | 5000 | IMG_3976
2469 | SRHR |  |  |  |  | Valve House Roofing System | 3 |  | 790900052 |  |  |  | 1978 | 0 |  |  |  |  | AC | [5 empty] | 0 | good | [7 empty] | 5000 | IMG_3961
2440 | SRHR |  |  |  | 00086922 | Valve House Sump Pump | 2 | Centrifugal Sump Pump, by Hydromatic Pumps, Model SHEF50 A1-2, 0.5 hp, 115/1/60; located in the basement level. | 790900052 |  |  |  | 2014 | 10 |  |  |  |  | BM | [5 empty] | 2 | good | [7 empty] | 1500 | IMG_6625
2463 | SRHR |  |  |  |  | Valve House Wall and Ceiling Paint | 1 |  | 790900052 |  |  |  | 1978 | [5 empty] | AC | [5 empty] | 0 | Localized bubbling/failure | Lead containing paint | fair | [5 empty] | 6000 | IMG_3964
2555 | SRHR |  |  |  |  | Valve House Washwater Pump Starter | 3 | Pump Starter; Klockner Moeller; ; ; 600V, size 1, 5hp | 790900052 |  |  |  | 1978 | 8 |  |  |  |  | ES | [5 empty] | 3 | [8 empty] | 5000 | PXL_20201117_140821211
2471 | SRHR |  |  |  |  | Vent House Access Door (Single) | 1 |  | 790900052 |  |  |  | 1996 | 0 |  |  |  |  | AC | [5 empty] | 0 | good | missing paint where previous sign was removed | [6 empty] | 3500 | IMG_4165
2493 | SRHR |  |  |  |  | Vent House Aluminum Checker Plate | 1 | [5 empty] | 1996 | 0 |  |  |  |  | SC | [5 empty] | 0 | good | [7 empty] | 3000 | IMG_4168
2484 | SRHR |  |  |  |  | Vent House Aluminum Guardrails | 3 | [5 empty] | 1996 | 0 |  |  |  |  | SC | [5 empty] | 0 | good | [7 empty] | 1000 | IMG_4168
2483 | SRHR |  |  |  |  | Vent House Concrete Roof | 4 | [5 empty] | 1996 | 0 |  |  |  |  | SC | [5 empty] | 0 | good | [7 empty] | 7000 | IMG_4169
2482 | SRHR |  |  |  |  | Vent House Concrete Walls | 4 | [5 empty] | 1996 | 0 |  |  |  |  | SC | [5 empty] | 0 | Fair | Bughole and spalling was observed on exterior at pour joint between walls and roof | [6 empty] | 20000 | IMG_4163
2486 | SRHR |  |  |  |  | Vent House Davit Socket Base | 3 | [5 empty] | 1996 | 0 |  |  |  |  | HSS | [5 empty] | 0 | not mounted on floor | [7 empty] | 2000 | IMG_4168
2485 | SRHR |  |  |  |  | Vent House Davit Socket Base | 3 | [5 empty] | 1996 | 0 |  |  |  |  | HSS | [5 empty] | 0 | good | [7 empty] | 2000 | IMG_4168
2470 | SRHR |  |  |  |  | Vent House Roofing System | 3 |  | 790900052 |  |  |  | 1996 | 0 |  |  |  |  | AC | [5 empty] | 0 | good | [7 empty] | 1500 | IMG_4165
2458 | SRHR |  |  |  | 00002107 | Washdown Pump | 3 | Washdown pump, centrifugal, split-case pump, by Taco model FM1208B2F, capacity 52 gpm at 260 ft TDH; 575/3/60; 10 hp, 3500 rpm motor by Unimount 125. | 790900052 |  |  |  | 2012 | 10 |  |  |  |  | PM | [5 empty] | 3 | Some minor leak through shaft | Some minor corrosion | regular maintenance | [5 empty] | 8000 | IMG_6587
2453 | SRHR |  |  |  | 00087402 | Washdown Water Service Ball Valve | 3 | 75 DIA, isolation ball valve, Washdown water suction line, flanged, 3-piece, manual, lever-operated, all SS construction, by NVC. | 790900052 |  |  |  | 0 | 20 |  |  |  |  | PM | [5 empty] | 2 | Good | Regular maintenance | [6 empty] | 500 | IMG_6599
2454 | SRHR |  |  |  |  | Washdown Water Service Ball Valve | 3 | 50 DIA, isolation ball valve, Washdown water discharge line, flanged, 3-piece, manual, lever-operated, all SS construction, by NVC. | 790900052 |  |  |  | 0 | 20 |  |  |  |  | PM | [5 empty] | 2 | Good | Regular maintenance | [6 empty] | 500 | IMG_6596
2457 | SRHR |  |  |  |  | Washdown Water Service Ball Valve | 3 | 50 DIA, isolation ball valve, Washdown water discharge line, pressure bypass, flanged, 3-piece, manual, lever-operated, all SS construction, by NVC. | 790900052 |  |  |  | 0 | 20 |  |  |  |  | PM | [5 empty] | 2 | Regular maintenance | [7 empty] | 500 | IMG_6587
2456 | SRHR |  |  |  | 00087406 | Washdown Water Service Check Valve | 3 | 50 DIA check valve in washdown water line discharge, flanged, all S.S. construction, by Haitima Valve | 790900052 |  |  |  | 0 | 10 |  |  |  |  | PM | [5 empty] | 2 | Good | [7 empty] | 500 | IMG_6592
2452 | SRHR |  |  |  | 00002108 | Washdown Water Service Isolation Gate Valve | 4 | 75 DIA Gate Valve, Washdown water pump suction, flanged, manual | 790900052 |  |  |  | 0 | 5 |  |  |  |  | PM | [5 empty] | 4 | Surface corrosion | Leak through the stem ,minor | Replace with new valve inclusing upstream suction elbow. | [5 empty] | 500 | IMG_6603
2455 | SRHR |  |  |  | 00087402 | Washdown Water Service Pressure Control Valve | 3 | 50 DIA pressure control valve in the Washdown water bypass line in discharge, flanged, by Singer Valve Co. Model 106-PR. | 790900052 |  |  |  | 0 | 10 |  |  |  |  | PM | [5 empty] | 3 | Good | [7 empty] | 2000 | IMG_6588
2569 | SRHR |  |  |  | 00082148 | xRHRSTR2 Network Access Closet | 4 | Network Panel | 790900052 |  |  |  | 2000 | 8 |  |  |  |  | SIC | [5 empty] | 3 | [8 empty] | 20000 | PXL_20201117_140643175