## Sheet1
seqNum | RehabRepairCost2 | RehabRepairYear2 | facility | Process | building | inspectorName | CategoryCode | assetTag | assetName | LocationORIGINAL | LocationTag | photoName | repCost | defect1 | defect2 | defect3 | Description | installationDate | installYear | remainingESL | InstType | InstMeva | ServiceArea | FacilityType | SerialNo | Parent | RotatingItem | Site | condition | COF | observations | RehabRepairCost | RehabRepairYear | repProjectName | rehabProjectName | rehab2ProjectName | manufacturer | LifeCycleCategory
2377 |  |  | PD6 |  |  |  | AC |  | Valve House Ceiling Paint |  | 00019041 | DSC00641 | 15000 | good |  |  |  |  | 2006 | 0 | [9 empty] | 1
2378 |  |  | PD6 |  |  |  | SC |  | Valve House Masonry Blockwalls |  | 00025383 | DSC00630 | 12000 | good |  |  | Staircase and reservoir access |  | 2006 | 0 | [9 empty] | 4
2379 |  |  | PD6 |  |  |  | SC |  | Valve House Precast Concrete Roof |  | 00025383 | DSC00612 | 2000 | good |  |  | staircase |  | 2006 | 0 | [9 empty] | 3
2380 |  |  | PD6 |  |  |  | SC |  | Valve House Aluminum Platform |  | 00019041 |  | 1500 | good |  |  | in overflow |  | 2006 | 0 | [9 empty] | 2
2381 |  |  | PD6 |  |  |  | SC |  | Rear Access House Concrete Floor |  | 00019042 | IMG_2248 | 24000 | good |  |  |  |  | 2006 | 0 | [9 empty] | 4
2382 |  |  | PD6 |  |  |  | HSS |  | Valve House First Extinguishers |  | 790900031 | IMG_2828 | 300 | good |  |  | Total of 3 |  | 2016 | 0 | [9 empty] | 2
2384 |  |  | PD6 |  |  |  | SW |  | Concrete Retaining Wall |  | 790900031 | DSC07813 | 50000 | good |  |  | 18m and 14.5m long |  | 2006 | 0 | [9 empty] | 2
2385 |  |  | PD6 |  |  |  | SW |  | Landscaping |  | 790900031 | DSC07845 | 750000 | good |  |  | approx 97250 sq m |  | 2006 | 0 | [9 empty] | 2
2386 |  |  | PD6 |  |  |  | SW |  | Reservoir Inflow Piping |  | 790900031 |  | 960000 | good |  |  | 1050mm diameter. Approx. 240m |  | 2006 | 0 | [9 empty] | 5
2387 |  |  | PD6 |  |  |  | SW |  | Reservoir Outflow Piping |  | 790900031 |  | 960000 | good |  |  | 1050mm diameter. Approx. 240m |  | 2006 | 0 | [9 empty] | 5
2388 |  |  | PD6 |  |  |  | SW |  | Geoweb Paver |  | 790900031 | DSC07858 | 20000 | Soil and sod had overgrown the geoweb paver. |  |  | approx 1400 sq m |  | 2006 | 0 | [9 empty] | 1
2389 |  |  | PD6 |  |  |  | SW |  | Emergency Overflow Outfall and Site Drainage |  | 790900031 | DSC07767 | 100000 | good |  |  |  |  | 2006 | 0 | [9 empty] | 4
2390 |  |  | PD6 |  |  |  | SW |  | Facility Access Gate 1 |  | 790900031 | DSC07785 | 3500 | bent at bottom |  |  | Entrance |  | 2006 | 0 | [9 empty] | 1
2391 |  |  | PD6 |  |  |  | SW |  | Site Chainlink Fencing |  | 790900031 | DSC07785 | 65000 | bent/out of plumb post at rear access house |  |  | approx 400m |  | 2012 | 0 | [9 empty] | 1
2393 |  |  | PD6 |  |  |  | SW |  | Bollards |  | 790900031 | IMG_2862 | 1000 | good |  |  |  |  | 2006 | 0 | [9 empty] | 2
2394 |  |  | PD6 |  |  |  | SW |  | Facility Access Gate 2 |  | 790900031 | DSC07802 | 3500 | good |  |  |  |  | 2006 | 0 | [9 empty] | 1
2395 |  |  | PD6 |  |  |  | BM |  | Motorized Damper MD-2 |  | 790900031 | IMG-2312 | 3000 | good |  |  | MD 2, Ventilation System, Damper c/w outdoor louver, main floor, north wall, 120VAC/1ph, Belimo actuator; powered from LP-A |  | 2006 | 10 | [9 empty] | 2
2396 |  |  | PD6 |  |  |  | BM |  | Motorized Damper MD-4 |  | 790900031 | IMG_2312 | 3000 | good |  |  | MD 4, Ventilation System, Damper c/w outdoor louver, main floor, west wall, 120VAC/1ph, Belimo actuator; powered from LP-A |  | 2006 | 0 | [9 empty] | 2
2397 |  |  | PD6 |  |  |  | BM | 00043525 | sump pump, P-2 |  | 790900031 | IMG_2043 | 3000 | good |  |  | sump pump, P-2; 120VAC/1ph, 4/10 hp; submersible, centrigugal, by Liberty Pumps model HT40-Series; powed from LP-A; |  | 2006 | 5 | [9 empty] | 2
2398 |  |  | PD6 |  |  |  | PM |  | Valve Local Disconnect Switch |  | 790900031 | IMG_2150 | 5000 | good |  |  | Actuator M200, Switch, Local Disconnect; by Siemens, 600 VAC, 3 poles, 30 Amps |  | 2006 | 10 | [9 empty] | 4
2399 |  |  | PD6 |  |  |  | PM |  | Valve Local Disconnect Switch |  | 790900031 | IMG_2129 | 5000 | good |  |  | Actuator M400, Switch, Local Disconnect; by Siemens, 600 VAC, 3 poles, 30 Amps |  | 2006 | 10 | [9 empty] | 4
2400 |  |  | PD6 |  |  |  | PM |  | Valve Local Disconnect Switch |  | 790900031 | IMG_2174 | 5000 | good |  |  | Actuator M600, Switch, Local Disconnect; by Siemens, 600 VAC, 3 poles, 30 Amps |  | 2006 | 10 | [9 empty] | 4
2401 |  |  | PD6 |  |  |  | PM |  | Washdown Pump Local Disconnect Switch |  | 790900031 | IMG_2179 | 5000 | good |  |  | Actuator M700, Switch, Local Disconnect; by Siemens, 600 VAC, 3 poles,60 amps |  | 2006 | 10 | [9 empty] | 4
2402 |  |  | PD6 |  |  |  | SIC |  | South Cell Level Transmitter, LIT-100 |  | 00025383 | IMG_2247 | 12000 | good |  |  | ; MILTRONICS; MULTIRANGER 100; 031405199VX; 100-230V, 36VA (17W), CONTACT RATING: 5A @250VAC; 1 |  | 2006 | 9 | [9 empty] | 3
2403 |  |  | PD6 |  |  |  | SIC |  | North Cell Level Transmitter, LIT-200 |  | 00025383 | IMG_2249 | 12000 | good |  |  | ; MILTRONICS; MULTIRANGER 100; 031405250VX; 100-230V, 36VA (17W), CONTACT RATING: 5A @250VAC; 1 |  | 2006 | 9 | [9 empty] | 3
2404 |  |  | PD6 |  |  |  | SIC | 00086987 | Control Panel |  | 00025383 | IMG_2255 | 17000 | good |  |  | Network access closet; Haffman; ; ; 1 |  | 2006 | 9 | [9 empty] | 3
2406 |  |  | PD6 |  |  |  | SIC |  | Telephone Port |  | 00025383 | IMG_2326 | 300 | good |  |  | Telephone; ; ; ; 1 |  | 2006 | 5 | [9 empty] | 2
2408 |  |  | PD6 |  |  |  | SIC |  | Valve Area Temperature Switch |  | 00025384 | IMG_2348 | 500 | good |  |  | ; Honeywell; ; ; ;2 switches |  | 2006 | 5 | [9 empty] | 2
2410 |  |  | PD6 |  |  |  | SIC |  | Telephone Port |  | 00025384 | IMG_2361 | 300 | good |  |  | Telephone; ; ; ; 1 |  | 2006 | 5 | [9 empty] | 2
2411 |  |  | PD6 |  |  |  | PM | 0002603 | M-100 Motorized Valve |  | 00025384 | IMG_2366 | 10000 | Valve does not fully close. Setpoints seems to be the problem. |  |  | ; rotork; IQ; D120930106; 575V, 3ph, 0.69A, 0.19kW; 1 |  | 2006 | 5 | [9 empty] | 3
2412 |  |  | PD6 |  |  |  | PM | 00026018 | M-600 Motorized Valve |  | 00025384 | IMG_2406 | 10000 | Valve does not fully close. Setpoints seems to be the problem. |  |  | ; rotork; IQ; ; 575V, 3ph, 0.69A, 0.19kW; 1 |  | 2006 | 5 | [9 empty] | 3
2413 |  |  | PD6 |  |  |  | PM | 00026015 | M-500 Motorized Valve |  | 00025384 | IMG_2430 | 10000 | Valve does not fully close. Setpoints seems to be the problem. |  |  | ; rotork; IQ; D120930104; 575V, 3ph, 0.69A, 0.19kW; 1 |  | 2006 | 5 | [9 empty] | 3
2414 |  |  | PD6 |  |  |  | PM | 00026009 | M-300 Motorized Valve |  | 00025384 | IMG_2443 | 10000 | Valve does not fully close. Setpoints seems to be the problem. |  |  | ; rotork; IQ; D120930102; 575V, 3ph, 0.69A, 0.19kW; 1 |  | 2006 | 5 | [9 empty] | 3
2415 |  |  | PD6 |  |  |  | PM | 00026012 | M-400 Motorized Valve |  | 00025384 | IMG_2458 | 10000 | Valve does not fully close. Setpoints seems to be the problem. |  |  | ; rotork; IQ; D120930105; 575V, 3ph, 0.69A, 0.19kW; 1 |  | 2006 | 5 | [9 empty] | 3
2416 |  |  | PD6 |  |  |  | PM | 00026006 | M-400 Motorized Valve |  | 00025384 | IMG_2465 | 10000 | Valve does not fully close. Setpoints seems to be the problem. |  |  | ; rotork; IQ; D120930103; 575V, 3ph, 0.69A, 0.19kW; 1 |  | 2006 | 5 | [9 empty] | 3
2418 |  |  | PD6 |  |  |  | SIC |  | Security Panels |  | 00019042 | IMG_2494 | 20000 | good |  |  | security access control; Honeywell; ; ; ; 2 |  | 2019 | 15 | [9 empty] | 3
2424 |  |  | PD6 |  |  |  | ES |  | Welding Receptacle |  | 00025383 | IMG_2186 | 9000 | good |  |  | Welding Receptacle; Appleton; Powertite; ;600V, 60A |  | 2006 | 16 | [9 empty] | 2
2425 |  |  | PD6 |  |  |  | ES |  | MCC Main Breaker |  | 00025383 | IMG_2198 | 11900 | good |  |  | Main Breaker; Siemens; ; ; 600V, 200A; |  | 2006 | 16 | [9 empty] | 2
2426 |  |  | PD6 |  |  |  | ES |  | M-100 Valve Local DS |  | 00025384 | IMG_2369 | 600 | good |  |  | M 100, local Switch, Disconnect; Siemens; ; ; 600V, 30A; |  | 2006 | 16 | [9 empty] | 2
2427 |  |  | PD6 |  |  |  | ES |  | M-500 Valve local DS |  | 00025384 | IMG_2431 | 600 | good |  |  | M 500, Switch, local Disconnect; Siemens; ; ; 600V, 30A; |  | 2006 | 16 | [9 empty] | 2
2428 |  |  | PD6 |  |  |  | ES |  | M-300 Valve local DS |  | 00025384 | IMG_2444 | 800 | good |  |  | M 300, Switch, local Disconnect; Siemens; ID361NF; ; 600V, 30A; |  | 2006 | 16 | [9 empty] | 2
2429 |  |  | PD6 |  |  |  | ES |  | LP-B Transformer |  | 00019042 | IMG_2496 | 11000 | good |  |  | transformer; EVI; CDTC0010VHC6XXBB; 10KVA, 3ph, 600-120/208V; |  | 2006 | 16 | [9 empty] | 3
2430 |  |  | PD6 |  |  |  | ES |  | MCC Level Lighting |  | 00025383 | IMG_2266 | 13200 | The lighting fixture was not LED type. It should be replaced with LED fixtures in the next upgrade. |  |  | lighting; ; ; 22 linear flurescent fixtures |  | 2006 | 16 | [9 empty] | 2
2431 |  |  | PD6 |  |  |  | ES |  | Reservoir Exterior Lighting |  | 790900031 | IMG_2316 | 1500 | One of the fixture's sensor did not work and kept the light on during the day time. |  |  | lighting; ; ; 2 LED flood lights with light sensor |  | 2006 | 16 | [9 empty] | 2
2432 |  |  | PD6 |  |  |  | ES |  | Valve Gallery Lighting |  | 00025384 | IMG_2358 | 6000 | The lighting fixture was not LED type. It should be replaced with LED fixtures in the next upgrade. |  |  | lighting; ; ; 10 linear flurescent fixtures |  | 2006 | 16 | [9 empty] | 2
2433 |  |  | PD6 |  |  |  | ES |  | East Hatch Building Exterior Light |  | 00019042 | IMG_2492 | 750 | One of the fixture's sensor did not work and kept the light on during the day time. |  |  | lighting; ; ; 1 LED flood lights with light sensor |  | 2006 | 16 | [9 empty] | 2
2434 |  |  | PD6 |  |  |  | ES |  | East Hatch Building Interior Light |  | 00019042 |  | 600 | The lighting fixture was not LED type. It should be replaced with LED fixtures in the next upgrade. |  |  | lighting; ; ; 1 linear flurescent fixtures |  | 2006 | 16 | [9 empty] | 2
2435 |  |  | PD6 |  |  |  | ES |  | MCC level Emergency Lighting |  | 00025383 | IMG_2329 | 2400 | good |  |  | emeregency lighting; ; ; 3 exit signs and 1 remote head |  | 2006 | 16 | [9 empty] | 2
2334 |  |  | PD6 |  |  |  | SC |  | North Cell Aluminum Grating |  | 790900031 | DSC07706 | 500 | good |  |  |  |  | 2006 | 0 | [9 empty] | 3
2335 |  |  | PD6 |  |  |  | SC |  | South Cell Aluminum Grating |  | 790900031 | IMG_2852 | 500 | good |  |  |  |  | 2006 | 0 | [9 empty] | 2
2336 |  |  | PD6 |  |  |  | SC |  | South Cell Aluminum Ladder |  | 790900031 | IMG_2847 | 5000 | corrosion at ladder top |  |  |  |  | 2006 | 0 | [9 empty] | 2
2337 |  |  | PD6 |  |  |  | SC |  | South Cell Concrete Floor Slab |  | 790900031 | IMG_2848 | 3700000 | Hairline cracking with efflorescence deposits | Rust spots | Debonded expansion joint sealant |  |  | 2006 | 0 | [9 empty] | 5
2338 |  |  | PD6 |  |  |  | SC |  | South Cell Concrete Walls |  | 790900031 | DSC07940 | 2700000 | Hairline cracking with efflorescence deposits | rust spots | active leaking at expansion joints on dividing wall |  |  | 2006 | 0 | [9 empty] | 5
2339 |  |  | PD6 |  |  |  | SC |  | South Cell Concrete Columns |  | 790900031 | DSC07940 | 400000 | Rust spots | Corroded exposed reinforcement | Loss of cement |  |  | 2006 | 0 | [9 empty] | 5
2340 |  |  | PD6 |  |  |  | SC |  | South Cell Concrete Roof |  | 790900031 | DSC07940 | 3600000 | Rust spots | Corroded wire ties | Exposed corroded reinforcement |  |  | 2006 | 0 | [9 empty] | 5
2341 |  |  | PD6 |  |  |  | SC |  | South Cell Concrete Beams |  | 790900031 | IMG_2848 | 7000 | Corroded wire ties |  |  |  |  | 2006 | 0 | [9 empty] | 5
2342 |  |  | PD6 |  |  |  | SC |  | North Cell Concrete Beams |  | 790900031 | DSC07735 | 7000 | Rust spots | Corroded wire ties |  |  |  | 2006 | 0 | [9 empty] | 5
2343 |  |  | PD6 |  |  |  | SC |  | Rear Access House Concrete Blockwalls |  | 00019042 | IMG_2248 | 7500 | good |  |  |  |  | 2006 | 0 | [9 empty] | 4
2344 |  |  | PD6 |  |  |  | SC |  | Rear Access House Precast Concrete Roof |  | 00019042 | IMG_2250 | 3000 | good |  |  |  |  | 2006 | 0 | [9 empty] | 3
2345 |  |  | PD6 |  |  |  | SC |  | Rear Access House Wood Truss Roof |  | 00019042 | IMG_2218 | 5000 | good |  |  |  |  | 2006 | 0 | [9 empty] | 3
2346 |  |  | PD6 |  |  |  | SC |  | Rear Access House Aluminum Guardrails |  | 00019042 | IMG_2247 | 1500 | Good | corrosion on grab handles |  |  |  | 2006 | 0 | [9 empty] | 2
2347 |  |  | PD6 |  |  |  | SC |  | Valve House Concrete Walls |  | 00025383 | DSC00640 | 200000 | good |  |  |  |  | 2006 | 0 | [9 empty] | 4
2348 |  |  | PD6 |  |  |  | SC |  | Valve House Precast Concrete Roof |  | 00019041 | DSC00641 | 50000 | good |  |  |  |  | 2006 | 0 | [9 empty] | 4
2349 |  |  | PD6 |  |  |  | SC |  | Valve House Wood Truss Roof |  | 00019041 | IMG_2862 | 50000 | good |  |  |  |  | 2006 | 0 | [9 empty] | 3
2350 |  |  | PD6 |  |  |  | SC |  | Valve House Guardrails |  | 00019041 | DSC00625 | 12000 | good |  |  |  |  | 2006 | 0 | [9 empty] | 3
2351 |  |  | PD6 |  |  |  | SC |  | Valve Gallery Concrete Floor Slab |  | 00025384 | DSC00676 | 115000 | good |  |  |  |  | 2006 | 0 | [9 empty] | 3
2352 |  |  | PD6 |  |  |  | SC |  | Valve Gallery Concrete Walls |  | 00025384 | DSC00676 | 300000 | cracking with efflorescence on reservoir walls |  |  |  |  | 2006 | 0 | [9 empty] | 4
2353 |  |  | PD6 |  |  |  | SC |  | Valve Gallery Concrete Beams |  | 00025384 | DSC00658 | 33000 | good |  |  |  |  | 2006 | 0 | [9 empty] | 4
2354 |  |  | PD6 |  |  |  | SC |  | Valve Gallery Aluminum Platform |  | 00025384 | DSC00682 | 15000 | good |  |  |  |  | 2006 | 0 | [9 empty] | 3
2355 |  |  | PD6 |  |  |  | SC |  | Valve House Aluminum Hatch |  | 00019041 | DSC00607 | 5000 | good |  |  | Overflow |  | 2006 | 0 | [9 empty] | 2
2356 |  |  | PD6 |  |  |  | AC |  | Rear Access House Access Door (Single) |  | 00019042 | DSC07861 | 3500 | good |  |  |  |  | 2006 | 0 | [9 empty] | 1
2357 |  |  | PD6 |  |  |  | AC |  | Valve House Access Door (Single) |  | 00019041 | DSC00629 | 5500 | good |  |  | To north cell |  | 2006 | 0 | [9 empty] | 1
2358 |  |  | PD6 |  |  |  | AC |  | Valve House Access Door (Single) |  | 00019041 | DSC00614 | 5500 | good |  |  | To south cell |  | 2006 | 0 | [9 empty] | 1
2359 |  |  | PD6 |  |  |  | AC |  | Valve Gallery Wall and Ceiling Paint |  | 00025384 | DSC00658 | 20000 | good |  |  |  |  | 2006 | 0 | [9 empty] | 1
2360 |  |  | PD6 |  |  |  | AC |  | Valve House Wall Paint |  | 00025383 | DSC00641 | 15000 | good |  |  |  |  | 2006 | 0 | [9 empty] | 1
2361 |  |  | PD6 |  |  |  | AC |  | Rear Access House Wall and Ceiling Paint |  | 00019042 | IMG_2247 | 2000 | good |  |  |  |  | 2006 | 0 | [9 empty] | 1
2362 |  |  | PD6 |  |  |  | AC |  | Rear Access House Exterior Brick Veneer |  | 00019042 | DSC07860 | 8000 | good |  |  |  |  | 2006 | 0 | [9 empty] | 1
2363 |  |  | PD6 |  |  |  | AC |  | Rear Access House Metal Roofing |  | 00019042 | DSC07860 | 3000 | good |  |  |  |  | 2006 | 0 | [9 empty] | 1
2364 |  |  | PD6 |  |  |  | AC |  | Access House Metal Roofing |  | 00025383 | DSC07844 | 35000 | good |  |  |  |  | 2006 | 0 | [9 empty] | 1
2365 |  |  | PD6 |  |  |  | AC |  | Access House Exterior Brick Veneer |  | 00025383 | DSC07844 | 65000 | good |  |  |  |  | 2006 | 0 | [9 empty] | 1
2366 |  |  | PD6 |  |  |  | AC |  | North Cell Stainless Door |  | 790900031 | DSC07714 | 10000 | Corrosion on hardware |  |  |  |  | 2006 | 0 | [9 empty] | 1
2367 |  |  | PD6 |  |  |  | AC |  | South Cell Stainless Door |  | 790900031 | DSC07939 | 10000 | Corrosion on hardware |  |  |  |  | 2006 | 0 | [9 empty] | 1
2368 |  |  | PD6 |  |  |  | SW |  | Drain Chamber Precast Concrete Structure |  | 790900031 | DSC07758 | 60000 | good |  |  | 2.4m diameter precast |  | 2006 | 0 | [9 empty] | 2
2371 |  |  | PD6 |  |  |  | SW |  | Drain Chamber Ladder |  | 790900031 | DSC07758 | 2500 | good |  |  |  |  | 2006 | 0 | [9 empty] | 2
2372 |  |  | PD6 |  |  |  | SW |  | Drain Chamber Manhole Cover and Frame |  | 790900031 | DSC07757 | 3000 | good |  |  |  |  | 2006 | 0 | [9 empty] | 2
2375 |  |  | PD6 |  |  |  | SW |  | Asphalt Access Road |  | 790900031 | DSC07804 | 215000 | Cracking was noted throughout. |  |  | approx. 3050 sq m. |  | 2006 | 0 | [9 empty] | 2
2328 |  |  | PD6 |  |  |  | SC |  | North Cell Concrete Floor Slab |  | 790900031 | DSC07720 | 3700000 | hairline cracking with efflorescence deposits | rust spots | Debonded expansion joints |  |  | 2006 | 0 | [9 empty] | 5
2329 |  |  | PD6 |  |  |  | SC |  | North Cell Concrete Walls |  | 790900031 | DSC07720 | 2700000 | Hairline cracking with Efflorescence deposits | Debonded expansion joints and active leaking at expansion joint at dividing wall | Bugholes |  |  | 2006 | 0 | [9 empty] | 4
2330 |  |  | PD6 |  |  |  | SC |  | North Cell Concrete Columns |  | 790900031 | DSC07720 | 400000 | Rust spots | Loss of cement |  |  |  | 2006 | 0 | [9 empty] | 5
2331 |  |  | PD6 |  |  |  | SC |  | North Cell Concrete Roof |  | 790900031 | DSC07720 | 3600000 | Rust spots | Corroded wire ties | Exposed corroded reinforcement |  |  | 2006 | 0 | [9 empty] | 5
2332 |  |  | PD6 |  |  |  | SC |  | North Cell Aluminum Ladder |  | 790900031 | DSC07734 | 5000 | Corrosion at top |  |  |  |  | 2006 | 0 | [9 empty] | 2
2150 |  |  | PD6 |  |  |  | SIC | 00018388 |  | Markham N PD6 RES MCC Level | 00025383 |  | 5000 | good |  |  | MKNRPVW101, Network, OIT |  | 2006 | 2 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M01026 | SCADA
2151 |  |  | PD6 |  |  |  | SIC | 00018394 | UPS | Markham N PD6 RES MCC Level | 00025383 |  | 1000 | good |  |  | MKNRUPS101, Network, UPS |  | 2006 | 2 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00728 | SCADA
2152 |  |  | PD6 |  |  |  | SIC | 00018395 |  | Markham N PD6 RES MCC Level | 00025383 |  | 2000 | good |  |  | MKNRRAD101, Network, Radio Modem |  | 2006 | 2 |  |  | East |  |  |  |  | W-WW |  | 3 | [6 empty] | M01018 | SCADA
2153 |  |  | PD6 |  |  |  | SIC | 00018396 | Network and Communication equipment | Markham N PD6 RES MCC Level | 00025383 | IMG_2510 | 8000 | good |  |  | MKNRRAD102, Network, Antenna & Cable; ; Wilson; ; ; ;1 |  | 2006 | 2 |  |  | East |  |  |  |  | W-WW |  | 3 | [7 empty] | SCADA
2154 |  |  | PD6 |  |  |  | SIC | 00018397 |  | Markham N PD6 RES MCC Level | 00025383 |  | 0 |  |  |  | MKNRRPU101, RPU, RPU Panel |  | 2006 | 0 |  |  | East |  |  |  |  | W-WW |  | 3 | [6 empty] | M00020 | SCADA
2155 |  |  | PD6 |  |  |  | SIC | 00018389 |  | Markham N PD6 RES Valve Gallery | 00025384 |  | 1500 | good |  |  | MKNRTSH800, High Alarm, Temperature Switch, Temperature |  | 2006 | 2 |  |  | East |  | F5000979 |  |  | W-WW |  | 2 | [6 empty] | M00996 | Instrumentation and Control
2156 |  |  | PD6 |  |  |  | SIC | 00018390 | Chlorine Analyzer | Markham N PD6 RES Valve Gallery | 00025384 | IMG_2373 | 15000 | good |  |  | MKNR_AIT1, Total Residual, Chlorine Analyzer, Chlorine; HACH; CL17 |  | 2006 | 2 |  |  | East |  | 060500015590 |  |  | W-WW |  | 3 | [6 empty] | M00482 | Instrumentation and Control
2157 |  |  | PD6 |  |  |  | SIC | 00018391 | High Level Floats | Markham N PD6 RES Valve Gallery | 790900031 | DSC07875 | 1000 | good |  |  | MKNRLSH101, High Level Alarm, Float Switch, Level; ; ; ; 2 |  | 2006 | 2 |  |  | East |  |  |  |  | W-WW |  | 3 | [6 empty] | M00061 | Instrumentation and Control
2158 |  |  | PD6 |  |  |  | SIC | 00018392 | Ultrasonic Level | Markham N PD6 RES MCC Level | 790900031 | DSC07877 | 7600 | good |  |  | MKNR_LIT1, Cell 1, Ultrasonic Level, Level; ; ; ; 1 |  | 2006 | 2 |  |  | East |  | 031405199VX |  |  | W-WW |  | 3 | [6 empty] | M00105 | Instrumentation and Control
2159 |  |  | PD6 |  |  |  | SIC | 00018393 | Cell 2 Ultrasonic Level sensor | Markham N PD6 RES MCC Level | 00025383 | DSC07942 | 7600 | good |  |  | MKNR_LIT2, Cell 2, Ultrasonic Level, Level |  | 2006 | 2 |  |  | East |  | 031405250VX |  |  | W-WW |  | 3 | [6 empty] | M00105 | Instrumentation and Control
2160 |  |  | PD6 |  |  |  | ES | 00043542 | Monorail Switch | Markham N PD6 RES Valve Gallery | 00025384 | IMG_2478 | 15000 | good |  |  | S 1, North Monorail Switch, Hoist Beam;Hammond; ; 575V, 3ph, 40hp |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 3 | [6 empty] | M00118
2161 |  |  | PD6 |  |  |  | ES | 00043543 | South Monorail Switch | Markham N PD6 RES Valve Gallery | 00025384 | IMG_2474 | 15000 | good |  |  | S 2, South Monorail Switch, Hoist Beam; Hammond; ; 575V, 3ph, 40hp |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 3 | [6 empty] | M00118
2162 |  |  | PD6 |  |  |  | BM | 00043544 | Electrical Unit Heater, EH-4 | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2183 | 2500 | good condition |  |  | EH 4, Heating System, Unit Heater, 7.5 kW, 575VAC/3ph, by Ouellet, located in basement, |  | 2006 | 5 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00111
2163 |  |  | PD6 |  |  |  | SC | 00043546 | Rear Access House Davit Base (South) | Markham N PD6 RES East Hatch Building | 00019042 | IMG_2235 | 3000 | good |  |  | South, Fall Arrest System, Davit Arm Base |  | 2006 | 0 |  |  | East |  |  |  |  | W-WW |  | 4 | [6 empty] | M10152
2164 |  |  | PD6 |  |  |  | SC | 00043545 | Rear Access House Davit Arm | Markham N PD6 RES East Hatch Building | 00019042 | IMG_2233 | 0 | good |  |  | Fall Arrest System, Davit Arm | 2008-01-05 | 2009 | 0 |  |  | East |  | 12420657 |  |  | W-WW |  | 4 | [6 empty] | M10152
2165 |  |  | PD6 |  |  |  | SC | 00043547 | Rear Access House Davit Base (North) | Markham N PD6 RES East Hatch Building | 00019042 | IMG_2234 | 3000 | good |  |  | North, Fall Arrest System, Davit Arm Base |  | 2006 | 0 |  |  | East |  |  |  |  | W-WW |  | 4 | [6 empty] | M10152
2166 |  |  | PD6 |  |  |  | ES | 00026045 | LP-B Panel | Markham N PD6 RES East Hatch Building | 00019042 | IMG_2502 | 10300 | Panel was inside wooden cabinet. It needed to be replaced with Nema 4X rated panel. | Minor corrosion |  | LP B, Panel Board, Lighting Panel; Siemens; ; 120/208V; 125A, 36CCT; 1 |  | 2006 | 10 |  |  | East |  |  |  |  | W-WW |  | 3 | [6 empty] | M00317
2167 |  |  | PD6 |  |  |  | HSS | 00043524 | Valve House First Aid Kit | Markham N PD6 RES MCC Level | 00025383 |  | 50 |  |  |  | First Aid Kit, First Aid Kit |  | 2006 | 0 |  |  | East |  |  |  |  | W-WW |  | 3 | [6 empty] | M10151
2168 |  |  | PD6 |  |  |  | ES | 00043528 |  | Markham N PD6 RES MCC Level | 00025383 |  | 0 |  |  |  | Outside Timer, Lighting, Outside Timer |  | 2006 | 0 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00523
2169 |  |  | PD6 |  |  |  | AC | 00019069 | Valve House Access Door (Single) | Markham N PD6 RES MCC Level | 00025383 | IMG_2862 | 3500 | good |  |  | Main Entrance, Door, Exterior Single Metal |  | 2006 | 0 |  |  | East |  |  |  |  | W-WW |  | 1
2170 |  |  | PD6 |  |  |  | AC | 00019046 | Valve House Access Door (Single) | Markham N PD6 RES MCC Level | 00025383 | DSC00630 | 3500 | good |  |  | Valve Gallery Stair Well, Door, Interior Single Metal With Window |  | 2006 |  |  |  | East |  |  |  |  | W-WW |  | 1
2171 |  |  | PD6 |  |  |  | AC | 00019068 | Valve House Access Door (Single) | Markham N PD6 RES Pipe Gallery Stairwell | 00019043 | IMG_2862 | 3500 | good |  |  | Access to Valve Gallery, Door, Exterior Single Metal |  | 2006 | 0 |  |  | East |  |  |  |  | W-WW |  | 1
2172 |  |  | PD6 |  |  |  | PM | 00043498 | Gate Valve | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2092 | 2000 | good |  |  | Wash Down Inlet Isolation, Valve, Gate, 75mm DIA, DI construction, non-rising stem, manual, located in basement |  | 2006 | 10 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00145
2173 |  |  | PD6 |  |  |  | PM | 00043499 | Air Vacuum Release Valve | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2137 | 2500 | good |  |  | Watermain Crossover, Valve, Air-Vacuum Release; 25 mm DIA, Val-Matic model 201C; located in basement |  | 2006 | 10 |  |  | East |  |  |  |  | W-WW |  | 3 | [6 empty] | M00926
2174 |  |  | PD6 |  |  |  | PM | 00043500 | Air Vacuum Release Valve | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2158 | 0 | good |  |  | North Watermain, Valve, Air-Vacuum Release, 25 mm DIA, Val-Matic model 201C; located in basement |  | 2006 | 10 |  |  | East |  |  |  |  | W-WW |  | 3 | [6 empty] | M00926
2175 |  |  | PD6 |  |  |  | PM | 00043501 | Gate Valve | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2147 | 5000 | good |  |  | North Cell Drain, Valve, Gate; 300 mm DIA, DI construction, rising stem, by AVK; located in basement |  | 2006 | 15 |  |  | East |  |  |  |  | W-WW |  | 3 | [6 empty] | M00210
2176 |  |  | PD6 |  |  |  | ES | 00043502 |  | Markham N PD6 RES MCC Level | 790900031 |  | 0 |  |  |  | Switch, Main Service |  | 2006 | 0 |  |  | East |  |  |  |  | W-WW |  | 3 | [6 empty] | M00125
2177 |  |  | PD6 |  |  |  | ES | 00043503 | Digital Meter | Markham N PD6 RES MCC Level | 00025383 | IMG_2201 | 28500 | good |  |  | DMU Monitor, Switch, MCC Equipment Control; Siemens; Access 9330; ; ; digital |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 3
2178 |  |  | PD6 |  |  |  | ES | 00043504 | EH-1 Breaker | Markham N PD6 RES MCC Level | 00025383 | IMG_2203 | 900 | good |  |  | Unit Heater EH 1, Switch, MCC Disconnect; Siemens; ; ; 600V, 20A; |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00125
2179 |  |  | PD6 |  |  |  | ES | 00043505 | EH-2 Breaker | Markham N PD6 RES MCC Level | 00025383 | IMG_2203 | 800 | good |  |  | Unit Heater EH 2, Switch, MCC Disconnect; Siemens; ; ; 600V, 15A; |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00125
2180 |  |  | PD6 |  |  |  | ES | 00043506 | EH-3 Breaker | Markham N PD6 RES MCC Level | 00025383 | IMG_2205 | 800 | good |  |  | Unit Heater EH 3, Switch, MCC Disconnect; Siemens; ; ; 600V, 15A; |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00125
2181 |  |  | PD6 |  |  |  | ES | 00043517 | EH-4 Breaker | Markham N PD6 RES MCC Level | 00025383 | IMG_2222 | 800 | good |  |  | Unit Heater EH 4, Switch, MCC Disconnect; Siemens; ; ; 600V, 15A; |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00125
2182 |  |  | PD6 |  |  |  | ES | 00043518 | EH-5 Breaker | Markham N PD6 RES MCC Level | 00025383 | IMG_2222 | 800 | good |  |  | Unit Heater EH 5, Switch, MCC Disconnect; Siemens; ; ; 600V, 15A; |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00125
2183 |  |  | PD6 |  |  |  | ES | 00043507 | Monorail M-1 Breaker | Markham N PD6 RES MCC Level | 00025383 | IMG_2205 | 800 | good |  |  | Monorail Crane M 1, Switch, MCC Disconnect; Siemens; ; ; 600V, 15A; |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 3 | [6 empty] | M00125
2184 |  |  | PD6 |  |  |  | ES | 00043508 | Monorail M-2 Breaker | Markham N PD6 RES MCC Level | 00025383 | IMG_2209 | 800 | good |  |  | Monorail Crane M 2, Switch, MCC Disconnect; Siemens; ; ; 600V, 15A; |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 3 | [6 empty] | M00125
2185 |  |  | PD6 |  |  |  | ES | 00043509 | M-100 Valve Breaker | Markham N PD6 RES MCC Level | 00025383 | IMG_2209 | 800 | good |  |  | Rotork Actuator M 100, Switch, MCC Disconnect; Siemens; ; ; 600V, 15A; |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00125
2186 |  |  | PD6 |  |  |  | ES | 00043510 | M-200 Valve Breaker | Markham N PD6 RES MCC Level | 00025383 | IMG_2214 | 800 | good |  |  | Rotork Actuator M 200, Switch, MCC Disconnect; Siemens; ; ; 600V, 15A; |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00125
2187 |  |  | PD6 |  |  |  | ES | 00043511 | M-300 Valve Breaker | Markham N PD6 RES MCC Level | 00025383 | IMG_2214 | 800 | good |  |  | Rotork Actuator M 300, Switch, MCC Disconnect; Siemens; ; ; 600V, 15A; |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00125
2188 |  |  | PD6 |  |  |  | ES | 00043512 | M-700 Valve Starter | Markham N PD6 RES MCC Level | 00025383 | IMG_2217 | 6400 | good |  |  | Washdown Pump M 700, Switch, MCC Equipment Control; Siemens; ; ; 600V, size 2 starter; |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00125
2189 |  |  | PD6 |  |  |  | ES | 00043513 | M-400 Valve Breaker | Markham N PD6 RES MCC Level | 00025383 | IMG_2218 | 800 | good |  |  | Rotork Actuator M 400, Switch, MCC Disconnect; Siemens; ; ; 600V, 15A; |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00125
2190 |  |  | PD6 |  |  |  | ES | 00043514 | M-500 Valve Breaker | Markham N PD6 RES MCC Level | 00025383 | IMG_2218 | 800 | good |  |  | Rotork Actuator M 500, Switch, MCC Disconnect; Siemens; ; ; 600V, 15A; |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00125
2191 |  |  | PD6 |  |  |  | ES | 00043515 | M-600 Valve Breaker | Markham N PD6 RES MCC Level | 00025383 | IMG_2219 | 800 | good |  |  | Rotork Actuator M 600, Switch, MCC Disconnect; Siemens; ; ; 600V, 15A; |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00125
2192 |  |  | PD6 |  |  |  | ES | 00043516 | Overhead Door Breaker | Markham N PD6 RES MCC Level | 00025383 | IMG_2219 | 800 | good |  |  | Overhead Door, Switch, MCC Disconnect; ; ; 600V, 15A; |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00125
2193 |  |  | PD6 |  |  |  | ES | 00043519 | Welding Receptacle Breaker | Markham N PD6 RES MCC Level | 00025383 | IMG_2223 | 1200 | good |  |  | Welding Receptacles, Switch, MCC Disconnect; ; ; 600V, 30A; |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00125
2194 |  |  | PD6 |  |  |  | ES | 00043520 | LP-A Transformer Breaker | Markham N PD6 RES MCC Level | 00025383 | IMG_2223 | 800 | good |  |  | Transformer LP A, Switch, MCC Disconnect; ; ; 600V, 15A; |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 3 | [6 empty] | M00125
2195 |  |  | PD6 |  |  |  | ES | 00043521 | Dehumidifier Transformer Breaker | Markham N PD6 RES MCC Level | 00025383 | IMG_2225 | 900 | good |  |  | Transformer DHU 1, Switch, MCC Disconnect; ; ; 600V, 20A; |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00125
2196 |  |  | PD6 |  |  |  | ES | 00043522 | LP-B Transformer Breaker | Markham N PD6 RES MCC Level | 00025383 | IMG_2225 | 900 | good |  |  | Transformer LP B, Switch, MCC Disconnect; ; ; 600V, 15A; |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00125
2197 |  |  | PD6 |  |  |  | HSS | 00043523 | Valve House Eye Wash Station | Markham N PD6 RES MCC Level | 00025383 | DSC07815 | 600 | good |  |  | Health and Safety Compliance Systems, Tank, Portable, Eye Wash |  | 2006 | 0 |  |  | East |  |  |  |  | W-WW |  | 3 | [6 empty] | M00233 | Health and Safety
2198 |  |  | PD6 |  |  |  | PM | 00043525 | Sump Pump, P-2 | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2043 | 3000 | good |  |  | Sump pump, P-2; 120VAC/1ph, 4/10 hp; submersible, centrifugal, by Liberty Pumps model HT40-Series; powered from LP-A; located in basement |  | 2006 | 5 |  |  | East |  |  |  |  | W-WW |  | 2
2199 |  |  | PD6 |  |  |  | PM | 00043494 | Gate Valve | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2052 | 5000 | good |  |  | South Cell Drain, Valve, Gate; 300 mm DIA, DI construction, rising stem, by AVK; located in basement |  | 2006 | 15 |  |  | East |  |  |  |  | W-WW |  | 3 | [6 empty] | M00210
2200 |  |  | PD6 |  |  |  | PM | 00043495 | Air Vacuum Release valve | Markham N PD6 RES MCC Level | 00025383 | IMG_2027 | 0 | good |  |  | South Watermain, Valve, Vacuum Release; 25 mm DIA, Val-Matic model 201C; located in basement |  | 2006 | 10 |  |  | East |  |  |  |  | W-WW |  | 3 | [6 empty] | M00926
2201 |  |  | PD6 |  |  |  | PM | 00026021 | Electrical Motor, reservoir washdown pump | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2082 | 8000 | good |  |  | Wash Down Pump, Electrical Motor, Induction; by Baldor Electric Co., 20 hp; 575VAC/3ph; 18.2 Amps; 3520 rpm; Class F , located in basement |  | 2006 | 1 |  |  | East |  |  |  |  | W-WW |  | 3 | [6 empty] | M00015
2202 |  |  | PD6 |  |  |  | PM | 00043496 | Check Valve | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2097 | 2000 | good |  |  | Wash Down Outlet, Valve, Swing Flex Check; by Val Matci model 503A, 75 mm DIA, DI construction, |  | 2006 | 10 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00926
2203 |  |  | PD6 |  |  |  | PM | 00043497 | Gate Valve | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2097 | 2000 | good |  |  | Wash Down Outlet, Valve, Gate, 75 mm DIA; flanged, OS&Y; DI construction, manual; AVK |  | 2006 | 15 |  |  | East |  | 25-080-4602600429 |  |  | W-WW |  | 2 | [6 empty] | M00210
2204 |  |  | PD6 |  |  |  | ES | 00043526 | EM-2 Emergency Battery Unit Light | Markham N PD6 RES Pipe Gallery Stairwell | 00019043 | IMG_2339 | 500 | good |  |  | EM 2, Lighting, Emergency |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00606
2205 |  |  | PD6 |  |  |  | ES | 00043530 | EM-3 Emergency Battery Unit Light | Markham N PD6 RES Mezzanine | 00019041 | IMG_2311 | 500 | good |  |  | EM 3, Lighting, Emergency |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00606
2206 |  |  | PD6 |  |  |  | ES | 00043527 | EM-1 Emergency Battery Unit Light | Markham N PD6 RES MCC Level | 00025383 | IMG_2257 | 500 | good |  |  | EM 1, Lighting, Emergency |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00606
2207 |  |  | PD6 |  |  |  | BM | 00043529 | Fire Extinguishers, HS-FE1, HS_FE2, HS_FE3 | Stouffville PD6 Reservoir | 790900031 | IMG_1971, IMG_2828, IMG_2826 | 500 | good |  |  | 3 Fire Extinguishers, Other Life Safety & Compliance, Kidde dry chemical |  | 2006 | 3 |  |  | East |  |  |  |  | W-WW |  | 3
2208 |  |  | PD6 |  |  |  | BM | 00026032 | Valve House Air Handling System | Markham N PD6 RES MCC Level | 790900031 | IMG_1933 | 35000 | good |  |  | DHU 1, Air Handling System, Dehumidifier, Bry- Air Model Mini PAC-350, 208VAC/3ph; main floor |  | 2006 | 8 |  |  | East |  |  |  |  | W-WW |  | 3
2209 |  |  | PD6 |  |  |  | ES | 00026033 | Dehumidifier Local DS | Markham N PD6 RES MCC Level | 00025383 | IMG_2261 | 1000 | good |  |  | Dehumidifier DHU 1, Switch, Local Disconnect |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00125
2210 |  |  | PD6 |  |  |  | ES | 00026034 | DHU-1 Transformer | Markham N PD6 RES MCC Level | 00025383 | IMG_2263 | 11900 | good |  |  | 15 kVA, Dehumidifier DHU 1, Transformer, Power; MARCUS; ;600-120/208V |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00620
2211 |  |  | PD6 |  |  |  | SIC | 00026042 | Security Panel | Markham N PD6 RES MCC Level | 00025383 | IMG_2244 | 7000 | good |  |  | Security System; Honeywell |  | 2006 | 2 |  |  | East |  |  |  |  | W-WW |  | 3 | [6 empty] | M01094
2212 |  |  | PD6 |  |  |  | ES | 00026043 | LP-A Panel | Markham N PD6 RES MCC Level | 00025383 | IMG_2236 | 10300 | good |  |  | LP A, Panel Board, Lighting Panel; Siemens; 120/208V, 125A, 30CCT |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 3
2213 |  |  | PD6 |  |  |  | SIC | 00026039 |  | Markham N PD6 RES MCC Level | 00025383 |  | 0 |  |  |  | RPU, RPU Panel |  | 2006 | 0 |  |  | East |  |  |  |  | W-WW |  | 3
2214 |  |  | PD6 |  |  |  | ES | 00026036 | MCC-1 | Markham N PD6 RES MCC Level | 00025383 | IMG_2193 | 60000 | good |  |  | MCC 1, Motor Control Centre; Siemens; tiastar; 600V, 600A, 4 Columns |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 3 | [6 empty] | M00125
2215 |  |  | PD6 |  |  |  | ES | 00026025 | EH-1 Local DS | Markham N PD6 RES MCC Level | 00025383 | IMG_2229 | 600 | good |  |  | Unit Heater EH 1, Switch, Local Disconnect; 600V, 30A, non-fused |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00125
2216 |  |  | PD6 |  |  |  | ES | 00026038 | Overhead Door local DS | Markham N PD6 RES MCC Level | 00025383 | IMG_2184 | 600 | good |  |  | Overhead Door, Switch, Local Disconnect |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00125
2217 |  |  | PD6 |  |  |  | ES | 00026026 | EH-2 local DS | Markham N PD6 RES MCC Level | 00025383 | IMG_2181 | 600 | good |  |  | Unit Heater EH 2, Switch, Local Disconnect; 600V, 30A, non-fused |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00125
2218 |  |  | PD6 |  |  |  | ES | 00026030 | EF-1 Exhaust Fan | Markham N PD6 RES MCC Level | 00025383 | IMG_2178 | 4000 | good |  |  | EF 1, Ventilation System, Exhaust Fan;Baldor; L3403; 1/4hp, 120V |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00015
2219 |  |  | PD6 |  |  |  | AC | 00019077 | Valve House Access Door (Single) | Markham N PD6 RES Mezzanine | 00019041 | DSC07842 | 3500 | good |  |  | North East, Door, Exterior Single Metal |  | 2006 | 0 |  |  | East |  |  |  |  | W-WW |  | 1
2220 |  |  | PD6 |  |  |  | SC | 00019072 | North Cell Aluminum Hatch | Markham N PD6 RES Mezzanine | 00019041 | DSC00627 | 5000 | good |  |  | North Cell, Hatch |  | 2006 | 0 |  |  | East |  |  |  |  | W-WW |  | 2
2221 |  |  | PD6 |  |  |  | SC | 00019071 | South Cell Aluminum Hatch | Markham N PD6 RES Mezzanine | 00019041 | DSC00610 | 5000 | good |  |  | South Cell, Hatch |  | 2006 | 0 |  |  | East |  |  |  |  | W-WW |  | 2
2222 |  |  | PD6 |  |  |  | SC | 00019063 | Precast Concrete Hatch | Markham N PD6 RES MCC Level | 00025383 | DSC00643 | 1500 | good |  |  | Concrete, Access To Valve Gallery, Hatch |  | 2006 | 0 |  |  | East |  |  |  |  | W-WW |  | 3
2223 |  |  | PD6 |  |  |  | SC | 00019079 | Access House Concrete Staircase | Markham N PD6 RES MCC Level | 00025383 | DSC07764 | 15000 | good |  |  | MCC Level to Mezzanine, Stair Interior, Concrete |  | 2006 | 0 |  |  | East |  |  |  |  | W-WW |  | 3
2224 |  |  | PD6 |  |  |  | BM | 00026047 | Rear Access House Baseboard Heater | Markham N PD6 RES East Hatch Building | 790900031 | IMG_2230 | 1000 | surface corrosion |  |  | North Side, Heating System, Baseboard Heater, Rear Access House, 1 kW |  | 2006 | 2 |  |  | East |  |  |  |  | W-WW |  | 2
2225 |  |  | PD6 |  |  |  | BM | 00026048 | Baseboard electrical heater | Markham N PD6 RES East Hatch Building | 790900031 | IMG_2244 | 1000 | surface corrosion |  |  | North Side, Heating System, Baseboard Heater, Rear Access House, 1 kW |  | 2006 | 2 |  |  | East |  |  |  |  | W-WW |  | 2
2226 |  |  | PD6 |  |  |  | SC | 00019065 | North Cell Concrete Staircase | Markham N PD6 RES Mezzanine | 00019041 | DSC07704 | 30000 | good |  |  | Access to North Cell, Stair Interior, Concrete |  | 2006 | 0 |  |  | East |  |  |  |  | W-WW |  | 3
2227 |  |  | PD6 |  |  |  | SC | 00019064 | South Cell Concrete Staircase | Markham N PD6 RES Mezzanine | 00019041 | IMG_2859 | 30000 | good |  |  | Access to South Cell, Stair Interior, Concrete |  | 2006 | 0 |  |  | East |  |  |  |  | W-WW |  | 3
2228 |  |  | PD6 |  |  |  | SC | 00019058 | Valve Gallery Concrete Staircase | Markham N PD6 RES Pipe Gallery Stairwell | 00019043 | DSC00646 | 20000 | good |  |  | Stair Interior, Concrete |  | 2006 | 0 |  |  | East |  |  |  |  | W-WW |  | 3
2229 |  |  | PD6 |  |  |  | BM | 00043548 | Motorized Damper, MD-3 | Markham N PD6 RES MCC Level | 790900031 | IMG_1927 | 0 | good |  |  | MD 3 Dehumidifier, Ventilation System, Damperc/w Belimo actuator |  | 2006 | 10 |  |  | East |  |  |  |  | W-WW |  | 3
2230 |  |  | PD6 |  |  |  | BM | 00026031 | Exhaust Fan, EF-2 | Markham N PD6 RES MCC Level | 790900031 | IMG_1903 | 5000 | good |  |  | EF 2, Ventilation System, Exhaust Fan,inline centrifugal, by Carnes model VIBK08L1A5CL93S G1, 115VAC /1ph; 0.25hp motor; powered from LP-A |  | 2006 | 10 |  |  | East |  |  |  |  | W-WW |  | 3
2231 |  |  | PD6 |  |  |  | ES | 00026023 | M-1 Disconnect Switch | Markham N PD6 RES MCC Level | 00025383 | IMG_2295 | 600 | good |  |  | Monorail Crane M 1, Switch, Local Disconnect; siemens; ID361NF, 600V, 30A, nonfused |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00125
2232 |  |  | PD6 |  |  |  | ES | 00026027 | EH-3 local DS | Markham N PD6 RES MCC Level | 00025383 | IMG_2308 | 600 | good |  |  | Unit Heater EH 3, Switch, Local Disconnect; siemens; 600V, 30A, nonfused |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00125
2233 |  |  | PD6 |  |  |  | ES | 00026035 | LP-A Transformer | Markham N PD6 RES MCC Level | 00025383 | IMG_2232 | 11900 | good |  |  | LP A, Transformer, Distribution; EVI; COTC6615VHC5VHC6XXBB; 15KVA, 600-120/208V |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 3 | [6 empty] | M00357
2234 |  |  | PD6 |  |  |  | ES | 00026024 | M-2 local DS | Markham N PD6 RES Valve Gallery | 00025384 | IMG_2343 | 600 | good |  |  | Monorail Crane M 2, Switch, Local Disconnect;Siemens; ID361NF; 600V, 30A, non-fused |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00125
2235 |  |  | PD6 |  |  |  | ES | 00026028 | EH-4 local DS | Markham N PD6 RES Valve Gallery | 00025384 | IMG_2345 | 600 | good |  |  | Unit Heater EH 4, Switch, Local Disconnect;Siemens; ID361NF; 600V, 30A, non-fused |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00125
2236 |  |  | PD6 |  |  |  | PM | 00026004 | Valve Local Disconnect Switch | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2025 | 5000 | good |  |  | Actuator M 100, Switch, Local Disconnect; by Siemens, 600 VAC, 3 poles, 30 Amps |  | 2006 | 10 |  |  | East |  |  |  |  | W-WW |  | 4 | [6 empty] | M00125
2237 |  |  | PD6 |  |  |  | PM | 00026003 | Butterfly valve electric actuator | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2018 | 10000 | good |  |  | M 100, Actuator, Electric; by Rotork Type IQ12, 575VAC/3 ph/60 Hz; torque 81 Nm |  | 2006 | 10 |  |  | East |  |  |  |  | W-WW |  | 4 | [6 empty] | M00120
2238 |  |  | PD6 |  |  |  | PM | 00026002 | Butterfly Valve | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2005 | 40000 | good |  |  | V 100, Valve, Butterfly,flanged, 1050 mm DIA, by Val Matic model 2042P1; Class #150B; electrical actuator; |  | 2006 | 15 |  |  | East |  |  |  |  | W-WW |  | 4
2239 |  |  | PD6 |  |  |  | ES | 00026029 | EH-5 Local DS | Markham N PD6 RES Valve Gallery | 00025384 | IMG_2402 | 600 | good |  |  | Unit Heater EH 5, Switch, Local Disconnect;Siemens; ID361NF; 600V, 30A, non-fused |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00125
2240 |  |  | PD6 |  |  |  | ES | 00026019 | M-600 local DS | Markham N PD6 RES Valve Gallery | 00025384 | IMG_2416 | 600 | good |  |  | Actuator M 600, Switch, Local Disconnect;Siemens; ID361NF; 600V, 30A, non-fused |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00125
2241 |  |  | PD6 |  |  |  | PM | 00026017 | Butterfly Valve | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2109 | 40000 | good |  |  | V 600, Valve, Butterfly, 1050 mm DIA, flanged, by Val Matic model 2042P1; Class #150B; electrical actuator; |  | 2006 | 15 |  |  | East |  |  |  |  | W-WW |  | 4
2242 |  |  | PD6 |  |  |  | PM | 00026018 | Electric Actuator for Butterfly Valve | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2109 | 10000 | good |  |  | M 600 , Actuator, Electric; by Rotork Type IQ12, 575VAC/3 ph/60 Hz; torque 81 Nm |  | 2006 | 10 |  |  | East |  |  |  |  | W-WW |  | 4 | [6 empty] | M00120
2243 |  |  | PD6 |  |  |  | ES | 00026022 | Washdown Pump Local DS | Markham N PD6 RES Valve Gallery | 00025384 | IMG_2419 | 1100 | good |  |  | Wash Down Pump, Switch, Local Disconnect;Siemens; ID362NF; 600V, 60A, non-fused |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00125
2244 |  |  | PD6 |  |  |  | PM | 00026016 | Valve Local Disconnect Switch | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2104 | 5000 | good |  |  | Actuator M 500, Switch, Local Disconnect, by Siemens, 600 VAC, 3 poles, 30 Amps |  | 2006 | 10 |  |  | East |  |  |  |  | W-WW |  | 4 | [6 empty] | M00125
2245 |  |  | PD6 |  |  |  | PM | 00026015 | Butterfly Valve Electric Actuator | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2104 | 10000 | good |  |  | M 500, Actuator, Electric; by Rotork Type IQ12, 575VAC/3 ph/60 Hz; torque 81 Nm |  | 2006 | 10 |  |  | East |  |  |  |  | W-WW |  | 4 | [6 empty] | M00120
2246 |  |  | PD6 |  |  |  | PM | 00026014 | Butterfly Valve | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2104 | 40000 | good |  |  | V 500, Valve, Butterfly, 1050 mm DIA, flanged, by Val Matic model 2042P1; Class #150B; electrical actuator; |  | 2006 | 15 |  |  | East |  |  |  |  | W-WW |  | 4
2247 |  |  | PD6 |  |  |  | PM | 00026010 | Valve Local Disconnect Switch | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2116 | 5000 | good |  |  | Actuator M300, Switch, Local Disconnect; by Siemens, 600 VAC, 3 poles, 30 Amps |  | 2006 | 10 |  |  | East |  |  |  |  | W-WW |  | 4 | [6 empty] | M00125
2248 |  |  | PD6 |  |  |  | PM | 00026008 | Butterfly Valve | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2120 | 40000 | good |  |  | V 300, Valve, Butterfly; 1050 mm DIA, flanged, by Val Matic model 2042P1; Class #150B; electrical actuator; |  | 2006 | 15 |  |  | East |  |  |  |  | W-WW |  | 4
2249 |  |  | PD6 |  |  |  | PM | 00026009 | Butterfly Valve Electric Actuator | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2114 | 10000 | good |  |  | M 300, Actuator, Electric; by Rotork Type IQ12, 575VAC/3 ph/60 Hz; torque 81 Nm |  | 2006 | 10 |  |  | East |  |  |  |  | W-WW |  | 4 | [6 empty] | M00120
2250 |  |  | PD6 |  |  |  | PM | 00026011 | Butterfly Valve | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2130 | 40000 | good |  |  | V 400, Valve, Butterfly; 1050 mm DIA, flanged, by Val Matic model 2042P1; Class #150B; electrical actuator; |  | 2006 | 15 |  |  | East |  |  |  |  | W-WW |  | 4
2251 |  |  | PD6 |  |  |  | PM | 00026012 | Butterfly Valve Electric Actuator | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2130 | 10000 | good |  |  | M 400, Actuator, Electric; by Rotork Type IQ12, 575VAC/3 ph/60 Hz; torque 81 Nm |  | 2006 | 10 |  |  | East |  |  |  |  | W-WW |  | 4 | [6 empty] | M00120
2252 |  |  | PD6 |  |  |  | ES | 00026013 | M-400 local DS | Markham N PD6 RES Valve Gallery | 00025384 | IMG_2461 | 600 | good |  |  | Actuator M 400, Switch, Local Disconnect;Siemens; ID361NF; 600V, 30A, non-fused |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00125
2253 |  |  | PD6 |  |  |  | ES | 00026007 | M-200 local DS | Markham N PD6 RES Valve Gallery | 00025384 | IMG_2466 | 600 | good |  |  | Actuator M 200, Switch, Local Disconnect;Siemens; ID361NF; 600V, 30A, non-fused |  | 2006 | 16 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00125
2254 |  |  | PD6 |  |  |  | BM | 00043533 | Electric Heater, EH-2 | Markham N PD6 RES MCC Level | 790900031 | IMG_1913 | 2500 | good |  |  | EH 2, Heating System, Unit Heater 5 kW, 575VAC/3ph, by Ouellet, located on main floor |  | 2006 | 5 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00111
2255 |  |  | PD6 |  |  |  | AC | 00043534 | Valve House Overhead Door | Markham N PD6 RES MCC Level | 00025383 | IMG_2862 | 8000 | corrosion at bottom of door frame |  |  | Door, Rollup Overhead |  | 2006 | 0 |  |  | East |  |  |  |  | W-WW |  | 1 | [6 empty] | M00328
2256 |  |  | PD6 |  |  |  | BM | 00043535 | Electric Heater, EH-1 | Markham N PD6 RES MCC Level | 790900031 | IMG_1920 | 3500 | good |  |  | EH 1, Heating System, Unit Heater 15kW, 575VAC/3ph, by Ouellet, located on main floor |  | 2006 | 0 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00111
2257 |  |  | PD6 |  |  |  | BM | 00043536 | Electric Heater, EH-3 | Markham N PD6 RES Mezzanine | 790900031 | IMG_1964 | 2500 | good |  |  | EH 3, Heating System, Unit Heater 5kW, 575VAC/3ph, by Ouellet, located on main floor, mezzanine |  | 2006 | 5 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00111
2258 |  |  | PD6 |  |  |  | SC | 00043537 | Valve House Monorail Hoist Beam | Markham N PD6 RES MCC Level | 00025383 | DSC00605 | 10000 | good |  |  | M 1, Overhead, Elevator, Hoist |  | 2006 | 0 |  |  | East |  | 6982 |  |  | W-WW |  | 3 | [6 empty] | M00091
2259 |  |  | PD6 |  |  |  | BM | 00043538 | Baseboard electrical heater, EH-6 | Markham N PD6 RES Pipe Gallery Stairwell | 790900031 | IMG_2198 | 1000 | good |  |  | EH 6, Heating System, Baseboard Heater, 1.25 kW, 120VAC/1ph, connected to LP-A, located on main floor in the stairwell to the basement; |  | 2006 | 5 |  |  | East |  |  |  |  | W-WW |  | 1 | [6 empty] | M00111
2260 |  |  | PD6 |  |  |  | SC | 00043539 | Valve Gallery Monorail Hoist Beam | Markham N PD6 RES Valve Gallery | 00025384 | DSC00659 | 40000 | good |  |  | M 2 Overhead, Elevator, Hoist |  | 2006 | 0 |  |  | East |  | 26771 |  |  | W-WW |  | 3 | [6 empty] | M00091
2261 |  |  | PD6 |  |  |  | BM | 00043540 | Electric Heater, EH-5 | Markham N PD6 RES Valve Gallery | 790900031 | IMG_1988 | 2500 | good |  |  | EH 5, Heating System, Unit Heater, 7.5 kW, 575VAC/3ph, by Ouellet, located in basement, in the west-south corner |  | 2006 | 5 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00111
2262 |  |  | PD6 |  |  |  | PM | 00043541 | Reservoir washdown pump | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2082 | 10000 | minor surface corrosion | Operation reported excessive noise and not sufficient pressure developed in the discharge | to be replaced with a new pump | Wash Down, Pump, End Suction Centrifugal; by Armstron model 2x1x10 4280 BF STD, 4.4 L/s at 82.4 m TDH, 14.91kW motor; 3600 rpm |  | 2006 | 1 |  |  | East |  | C523007 |  |  | W-WW |  | 2 | [6 empty] | M00007
2263 |  |  | PD6 |  |  |  | PM | 00026006 | Butterfly Valve Electric Actuator | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2149 | 10000 | good |  |  | M 200, Actuator, Electric; by Rotork Type IQ12, 575VAC/3 ph/60 Hz; torque 81 Nm |  | 2006 | 10 |  |  | East |  |  |  |  | W-WW |  | 4 | [6 empty] | M00120
2264 |  |  | PD6 |  |  |  | PM | 00026005 | Butterfly Valve | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2149 | 40000 | good |  |  | V 200, Valve, Butterfly; 1050 mm DIA, flanged, by Val Matic model 2042P1; Class #150B; electrical actuator; |  | 2006 | 15 |  |  | East |  |  |  |  | W-WW |  | 4
2265 |  |  | PD6 |  |  |  | SC | 00019059 | Valve House Concrete Floor Slab | Markham N PD6 RES MCC Level | 00025383 | DSC00615 | 240000 | good |  |  | Floor Slab, Concrete |  | 2006 | 0 |  |  | East |  |  |  |  | W-WW |  | 3 | [7 empty] | Structural
2266 |  |  | PD6 |  |  |  | BM | 00043549 | Motorized Damper MD-1 | Markham N PD6 RES MCC Level | 790900031 | IMG_1959 | 3000 | good |  |  | MD 1, Ventilation System, Damper c/w outdoor louver, main floor, south wall, 120VAC/1ph, Belimo actuator; powered from LP-A |  | 2006 | 10 |  |  | East |  |  |  |  | W-WW |  | 2
2268 |  |  | PD6 |  |  |  | PM | 00019051 | Service Water Piping | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2174 | 2000 | good |  |  | Water Main, Piping, Service Water; 50-75 mm DIA, S.S., thermally insulated. |  | 2006 | 20 |  |  | East |  |  |  |  | W-WW |  | 3
2269 |  |  | PD6 |  |  |  | PM | 00019056 | Hose down water piping | Markham N PD6 RES Valve Gallery | 790900031 | IMG-2065 | 2000 | good |  |  | Hose Down Water, Piping, Insulated |  | 2006 | 20 |  |  | East |  |  |  |  | W-WW |  | 2
2270 |  |  | PD6 |  |  |  | PM | 00019055 | Washwater, Piping | Markham N PD6 RES Valve Gallery | 790900031 | IMG_1 | 5000 | good |  |  | Washwater, Piping, Discharge, in South Cell |  | 2006 | 20 |  |  | East |  |  |  |  | W-WW |  | 2
2271 |  |  | PD6 |  |  |  | PM | 00019054 | Over Flow Piping | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2056 | 20000 | good |  |  | Over Flow, Piping, 1050 mm DIA, all S.S., welded construction, |  | 2006 | 20 |  |  | East |  |  |  |  | W-WW |  | 4
2272 |  |  | PD6 |  |  |  | PM | 00019053 | Access Platform | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2065 | 15000 | good |  |  | Over Water Main Piping, Access Platform, Aluminum Grating |  | 2006 | 20 |  |  | East |  |  |  |  | W-WW |  | 2
2273 |  |  | PD6 |  |  |  | PM | 00019052 | Washwater, Piping, Suction | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2076 | 5000 | good |  |  | Washwater, Piping, Suction; all S.S. welded construction, 75 nmm DIA, flanged connection to valves, non-insulated |  | 2006 | 20 |  |  | East |  |  |  |  | W-WW |  | 3
2274 |  |  | PD6 |  |  |  | PM | 00019050 |  | Markham N PD6 RES Valve Gallery | 790900031 |  | 0 |  |  |  | Overflow, Piping, Insulated |  | 2006 | 0 |  |  | East |  |  |  |  | W-WW |  | 3
2275 |  |  | PD6 |  |  |  | PM | 00019049 | Sampling Piping | Markham N PD6 RES Valve Gallery | 790900031 | IMG_2031 | 500 | good |  |  | Sample port, Piping, Stainless Steel, 10 mm DIA |  | 2006 | 15 |  |  | East |  |  |  |  | W-WW |  | 4
2276 |  |  | PD6 |  |  |  | PM | 00019048 |  | Markham N PD6 RES Valve Gallery | 790900031 |  | 0 |  |  |  | Piping, Chemical Tubing |  | 2006 | 0 |  |  | East |  |  |  |  | W-WW |  | 3
2277 |  |  | PD6 |  |  |  | PM | 00019047 |  | Markham N PD6 RES Valve Gallery | 790900031 |  | 0 |  |  |  | ABS Suction Pipe Discharge, Piping |  | 2006 | 0 |  |  | East |  |  |  |  | W-WW |  | 4
2278 |  |  | PD6 |  |  |  | AC | 00019045 | Valve Gallery Access Door (Single) | Markham N PD6 RES Valve Gallery | 00025384 | DSC00651 | 3500 | good |  |  | Access, Door, Interior Single Metal With Window |  | 2006 | 0 |  |  | East |  |  |  |  | W-WW |  | 1
2279 |  |  | PD6 |  |  |  | BM | 00019057 | Exhaust Fan, EF-1 | Markham N PD6 RES Valve Gallery | 790900031 | IMG_1898 | 6000 | good |  |  | Ducting, Ventilation System, Exhaust Fan EF-1, 120VAC/1ph, in-line centrifugal, powered from LP-A |  | 2006 | 10 |  |  | East |  |  |  |  | W-WW |  | 2
2280 |  |  | PD6 |  |  |  | HSS | 00077844 |  | Stouffville PD6 Reservoir | 790900031 |  | 0 |  |  |  | Health and Safety Compliance Systems, Spill Containment, Chemical Spill Kit | 2025-01-16 | 2016 | 0 |  |  | East |  |  |  |  | W-WW |  | 3 | [6 empty] | M10095 | Health and Safety
2281 |  |  | PD6 |  |  |  | SIC | 00086196 | Flow Transmitter | Markham N PD6 RES MCC Level | 00025383 | IMG_2272 | 5000 | good |  |  | MKRSMR_RES_FIT1, Cell 1 Inlet/Outlet Line Clamp On Flow Transmitter, Flow Meter, Flow; Endress + Hausser; PROSONIC FLOW 93; P50AFC02000; 18VA, NEMA 4X;1 | 2013-09-19 | 2019 | 15 |  |  | East |  | P50AFC02000 |  |  | W-WW |  | 3 | [6 empty] | M00405 | Instrumentation and Control
2282 |  |  | PD6 |  |  |  | SIC | 00086261 |  | Markham N PD6 RES MCC Level | 00025383 | IMG_2288 | 0 | good |  |  | MKRSMR Advantech Monitor, OIT, Monitor, PAC Panel | 2027-08-19 | 2019 | 14 |  |  | East |  | KSA1976795 |  |  | W-WW |  | 2 | [6 empty] | M10189 | Instrumentation and Control
2283 |  |  | PD6 |  |  |  | SIC | 00086260 | MKRSMR Control Panel | Markham N PD6 RES MCC Level | 00025383 | IMG_2286 | 100000 | good |  |  | MKRSMR PAC Panel, Control Panel, PAC Panel, Indoor; Summa; SIRSMR_PAC; 14E-088¦SIRSMR_PAC; 120V, 12A, Type 12; 1 | 2027-08-19 | 2019 | 15 |  |  | East |  | 14E-088/MKRSMR_PAC |  |  | W-WW |  | 3 | [6 empty] | M00844 | Instrumentation and Control
2284 |  |  | PD6 |  |  |  | SIC | 00086263 |  | Markham N PD6 RES MCC Level | 00025383 |  | 4000 | good |  |  | MKRSMR UPS, Uninterruptible Power Supply, PAC Tower UPS | 2027-08-19 | 2019 | 14 |  |  | East |  | PC23K09B33 |  |  | W-WW |  | 2 | [6 empty] | M10181 | Instrumentation and Control
2285 |  |  | PD6 |  |  |  | SIC | 00086197 | Flow Meter | Markham N PD6 RES MCC Level | 00025383 | IMG_2276 | 5000 | good |  |  | MKRSMR_RES_FIT2, Cell 2 Inlet/Outlet Line clamp on Flow Transmitter, Flow Meter, Flow; Endress + Hausser; PROSONIC FLOW 93; P50AFC02000; 18VA, NEMA 4X;1 | 2013-09-19 | 2019 | 14 |  |  | East |  | P50AFD02000 |  |  | W-WW |  | 3 | [6 empty] | M00405 | Instrumentation and Control
2286 |  |  | PD6 |  |  |  | SIC | 00086265 | Building Thermostat | Markham N PD6 RES MCC Level | 00025383 | IMG_2280 | 1500 | good |  |  | MKVCSA_BLDS_TSH1, MCC Level High Temperature Switch, Temperature Switch, Temperature; Honeywell; | 2023-08-19 | 2019 | 15 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00076 | Instrumentation and Control
2287 |  |  | PD6 |  |  |  | SIC | 00086264 | Building Thermostat | Markham N PD6 RES MCC Level | 00025383 | IMG_2283 | 500 | good |  |  | MKVCSA_BLDS_TSL1, MCC Level Low Temperature Switch, Temperature Switch, Temperature; Honeywell | 2023-08-19 | 2019 | 15 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00076 | Instrumentation and Control
2288 |  |  | PD6 |  |  |  | SIC | 00086268 | Valve Gallery Temp Switch | Markham N PD6 RES Valve Gallery | 00025384 | IMG_2396 | 1500 | good |  |  | MKRSMR_BLDS_TSH2, Valve Gallery High Temperature Switch, Temperature Switch, Temperature; Honeywell | 2023-08-19 | 2019 | 15 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00076 | Instrumentation and Control
2289 |  |  | PD6 |  |  |  | SIC | 00086267 | Valve Gallery Low Temp Switch | Markham N PD6 RES Valve Gallery | 00025384 | IMG_2397 | 1500 | good |  |  | MKRSMR_BLDS_TSL2, Valve Gallery Low Temperature Switch, Temperature Switch, Temperature; Honeywell | 2023-08-19 | 2019 | 15 |  |  | East |  |  |  |  | W-WW |  | 2 | [6 empty] | M00076 | Instrumentation and Control