## Sheet1
seqNum | Unnamed: 0 | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16 | Unnamed: 17 | Unnamed: 18 | Unnamed: 19 | Unnamed: 20 | assetTag | facility | Description | Process | building | inspectorName | CategoryCode | installYear | assetName | manufacturer | TransmitterModel | TransducerModel | TransducerSerial | InstMeva | installationDate | remainingESL | InstType | ServiceArea | FacilityType | LifeCycleCategory | SerialNo | Parent | RotatingItem | Status | Site | condition | COF | defect1 | defect2 | defect3 | observations | RehabRepairCost | RehabRepairYear | RehabRepairCost2 | RehabRepairYear2 | repCost | photoName | repProjectName | rehabProjectName | rehab2ProjectName | InspectionYear | rehabComment1 | rehabCost1 | rehabComment2 | rehabCost2 | defect1Input | defect2Input | defect3Input
5709 | [21 empty] | 00040849 | RHB | Cook Gemeni model GN-620: 1/3HP, 120V, 1p, 950rpm |  |  |  | BM | 2008 | Chemical Room Exhaust Fan | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2500 | IMG_3988 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5710 | [21 empty] | 00040848 | RHB | Ceiling-mounted unit heater: Chromalox Model EUH. 5kW/600V/3p |  |  |  | BM | 2008 | Chemical Room Electric Heater | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2500 | IMG_3982 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5711 | [21 empty] | 00022644 | RHB | Diameter: 63mm, Watts Model 909 |  |  |  | BM | 2008 | Drain Line Reduced Pressure Principle Backflow Preventer | [6 empty] | 17 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 3500 | IMG_4127 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5712 | [21 empty] | 00040842 | RHB | Cook Gemeni model GN-620: 1/3HP, 120V, 1p, 950rpm |  |  |  | BM | 2008 | Electrical Room Exhaust Fan | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2500 | IMG_3959 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5713 | [21 empty] | 00040843 | RHB | Ceiling-mounted unit heater by Ouellet. 5kW/600V/3p |  |  |  | BM | 2008 | Electrical Room Electrical Heater | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2500 | IMG_3952 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5714 | [21 empty] | 00086557 | RHB | Portable dehumidifier by Comfort Aire |  |  |  | BM | 2008 | Dehumidifier | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2000 | IMG_3983 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5715 | [21 empty] | 00022645 | RHB | Diameter: 25mm, Watts Model 007QT |  |  |  | BM | 2008 | Potable Cold Water Line Double Check Valve Backflow Preventer | [6 empty] | 17 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2000 | IMG_4095 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5716 | [21 empty] | 00022646 | RHB | Diameter: 50mm, Watts Model 909 |  |  |  | BM | 2008 | Potable Cold Water Line Reduced Pressure Principle Backflow Preventer | [6 empty] | 17 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2000 | IMG_4085 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5717 | [21 empty] | 00040829 | RHB | Cook Gemeni model GN-860: 1/2HP, 120V, 1p, 1050rpm |  |  |  | BM | 2008 | Valve Room Exhaust Fan | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2500 | IMG_4167 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5718 | [21 empty] | 00040823 | RHB | Ceiling-mounted unit heater: Chromalox Model EUH. 7.5kW/600V/3p |  |  |  | BM | 2008 | Valve Room Electric Heater 2 | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2500 | IMG_4152 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5719 | [21 empty] | 00040824 | RHB | Ceiling-mounted unit heater: Chromalox Model EUH. 7.5kW/600V/3p |  |  |  | BM | 2008 | Valve Room Electric Heater 1 | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2500 | IMG_113057 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5720 | [21 empty] | 00040860 | RHB | Eemax model EX1608TC-CNL: 16.8kW, 240VAC |  |  |  | BM | 2008 | Washroom Tankless Water Heater | [6 empty] | 17 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 3000 | IMG_4005 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5721 | [21 empty] | 00018658 | RHB | Cook Gemeni model GN-140: 1/6HP, 120V, 1p, 1500rpm |  |  |  | BM | 2008 | Washroom Exhaust Fan | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2500 | IMG_3947 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5722 | [21 empty] | 00040866 | RHB | Wall-mounted heater by Dimplex: 1.5kW/208V/1p |  |  |  | BM | 2008 | Washroom Electric Heater | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2500 | IMG_3940 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5723 | [21 empty] | 00086555 | RHB | Control,UPS,Rack,Extended Battery Module,1500VA |  |  |  | SIC | 2008 | RPU Panel UPS | [6 empty] | 8 | [9 empty] | 3 | 2 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 3000 | PXL_20211116_141808533 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0
5724 | [21 empty] | 00040838 | RHB | 600V, 200A, 36CCT |  |  |  | ES | 2008 | Distribution Panel DPA | [6 empty] | 12 | [9 empty] | 3 | 2 | Missing was observed arc flash label. |  |  | The asset was observed to be in fair condition.Install arc flash label Asset to be replaced in the long term. | 500 |  | 0 |  | 12000 | PXL_20211116_140908092 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 | Install arc flash label | 500 |  | 0 | missing arc flash label
5725 | [21 empty] | 00040837 | RHB | 120/208V, 200A, 60CCT |  |  |  | ES | 2008 | Lighting Panel LPA | [6 empty] | 12 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 12000 | PXL_20211116_140743801 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
5726 | [21 empty] | 00087415 | RHB |  |  |  |  | ES | 2008 | Generator Transfer Panel | [6 empty] | 12 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 4000 | PXL_20211116_141739155 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
5727 | [21 empty] | 00040841 | RHB | 600V-208V, 45kVA |  |  |  | ES | 2008 | Transformer | [6 empty] | 12 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 8000 | PXL_20211116_140728211 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
5728 | [21 empty] | 00077745 | RHB |  |  |  |  | ES | 2017 | Portable Generator | [6 empty] | 21 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 7000 | PXL_20211116_141707164 |  |  |  | 0 |  | 0 |  | 0 | good
5729 | [21 empty] | 00040827 | RHB |  |  |  |  | ES | 2008 | Heat Tracing Panel #1 | [6 empty] | 12 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 5000 | PXL_20211116_135842916 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
5730 | [21 empty] | 00040828 | RHB |  |  |  |  | ES | 2008 | Heat Tracing Panel #2 | [6 empty] | 12 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 5000 | PXL_20211116_135847213 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
5732 | [21 empty] | 00040853 | RHB | Health and Safety,Emergency Eye Wash Station,Plumbed |  |  |  | HSS | 2008 | Emergency Eye Wash Station | [6 empty] | 8 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 2000 | img_3970 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
5736 | [21 empty] | 00040814 | RHB | Diameter: 75mm, Val-matic Swing Flex Model No. 503A |  |  |  | PM | 2008 | Circulation Line Check Valve | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 3000 | IMG_4125 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5737 | [21 empty] | 00040813 | RHB | Diameter: 75mm |  |  |  | PM | 2008 | Circulation Line Gate Valve | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2000 | IMG_4123 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5738 | [21 empty] | 00040818 | RHB | Diameter: 100mm |  |  |  | PM | 2008 | Circulation Line Gate Valve | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2000 | IMG_4028 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5739 | [21 empty] | 00040815 | RHB | Goulds G&L Series SSH, Imp. diameter: 6.375", 2HP, 575-3-60 motor supply |  |  |  | PM | 2008 | Circulation Line Centrifugal Circulation Pump | [6 empty] | 17 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 8000 | IMG_104552 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5740 | [21 empty] | 00040822 | RHB | Diameter: 200mm, Mueller Model |  |  |  | PM | 2008 | Tank Overflow Drain Line Gate Valve | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 3000 | IMG_4038 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5741 | [21 empty] | 00040812 | RHB | Diameter: 450mm |  |  |  | PM | 2008 | Tank Inlet Line Butterfly Valve | [6 empty] | 17 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 8000 | IMG_4119 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5742 | [21 empty] | 00040811 | RHB | Diameter: 450mm, Val-matic Swing Flex Model No. 518A |  |  |  | PM | 2008 | Tank Inlet Line Check Valve | [6 empty] | 17 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 7500 | IMG_4112 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5743 | [21 empty] | 00040809 | RHB | Diameter: 300mm, Cla-Val Model |  |  |  | PM | 2008 | Inlet/Outlet Line Altitude Valve | [6 empty] | 17 | [9 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 20000 | IMG_4100 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5744 | [21 empty] | 00040803 | RHB | Diameter: 50mm |  |  |  | PM | 2008 | Inlet/Outlet Line Air Release Valve | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2500 | IMG_4051 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5745 | [21 empty] | 00040810 | RHB | Diameter: 300mm |  |  |  | PM | 2008 | Inlet/Outlet Line Butterfly Valve | [6 empty] | 17 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 5000 | IMG_4108 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5746 | [21 empty] | 00040806 | RHB | Limitorque electric actuator, 1140rpm motor, 575-3-60 motor supply |  |  |  | PM | 2008 | Inlet/Outlet Line Electric Actuator | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 5000 | IMG_4060 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5747 | [21 empty] | 00040807 | RHB | Diameter: 300mm, DeZurik Model |  |  |  | PM | 2008 | Inlet/Outlet Line Butterfly Valve | [6 empty] | 17 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 5000 | IMG_4061 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5748 | [21 empty] | 00040808 | RHB | Diameter: 300mm, Cla-Val solenoid control valve |  |  |  | PM | 2008 | Inlet/Outlet Line Control Valve | [6 empty] | 17 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 8000 | IMG_4072 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5749 | [21 empty] | 00040821 | RHB | Diameter: 450mm |  |  |  | PM | 2008 | Tank Outlet Line Butterfly Valve | [6 empty] | 17 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 5000 | IMG_4035 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5750 | [21 empty] | 00040820 | RHB | Diameter: 450mm |  |  |  | PM | 2008 | Tank Outlet Line Butterfly Valve | [6 empty] | 17 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 5000 | IMG_113324 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5751 | [21 empty] | 00040819 | RHB | Diameter: 450mm, Val-matic Swing Flex Model No. 518A |  |  |  | PM | 2008 | Tank Outlet Line Check Valve | [6 empty] | 17 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 7500 | IMG_4020 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5752 | [21 empty] | 00040804 | RHB | Diameter: 100mm |  |  |  | PM | 2008 | Pressure Relief Line Gate Valve | [6 empty] | 17 | [9 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2000 | IMG_4056 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5753 | [21 empty] | 00086560 | RHB |  |  |  |  | SIC | 2008 | Chemical Room Sump Level Switch | [6 empty] | 8 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 1000 | IMG_3999 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
5754 | [21 empty] | 00040850 | RHB |  |  |  |  | SIC | 2008 | Chemical Room Low Temperature Switch | [6 empty] | 8 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 800 | PXL_20211116_141930615 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
5755 | [21 empty] | 00040847 | RHB | Instrumentation,Switch,Temperature,Low |  |  |  | SIC | 2008 | Electrical and SCADA Room Low Temperature Switch | [6 empty] | 8 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 800 | PXL_20211116_141621691 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
5756 | [21 empty] | 00085391 | RHB |  |  |  |  | SIC | 2018 | RPU Panel | [6 empty] | 12 | [9 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 95000 | PXL_20211116_141808533 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5757 | [21 empty] | 00085392 | RHB |  |  |  |  | SIC | 2018 | Network Access Closet | [6 empty] | 12 | [9 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 18000 | PXL_20211116_141645777 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5758 | [21 empty] | 00085396 | RHB | Switch,3000,Layer 3 |  |  |  | SIC | 2018 | Network Switch | [6 empty] | 12 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2000 | PXL_20211116_141645777 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
5759 | [21 empty] | 00086561 | RHB | 5gHz,PTP500 |  |  |  | SIC | 2018 | Wide Area Network Radio | [6 empty] | 12 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2000 | PXL_20211116_141645777 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
5760 | [21 empty] | 00086563 | RHB | 900mHz,iNET |  |  |  | SIC | 2018 | Wide Area Network Radio | [6 empty] | 12 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2000 | PXL_20211116_141645777 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
5761 | [21 empty] | 00086562 | RHB | 900mHz,iNET |  |  |  | SIC | 2018 | Wide Area Network Radio | [6 empty] | 12 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2000 | PXL_20211116_141645777 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
5762 | [21 empty] | 00040852 | RHB | Instrumentation,Switch,Flow,High |  |  |  | SIC | 2008 | Eyewash Flow Switch | [6 empty] | 8 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 800 | PXL_20211116_141926309 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
5763 | [21 empty] | 00045567 | RHB | Instrumentation,Transmitters,Position |  |  |  | SIC | 2008 | Position Transmitter | [6 empty] | 8 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 1500 | PXL_20211116_140049452 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
5764 | [21 empty] | 00040833 | RHB | Instrumentation,Analysers,Chlorine,Total Chlorine,CL17 |  |  |  | SIC | 2008 | Inlet Total Chlorine Residual Analyser | [6 empty] | 8 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 28000 | PXL_20211116_135944275 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
5765 | [21 empty] | 00085393 | RHB | Instrumentation,Flow Meter,Electromagnetic,Non-Revenue Water |  |  |  | SIC | 2018 | Flow Transmitter | [6 empty] | 12 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 6000 | PXL_20211116_135920183 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5766 | [21 empty] | 00086556 | RHB | Instrumentation,Sensing Elements,Flow |  |  |  | SIC | 2018 | Flow Sensor | [6 empty] | 12 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 5000 | PXL_20211116_140209541 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5767 | [21 empty] | 00040833 | RHB | Instrumentation,Analysers,Chlorine,Total Chlorine,CL17 |  |  |  | SIC | 2008 | Outlet Total Chlorine Residual Analyser | [6 empty] | 8 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 28000 | PXL_20211116_135937133 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
5769 | [21 empty] | 00085394 | RHB | Instrumentation,Transmitters,Pressure,Gauge |  |  |  | SIC | 2018 | System Pressure Transmitter | [6 empty] | 12 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 3000 | PXL_20211116_140106684 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5770 | [21 empty] | 00085395 | RHB |  |  |  |  | SIC | 2018 | Pressure Gauge | [6 empty] | 12 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 700 | PXL_20211116_140526499 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5771 | [21 empty] | 00040826 | RHB |  |  |  |  | SIC | 2008 | Valve Room Low Temperature Switch | [6 empty] | 8 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 800 | PXL_20211116_135758462 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
5772 | [21 empty] | 00085351 | RHB |  |  |  |  | SIC | 2018 | OIT Monitor | [6 empty] | 12 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 10000 | PXL_20211116_135815110 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5773 | [21 empty] | 00085352 | RHB | Computer,OIT,CPU,2184 |  |  |  | SIC | 2018 | OIT Computer | [6 empty] | 12 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 3000 | PXL_20211116_135815110 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
5774 | [22 empty] | RHB |  |  |  |  | AC | 2008 | Atrium Access Door (Double) | [6 empty] | 8 | [9 empty] | 3 | 1 | Weathered paint was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 5500 | IMG_9857 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Weathered paint
5775 | [22 empty] | RHB |  |  |  |  | AC | 2008 | Valve Room Access Door (Double) | [6 empty] | 8 | [9 empty] | 2 | 1 |  | Broken glass on one door was observed. |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 5500 | IMG_9875 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good | broken glass on one door
5776 | [22 empty] | RHB |  |  |  |  | AC | 2008 | Chemical Room Interior Access Door (Single) | [6 empty] | 8 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 3500 | IMG_9863 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
5777 | [22 empty] | RHB |  |  |  |  | AC | 2008 | Chemical Room Exterior Access Door (Single) | [6 empty] | 8 | [9 empty] | 3 | 1 | Weathered exterior paint was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 3500 | IMG_9864 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | weathered exterior paint
5778 | [22 empty] | RHB |  |  |  |  | AC | 2008 | Washroom Access Door (Single) | [6 empty] | 8 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 3500 | IMG_9859 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
5779 | [22 empty] | RHB |  |  |  |  | AC | 2008 | Electrical and SCADA Room Access Door (Single) | [6 empty] | 8 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 3500 | IMG_9879 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
5780 | [22 empty] | RHB |  |  |  |  | AC | 2008 | Electrical and SCADA Room Floor Coating | [6 empty] | 8 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 12000 | IMG_9880 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
5781 | [22 empty] | RHB |  |  |  |  | AC | 2008 | Electrical and SCADA Room Wall Paint | [6 empty] | 8 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 1200 | IMG_9881 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
5782 | [22 empty] | RHB |  |  |  |  | AC | 2008 | Valve Room Wall Paint | [6 empty] | 8 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 3000 | IMG_9876 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
5783 | [22 empty] | RHB |  |  |  |  | AC | 2008 | Valve Room Floor Coating | [6 empty] | 8 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 40000 | IMG_9876 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
5784 | [22 empty] | RHB |  |  |  |  | AC | 2008 | Chemical Room Floor Coating | [6 empty] | 8 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 10000 | IMG_9864 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
5785 | [22 empty] | RHB |  |  |  |  | AC | 2008 | Chemical Room Wall Paint | [6 empty] | 8 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 1200 | IMG_9864 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
5786 | [22 empty] | RHB |  |  |  |  | AC | 2008 | Washroom Wall Paint | [6 empty] | 8 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 800 | IMG_9861 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
5787 | [22 empty] | RHB |  |  |  |  | AC | 2008 | Washroom Floor Coating | [6 empty] | 8 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 2200 | IMG_9860 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
5788 | [22 empty] | RHB |  |  |  |  | AC | 2008 | Atrium Floor Coating | [6 empty] | 8 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 16000 | IMG_9886 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
5789 | [22 empty] | RHB |  |  |  |  | AC | 2008 | Atrium Wall Paint | [6 empty] | 8 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 1500 | IMG_9886 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
5790 | [22 empty] | RHB |  |  |  |  | AC | 2008 | Chemical Room Window | [6 empty] | 8 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 3000 | IMG_9871 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
5791 | [22 empty] | RHB |  |  |  |  | SC | 2008 | Elevated Tank Concrete Foundation | [6 empty] | 47 | [9 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 0 | 2031 | 0 |  | 600000 |  |  | North Richmond Hill Bloomington Road West ET Capital Project 1 |  | 0 |  | 0 |  | 0 | Good
5792 | [22 empty] | RHB |  |  |  |  | SC | 2008 | Elevated Tank Concrete Pedestal | [6 empty] | 47 | [9 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 0 | 2031 | 0 |  | 1100000 | IMG_9851 |  | North Richmond Hill Bloomington Road West ET Capital Project 1 |  | 0 |  | 0 |  | 0 | Good
5793 | [22 empty] | RHB |  |  |  |  | SC | 2008 | Chemical Room Concrete Blockwalls | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 0 | 2031 | 0 |  | 20000 | IMG_9864 |  | North Richmond Hill Bloomington Road West ET Capital Project 1 |  | 0 |  | 0 |  | 0 | Good
5794 | [22 empty] | RHB |  |  |  |  | SC | 2008 | Chemical Room Concrete Floor Slab | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 0 | 2031 | 0 |  | 15000 | IMG_9864 |  | North Richmond Hill Bloomington Road West ET Capital Project 1 |  | 0 |  | 0 |  | 0 | Good
5795 | [22 empty] | RHB |  |  |  |  | SC | 2008 | Chemical Room Composite Roof Slab | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 12000 | IMG_9864 |  |  |  | 0 |  | 0 |  | 0 | Good
5796 | [22 empty] | RHB |  |  |  |  | SC | 2008 | Electrical and SCADA Room Composite Roof Slab | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 15000 | IMG_9881 |  |  |  | 0 |  | 0 |  | 0 | Good
5797 | [22 empty] | RHB |  |  |  |  | SC | 2008 | Electrical and SCADA Room Concrete Floor Slab | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 0 | 2031 | 0 |  | 18000 | IMG_9880 |  | North Richmond Hill Bloomington Road West ET Capital Project 1 |  | 0 |  | 0 |  | 0 | Good
5798 | [22 empty] | RHB |  |  |  |  | SC | 2008 | Electrical and SCADA Room Concrete Blockwalls | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 0 | 2031 | 0 |  | 20000 | IMG_9881 |  | North Richmond Hill Bloomington Road West ET Capital Project 1 |  | 0 |  | 0 |  | 0 | Good
5799 | [22 empty] | RHB |  |  |  |  | SC | 2008 | Valve Room Concrete Blockwalls | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 0 | 2031 | 0 |  | 45000 | IMG_9877 |  | North Richmond Hill Bloomington Road West ET Capital Project 1 |  | 0 |  | 0 |  | 0 | Good
5800 | [22 empty] | RHB |  |  |  |  | SC | 2008 | Valve Room Concrete Floor Slab | [6 empty] | 47 | [9 empty] | 2 | 3 | Minor hairline cracking was observed. |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 0 | 2031 | 0 |  | 65000 | IMG_9877 |  | North Richmond Hill Bloomington Road West ET Capital Project 1 |  | 0 |  | 0 |  | 0 | Minor hairline cracking
5801 | [22 empty] | RHB |  |  |  |  | SC | 2008 | Valve Room Composite Roof Slab | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 55000 | IMG_9877 |  |  |  | 0 |  | 0 |  | 0 | Good
5802 | [22 empty] | RHB |  |  |  |  | SC | 2008 | Washroom Composite Roof Slab | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 3000 | IMG_9861 |  |  |  | 0 |  | 0 |  | 0 | Good
5803 | [22 empty] | RHB |  |  |  |  | SC | 2008 | Washroom Concrete Blockwalls | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 0 | 2031 | 0 |  | 10000 | IMG_9861 |  | North Richmond Hill Bloomington Road West ET Capital Project 1 |  | 0 |  | 0 |  | 0 | Good
5804 | [22 empty] | RHB |  |  |  |  | SC | 2008 | Washroom Concrete Floor Slab | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 0 | 2031 | 0 |  | 3500 | IMG_9860 |  | North Richmond Hill Bloomington Road West ET Capital Project 1 |  | 0 |  | 0 |  | 0 | Good
5805 | [22 empty] | RHB | ground to platform |  |  |  | SC | 2008 | Elevated Tank Ladder (Base to Platform) | [6 empty] | 47 | [9 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 20000 | IMG_9888 |  |  |  | 0 |  | 0 |  | 0 | Good
5806 | [22 empty] | RHB | platform to u/s tank |  |  |  | SC | 2008 | Elevated Tank Ladder (Platform to U/S Tank) | [6 empty] | 47 | [9 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 3000 | IMG_9921 |  |  |  | 0 |  | 0 |  | 0 | Good
5807 | [22 empty] | RHB | platform to tank exterior |  |  |  | SC | 2008 | Elevated Tank Ladder (Platform to Roof) | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 8000 | IMG_9941 |  |  |  | 0 |  | 0 |  | 0 | Good
5808 | [22 empty] | RHB |  |  |  |  | SC | 2008 | Chemical Room FRP Grating | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 2500 | IMG_9864 |  |  |  | 0 |  | 0 |  | 0 | Good
5809 | [22 empty] | RHB |  |  |  |  | SC | 2008 | Atrium Aluminum Staircase | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 15000 | IMG_9886 |  |  |  | 0 |  | 0 |  | 0 | Good
5810 | [22 empty] | RHB |  |  |  |  | SC | 2008 | Atrium Aluminum Guardrail | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 10000 | IMG_9901 |  |  |  | 0 |  | 0 |  | 0 | Good
5811 | [22 empty] | RHB |  |  |  |  | SC | 2008 | Elevated Tank Platform | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 50000 | IMG_9891 |  |  |  | 0 |  | 0 |  | 0 | Good
5812 | [22 empty] | RHB | platform |  |  |  | HSS | 2008 | Elevated Tank Davit Arm Base 1 | [6 empty] | 8 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 5000 | IMG_9948 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
5813 | [22 empty] | RHB |  |  |  |  | HSS | 2008 | Platform Level Anchor Point | [6 empty] | 8 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 2000 | IMG_9923 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
5814 | [22 empty] | RHB |  |  |  |  | HSS | 2008 | Roof Anchor Point 1 | [6 empty] | 8 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 2000 | IMG_9939 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
5815 | [22 empty] | RHB |  |  |  |  | HSS | 2008 | Roof Anchor Point 2 | [6 empty] | 8 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 2000 | IMG_9940 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
5816 | [22 empty] | RHB |  |  |  |  | HSS | 2008 | Roof Anchor Point 3 | [6 empty] | 8 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 2000 | IMG_9940 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
5817 | [22 empty] | RHB | roof |  |  |  | HSS | 2008 | Elevated Tank Davit Arm Base 2 | [6 empty] | 8 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 5000 | IMG_9940 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
5818 | [22 empty] | RHB | roof |  |  |  | SC | 2008 | Elevated Tank Roof Hatch 1 | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 5000 | IMG_9940 |  |  |  | 0 |  | 0 |  | 0 | Good
5819 | [22 empty] | RHB | roof |  |  |  | SC | 2008 | Elevated Tank Roof Hatch 2 | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 5000 | IMG_9939 |  |  |  | 0 |  | 0 |  | 0 | Good
5820 | [22 empty] | RHB | roof |  |  |  | SC | 2008 | Elevated Tank Roof Hatch/Vent | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 5000 | IMG_9938 |  |  |  | 0 |  | 0 |  | 0 | Good
5821 | [22 empty] | RHB | roof |  |  |  | SC | 2008 | Elevated Tank Guardrail | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 40000 | IMG_9927 |  |  |  | 0 |  | 0 |  | 0 | Good
5822 | [22 empty] | RHB |  |  |  |  | SC | 2008 | Elevated Tank Steel Tank | [6 empty] | 47 | [9 empty] | 3 | 5 | Minor corrosion was observed at areas. |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 2500000 | IMG_9850 |  |  |  | 0 |  | 0 |  | 0 | minor corrosion at areas
5823 | [22 empty] | RHB |  |  |  |  | SC | 2008 | Elevated Tank Interior Coating | [6 empty] | 47 | [9 empty] | 3 | 3 |  |  |  | The asset was assumed to be in fair condition.overcoating Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 660000 |  |  |  |  | 0 | overcoating | 0 |  | 0
5824 | [22 empty] | RHB |  |  |  |  | SC | 2008 | Elevated Tank Exterior Coating | [6 empty] | 47 | [9 empty] | 3 | 3 | Localized areas of peeled/missing coating was observed. |  |  | The asset was observed to be in fair condition.overcoating Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 1140000 | IMG_9850 |  |  |  | 0 | overcoating | 0 |  | 0 | localized areas of peeled/missing coating
5828 | [22 empty] | RHB |  |  |  |  | SW | 2008 | Dechlorination Chamber Concrete Structure | [6 empty] | 7 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 10000 | IMG_9914 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
5829 | [22 empty] | RHB |  |  |  |  | SW | 2008 | Dechlorination Chamber Access Ladder | [6 empty] | 7 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 1500 | IMG_9914 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
5830 | [22 empty] | RHB |  |  |  |  | SW | 2008 | Dechlorination Chamber Manhole Frame and Cover | [6 empty] | 7 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 3000 | IMG_9913 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
5831 | [22 empty] | RHB |  |  |  |  | SW | 2008 | Sanitary Chamber Manhole Frame and Cover | [6 empty] | 7 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 3000 | IMG_9915 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
5832 | [22 empty] | RHB | 1800mm diameter maintenance hole, approx. 2.5m depth. Includes 450mm gate valve, 50mm sampling port and thrust block (with flange) |  |  |  | SW | 2008 | Sanitary Chamber Concrete Structure | [6 empty] | 7 | [9 empty] | 3 | 3 | Cracks was observed in moduloc. |  |  | The asset was observed to be in fair condition.Remove and replace moduloc. Asset to be replaced in the intermediate term. | 3000 |  | 0 |  | 55000 | IMG_9917 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 | Remove and replace moduloc. | 3000 |  | 0 | Cracks in moduloc
5833 | [22 empty] | RHB |  |  |  |  | SW | 2008 | Sanitary Chamber Access Ladder | [6 empty] | 7 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 10000 | IMG_9917 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
5834 | [22 empty] | RHB | 1200mm maintenance hole, approx 1.5m deep. Includes 450mm eccentric slip on checkvalve |  |  |  | SW | 2008 | Overflow Chamber Concrete Structure | [6 empty] | 7 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 20000 | IMG_9911 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
5835 | [22 empty] | RHB |  |  |  |  | SW | 2008 | Overflow Chamber Access Ladder | [6 empty] | 7 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 1500 | IMG_9911 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
5836 | [22 empty] | RHB |  |  |  |  | SW | 2008 | Overflow Chamber Manhole Frame and Cover | [6 empty] | 7 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 3000 | IMG_9910 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
5837 | [22 empty] | RHB |  |  |  |  | SW | 2008 | Sanitary Chamber Access Platform | [6 empty] | 7 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 3000 | IMG_9917 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
5838 | [22 empty] | RHB | tank underside |  |  |  | SC | 2008 | Elevated Tank Tank Hatch | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 5000 | IMG_9922 |  |  |  | 0 |  | 0 |  | 0 | Good
5839 | [22 empty] | RHB | tank underside |  |  |  | SC | 2008 | Atrium Concrete Blockwall | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 0 | 2031 | 0 |  | 20000 | IMG_9886 |  | North Richmond Hill Bloomington Road West ET Capital Project 1 |  | 0 |  | 0 |  | 0 | Good
5840 | [22 empty] | RHB | roof |  |  |  | SC | 2008 | Elevated Tank Antenna Structure | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 30000 | IMG_9945 |  |  |  | 0 |  | 0 |  | 0 | Good
5937 | [22 empty] | RHB |  |  |  |  | HSS | 2008 | Chemical Room Smoke Detector | [6 empty] | 8 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 1000 | PXL_20211116_141906956 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
5938 | [22 empty] | RHB |  |  |  |  | HSS | 2008 | Electrical and SCADA Room Smoke Detector | [6 empty] | 8 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 1000 | PXL_20211116_140710468 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
5940 | [22 empty] | RHB | Antennas (x9) |  |  |  | SIC | 2008 | Antennas | [6 empty] | 8 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 90000 | IMG_9943 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
5941 | [22 empty] | RHB |  |  |  |  | SIC | 2008 | Yagi Antenna | [6 empty] | 8 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 10000 | IMG_9937 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
5943 | [22 empty] | RHB | 600V, 250kA |  |  |  | ES | 2008 | Surge Protection TVSS | [6 empty] | 12 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 8000 | PXL_20211116_140858856 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
5944 | [22 empty] | RHB | 600V, 200A |  |  |  | ES | 2008 | Main Fused Disconnect Switch | [6 empty] | 12 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 10000 | PXL_20211116_140858856 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
5939 | [22 empty] | RHB |  |  |  |  | HSS | 2008 | Valve Room Smoke Detector | [6 empty] | 8 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 1000 | PXL_20211116_135859101 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
5945 | [22 empty] | RHB | 600V, 30A, fused |  |  |  | ES | 2015 | Non-Fused Disconnect Switch DG1 | [6 empty] | 19 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 1500 | PXL_20211116_141608051 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
5946 | [22 empty] | RHB |  |  |  |  | ES | 2015 | Generation Meter | [6 empty] | 19 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 4000 | PXL_20211116_141612192 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
5947 | [22 empty] | RHB | 600V, 30A |  |  |  | ES | 2015 | Fused Disconnect Switch DG2 | [6 empty] | 19 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2000 | PXL_20211116_141608051 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
5948 | [21 empty] | 00084808 | RHB | 600V, 10kW |  |  |  | ES | 2015 | Solar Power Inverter | [6 empty] | 19 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 15000 | PXL_20211116_142849609 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
5951 | [22 empty] | RHB | 600V, 200A |  |  |  | ES | 2015 | Main Servive Breaker | [6 empty] | 19 | [9 empty] | 3 | 3 | Missing was observed arc flash label. |  |  | The asset was observed to be in fair condition.Install missing arc flash label. Asset to be replaced in the long term. | 500 |  | 0 |  | 10000 | PXL_20211116_142348771 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 | Install missing arc flash label. | 500 |  | 0 | missing arc flash label
5952 | [22 empty] | RHB | 8 linear flurscent, 1 exit, 1 battery |  |  |  | ES | 2008 | Valve Room Lighting | [6 empty] | 12 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition.non-LED fixtures to be replaced with LED type in the next capital project. Asset to be replaced in the long term. | 5000 |  | 0 |  | 11000 | PXL_20211116_135859101 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 | non-LED fixtures to be replaced with LED type in the next capital project. | 5000 |  | 0 | good
5953 | [22 empty] | RHB | 2 linear flurscent, 1 remote head |  |  |  | ES | 2008 | Electrical Room Lighting | [6 empty] | 12 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition.non-LED fixtures to be replaced with LED type in the next capital project. Asset to be replaced in the long term. | 2000 |  | 0 |  | 3000 | PXL_20211116_140709191 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 | non-LED fixtures to be replaced with LED type in the next capital project. | 2000 |  | 0 | good
5955 | [22 empty] | RHB | 16 wallmount, 1 exit, 2 flood light, 4 remote head, 4 linear flurscent |  |  |  | ES | 2008 | Elevated Tank Lighting | [6 empty] | 12 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition.non-LED fixtures to be replaced with LED type in the next capital project. Asset to be replaced in the long term. | 4000 |  | 0 |  | 50000 | PXL_20211116_141906956 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 | non-LED fixtures to be replaced with LED type in the next capital project. | 4000 |  | 0 | good
5956 | [22 empty] | RHB | washroom and floor drains connect to sanitary service. Water service line for washroom. |  |  |  | BM | 2008 | Plumbing and Drainage | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 10000 | IMG_4226 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
5957 | [22 empty] | RHB | 1 toilet and 1 sink |  |  |  | BM | 2008 | Washroom Fixtures | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2000 | IMG_3936 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
5958 | [22 empty] | RHB | Electrical underground duct system and conduit system |  |  |  | ES | 2008 | Electrical Duct System and Conduit System | [6 empty] | 12 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 60000 | IMG_9941 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
5959 | [22 empty] | RHB |  |  |  |  | ES | 2008 | Elevated Tank Lightning Protection System | [6 empty] | 12 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 5000 | IMG_9944 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
5960 | [22 empty] | RHB | Two warning lights, assumed installation year: 2010 |  |  |  | ES | 2008 | Aircraft Obstruction Lights | [6 empty] | 12 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 1000 | IMG_9944 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5961 | [22 empty] | RHB |  |  |  |  | ES | 2008 | Elevated Tank Grounding | [6 empty] | 12 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 10000 | IMG_9901 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
5962 | [22 empty] | RHB |  |  |  |  | ES | 2008 | Elevated Tank Inlet Pipe Heat Tracing | [6 empty] | 12 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 15000 | IMG_4178 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
5949 | [21 empty] | 00084809 | RHB | 3 array, 12 modules each |  |  |  | ES | 2015 | Solar Power Modules | [6 empty] | 19 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 40000 | PXL_20211116_143147485 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
5950 | [22 empty] | RHB |  |  |  |  | ES | 2015 | Hydro Meter | [6 empty] | 19 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 6000 | PXL_20211116_142339795 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
5954 | [22 empty] | RHB | 3 linear flurscent, 1 exit, 1 remote head |  |  |  | ES | 2008 | Chemical Room Lighting | [6 empty] | 12 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition.non-LED fixtures to be replaced with LED type in the next capital project. Asset to be replaced in the long term. | 3000 |  | 0 |  | 5000 | PXL_20211116_141906956 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 | non-LED fixtures to be replaced with LED type in the next capital project. | 3000 |  | 0 | good
5963 | [22 empty] | RHB |  |  |  |  | ES | 2008 | Elevated Tank Outlet Pipe Heat Tracing | [6 empty] | 12 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 15000 | IMG_20211116_113909 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
5964 | [22 empty] | RHB | Diameter: 450mm, length: 50 meters |  |  |  | PM | 2008 | Tank Overflow Drain Line Piping | [6 empty] | 17 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 82000 | IMG_4174 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5965 | [22 empty] | RHB | Diameter: 100mm, length: 15 meters |  |  |  | PM | 2008 | Circulation Line Piping | [6 empty] | 17 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 6000 | IMG_4174 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5966 | [22 empty] | RHB | Diameter: 450mm, length: 20 meters |  |  |  | PM | 2008 | Inlet/Outlet Line Piping | [6 empty] | 17 | [9 empty] | 2 | 5 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 25000 | IMG_4055 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5967 | [22 empty] | RHB | Diameter: 450mm, length: 30 meters |  |  |  | PM | 2008 | Inlet Line Piping | [6 empty] | 17 | [9 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 49000 | IMG_4050 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5968 | [22 empty] | RHB | Diameter: 450mm, length: 25 meters |  |  |  | PM | 2008 | Outlet Line Piping | [6 empty] | 17 | [9 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 41000 | IMG_4158 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5969 | [22 empty] | RHB | Diameter: 450mm |  |  |  | PM | 2008 | Tank Overflow Drain Line Duckbill Valve | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 4000 | IMG_3917 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
5970 | [22 empty] | RHB |  |  |  |  | PM | 2008 | Elevated Tank Frostproof Vent/Vacuum Relief Unit | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 6000 | IMG_9938 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
5971 | [22 empty] | RHB | Approximately 3 in total |  |  |  | HSS | 2007 | Fire Extinguishers | [6 empty] | 7 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 2000 | IMG_3971 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
5972 | [22 empty] | RHB | including valve, gauges, and a pump |  |  |  | PM | 2008 | Recirculation System | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 15000 | IMG_4179 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
5973 | [22 empty] | RHB | security system for the entire ET |  |  |  | SIC | 2008 | Security System | [6 empty] | 8 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 60000 | IMG_4222 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
5974 | [22 empty] | RHB | 9.0m long, 2.4m high chainlink swing gate |  |  |  | SW | 2008 | Swing Gate | [6 empty] | 7 | [9 empty] | 3 | 2 | Paint chipping off was observed. | Minor damage to mesh was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 5000 | IMG_20211116_094340 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Paint chipping off | Minor damage to mesh
5975 | [22 empty] | RHB | 2.4m high chainlink fence along property line (approx. 375m in length) |  |  |  | SW | 2008 | Chainlink fence | [6 empty] | 7 | [9 empty] | 3 | 2 | Paint chipping off fence was observed. | Horizontal fence bar missing or damaged at north side and south-east corners was observed. |  | The asset was observed to be in fair condition.Install new horizontal fence bars at corners Asset to be replaced in the intermediate term. | 1000 |  | 0 |  | 75000 | IMG_20211116_094518 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 | Install new horizontal fence bars at corners | 1000 |  | 0 | Paint chipping off fence | Horizontal fence bar missing or damaged at north side and south-east corners
5976 | [22 empty] | RHB | Pedestrian swing gate located east of vehicle entrance |  |  |  | SW | 2008 | Pedestrian Swing Gate | [6 empty] | 7 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 3000 | IMG_20211116_095248 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
5977 | [22 empty] | RHB | Overflow detention area (dry pond), including emergency overflow overland |  |  |  | SW | 2008 | Overflow Detention Area | [6 empty] | 7 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 25000 | IMG_20211116_100019 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
5978 | [22 empty] | RHB | Overflow outlet, including armtec headwall and riprap |  |  |  | SW | 2008 | Overflow Outlet | [6 empty] | 7 | [9 empty] | 3 | 3 | Minor ponding by outlet was observed. |  |  | The asset was observed to be in fair condition.Remove and replace rip rap around outlet. Asset to be replaced in the intermediate term. | 5000 |  | 0 |  | 15000 | IMG_20211116_100057 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 | Remove and replace rip rap around outlet. | 5000 |  | 0 | Minor ponding by outlet
5979 | [22 empty] | RHB | DICB in dry pond |  |  |  | SW | 2008 | DICB in dry pond | [6 empty] | 7 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 5000 | IMG_20211116_100214 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
5980 | [22 empty] | RHB | 450mm PVC storm sewer, total length 85m (in two sections), approx 2.0m in depth |  |  |  | SW | 2008 | Storm Sewer | [6 empty] | 7 | [9 empty] | 3 | 2 | Not observed was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 90000 |  | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Not observed
5982 | [22 empty] | RHB | 150mm PVC sewer, 27m in length, approx 2.0m in depth |  |  |  | SW | 2008 | Sanitary Sewer | [6 empty] | 7 | [9 empty] | 3 | 3 | Not observed was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 25000 |  | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Not observed
5984 | [22 empty] | RHB | 450mm CPP watermain (C303), approx 65m in length |  |  |  | SW | 2008 | Watermain | [6 empty] | 7 | [9 empty] | 3 | 2 | Not observed was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 130000 |  | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Not observed
5986 | [22 empty] | RHB | Asphalt driveway from entrance to site, and around tank pedestal. Approx area 600m2. Road makeup (based on record drawings) is 40mm HL3, 80mm HL8, 150mm granular A, 400mm granular B. |  |  |  | SW | 2008 | Asphalt driveway | [6 empty] | 7 | [9 empty] | 3 | 2 | Cracks was observed in various areas. | Asphalt settled and damaged adjacent to the tank was observed. | Potential utility cuts not permanently restored was observed. | The asset was observed to be in fair condition.Remove and replace asphalt layers, or full depth reconstruction (dependent on geotechnical investigation). Asset to be replaced in the intermediate term. | 60000 |  | 0 |  | 60000 | IMG_20211116_100720 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 | Remove and replace asphalt layers, or full depth reconstruction (dependent on geotechnical investigation). | 60000 |  | 0 | Cracks in various areas | Asphalt settled and damaged adjacent to the tank | Potential utility cuts not permanently restored
5987 | [22 empty] | RHB | general sod on site |  |  |  | SW | 2008 | Landscaping | [6 empty] | 7 | [9 empty] | 3 | 1 | Damage along driveway was observed. |  |  | The asset was observed to be in fair condition.Regrade areas along driveway, and install new top soil and sod. Alternatively, place gravel shoulder Asset to be replaced in the intermediate term. | 5000 |  | 0 |  | 70000 | IMG_20211116_100418 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 | Regrade areas along driveway, and install new top soil and sod. Alternatively, place gravel shoulder | 5000 |  | 0 | Damage along driveway
5988 | [22 empty] | RHB | Concrete bollards (quantity of 4) |  |  |  | SW | 2008 | Bollards | [6 empty] | 7 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 6000 | IMG_20211116_100635 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good