## Sheet1
assetTag | seqNum | facility | Description | Process | building | inspectorName | CategoryCode | installYear | LocationORIGINAL | LocationTag | assetName | manufacturer | TransmitterModel | TransducerModel | TransducerSerial | InstMeva | installationDate | remainingESL | InstType | ServiceArea | FacilityType | LifeCycleCategory | SerialNo | Parent | RotatingItem | Status | Site | condition | COF | defect1 | defect2 | defect3 | observations | RehabRepairCost | RehabRepairYear | RehabRepairCost2 | RehabRepairYear2 | repCost | photoName | repProjectName | rehabProjectName | rehab2ProjectName | InspectionYear | rehabComment1 | rehabCost1 | rehabComment2 | rehabCost2 | defect1Input | defect2Input | defect3Input
00040849 | 5709 | RHB | Cook Gemeni model GN-620: 1/3HP, 120V, 1p, 950rpm |  |  |  | BM | 2008 | Chemical Room | 1000111 | Chemical Room Exhaust Fan | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2500 | IMG_3988 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00040848 | 5710 | RHB | Ceiling-mounted unit heater: Chromalox Model EUH. 5kW/600V/3p |  |  |  | BM | 2008 | Chemical Room | 1000111 | Chemical Room Electric Heater | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2500 | IMG_3982 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00022644 | 5711 | RHB | Diameter: 63mm, Watts Model 909 |  |  |  | BM | 2008 | Valve Room | 1000112 | Drain Line Reduced Pressure Principle Backflow Preventer | [6 empty] | 17 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 3500 | IMG_4127 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00040842 | 5712 | RHB | Cook Gemeni model GN-620: 1/3HP, 120V, 1p, 950rpm |  |  |  | BM | 2008 | Electrical and SCADA Room | 1000113 | Electrical Room Exhaust Fan | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2500 | IMG_3959 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00040843 | 5713 | RHB | Ceiling-mounted unit heater by Ouellet. 5kW/600V/3p |  |  |  | BM | 2008 | Electrical and SCADA Room | 1000113 | Electrical Room Electrical Heater | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2500 | IMG_3952 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00086557 | 5714 | RHB | Portable dehumidifier by Comfort Aire |  |  |  | BM | 2008 | Valve Room | 1000111 | Dehumidifier | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2000 | IMG_3983 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00022645 | 5715 | RHB | Diameter: 25mm, Watts Model 007QT |  |  |  | BM | 2008 | Valve Room | 1000112 | Potable Cold Water Line Double Check Valve Backflow Preventer | [6 empty] | 17 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2000 | IMG_4095 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00022646 | 5716 | RHB | Diameter: 50mm, Watts Model 909 |  |  |  | BM | 2008 | Valve Room | 1000112 | Potable Cold Water Line Reduced Pressure Principle Backflow Preventer | [6 empty] | 17 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2000 | IMG_4085 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00040829 | 5717 | RHB | Cook Gemeni model GN-860: 1/2HP, 120V, 1p, 1050rpm |  |  |  | BM | 2008 | Valve Room | 1000112 | Valve Room Exhaust Fan | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2500 | IMG_4167 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00040823 | 5718 | RHB | Ceiling-mounted unit heater: Chromalox Model EUH. 7.5kW/600V/3p |  |  |  | BM | 2008 | Valve Room | 1000112 | Valve Room Electric Heater 2 | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2500 | IMG_4152 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00040824 | 5719 | RHB | Ceiling-mounted unit heater: Chromalox Model EUH. 7.5kW/600V/3p |  |  |  | BM | 2008 | Valve Room | 1000112 | Valve Room Electric Heater 1 | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2500 | IMG_113057 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00040860 | 5720 | RHB | Eemax model EX1608TC-CNL: 16.8kW, 240VAC |  |  |  | BM | 2008 | Valve Room | 1000114 | Washroom Tankless Water Heater | [6 empty] | 17 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 3000 | IMG_4005 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00018658 | 5721 | RHB | Cook Gemeni model GN-140: 1/6HP, 120V, 1p, 1500rpm |  |  |  | BM | 2008 | Washroom | 1000114 | Washroom Exhaust Fan | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2500 | IMG_3947 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00040866 | 5722 | RHB | Wall-mounted heater by Dimplex: 1.5kW/208V/1p |  |  |  | BM | 2008 | Washroom | 1000114 | Washroom Electric Heater | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2500 | IMG_3940 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00086555 | 5723 | RHB | Control,UPS,Rack,Extended Battery Module,1500VA |  |  |  | SIC | 2008 | Electrical and SCADA Room | 1000113 | RPU Panel UPS | [6 empty] | 8 | [9 empty] | 3 | 2 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 3000 | PXL_20211116_141808533 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0
00040838 | 5724 | RHB | 600V, 200A, 36CCT |  |  |  | ES | 2008 | Electrical and SCADA Room | 1000113 | Distribution Panel DPA | [6 empty] | 12 | [9 empty] | 3 | 2 | Missing arc flash label. |  |  | The asset was observed to be in fair condition. Install arc flash label Asset to be replaced in the long term. | 500 | 2021 | 0 |  | 12000 | PXL_20211116_140908092 | North Richmond Hill Bloomington Road West ET Capital Project 2 | North Richmond Hill Bloomington Road West ET Immediate Project |  | 0 | Install arc flash label | 500 |  | 0 | missing arc flash label
00040837 | 5725 | RHB | 120/208V, 200A, 60CCT |  |  |  | ES | 2008 | Electrical and SCADA Room | 1000113 | Lighting Panel LPA | [6 empty] | 12 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 12000 | PXL_20211116_140743801 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
00087415 | 5726 | RHB |  |  |  |  | ES | 2008 | Electrical and SCADA Room | 1000113 | Generator Transfer Panel | [6 empty] | 12 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 4000 | PXL_20211116_141739155 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
00040841 | 5727 | RHB | 600V-208V, 45kVA |  |  |  | ES | 2008 | Electrical and SCADA Room | 1000113 | Transformer | [6 empty] | 12 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 8000 | PXL_20211116_140728211 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
00077745 | 5728 | RHB |  |  |  |  | ES | 2017 | Electrical and SCADA Room | 1000113 | Portable Generator | [6 empty] | 21 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 7000 | PXL_20211116_141707164 |  |  |  | 0 |  | 0 |  | 0 | good
00040827 | 5729 | RHB |  |  |  |  | ES | 2008 | Elevated Tank Pedestal | 1000115 | Heat Tracing Panel #1 | [6 empty] | 12 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 5000 | PXL_20211116_135842916 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
00040828 | 5730 | RHB |  |  |  |  | ES | 2008 | Elevated Tank Pedestal | 1000115 | Heat Tracing Panel #2 | [6 empty] | 12 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 5000 | PXL_20211116_135847213 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
00040853 | 5732 | RHB | Health and Safety, Emergency Eye Wash Station, Plumbed |  |  |  | HSS | 2008 | Chemical Room | 1000111 | Emergency Eye Wash Station | [6 empty] | 8 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 2000 | img_3970 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
00040814 | 5736 | RHB | Diameter: 75mm, Val-matic Swing Flex Model No. 503A |  |  |  | PM | 2008 | Valve Room | 1000112 | Circulation Line Check Valve | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 3000 | IMG_4125 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00040813 | 5737 | RHB | Diameter: 75mm |  |  |  | PM | 2008 | Valve Room | 1000112 | Circulation Line Gate Valve | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2000 | IMG_4123 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00040818 | 5738 | RHB | Diameter: 100mm |  |  |  | PM | 2008 | Valve Room | 1000112 | Circulation Line Gate Valve | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2000 | IMG_4028 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00040815 | 5739 | RHB | Goulds G&L Series SSH, Imp. diameter: 6.375", 2HP, 575-3-60 motor supply |  |  |  | PM | 2008 | Valve Room | 1000112 | Circulation Line Centrifugal Circulation Pump | [6 empty] | 17 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 8000 | IMG_104552 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00040822 | 5740 | RHB | Diameter: 200mm, Mueller Model |  |  |  | PM | 2008 | Valve Room | 1000112 | Tank Overflow Drain Line Gate Valve | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 3000 | IMG_4038 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00040812 | 5741 | RHB | Diameter: 450mm |  |  |  | PM | 2008 | Valve Room | 1000112 | Tank Inlet Line Butterfly Valve | [6 empty] | 17 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 8000 | IMG_4119 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00040811 | 5742 | RHB | Diameter: 450mm, Val-matic Swing Flex Model No. 518A |  |  |  | PM | 2008 | Valve Room | 1000112 | Tank Inlet Line Check Valve | [6 empty] | 17 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 7500 | IMG_4112 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00040809 | 5743 | RHB | Diameter: 300mm, Cla-Val Model |  |  |  | PM | 2008 | Valve Room | 1000112 | Inlet/Outlet Line Altitude Valve | [6 empty] | 17 | [9 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 20000 | IMG_4100 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00040803 | 5744 | RHB | Diameter: 50mm |  |  |  | PM | 2008 | Valve Room | 1000112 | Inlet/Outlet Line Air Release Valve | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2500 | IMG_4051 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00040810 | 5745 | RHB | Diameter: 300mm |  |  |  | PM | 2008 | Valve Room | 1000112 | Inlet/Outlet Line Butterfly Valve | [6 empty] | 17 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 5000 | IMG_4108 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00040806 | 5746 | RHB | Limitorque electric actuator, 1140rpm motor, 575-3-60 motor supply |  |  |  | PM | 2008 | Valve Room | 1000112 | Inlet/Outlet Line Electric Actuator | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 5000 | IMG_4060 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00040807 | 5747 | RHB | Diameter: 300mm, DeZurik Model |  |  |  | PM | 2008 | Valve Room | 1000112 | Inlet/Outlet Line Butterfly Valve | [6 empty] | 17 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 5000 | IMG_4061 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00040808 | 5748 | RHB | Diameter: 300mm, Cla-Val solenoid control valve |  |  |  | PM | 2008 | Valve Room | 1000112 | Inlet/Outlet Line Control Valve | [6 empty] | 17 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 8000 | IMG_4072 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00040821 | 5749 | RHB | Diameter: 450mm |  |  |  | PM | 2008 | Valve Room | 1000112 | Tank Outlet Line Butterfly Valve | [6 empty] | 17 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 5000 | IMG_4035 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00040820 | 5750 | RHB | Diameter: 450mm |  |  |  | PM | 2008 | Valve Room | 1000112 | Tank Outlet Line Butterfly Valve | [6 empty] | 17 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 5000 | IMG_113324 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00040819 | 5751 | RHB | Diameter: 450mm, Val-matic Swing Flex Model No. 518A |  |  |  | PM | 2008 | Valve Room | 1000112 | Tank Outlet Line Check Valve | [6 empty] | 17 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 7500 | IMG_4020 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00040804 | 5752 | RHB | Diameter: 100mm |  |  |  | PM | 2008 | Valve Room | 1000112 | Pressure Relief Line Gate Valve | [6 empty] | 17 | [9 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2000 | IMG_4056 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00086560 | 5753 | RHB |  |  |  |  | SIC | 2008 | Chemical Room | 1000111 | Chemical Room Sump Level Switch | [6 empty] | 8 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 1000 | IMG_3999 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
00040850 | 5754 | RHB |  |  |  |  | SIC | 2008 | Chemical Room | 1000111 | Chemical Room Low Temperature Switch | [6 empty] | 8 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 800 | PXL_20211116_141930615 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
00040847 | 5755 | RHB | Instrumentation,Switch,Temperature,Low |  |  |  | SIC | 2008 | Electrical and SCADA Room | 1000113 | Electrical and SCADA Room Low Temperature Switch | [6 empty] | 8 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 800 | PXL_20211116_141621691 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
00085391 | 5756 | RHB |  |  |  |  | SIC | 2018 | Electrical and SCADA Room | 1000113 | RPU Panel | [6 empty] | 12 | [9 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 95000 | PXL_20211116_141808533 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00085392 | 5757 | RHB |  |  |  |  | SIC | 2018 | Electrical and SCADA Room | 1000113 | Network Access Closet | [6 empty] | 12 | [9 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 18000 | PXL_20211116_141645777 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00085396 | 5758 | RHB | Switch,3000,Layer 3 |  |  |  | SIC | 2018 | Electrical and SCADA Room | 1000113 | Network Switch | [6 empty] | 12 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2000 | PXL_20211116_141645777 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
00086561 | 5759 | RHB | 5gHz,PTP500 |  |  |  | SIC | 2018 | Electrical and SCADA Room | 1000113 | Wide Area Network Radio | [6 empty] | 12 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2000 | PXL_20211116_141645777 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
00086563 | 5760 | RHB | 900mHz,iNET |  |  |  | SIC | 2018 | Electrical and SCADA Room | 1000113 | Wide Area Network Radio | [6 empty] | 12 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2000 | PXL_20211116_141645777 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
00086562 | 5761 | RHB | 900mHz,iNET |  |  |  | SIC | 2018 | Electrical and SCADA Room | 1000113 | Wide Area Network Radio | [6 empty] | 12 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2000 | PXL_20211116_141645777 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
00040852 | 5762 | RHB | Instrumentation,Switch,Flow,High |  |  |  | SIC | 2008 | Chemical Room | 1000111 | Eyewash Flow Switch | [6 empty] | 8 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 800 | PXL_20211116_141926309 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
00045567 | 5763 | RHB | Instrumentation,Transmitters,Position |  |  |  | SIC | 2008 | Valve Room | 1000112 | Position Transmitter | [6 empty] | 8 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 1500 | PXL_20211116_140049452 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
00040833 | 5764 | RHB | Instrumentation,Analysers,Chlorine,Total Chlorine,CL17 |  |  |  | SIC | 2008 | Valve Room | 1000112 | Inlet Total Chlorine Residual Analyser | [6 empty] | 8 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 28000 | PXL_20211116_135944275 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
00085393 | 5765 | RHB | Instrumentation,Flow Meter,Electromagnetic,Non-Revenue Water |  |  |  | SIC | 2018 | Valve Room | 1000112 | Flow Transmitter | [6 empty] | 12 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 6000 | PXL_20211116_135920183 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00086556 | 5766 | RHB | Instrumentation,Sensing Elements,Flow |  |  |  | SIC | 2018 | Valve Room | 1000112 | Flow Sensor | [6 empty] | 12 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 5000 | PXL_20211116_140209541 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00040833 | 5767 | RHB | Instrumentation,Analysers,Chlorine,Total Chlorine,CL17 |  |  |  | SIC | 2008 | Valve Room | 1000112 | Outlet Total Chlorine Residual Analyser | [6 empty] | 8 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 28000 | PXL_20211116_135937133 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
00085394 | 5769 | RHB | Instrumentation,Transmitters,Pressure,Gauge |  |  |  | SIC | 2018 | Valve Room | 1000112 | System Pressure Transmitter | [6 empty] | 12 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 3000 | PXL_20211116_140106684 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00085395 | 5770 | RHB |  |  |  |  | SIC | 2018 | Valve Room | 1000112 | Pressure Gauge | [6 empty] | 12 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 700 | PXL_20211116_140526499 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00040826 | 5771 | RHB |  |  |  |  | SIC | 2008 | Valve Room | 1000112 | Valve Room Low Temperature Switch | [6 empty] | 8 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 800 | PXL_20211116_135758462 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
00085351 | 5772 | RHB |  |  |  |  | SIC | 2018 | Valve Room | 1000112 | OIT Monitor | [6 empty] | 12 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 10000 | PXL_20211116_135815110 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
00085352 | 5773 | RHB | Computer,OIT,CPU,2184 |  |  |  | SIC | 2018 | Valve Room | 1000112 | OIT Computer | [6 empty] | 12 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 3000 | PXL_20211116_135815110 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
| 5774 | RHB |  |  |  |  | AC | 2008 |  | 1000116 | Atrium Access Door (Double) | [6 empty] | 8 | [9 empty] | 3 | 1 | Weathered paint was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 5500 | IMG_9857 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Weathered paint
| 5775 | RHB |  |  |  |  | AC | 2008 |  | 1000112 | Valve Room Access Door (Double) | [6 empty] | 8 | [9 empty] | 2 | 1 |  | Broken glass on one door was observed. |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 5500 | IMG_9875 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good | broken glass on one door
| 5776 | RHB |  |  |  |  | AC | 2008 |  | 1000111 | Chemical Room Interior Access Door (Single) | [6 empty] | 8 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 3500 | IMG_9863 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
| 5777 | RHB |  |  |  |  | AC | 2008 |  | 1000111 | Chemical Room Exterior Access Door (Single) | [6 empty] | 8 | [9 empty] | 3 | 1 | Weathered exterior paint was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 3500 | IMG_9864 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | weathered exterior paint
| 5778 | RHB |  |  |  |  | AC | 2008 |  | 1000114 | Washroom Access Door (Single) | [6 empty] | 8 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 3500 | IMG_9859 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
| 5779 | RHB |  |  |  |  | AC | 2008 |  | 1000113 | Electrical and SCADA Room Access Door (Single) | [6 empty] | 8 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 3500 | IMG_9879 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
| 5780 | RHB |  |  |  |  | AC | 2008 |  | 1000113 | Electrical and SCADA Room Floor Coating | [6 empty] | 8 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 12000 | IMG_9880 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
| 5781 | RHB |  |  |  |  | AC | 2008 |  | 1000113 | Electrical and SCADA Room Wall Paint | [6 empty] | 8 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 1200 | IMG_9881 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
| 5782 | RHB |  |  |  |  | AC | 2008 |  | 1000112 | Valve Room Wall Paint | [6 empty] | 8 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 3000 | IMG_9876 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
| 5783 | RHB |  |  |  |  | AC | 2008 |  | 1000112 | Valve Room Floor Coating | [6 empty] | 8 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 40000 | IMG_9876 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
| 5784 | RHB |  |  |  |  | AC | 2008 |  | 1000111 | Chemical Room Floor Coating | [6 empty] | 8 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 10000 | IMG_9864 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
| 5785 | RHB |  |  |  |  | AC | 2008 |  | 1000111 | Chemical Room Wall Paint | [6 empty] | 8 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 1200 | IMG_9864 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
| 5786 | RHB |  |  |  |  | AC | 2008 |  | 1000114 | Washroom Wall Paint | [6 empty] | 8 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 800 | IMG_9861 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
| 5787 | RHB |  |  |  |  | AC | 2008 |  | 1000114 | Washroom Floor Coating | [6 empty] | 8 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 2200 | IMG_9860 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
| 5788 | RHB |  |  |  |  | AC | 2008 |  | 1000115 | Atrium Floor Coating | [6 empty] | 8 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 16000 | IMG_9886 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
| 5789 | RHB |  |  |  |  | AC | 2008 |  | 1000115 | Atrium Wall Paint | [6 empty] | 8 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 1500 | IMG_9886 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
| 5790 | RHB |  |  |  |  | AC | 2008 |  | 1000111 | Chemical Room Window | [6 empty] | 8 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 3000 | IMG_9871 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
| 5822 | RHB |  |  |  |  | SC | 2008 |  | 1000116 | Elevated Tank Steel Tank | [6 empty] | 47 | [9 empty] | 3 | 5 | Minor corrosion was observed at areas. |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 2500000 | IMG_9850 |  |  |  | 0 |  | 0 |  | 0 | minor corrosion at areas
| 5824 | RHB |  |  |  |  | SCS | 2008 |  | 1000116 | Elevated Tank Exterior Coating | [6 empty] | 17 | [9 empty] | 3 | 4 | Localized areas of peeled/missing coating was observed. |  |  | The asset was observed to be in fair condition. Overcoating Asset to be replaced at the end of remaining service life. | 342000 | 2025 | 0 |  | 1140000 | IMG_9850 | North Richmond Hill Bloomington Road West ET Capital Project 2 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  | 0 | overcoating | 0 |  | 0 | localized areas of peeled/missing coating
| 5792 | RHB |  |  |  |  | SC | 2008 |  | 1000115 | Elevated Tank Concrete Pedestal | [6 empty] | 47 | [9 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 50000 | 2031 | 0 |  | 1100000 | IMG_9851 |  | North Richmond Hill Bloomington Road West ET Capital Project 2 |  | 0 |  | 0 |  | 0 | Good
| 5823 | RHB |  |  |  |  | SCS | 2008 |  | 1000116 | Elevated Tank Interior Coating | [6 empty] | 17 | [9 empty] | 3 | 4 |  |  |  | The asset was assumed to be in fair condition. Overcoating in the next capital project. Asset to be replaced at the end of remaining service life. | 200000 | 2025 | 0 |  | 660000 |  | North Richmond Hill Bloomington Road West ET Capital Project 2 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  | 0 | overcoating | 0 |  | 0
| 5791 | RHB |  |  |  |  | SC | 2008 |  | 1000115 | Elevated Tank Concrete Foundation | [6 empty] | 47 | [9 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 50000 | 2031 | 0 |  | 600000 | IMG_3924 |  | North Richmond Hill Bloomington Road West ET Capital Project 2 |  | 0 |  | 0 |  | 0 | Good
| 5800 | RHB |  |  |  |  | SC | 2008 |  | 1000112 | Valve Room Concrete Floor Slab | [6 empty] | 47 | [9 empty] | 2 | 3 | Minor hairline cracking was observed. |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 6000 | 2031 | 0 |  | 65000 | IMG_9877 |  | North Richmond Hill Bloomington Road West ET Capital Project 2 |  | 0 |  | 0 |  | 0 | Minor hairline cracking
| 5801 | RHB |  |  |  |  | SC | 2008 |  | 1000112 | Valve Room Composite Roof Slab | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. |  |  | 0 |  | 55000 | IMG_9877 |  |  |  | 0 |  | 0 |  | 0 | Good
| 5811 | RHB |  |  |  |  | SC | 2008 |  | 1000115 | Elevated Tank Platform | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 50000 | IMG_9891 |  |  |  | 0 |  | 0 |  | 0 | Good
| 5799 | RHB |  |  |  |  | SC | 2008 |  | 1000112 | Valve Room Concrete Blockwalls | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 2000 | 2031 | 0 |  | 45000 | IMG_9877 |  | North Richmond Hill Bloomington Road West ET Capital Project 2 |  | 0 |  | 0 |  | 0 | Good
| 5821 | RHB | roof |  |  |  | SC | 2008 |  | 1000116 | Elevated Tank Guardrail | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 40000 | IMG_9927 |  |  |  | 0 |  | 0 |  | 0 | Good
| 5805 | RHB | ground to platform |  |  |  | SC | 2008 |  | 1000115 | Elevated Tank Ladder (Base to Platform) | [6 empty] | 47 | [9 empty] | 2 | 4 | The fail arrest system was not compliant to current CSA standard. |  |  | The asset was observed to be in good condition. The fail arrest system was not compliant to current CSA standard. Replace the fail arrest system immediately. Asset to be replaced at the end of remaining service life. | 5000 | 2021 | 0 |  | 30000 | IMG_9888 |  | North Richmond Hill Bloomington Road West ET Immediate Project |  | 0 |  | 0 |  | 0 | Good
| 5840 | RHB | roof |  |  |  | SC | 2008 |  | 1000116 | Elevated Tank Antenna Structure | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 30000 | IMG_9945 |  |  |  | 0 |  | 0 |  | 0 | Good
| 5793 | RHB |  |  |  |  | SC | 2008 |  | 1000111 | Chemical Room Concrete Blockwalls | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 2000 | 2031 | 0 |  | 20000 | IMG_9864 |  | North Richmond Hill Bloomington Road West ET Capital Project 2 |  | 0 |  | 0 |  | 0 | Good
| 5798 | RHB |  |  |  |  | SC | 2008 |  | 1000113 | Electrical and SCADA Room Concrete Blockwalls | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 2000 | 2031 | 0 |  | 20000 | IMG_9881 |  | North Richmond Hill Bloomington Road West ET Capital Project 2 |  | 0 |  | 0 |  | 0 | Good
| 5839 | RHB | tank underside |  |  |  | SC | 2008 |  | 1000116 | Atrium Concrete Blockwall | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 2000 | 2031 | 0 |  | 20000 | IMG_9886 |  | North Richmond Hill Bloomington Road West ET Capital Project 2 |  | 0 |  | 0 |  | 0 | Good
| 5797 | RHB |  |  |  |  | SC | 2008 |  | 1000113 | Electrical and SCADA Room Concrete Floor Slab | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 2000 | 2031 | 0 |  | 18000 | IMG_9880 |  | North Richmond Hill Bloomington Road West ET Capital Project 2 |  | 0 |  | 0 |  | 0 | Good
| 5794 | RHB |  |  |  |  | SC | 2008 |  | 1000111 | Chemical Room Concrete Floor Slab | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 1500 | 2031 | 0 |  | 15000 | IMG_9864 |  | North Richmond Hill Bloomington Road West ET Capital Project 2 |  | 0 |  | 0 |  | 0 | Good
| 5796 | RHB |  |  |  |  | SC | 2008 |  | 1000113 | Electrical and SCADA Room Composite Roof Slab | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 15000 | IMG_9881 |  |  |  | 0 |  | 0 |  | 0 | Good
| 5809 | RHB |  |  |  |  | SC | 2008 |  | 1000115 | Atrium Aluminum Staircase | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 15000 | IMG_9886 |  |  |  | 0 |  | 0 |  | 0 | Good
| 5795 | RHB |  |  |  |  | SC | 2008 |  | 1000111 | Chemical Room Composite Roof Slab | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 12000 | IMG_9864 |  |  |  | 0 |  | 0 |  | 0 | Good
| 5803 | RHB |  |  |  |  | SC | 2008 |  | 1000114 | Washroom Concrete Blockwalls | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 1000 | 2031 | 0 |  | 10000 | IMG_9861 |  | North Richmond Hill Bloomington Road West ET Capital Project 2 |  | 0 |  | 0 |  | 0 | Good
| 5812 | RHB | platform |  |  |  | HSS | 2008 |  | 1000115 | Elevated Tank Davit Arm Base 1 | [6 empty] | 47 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of service life. | 0 |  | 0 |  | 5000 | IMG_9948 |  |  |  | 0 |  | 0 |  | 0 | Good
| 5813 | RHB |  |  |  |  | HSS | 2008 |  | 1000115 | Platform Level Anchor Point | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of service life. | 0 |  | 0 |  | 2000 | IMG_9923 |  |  |  | 0 |  | 0 |  | 0 | Good
| 5814 | RHB |  |  |  |  | HSS | 2008 |  | 1000115 | Roof Anchor Point 1 | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of service life. | 0 |  | 0 |  | 2000 | IMG_9939 |  |  |  | 0 |  | 0 |  | 0 | Good
| 5815 | RHB |  |  |  |  | HSS | 2008 |  | 1000115 | Roof Anchor Point 2 | [6 empty] | 47 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of service life. | 0 |  | 0 |  | 2000 | IMG_9940 |  |  |  | 0 |  | 0 |  | 0 | Good
| 5816 | RHB |  |  |  |  | HSS | 2008 |  | 1000115 | Roof Anchor Point 3 | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of service life. | 0 |  | 0 |  | 2000 | IMG_9940 |  |  |  | 0 |  | 0 |  | 0 | Good
| 5817 | RHB | roof |  |  |  | HSS | 2008 |  | 1000115 | Elevated Tank Davit Arm Base 2 | [6 empty] | 47 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of service life. | 0 |  | 0 |  | 5000 | IMG_9940 |  |  |  | 0 |  | 0 |  | 0 | Good
| 5807 | RHB | platform to tank exterior |  |  |  | SC | 2008 |  | 1000115 | Elevated Tank Ladder (Platform to Roof) | [6 empty] | 47 | [9 empty] | 2 | 3 | The fail arrest system was not compliant to current CSA standard. |  |  | The asset was observed to be in good condition. The fail arrest system was not compliant to current CSA standard. Replace the fail arrest system immediately. Asset to be replaced at the end of remaining service life. | 5000 | 2021 | 0 |  | 10000 | IMG_9941 |  | North Richmond Hill Bloomington Road West ET Immediate Project |  | 0 |  | 0 |  | 0 | Good
| 5810 | RHB |  |  |  |  | SC | 2008 |  | 1000115 | Atrium Aluminum Guardrail | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 10000 | IMG_9901 |  |  |  | 0 |  | 0 |  | 0 | Good
| 5989 | RHB |  |  |  |  | SC | 2008 |  | 1000116 | Elevated Tank Interior Ladder (Roof to Tank) | [6 empty] | 47 | [9 empty] | 2 | 4 | The fail arrest system was not compliant to current CSA standard. |  |  | The asset was observed to be in good condition. The fail arrest system was not compliant to current CSA standard. Replace the fail arrest system immediately. Asset to be replaced at the end of remaining service life. | 5000 | 2021 | 0 | 0 | 10000 |  |  | North Richmond Hill Bloomington Road West ET Immediate Project |  | 0 |  | 0 |  | 0
| 5818 | RHB | roof |  |  |  | SC | 2008 |  | 1000115 | Elevated Tank Roof Hatch 1 | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 5000 | IMG_9940 |  |  |  | 0 |  | 0 |  | 0 | Good
| 5819 | RHB | roof |  |  |  | SC | 2008 |  | 1000115 | Elevated Tank Roof Hatch 2 | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 5000 | IMG_9939 |  |  |  | 0 |  | 0 |  | 0 | Good
| 5820 | RHB | roof |  |  |  | SC | 2008 |  | 1000115 | Elevated Tank Roof Hatch/Vent | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 5000 | IMG_9938 |  |  |  | 0 |  | 0 |  | 0 | Good
| 5838 | RHB | tank underside |  |  |  | SC | 2008 |  | 1000115 | Elevated Tank Tank Hatch | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 5000 | IMG_9922 |  |  |  | 0 |  | 0 |  | 0 | Good
| 5828 | RHB |  |  |  |  | SW | 2008 |  | 1000117 | Dechlorination Chamber Concrete Structure | [6 empty] | 47 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. | 0 |  | 0 |  | 10000 | IMG_9914 |  |  |  | 0 |  | 0 |  | 0 | Good
| 5829 | RHB |  |  |  |  | SW | 2008 |  | 1000117 | Dechlorination Chamber Access Ladder | [6 empty] | 47 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. | 0 |  | 0 |  | 1500 | IMG_9914 |  |  |  | 0 |  | 0 |  | 0 | Good
| 5830 | RHB |  |  |  |  | SW | 2008 |  | 1000117 | Dechlorination Chamber Manhole Frame and Cover | [6 empty] | 47 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. | 0 |  | 0 |  | 3000 | IMG_9913 |  |  |  | 0 |  | 0 |  | 0 | Good
| 5831 | RHB |  |  |  |  | SW | 2008 |  | 1000117 | Sanitary Chamber Manhole Frame and Cover | [6 empty] | 47 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. | 0 |  | 0 |  | 3000 | IMG_9915 |  |  |  | 0 |  | 0 |  | 0 | Good
| 5832 | RHB | 1800mm diameter maintenance hole, approx. 2.5m depth. Includes 450mm gate valve, 50mm sampling port and thrust block (with flange) |  |  |  | SW | 2008 |  | 1000117 | Sanitary Chamber Concrete Structure | [6 empty] | 47 | [9 empty] | 3 | 3 | Cracks was observed in moduloc. |  |  | The asset was observed to be in fair condition. Remove and replace moduloc. | 3000 | 2025 | 0 |  | 55000 | IMG_9917 |  | North Richmond Hill Bloomington Road West ET Capital Project 1 |  | 0 | Remove and replace moduloc. | 3000 |  | 0 | Cracks in moduloc
| 5833 | RHB |  |  |  |  | SW | 2008 |  | 1000117 | Sanitary Chamber Access Ladder | [6 empty] | 47 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. | 0 |  | 0 |  | 10000 | IMG_9917 |  |  |  | 0 |  | 0 |  | 0 | Good
| 5834 | RHB | 1200mm maintenance hole, approx. 1.5m deep. Includes 450mm eccentric slip on check valve |  |  |  | SW | 2008 |  | 1000117 | Overflow Chamber Concrete Structure | [6 empty] | 47 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. | 0 |  | 0 |  | 20000 | IMG_9911 |  |  |  | 0 |  | 0 |  | 0 | Good
| 5835 | RHB |  |  |  |  | SW | 2008 |  | 1000117 | Overflow Chamber Access Ladder | [6 empty] | 47 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. | 0 |  | 0 |  | 1500 | IMG_9911 |  |  |  | 0 |  | 0 |  | 0 | Good
| 5836 | RHB |  |  |  |  | SW | 2008 |  | 1000117 | Overflow Chamber Manhole Frame and Cover | [6 empty] | 47 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. | 0 |  | 0 |  | 3000 | IMG_9910 |  |  |  | 0 |  | 0 |  | 0 | Good
| 5837 | RHB |  |  |  |  | SW | 2008 |  | 1000117 | Sanitary Chamber Access Platform | [6 empty] | 47 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. | 0 |  | 0 |  | 3000 | IMG_9917 |  |  |  | 0 |  | 0 |  | 0 | Good
| 5804 | RHB |  |  |  |  | SC | 2008 |  | 1000114 | Washroom Concrete Floor Slab | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 1000 | 2031 | 0 |  | 3500 | IMG_9860 |  | North Richmond Hill Bloomington Road West ET Capital Project 2 |  | 0 |  | 0 |  | 0 | Good
| 5802 | RHB |  |  |  |  | SC | 2008 |  | 1000114 | Washroom Composite Roof Slab | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 3000 | IMG_9861 |  |  |  | 0 |  | 0 |  | 0 | Good
| 5806 | RHB | platform to u/s tank |  |  |  | SC | 2008 |  | 1000115 | Elevated Tank Ladder (Platform to U/S Tank) | [6 empty] | 47 | [9 empty] | 2 | 4 | The fail arrest system was not compliant to current CSA standard. |  |  | The asset was observed to be in good condition. The fail arrest system was not compliant to current CSA standard. Replace the fail arrest system immediately. Asset to be replaced at the end of remaining service life. | 2000 | 2021 | 0 |  | 3000 | IMG_9921 |  | North Richmond Hill Bloomington Road West ET Immediate Project |  | 0 |  | 0 |  | 0 | Good
| 5937 | RHB |  |  |  |  | HSS | 2008 |  | 1000111 | Chemical Room Smoke Detector | [6 empty] | 8 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 1000 | PXL_20211116_141906956 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
| 5938 | RHB |  |  |  |  | HSS | 2008 |  | 1000113 | Electrical and SCADA Room Smoke Detector | [6 empty] | 8 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 1000 | PXL_20211116_140710468 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
| 5940 | RHB | Antennas (x9) |  |  |  | SIC | 2008 |  | 1000116 | Antennas | [6 empty] | 8 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 90000 | IMG_9943 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
| 5941 | RHB |  |  |  |  | SIC | 2008 |  | 1000116 | Yagi Antenna | [6 empty] | 8 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 10000 | IMG_9937 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
| 5943 | RHB | 600V, 250kA |  |  |  | ES | 2008 |  | 1000113 | Surge Protection TVSS | [6 empty] | 12 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 8000 | PXL_20211116_140858856 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
| 5944 | RHB | 600V, 200A |  |  |  | ES | 2008 |  | 1000113 | Main Fused Disconnect Switch | [6 empty] | 12 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 10000 | PXL_20211116_140858856 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
| 5939 | RHB |  |  |  |  | HSS | 2008 |  | 1000112 | Valve Room Smoke Detector | [6 empty] | 8 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 1000 | PXL_20211116_135859101 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | Good
| 5945 | RHB | 600V, 30A, fused |  |  |  | ES | 2015 |  | 1000113 | Non-Fused Disconnect Switch DG1 | [6 empty] | 19 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 1500 | PXL_20211116_141608051 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
| 5946 | RHB |  |  |  |  | ES | 2015 |  | 1000113 | Generation Meter | [6 empty] | 19 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 4000 | PXL_20211116_141612192 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
| 5947 | RHB | 600V, 30A |  |  |  | ES | 2015 |  | 1000113 | Fused Disconnect Switch DG2 | [6 empty] | 19 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2000 | PXL_20211116_141608051 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
00084808 | 5948 | RHB | 600V, 10kW |  |  |  | ES | 2015 |  | 1000113 | Solar Power Inverter | [6 empty] | 19 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 15000 | PXL_20211116_142849609 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
| 5951 | RHB | 600V, 200A |  |  |  | ES | 2015 |  | 1000116 | Main Service Breaker | [6 empty] | 19 | [9 empty] | 3 | 3 | Missing arc flash label. |  |  | The asset was observed to be in fair condition. Install missing arc flash label. Asset to be replaced in the long term. | 500 | 2021 | 0 |  | 10000 | PXL_20211116_142348771 | North Richmond Hill Bloomington Road West ET Capital Project 2 | North Richmond Hill Bloomington Road West ET Immediate Project |  | 0 | Install missing arc flash label. | 500 |  | 0 | missing arc flash label
| 5952 | RHB | 8 linear fluorescent, 1 exit, 1 battery |  |  |  | ES | 2008 |  | 1000112 | Valve Room Lighting | [6 empty] | 12 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Non-LED fixtures to be replaced with LED type in the next capital project. Asset to be replaced in the long term. | 5000 | 2025 | 0 |  | 11000 | PXL_20211116_135859101 | North Richmond Hill Bloomington Road West ET Capital Project 2 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  | 0 | non-LED fixtures to be replaced with LED type in the next capital project. | 5000 |  | 0 | good
| 5953 | RHB | 2 linear fluorescent, 1 remote head |  |  |  | ES | 2008 |  | 1000113 | Electrical Room Lighting | [6 empty] | 12 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Non-LED fixtures to be replaced with LED type in the next capital project. Asset to be replaced in the long term. | 2000 | 2025 | 0 |  | 3000 | PXL_20211116_140709191 | North Richmond Hill Bloomington Road West ET Capital Project 2 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  | 0 | non-LED fixtures to be replaced with LED type in the next capital project. | 2000 |  | 0 | good
| 5955 | RHB | 16 wall mount, 1 exit, 2 flood light, 4 remote head, 4 linear fluorescent |  |  |  | ES | 2008 |  | 1000116 | Elevated Tank Lighting | [6 empty] | 12 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Non-LED fixtures to be replaced with LED type in the next capital project. Asset to be replaced in the long term. | 4000 | 2025 | 0 |  | 50000 | PXL_20211116_141906956 | North Richmond Hill Bloomington Road West ET Capital Project 2 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  | 0 | non-LED fixtures to be replaced with LED type in the next capital project. | 4000 |  | 0 | good
| 5956 | RHB | washroom and floor drains connect to sanitary service. Water service line for washroom. |  |  |  | BM | 2008 |  | 1000116 | Plumbing and Drainage | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 10000 | IMG_4226 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
| 5957 | RHB | 1 toilet and 1 sink |  |  |  | BM | 2008 |  | 1000114 | Washroom Fixtures | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 2000 | IMG_3936 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
| 5958 | RHB | Electrical underground duct system and conduit system |  |  |  | ES | 2008 |  | 1000116 | Electrical Duct System and Conduit System | [6 empty] | 12 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 60000 | IMG_9941 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
| 5959 | RHB |  |  |  |  | ES | 2008 |  | 1000116 | Elevated Tank Lightning Protection System | [6 empty] | 12 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 5000 | IMG_9944 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
| 5960 | RHB | Two warning lights, assumed installation year: 2010 |  |  |  | ES | 2008 |  | 1000116 | Aircraft Obstruction Lights | [6 empty] | 12 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 1000 | IMG_9944 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
| 5961 | RHB |  |  |  |  | ES | 2008 |  |  | Elevated Tank Grounding | [6 empty] | 25 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 10000 | IMG_9901 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
| 5962 | RHB |  |  |  |  | ES | 2008 |  |  | Elevated Tank Inlet Pipe Heat Tracing | [6 empty] | 12 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 15000 | IMG_4178 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
00084809 | 5949 | RHB | 3 array, 12 modules each |  |  |  | ES | 2015 |  | 1000113 | Solar Power Modules | [6 empty] | 19 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 40000 | PXL_20211116_143147485 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
| 5950 | RHB |  |  |  |  | ES | 2015 |  | 1000116 | Hydro Meter | [6 empty] | 19 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 6000 | PXL_20211116_142339795 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
| 5954 | RHB | 3 linear fluorescent, 1 exit, 1 remote head |  |  |  | ES | 2008 |  | 1000111 | Chemical Room Lighting | [6 empty] | 12 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition.non-LED fixtures to be replaced with LED type in the next capital project. Asset to be replaced in the long term. | 3000 |  | 0 |  | 5000 | PXL_20211116_141906956 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 | non-LED fixtures to be replaced with LED type in the next capital project. | 3000 |  | 0 | good
| 5963 | RHB |  |  |  |  | ES | 2008 |  |  | Elevated Tank Outlet Pipe Heat Tracing | [6 empty] | 12 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 15000 | IMG_20211116_113909 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
| 5964 | RHB | Diameter: 450mm, length: 50 meters |  |  |  | PM | 2008 |  |  | Tank Overflow Drain Line Piping | [6 empty] | 17 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 82000 | IMG_4174 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
| 5965 | RHB | Diameter: 100mm, length: 15 meters |  |  |  | PM | 2008 |  |  | Circulation Line Piping | [6 empty] | 17 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 6000 | IMG_4174 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
| 5966 | RHB | Diameter: 450mm, length: 20 meters |  |  |  | PM | 2008 |  |  | Inlet/Outlet Line Piping | [6 empty] | 17 | [9 empty] | 2 | 5 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 25000 | IMG_4055 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
| 5967 | RHB | Diameter: 450mm, length: 30 meters |  |  |  | PM | 2008 |  |  | Inlet Line Piping | [6 empty] | 17 | [9 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 49000 | IMG_4050 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
| 5968 | RHB | Diameter: 450mm, length: 25 meters |  |  |  | PM | 2008 |  |  | Outlet Line Piping | [6 empty] | 17 | [9 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 41000 | IMG_4158 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
| 5969 | RHB | Diameter: 450mm |  |  |  | PM | 2008 |  |  | Tank Overflow Drain Line Duckbill Valve | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 4000 | IMG_3917 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
| 5970 | RHB |  |  |  |  | PM | 2008 |  |  | Elevated Tank Frostproof Vent/Vacuum Relief Unit | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 6000 | IMG_9938 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
| 5971 | RHB | Approximately 3 in total |  |  |  | HSS | 2008 |  | 1000116 | Fire Extinguishers | [6 empty] | 8 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 2000 | IMG_3971 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
| 5972 | RHB | including valve, gauges, and a pump |  |  |  | PM | 2008 |  | 1000112 | Recirculation System | [6 empty] | 17 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 15000 | IMG_4179 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
| 5973 | RHB | security system for the entire ET |  |  |  | SIC | 2008 |  | 1000116 | Security System | [6 empty] | 8 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 60000 | IMG_4222 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 |  | 0 |  | 0 | good
| 5974 | RHB | 9.0m long, 2.4m high chainlink swing gate |  |  |  | SW | 2008 |  | 1000117 | Swing Gate | [6 empty] | 12 | [9 empty] | 3 | 2 | Paint chipping off. | Minor damage to mesh was observed. |  | The asset was observed to be in fair condition. Asset to be replaced in the intermediate term. | 0 |  | 0 |  | 5000 | IMG_20211116_094340 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Paint chipping off | Minor damage to mesh
| 5975 | RHB | 2.4m high chainlink fence along property line (approx. 375m in length) |  |  |  | SW | 2008 |  | 1000117 | Chainlink fence | [6 empty] | 12 | [9 empty] | 3 | 2 | Paint chipping off fence was observed. | Horizontal fence bar missing & damaged at north side and south-east corners were observed. |  | The asset was observed to be in fair condition. Install new horizontal fence bars at corners. Asset to be replaced in the long term. | 1000 | 2025 | 0 |  | 75000 | IMG_20211116_094518 | North Richmond Hill Bloomington Road West ET Capital Project 2 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  | 0 | Install new horizontal fence bars at corners | 1000 |  | 0 | Paint chipping off fence | Horizontal fence bar missing or damaged at north side and south-east corners
| 5976 | RHB | Pedestrian swing gate located east of vehicle entrance |  |  |  | SW | 2008 |  | 1000115 | Pedestrian Swing Gate | [6 empty] | 12 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | 3000 | IMG_20211116_095248 | North Richmond Hill Bloomington Road West ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
| 5977 | RHB | Overflow detention area (dry pond), including emergency overflow overland |  |  |  | SW | 2008 |  | 1000117 | Overflow Detention Area | [6 empty] | 47 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. | 0 |  | 0 |  | 25000 | IMG_20211116_100019 |  |  |  | 0 |  | 0 |  | 0 | Good
| 5978 | RHB | Overflow outlet, including armtec headwall and riprap |  |  |  | SW | 2008 |  | 1000116 | Overflow Outlet | [6 empty] | 47 | [9 empty] | 3 | 3 | Minor ponding by outlet was observed. |  |  | The asset was observed to be in fair condition. Remove and replace rip rap around outlet. | 5000 | 2025 | 0 |  | 15000 | IMG_20211116_100057 |  | North Richmond Hill Bloomington Road West ET Capital Project 1 |  | 0 | Remove and replace rip rap around outlet. | 5000 |  | 0 | Minor ponding by outlet
| 5979 | RHB | DICB in dry pond |  |  |  | SW | 2008 |  | 1000117 | DICB in dry pond | [6 empty] | 47 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. | 0 |  | 0 |  | 5000 | IMG_20211116_100214 |  |  |  | 0 |  | 0 |  | 0 | Good
| 5980 | RHB | 450mm PVC storm sewer, total length 85m (in two sections), approx. 2.0m in depth |  |  |  | SW | 2008 |  | 1000117 | Storm Sewer | [6 empty] | 47 | [9 empty] | 3 | 2 |  |  |  | The asset was assumed to be in good condition. | 0 |  | 0 |  | 90000 |  |  |  |  | 0 |  | 0 |  | 0 | Not observed
| 5982 | RHB | 150mm PVC sewer, 27m in length, approx. 2.0m in depth |  |  |  | SW | 2008 |  | 1000117 | Sanitary Sewer | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was assumed to be in fair condition. | 0 |  | 0 |  | 25000 |  |  |  |  | 0 |  | 0 |  | 0 | Not observed
| 5984 | RHB | 450mm CPP watermain (C303), approx. 65m in length |  |  |  | SW | 2008 |  | 1000117 | Watermain | [6 empty] | 47 | [9 empty] | 2 | 5 |  |  |  | The asset was assumed to be in good condition. | 0 |  | 0 |  | 130000 |  |  |  |  | 0 |  | 0 |  | 0 | Not observed
| 5986 | RHB | Asphalt driveway from entrance to site, and around tank pedestal. Approx. area 600m2. Road makeup (based on record drawings) is 40mm HL3, 80mm HL8, 150mm granular A, 400mm granular B. |  |  |  | SW | 2008 |  | 1000117 | Asphalt driveway | [6 empty] | 4 | [9 empty] | 3 | 2 | Cracks was observed in various areas. | Asphalt settled and damaged adjacent to the tank was observed. | Potential utility cuts not permanently restored was observed. | The asset was observed to be in fair condition. Remove and replace asphalt layers, or full depth reconstruction (dependent on geotechnical investigation). |  |  | 0 |  | 60000 | IMG_20211116_100720 | North Richmond Hill Bloomington Road West ET Capital Project 1 |  |  | 0 | Remove and replace asphalt layers, or full depth reconstruction (dependent on geotechnical investigation). | 60000 |  | 0 | Cracks in various areas | Asphalt settled and damaged adjacent to the tank | Potential utility cuts not permanently restored
| 5987 | RHB | general sod on site |  |  |  | SW | 2008 |  | 1000117 | Landscaping | [6 empty] | 47 | [9 empty] | 3 | 1 | Damage along driveway was observed. |  |  | The asset was observed to be in fair condition. Regrade areas along driveway, and install new top soil and sod. Alternatively, place gravel shoulder. Asset to be replaced at the end of the service life. | 5000 | 2025 | 0 |  | 70000 | IMG_20211116_100418 |  | North Richmond Hill Bloomington Road West ET Capital Project 1 |  | 0 | Regrade areas along driveway, and install new top soil and sod. Alternatively, place gravel shoulder | 5000 |  | 0 | Damage along driveway
| 5988 | RHB | Concrete bollards (quantity of 4) |  |  |  | SW | 2008 |  | 1000117 | Bollards | [6 empty] | 47 | [9 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. | 0 |  | 0 |  | 6000 | IMG_20211116_100635 |  |  |  | 0 |  | 0 |  | 0 | Good
| 5808 | RHB |  |  |  |  | SC | 2008 |  | 1000111 | Chemical Room FRP Grating | [6 empty] | 47 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | 2500 | IMG_9864 |  |  |  | 0 |  | 0 |  | 0 | Good