## Sheet1
AssetID | AssetName | AssetCategory | AssessmentYear | InstallYear | AvgESL
8 | HWSUR, INLET OUTLET BUTTERFLY VALVE No.1 | Process Mechanical |  | 1950 | 30
9 | HWSUR, INLET OUTLET BUTTERFLY VALVE No.2 | Process Mechanical |  | 1950 | 30
20 | HWSUR, Inlet Butterfly Valve No.1 | Process Mechanical |  | 2000 | 30
21 | HWSUR, Inlet Butterfly Valve No.2 | Process Mechanical |  | 2000 | 30
22 | HWSUR, Inlet Butterfly Valve No.3 | Process Mechanical |  | 2000 | 30
23 | HWSUR, SURGE ANTICIPATOR VALVE NO.1 | Process Mechanical |  | 2000 | 30
24 | HWSUR, SURGE ANTICIPATOR VALVE NO.2 | Process Mechanical |  | 2000 | 30
25 | HWSUR, SURGE PRESSURE RELIEF VALVE NO.3 | Process Mechanical |  | 2000 | 30
28 | HWSUR, SURGE BUILDING HEADER PRESSURE TRANSMITTER | Process Instrumentation |  | 2016 | 15
33 | V2 Control Panel | Process Electrical |  |  | 25
47 | HWSUR, ISOLATION GATE VALVE NO.1 | Process Mechanical |  | 2000 | 30
48 | HWSUR, ISOLATION GATE VALVE NO.2 | Process Mechanical |  | 2000 | 30
49 | HWSUR, ISOLATION GATE VALVE NO.3 | Process Mechanical |  | 2000 | 30
50 | HWSUR, AIR RELEASE VALVE NO.1 | Process Mechanical |  | 2000 | 30
51 | HWSUR, AIR RELEASE VALVE NO.2 | Process Mechanical |  | 2000 | 30
52 | HWSUR, AIR RELEASE VALVE NO.3 | Process Mechanical |  | 2000 | 30
53 | HWSUR, ISOLATION GATE VALVE NO.4 | Process Mechanical |  | 2000 | 30
54 | HWSUR, AIR RELEASE VALVE NO.4 | Process Mechanical |  | 2000 | 30
55 | HWSUR, BYPASS GATE VALVE NO.1 | Process Mechanical |  | 1950 | 30
56 | HWSUR, DECOMMISSIONED GATE VALVE NO.1 | Process Mechanical |  | 1950 | 30
57 | HWSUR, Valve 1 Process Piping | Process Mechanical |  | 2000 | 30
58 | Sidewalk | Site Works |  | 2001 | 20
59 | Lighting Panel LP-A | Building Electrical |  | 2001 | 25
60 | Terminal Blocks Panel | Building Electrical |  | 2001 | 25
61 | Intrinsically Safe Relay | Process Electrical |  | 2000 | 25
62 | V2 Control Panel | Process Electrical |  |  | 25
63 | V2 Control Panel | Process Electrical |  | 2000 | 25
64 | V1 Control Panel | Process Electrical |  | 2000 | 25
65 | Interior Lighting Fixtures | Building Electrical |  | 2000 | 25
66 | Emergency Lighting Fixtures | Building Electrical |  | 2000 | 25
67 | Exterior Lighting Fixture | Building Electrical |  | 2000 | 25
68 | Unit Heater 1 (Ground Level) | Building Mechanical |  | 2000 | 30
69 | Unit Heater 2 (Lower Level) | Building Mechanical |  | 2000 | 30
70 | Unit Heater (Portable) | Building Mechanical |  | 2000 | 30
71 | Exhaust Fan EF-1 | Building Mechanical |  | 2000 | 30
72 | Roof Drain | Building Mechanical |  | 2000 | 30
73 | Fire Extinguisher | Building Mechanical |  | 2020 | 30
74 | Motorized Louvre and Ducting | Building Mechanical |  | 2000 | 30
75 | Dehumidifier (Portable) | Building Mechanical |  | 2000 | 30
80 | V2 Control Panel | Process Electrical |  |  | 25
95 | Building Architectural | Building Architectural |  |  | 30
96 | Process Structural | Process Structural |  |  | 60
98 | Building Structural | Building Structural |  |  | 60
100 | Clay Brick Walls (1950) | Building Structural |  | 1950 | 60
101 | Clay Brick Walls (2000) | Building Architectural |  | 2000 | 30
102 | Concrete Foundation Walls | Building Structural |  | 1950 | 60
103 | Clay Brick Walls (2000) | Building Architectural |  | 2000 | 30
104 | Coping Stone | Building Architectural |  | 1950 | 30
105 | Roofing | Building Architectural |  | 2000 | 30
106 | Windows | Building Architectural |  | 2000 | 30
108 | Double Steel Door | Building Architectural |  | 2000 | 30
109 | Interior Clay Brick Walls | Building Structural |  | 1950 | 60
110 | Concrete Masonry Bond Beam | Building Structural |  | 2000 | 60
111 | Precast Concrete Roof | Building Structural |  | 2000 | 60
112 | Concrete Floor Slab | Building Structural |  | 1950 | 60
113 | Concrete Floor Beams | Building Structural |  | 1950 | 60
114 | Steel Monorail Beam | Process Structural |  | 2000 | 60
115 | Steel Platform with Grating | Process Structural |  | 1950 | 60
116 | Aluminum Platform with Grating | Process Structural |  | 2000 | 60
117 | Steel Floor Beams | Building Structural |  | 1950 | 60
118 | Galvanized Steel Floor Grating | Building Structural |  | 1950 | 60
119 | Aluminum Ladder | Process Structural |  | 2000 | 60
120 | Steel Ladders | Process Structural |  | 1950 | 60
121 | Concrete Masonry Infill Wall | Building Architectural |  | 2000 | 30
122 | Aluminum Hinged Cover | Building Architectural |  | 2000 | 30
123 | Steel Platform Railings | Building Architectural |  | 1950 | 30
124 | Aluminum Platform Railings | Building Architectural |  | 2000 | 30
125 | Ground Floor Steel Railings | Building Architectural |  | 1950 | 30
126 | Concrete Foundation Walls | Building Structural |  | 1950 | 60
127 | Concrete Base Slab | Building Structural |  | 1950 | 60
128 | Aluminum Platform with Grating | Process Structural |  | 2000 | 60
129 | Aluminum Ladders | Process Structural |  | 2000 | 60
130 | Aluminum Platform Railings | Building Architectural |  | 2000 | 30
131 | Site Civil | Site Works |  | 1950 | 20
132 | Building Electrical | Building Electrical |  |  | 25
133 | Building Mechanical | Building Mechanical |  |  | 30
135 | Surge Suppression Inlet | Process Mechanical |  |  | 30
136 | Surge Anticipator Valve 1 | Process Mechanical |  |  | 30
137 | Surge Anticipator Valve 2 | Process Mechanical |  |  | 30
138 | Surge Pressure Relief Valve 3 | Process Mechanical |  |  | 30
139 | Surge Suppression Discharge | Process Mechanical |  |  | 30
140 | HWSUR, Discharge Process Piping | Process Mechanical |  | 1950 | 30
142 | HWSUR, Inlet Process Piping | Process Mechanical |  | 2000 | 30
143 | HWSUR, Valve 2 Process Piping | Process Mechanical |  | 2000 | 30
144 | HWSUR, Valve 3 Process Piping | Process Mechanical |  | 2000 | 30
145 | Pressure Supply Header | Process Mechanical |  | 2000 | 30

## Final
CommentID | ParentID | Comment | DBNotes
1 | 8 | Poor
2 | 8 | Denso tape had been applied to the valve to protect against corrosion. Discolouration of the tape and corrosion of the valve wheel was observed. The valve was beyond its expected service life.
3 | 9 | Poor
4 | 9 | Denso tape had been applied to the valve to protect against corrosion. Discolouration of the tape and corrosion of the valve wheel was observed. The valve was beyond its expected service life.
180 | 20 | The City reported that operators are required to stand on the railings to operate the butterfly valve. The operators risk falling to the lower level, or backwards to the ground level.
5 | 20 | Poor
6 | 20 | Corrosion and deterioration was observed on the surface of the valve.
140 | 20 | This valve could not be opened during the hydraulic control valve inspection dated October 2019.
181 | 21 | The City reported that operators are required to stand on the railings to operate the butterfly valve. The operators risk falling to the lower level, or backwards to the ground level.
7 | 21 | Poor
8 | 21 | Corrosion and deterioration was observed on the surface of the valve.
143 | 21 | This valve could not be opened during the hydraulic control valve inspection dated October 2019.
182 | 22 | The City reported that operators are required to stand on the railings to operate the butterfly valve. The operators risk falling to the lower level, or backwards to the ground level.
9 | 22 | Poor
10 | 22 | Corrosion and deterioration was observed on the surface of the valve.
146 | 22 | This valve could not be opened during the hydraulic control valve inspection dated October 2019.
189 | 23 | The valve was found to be operable and in fair condition (DEVINE Flow Solutions, 2019).
147 | 23 | Fair
148 | 23 | The City reported that the electronics on the surge anticipators are failing regularly.
190 | 24 | The valve was found to be operable, however the visible portion of the valves' stem protruding from the valve cover was severely corroded (DEVINE Flow Solutions, 2019).
149 | 24 | Fair
150 | 24 | The City reported that the electronics on the surge anticipators are failing regularly.
191 | 25 | The valve was found to be operable and in fair condition (DEVINE Flow Solutions, 2019).
151 | 25 | Fair
152 | 25 | The City reported that the electronics on the surge anticipators are failing regularly.
14 | 28 | The pressure transmitter appeared to be in good condition.
15 | 29 | The sidewalk was in fair condition. Minor wear and overgrown vegetation were observed. | 29_merge
16 | 30 | The lighting panel appeared to be in good condition, but was approaching the end of its expected service life. | 30_merge
17 | 31 | The panel appeared to be in good condition, but was approaching the end of its expected service life. | 31_merge
18 | 32 | The equipment in the panel appeared to be in good condition, however there was a hole cut out of the panel cover. | 32_merge
19 | 34 | The panel appeared to be in good condition, but was approaching the end of its expected service life. | 34_merge
20 | 35 | The panel appeared to be in good condition, but was approaching the end of its expected service life. | 35_merge
21 | 36 | The lighting appeared to be in fair condition. One of the fixture covers was missing. | 36_merge
22 | 37 | The fixtures appeared to be in good condition, but were approaching the end of their expected service life. | 37_merge
23 | 38 | The lighting fixture appeared to be in good condition, but was appraochign the end of its expected service life. | 38_merge
24 | 39 | The unit heater appeared to be in fair condition with minor discolouration. | 39_merge
25 | 40 | The unit heater appeared to be in fair condition with minor discolouration. | 40_merge
26 | 41 | A portable unit heater was found on the ground level. | 41_merge
27 | 42 | The exhaust fan appeared to be in good condition. | 42_merge
28 | 43 | The roof drain appeared to be in good condition. | 43_merge
29 | 44 | The fire extinguigher appeared to be in good condition. | 44_merge
30 | 45 | The motorized louvre and ducting appeared to be in good condition. | 45_merge
31 | 46 | The portable dehumidifier appeared to be in fair condition and was found unplugged. | 46_merge
32 | 47 | Good | 47_merge
33 | 48 | Good | 48_merge
34 | 49 | Good | 49_merge
35 | 50 | Good | 50_merge
36 | 51 | Good | 51_merge
37 | 52 | Good | 52_merge
38 | 53 | Good | 53_merge
39 | 54 | Good | 54_merge
40 | 55 | Poor | 55_merge
41 | 55 | Severe corrosion and deterioration was observed on the surface of the valve | 55_merge
42 | 56 | Very Poor | 56_merge
43 | 56 | Corrosion was observed throughout the surface of the valve. | 56_merge
185 | 57 | The pressure gauge on the piping was damaged and the piping port was clogged (DEVINE Flow Solutions, 2019).
44 | 57 | Fair | 57_merge
45 | 57 | Discolouration was observed on the piping. | 57_merge
46 | 57 | Material of the pipe and valve are not consistent in the building. Cost estimates is based on 316 SS. | 57_merge
48 | 58 | The sidewalk was in fair condition. Minor wear and overgrown vegetation were observed. | 29_merge
49 | 59 | The lighting panel appeared to be in good condition, but was approaching the end of its expected service life. | 30_merge
50 | 60 | The panel appeared to be in good condition, but was approaching the end of its expected service life. | 31_merge
51 | 61 | The equipment in the panel appeared to be in good condition, however there was a hole cut out of the panel cover. | 32_merge
52 | 63 | The panel appeared to be in fair condition, and was approaching the end of its expected service life. The battery pack in the panel was replaced in February 2009, however the City reported issues with the battery. | 34_merge
53 | 64 | The panel appeared to be in fair condition, and was approaching the end of its expected service life. The battery pack in the panel was replaced in February 2009, however the City reported issues with the battery. | 35_merge
54 | 65 | The lighting appeared to be in fair condition. One of the fixture covers was missing. | 36_merge
55 | 66 | The fixtures appeared to be in good condition, but were approaching the end of their expected service life. | 37_merge
56 | 67 | The lighting fixture appeared to be in good condition, but was appraochign the end of its expected service life. | 38_merge
188 | 68 | The City reported that freezing during cold weather has caused the pilots on the surge anticipator valves to break.
57 | 68 | The unit heater appeared to be in fair condition with minor discolouration. | 39_merge
58 | 69 | The unit heater appeared to be in fair condition with minor discolouration. | 40_merge
59 | 70 | A portable unit heater was found on the ground level. | 41_merge
60 | 71 | The exhaust fan appeared to be in good condition. | 42_merge
61 | 72 | The roof drain appeared to be in good condition. | 43_merge
62 | 73 | The fire extinguisher appeared to be in good condition. | 44_merge
63 | 74 | The motorized louvre and ducting appeared to be in good condition. | 45_merge
184 | 75 | The City reported that the building is damp and musty.
64 | 75 | The portable dehumidifier appeared to be in fair condition and was found unplugged. | 46_merge
65 | 76 | The sidewalk was in fair condition. Minor wear and overgrown vegetation were observed. | 29_merge
66 | 77 | The lighting panel appeared to be in good condition, but was approaching the end of its expected service life. | 30_merge
67 | 78 | The panel appeared to be in good condition, but was approaching the end of its expected service life. | 31_merge
68 | 79 | The equipment in the panel appeared to be in good condition, however there was a hole cut out of the panel cover. | 32_merge
69 | 81 | The panel appeared to be in good condition, but was approaching the end of its expected service life. | 34_merge
70 | 82 | The panel appeared to be in good condition, but was approaching the end of its expected service life. | 35_merge
71 | 83 | The lighting appeared to be in fair condition. One of the fixture covers was missing. | 36_merge
72 | 84 | The fixtures appeared to be in good condition, but were approaching the end of their expected service life. | 37_merge
73 | 85 | The lighting fixture appeared to be in good condition, but was appraochign the end of its expected service life. | 38_merge
74 | 86 | The unit heater appeared to be in fair condition with minor discolouration. | 39_merge
75 | 87 | The unit heater appeared to be in fair condition with minor discolouration. | 40_merge
76 | 88 | A portable unit heater was found on the ground level. | 41_merge
77 | 89 | The exhaust fan appeared to be in good condition. | 42_merge
78 | 90 | The roof drain appeared to be in good condition. | 43_merge
79 | 91 | The fire extinguigher appeared to be in good condition. | 44_merge
80 | 92 | The motorized louvre and ducting appeared to be in good condition. | 45_merge
81 | 93 | The portable dehumidifier appeared to be in fair condition and was found unplugged. | 46_merge
82 | 96 | There is not enough space in the building and it would be beneficial to undergo a building expansion. | 49_merge
83 | 100 | Step cracking, popped mortar and spalled brick | 54_merge
84 | 101 | surface wear and spalling throughout | 55_merge
85 | 102 | Hairline cracking and minor spalling | 56_merge
86 | 103 | good | 57_merge
87 | 103 |  | 57_merge
88 | 104 | separation of mortar joints | 58_merge
90 | 105 | The roof was not observed, but was assumed to be in fair condition based on age. | 59_merge
133 | 105 | if monorail is to be brought back into service, it is recommended to coordinate deficient beam anchorage repacement with roofing replacement, as roofing will need to be removed to facilitate monorail anchorage replacement.
91 | 106 | cracked/failed caulking | 60_merge
92 | 107 | worn paint | 61_merge
93 | 108 | localized moderate corrosion, steel deformation and failed caulking | 62_merge
94 | 109 | localized step cracking and severely corroded steel beams embedded in top of walls | 63_merge
95 | 110 | surface wear and staining | 64_merge
172 | 111 | fair
96 | 111 | localized spalling | 65_merge
97 | 112 | localized spalling at top and underside and failed previously patched spalling around openings | 66_merge
98 | 113 | exposed aggregate and localized spalling with exposed rebar | 67_merge
99 | 114 | corroded anchor rods and surface rust | 68_merge
100 | 114 | currently not in use and would like to have it recertified. | 68_merge
101 | 114 | no trolly currently installed. Recertification will be challenging as it is supported by prestressed roof slab. | 68_merge
102 | 115 | moderate corrosion of platform support angles and anchors | 69_merge
103 | 116 | missing anchor bolts on northeast column | 70_merge
104 | 116 | grating not clipped in place | 70_merge
105 | 117 | surface corrosion and missing nut on connection to support angle | 71_merge
106 | 118 | heavy localized corrosion | 72_merge
107 | 118 | grating not clipped in place | 72_merge
108 | 119 | operators would prefer to remove ladder safety rail as it is not used during operation. | 73_merge
109 | 119 | only 570mm clearance to wall behind ladder. Recommended minimum is 760mm for ease of use | 73_merge
110 | 119 | good | 73_merge
130 | 119 | ladder safety rail may be removed if desired.
111 | 120 | surface rust on mounting brackets | 74_merge
112 | 120 | operators would prefer to remove ladder safety rails as they are not used during operation. | 74_merge
113 | 120 | loose ladder safety rail on north ladder | 74_merge
131 | 120 | ladder safety rails may be removed if desired.
114 | 121 | good | 75_merge
115 | 122 | good | 76_merge
116 | 123 | surface corrosion | 77_merge
117 | 123 | measured guardrail height of 1050mm. Code requires 1070mm. No kick plate | 77_merge
118 | 123 | No guardrail in middle portion of platform, only safety chain that was left unattached | 77_merge
119 | 124 | good | 78_merge
120 | 124 | measured guardrail height of 1050mm. Code requires 1070mm | 78_merge
179 | 125 | The City reported that operators are required to stand on the railings to operate the butterfly valves overhead. The operators risk falling to the lower level, or backwards to the ground level.
121 | 125 | minor surface corrosion and loss of paint | 79_merge
122 | 125 | measured guardrail height of 1020mm. Code requires 1070mm. Missing kick plate throughout and missing mid-rail in one location | 79_merge
123 | 126 | localized exposed aggregate, leaking around pipe and conduit penetrations | 80_merge
124 | 127 | surface wear | 81_merge
125 | 128 | good | 82_merge
126 | 129 | good | 83_merge
127 | 129 | operators would prefer to remove ladder safety rail as it is not used during operation. | 83_merge
132 | 129 | Ladder safety rail may be removed if desired. Fall protection with a davit and harness shall be used when accessing the lower level through the hatch.
128 | 130 | good | 84_merge
129 | 130 | measured guardrail height of 1040mm. Code requires 1070mm | 84_merge
170 | 140 | Fair
171 | 140 | Denso tape had been applied to the discharge piping on the lower level to protect against corrosion. Discolouration was observed on the pipe on the lower level with localized corrosion of the pipe on the main level.
168 | 142 | Fair
169 | 142 | Minor discolouration was observed on the 500mm diameter stainless steel surge header and inlet piping. Denso tape had been applied to the 1200mm diameter piping from the high lift pumping station to protect against corrosion.
174 | 143 | Fair
176 | 143 | Discolouration was observed on the piping.
178 | 143 | Material of the pipe and valve are not consistent in the building. Cost estimates is based on 316 SS.
186 | 143 | The pressure gauge on the piping was damaged and the piping port was clogged (DEVINE Flow Solutions, 2019).
173 | 144 | Fair
175 | 144 | Discolouration was observed on the piping.
177 | 144 | Material of the pipe and valve are not consistent in the building. Cost estimates is based on 316 SS.
187 | 144 | The pressure gauge on the piping was damaged and the piping port was clogged (DEVINE Flow Solutions, 2019).
183 | 145 | The City reported that the pressure sensing line was previously tapped into to install an eye wash station and hot water tank in the ammonia room in the High Lift Pumping Station. This seems to be causing issues with the pilot system.
193 | 145 | DEVINE Flow Solutions recommended to modify the pilot system supply piping so that all valves receive supply pressure from the main header, not from the high lift station's discharge header. This would eliminate the burried pipe.

## Jonathan
ParentID | Assetname | ConditionRating |  | Name | Combined | Comment1 | Comment2 | Comment3 | Comment4
8 | HWSUR, INLET OUTLET BUTTERFLY VALVE No.1 | 4 | poor | hwsur, inlet outlet butterfly valve no.1 | The inlet outlet butterfly valve No.1 was observed to be in poor condition as discolouration of the tape and corrosion of the valve wheel was observed. Denso tape had been applied to the valve to protect against corrosion. The valve was beyond its expected service life. | Denso tape had been applied to the valve to protect against corrosion. Discolouration of the tape and corrosion of the valve wheel was observed. The valve was beyond its expected service life.
9 | HWSUR, INLET OUTLET BUTTERFLY VALVE No.2 | 4 | poor | hwsur, inlet outlet butterfly valve no.2 | The inlet outlet butterfly valve No.2 was observed to be in poor condition as discolouration of the tape and corrosion of the valve wheel was observed. Denso tape had been applied to the valve to protect against corrosion. The valve was beyond its expected service life. | Denso tape had been applied to the valve to protect against corrosion. Discolouration of the tape and corrosion of the valve wheel was observed. The valve was beyond its expected service life.
20 | HWSUR, Inlet Butterfly Valve No.1 | 4 | poor | hwsur, inlet butterfly valve no.1 | The inlet butterfly valve No.3 was observed to be in poor condition. Corrosion and deterioration was observed on the surface of the valve. The City reported that operators are required to stand on the railings to operate the butterfly valve. The operators risk falling to the lower level, or backwards to the ground level. This valve could not be opened during the hydraulic control valve inspection dated October 2019. | The City reported that operators are required to stand on the railings to operate the butterfly valve. The operators risk falling to the lower level, or backwards to the ground level. | This valve could not be opened during the hydraulic control valve inspection dated October 2019. | Corrosion and deterioration was observed on the surface of the valve.
21 | HWSUR, Inlet Butterfly Valve No.2 | 4 | poor | hwsur, inlet butterfly valve no.2 | The inlet butterfly valve No.2 was observed to be in poor condition. Corrosion and deterioration was observed on the surface of the valve. The City reported that operators are required to stand on the railings to operate the butterfly valve. The operators risk falling to the lower level, or backwards to the ground level. This valve could not be opened during the hydraulic control valve inspection dated October 2019. | The City reported that operators are required to stand on the railings to operate the butterfly valve. The operators risk falling to the lower level, or backwards to the ground level. | This valve could not be opened during the hydraulic control valve inspection dated October 2019. | Corrosion and deterioration was observed on the surface of the valve.
22 | HWSUR, Inlet Butterfly Valve No.3 | 4 | poor | hwsur, inlet butterfly valve no.3 | The inlet butterfly valve No.3 was observed to be in poor condition. Corrosion and deterioration was observed on the surface of the valve. The City reported that operators are required to stand on the railings to operate the butterfly valve. The operators risk falling to the lower level, or backwards to the ground level. This valve could not be opened during the hydraulic control valve inspection dated October 2019. | The City reported that operators are required to stand on the railings to operate the butterfly valve. The operators risk falling to the lower level, or backwards to the ground level. | This valve could not be opened during the hydraulic control valve inspection dated October 2019. | Corrosion and deterioration was observed on the surface of the valve.
23 | HWSUR, SURGE ANTICIPATOR VALVE NO.1 | 3 | fair | hwsur, surge anticipator valve no.1 | The surge anticipator valve No.1 was observed to be in fair condition. The valve was found to be operable and in fair condition (DEVINE Flow Solutions, 2019). The City reported that the electronics on the surge anticipators are failing regularly. | The valve was found to be operable and in fair condition (DEVINE Flow Solutions, 2019). | The City reported that the electronics on the surge anticipators are failing regularly.
24 | HWSUR, SURGE ANTICIPATOR VALVE NO.2 | 3 | fair | hwsur, surge anticipator valve no.2 | The surge anticipator valve No.2 was observed to be in fair condition. The valve was found to be operable, however the visible portion of the valves' stem protruding from the valve cover was severely corroded (DEVINE Flow Solutions, 2019). The City reported that the electronics on the surge anticipators are failing regularly. | The valve was found to be operable, however the visible portion of the valves' stem protruding from the valve cover was severely corroded (DEVINE Flow Solutions, 2019). | The City reported that the electronics on the surge anticipators are failing regularly.
25 | HWSUR, SURGE PRESSURE RELIEF VALVE NO.3 | 3 | fair | hwsur, surge pressure relief valve no.3 | The surge pressure relief valve No.3 was observed to be in fair condition. The valve was found to be operable and in fair condition (DEVINE Flow Solutions, 2019). The City reported that the electronics on the surge anticipators are failing regularly. | The valve was found to be operable and in fair condition (DEVINE Flow Solutions, 2019). | The City reported that the electronics on the surge anticipators are failing regularly.
28 | HWSUR, SURGE BUILDING HEADER PRESSURE TRANSMITTER | 2 | good | hwsur, surge building header pressure transmitter | The surge building header pressure transmitter was observed to be in good condition. | The pressure transmitter appeared to be in good condition.
47 | HWSUR, ISOLATION GATE VALVE NO.1 | 2 | good | hwsur, isolation gate valve no.1 | The isolation gate valve No.1 was observed to be in good condition.
48 | HWSUR, ISOLATION GATE VALVE NO.2 | 2 | good | hwsur, isolation gate valve no.2 | The isolation gate valve No.2 was observed to be in good condition.
49 | HWSUR, ISOLATION GATE VALVE NO.3 | 2 | good | hwsur, isolation gate valve no.3 | The isolation gate valve No.3 was observed to be in good condition.
50 | HWSUR, AIR RELEASE VALVE NO.1 | 2 | good | hwsur, air release valve no.1 | The air release valve No.1 was observed to be in good condition.
51 | HWSUR, AIR RELEASE VALVE NO.2 | 2 | good | hwsur, air release valve no.2 | The air release valve No.2 was observed to be in good condition.
52 | HWSUR, AIR RELEASE VALVE NO.3 | 2 | good | hwsur, air release valve no.3 | The air release valve No.3 was observed to be in good condition.
53 | HWSUR, ISOLATION GATE VALVE NO.4 | 2 | good | hwsur, isolation gate valve no.4 | The isolation gate valve No.4 was observed to be in good condition.
54 | HWSUR, AIR RELEASE VALVE NO.4 | 2 | good | hwsur, air release valve no.4 | The air release valve No.4 was observed to be in good condition.
55 | HWSUR, BYPASS GATE VALVE NO.1 | 4 | poor | hwsur, bypass gate valve no.1 | The bypass gate valve No.1 was observed to be in poor condition. Severe corrosion and deterioration was observed on the surface of the valve | Severe corrosion and deterioration was observed on the surface of the valve
56 | HWSUR, DECOMMISSIONED GATE VALVE NO.1 | 5 | very poor | hwsur, decommissioned gate valve no.1 | The decommissioned gate valve No.1 was observed to be in very poor condition. Corrosion was observed throughout the surface of the valve. | Corrosion was observed throughout the surface of the valve.
57 | HWSUR, Valve 1 Process Piping | 3 | fair | hwsur, valve 1 process piping | The valve 1 process piping was observed to be in fair condition. The pressure gauge on the piping was damaged and the piping port was clogged (DEVINE Flow Solutions, 2019). Discolouration was observed on the piping. Material of the pipe and valve are not consistent in the building. Cost estimates is based on 316 SS. | The pressure gauge on the piping was damaged and the piping port was clogged (DEVINE Flow Solutions, 2019). | Discolouration was observed on the piping. | Material of the pipe and valve are not consistent in the building. Cost estimates is based on 316 SS.
58 | Sidewalk | 3 | fair | sidewalk | The sidewalk was observed to be in fair condition. Minor wear and overgrown vegetation were observed. | The sidewalk was in fair condition. Minor wear and overgrown vegetation were observed.
59 | Lighting Panel LP-A | 2 | good | lighting panel lp-a | The lighting panel LP-A was observed to be in good condition, but was approaching the end of its expected service life. | The lighting panel appeared to be in good condition, but was approaching the end of its expected service life.
60 | Terminal Blocks Panel | 2 | good | terminal blocks panel | The terminal blocks panel was observed to be in good condition, but was approaching the end of its expected service life. | The panel appeared to be in good condition, but was approaching the end of its expected service life.
61 | Intrinsically Safe Relay | 2 | good | intrinsically safe relay | The intrinsically safe relay was observed to be in good condition, however there was a hole cut out of the panel cover. | The equipment in the panel appeared to be in good condition, however there was a hole cut out of the panel cover.
63 | V2 Control Panel | 3 | fair | v2 control panel | The v2 control panel was observed to be in fair condition and was approaching the end of its expected service life. The battery pack in the panel was replaced in February 2009, however the City reported issues with the battery. | The panel appeared to be in fair condition, and was approaching the end of its expected service life. The battery pack in the panel was replaced in February 2009, however the City reported issues with the battery.
64 | V1 Control Panel | 3 | fair | v1 control panel | The v1 control panel was observed to be in fair condition and was approaching the end of its expected service life. The battery pack in the panel was replaced in February 2009, however the City reported issues with the battery. | The panel appeared to be in fair condition, and was approaching the end of its expected service life. The battery pack in the panel was replaced in February 2009, however the City reported issues with the battery.
65 | Interior Lighting Fixtures | 3 | fair | interior lighting fixtures | The interior lighting fixtures were observed to be in fair condition. One of the fixture covers was missing. | The lighting appeared to be in fair condition. One of the fixture covers was missing.
66 | Emergency Lighting Fixtures | 2 | good | emergency lighting fixtures | The emergency lighting fixtures were observed to be in good condition, but were approaching the end of their expected service life. | The fixtures appeared to be in good condition, but were approaching the end of their expected service life.
67 | Exterior Lighting Fixture | 2 | good | exterior lighting fixture | The exterior lighting fixture was observed to be in good condition, but was approaching the end of its expected service life. | The lighting fixture appeared to be in good condition, but was appraochign the end of its expected service life.
68 | Unit Heater 1 (Ground Level) | 3 | fair | unit heater 1 (ground level) | The unit heater appeared to be in fair condition with minor discolouration. The City reported that freezing during cold weather has caused the pilots on the surge anticipator valves to break. | The City reported that freezing during cold weather has caused the pilots on the surge anticipator valves to break. | The unit heater appeared to be in fair condition with minor discolouration.
69 | Unit Heater 2 (Lower Level) | 3 | fair | unit heater 2 (lower level) | The unit heater appeared to be in fair condition with minor discolouration. | The unit heater appeared to be in fair condition with minor discolouration.
70 | Unit Heater (Portable) | 2 | good | unit heater (portable) | The unit heater (portable) was observed to be in good condition. A portable unit heater was found on the ground level. | A portable unit heater was found on the ground level.
71 | Exhaust Fan EF-1 | 2 | good | exhaust fan ef-1 | The exhaust fan EF-1 was observed to be in good condition. | The exhaust fan appeared to be in good condition.
72 | Roof Drain | 2 | good | roof drain | The roof drain was observed to be in good condition. | The roof drain appeared to be in good condition.
73 | Fire Extinguisher | 2 | good | fire extinguisher | The fire extinguisher was observed to be in good condition. | The fire extinguisher appeared to be in good condition.
74 | Motorized Louvre and Ducting | 2 | good | motorized louvre and ducting | The motorized louvre and ducting were observed to be in good condition. | The motorized louvre and ducting appeared to be in good condition.
75 | Dehumidifier (Portable) | 3 | fair | dehumidifier (portable) | The portable dehumidifier appeared to be in fair condition and was found unplugged. The City reported that the building is damp and musty. | The City reported that the building is damp and musty. | The portable dehumidifier appeared to be in fair condition and was found unplugged.
100 | Clay Brick Walls (1950) | 3 | fair | clay brick walls (1950) | The clay brick walls (1950) were observed to be in fair condition. Step cracking, popped mortar and spalled brick were observed. | Step cracking, popped mortar and spalled brick
101 | Clay Brick Walls (2000) | 3 | fair | clay brick walls (2000) | The clay brick walls (2000) were observed to be in fair condition. Surface wear and spalling were observed throughout. | surface wear and spalling throughout
102 | Concrete Foundation Walls | 3 | fair | concrete foundation walls | The concrete foundation walls were observed to be in fair condition. Hairline cracking and minor spalling were observed. | Hairline cracking and minor spalling
103 | Clay Brick Walls (2000) | 2 | good | clay brick walls (2000) | The clay brick walls (2000) were observed to be in good condition.
104 | Coping Stone | 3 | fair | coping stone | The coping stone was observed to be in fair condition. Separation of mortar joints was noted. | separation of mortar joints
105 | Roofing | 3 | fair | roofing | The roof was not observed, but was assumed to be in fair condition based on age. If monorail is to be brought back into service, it is recommended to coordinate deficient beam anchorage replacement with roofing replacement, as roofing will need to be removed to facilitate monorail anchorage replacement. | The roof was not observed, but was assumed to be in fair condition based on age. | if monorail is to be brought back into service, it is recommended to coordinate deficient beam anchorage repacement with roofing replacement, as roofing will need to be removed to facilitate monorail anchorage replacement.
106 | Windows | 3 | fair | windows | The windows was observed to be in fair condition. Cracked/failed caulking was observed. | cracked/failed caulking
108 | Double Steel Door | 3 | fair | double steel door | The double steel door was observed to be in fair condition. Localized moderate corrosion, steel deformation and failed caulking were noted. | localized moderate corrosion, steel deformation and failed caulking
109 | Interior Clay Brick Walls | 3 | fair | interior clay brick walls | The interior clay brick walls were observed to be in fair condition. Localized step cracking and severely corroded steel beams embedded in top of walls were noted. | localized step cracking and severely corroded steel beams embedded in top of walls
110 | Concrete Masonry Bond Beam | 3 | fair | concrete masonry bond beam | The concrete masonry bond beam was observed to be in fair condition. Surface wear and staining were noted. | surface wear and staining
111 | Precast Concrete Roof | 3 | fair | precast concrete roof | The precast concrete roof was observed to be in fair condition. Localized spalling was noted. | fair | localized spalling
112 | Concrete Floor Slab | 3 | fair | concrete floor slab | The concrete floor slab was observed to be in fair condition. Localized spalling at top and underside and failed previously patched spalling around openings were noted. | localized spalling at top and underside and failed previously patched spalling around openings
113 | Concrete Floor Beams | 3 | fair | concrete floor beams | The concrete floor beams were observed to be in fair condition. Exposed aggregate and localized spalling with exposed rebar were noted. | exposed aggregate and localized spalling with exposed rebar
114 | Steel Monorail Beam | 3 | fair | steel monorail beam | The steel monorail beam was observed to be in fair condition. Corroded anchor rods and surface rust currently not in use and the City would like to have it recertified. no trolly currently installed. Recertification will be challenging as it is supported by prestressed. roof slab. | corroded anchor rods and surface rust | currently not in use and would like to have it recertified. | no trolly currently installed. Recertification will be challenging as it is supported by prestressed roof slab.
115 | Steel Platform with Grating | 3 | fair | steel platform with grating | The steel platform with grating was observed to be in fair condition. Moderate corrosion of platform support angles and anchors was noted. | moderate corrosion of platform support angles and anchors
116 | Aluminum Platform with Grating | 3 | fair | aluminum platform with grating | The aluminum platform with grating was observed to be in fair condition. Missing anchor bolts on northeast column and the grating were not clipped in place. | missing anchor bolts on northeast column | grating not clipped in place
117 | Steel Floor Beams | 3 | fair | steel floor beams | The steel floor beams were observed to be in fair condition. Surface corrosion and missing nut on connection to support angle were noted. | surface corrosion and missing nut on connection to support angle
118 | Galvanized Steel Floor Grating | 3 | fair | galvanized steel floor grating | The galvanized steel floor grating was observed to be in fair condition. Heavy localized corrosion grating was not clipped in place. | heavy localized corrosion | grating not clipped in place
119 | Aluminum Ladder | 2 | good | aluminum ladder | The aluminum ladder was observed to be in good condition. Operators would prefer to remove ladder safety rail as it is not used during operation. There was only 570mm clearance to wall behind ladder. Recommended minimum is 760mm for ease of use. | operators would prefer to remove ladder safety rail as it is not used during operation. | only 570mm clearance to wall behind ladder. Recommended minimum is 760mm for ease of use |  | ladder safety rail may be removed if desired.
120 | Steel Ladders | 4 | poor | steel ladders | The steel ladders was observed to be in poor condition. Surface rust on mounting brackets and loose ladder safety rail on north ladder were noted. Operators would prefer to remove ladder safety rails as they are not used during operation. | surface rust on mounting brackets | operators would prefer to remove ladder safety rails as they are not used during operation. | loose ladder safety rail on north ladder | ladder safety rails may be removed if desired.
121 | Concrete Masonry Infill Wall | 2 | good | concrete masonry infill wall | The concrete masonry infill wall was observed to be in good condition.
122 | Aluminum Hinged Cover | 2 | good | aluminum hinged cover | The aluminum hinged cover was observed to be in good condition.
123 | Steel Platform Railings | 4 | poor | steel platform railings | The steel platform railings were observed to be in poor condition. Surface corrosion was noted. No kick plates or guardrails installed in middle portion of platform, only safety chain that was left unattached. The guardrail height was measured to be 1050mm. Code requires 1070mm. | surface corrosion | measured guardrail height of 1050mm. Code requires 1070mm. No kick plate | No guardrail in middle portion of platform, only safety chain that was left unattached
124 | Aluminum Platform Railings | 2 | good | aluminum platform railings | The aluminum platform railings were observed to be in good condition, however, guardrail height was measured to be 1050mm. Code requires 1070mm. | measured guardrail height of 1050mm. Code requires 1070mm
125 | Ground Floor Steel Railings | 4 | poor | ground floor steel railings | The ground floor steel railings were observed to be in poor condition. Minor surface corrosion and loss of paint were noted. Missing kick plate throughout and missing mid-rail in one location were observed at the time of the inspection. The City reported that operators are required to stand on the railings to operate the butterfly valves overhead. The operators risk falling to the lower level, or backwards to the ground level. The guardrail height was measured to be 1020mm. Code requires 1070mm. | The City reported that operators are required to stand on the railings to operate the butterfly valves overhead. The operators risk falling to the lower level, or backwards to the ground level. | minor surface corrosion and loss of paint | measured guardrail height of 1020mm. Code requires 1070mm. Missing kick plate throughout and missing mid-rail in one location
126 | Concrete Foundation Walls | 3 | fair | concrete foundation walls | The concrete foundation walls were observed to be in fair condition. Localized exposed aggregate, leaking around pipe and conduit penetrations were noted. | localized exposed aggregate, leaking around pipe and conduit penetrations
127 | Concrete Base Slab | 3 | fair | concrete base slab | The concrete base slab was observed to be in fair condition. Surface wear was noted. | surface wear
128 | Aluminum Platform with Grating | 2 | good | aluminum platform with grating | The aluminum platform with grating was observed to be in good condition.
129 | Aluminum Ladders | 2 | good | aluminum ladders | The aluminum ladders were observed to be in good condition. Operators would prefer to remove ladder safety rail as it is not used during operation. Ladder safety rail may be removed if desired. Fall protection with a davit and harness shall be used when accessing the lower level through the hatch. | operators would prefer to remove ladder safety rail as it is not used during operation. | Ladder safety rail may be removed if desired. Fall protection with a davit and harness shall be used when accessing the lower level through the hatch.
130 | Aluminum Platform Railings | 2 | good | aluminum platform railings | The aluminum platform railings were observed to be in good condition, however, The guardrail height was measured to be 1040mm. Code requires 1070mm. | measured guardrail height of 1040mm. Code requires 1070mm
140 | HWSUR, Discharge Process Piping | 3 | fair | hwsur, discharge process piping | The discharge process piping was observed to be in fair condition. Discolouration was observed on the pipe on the lower level with localized corrosion of the pipe on the main level. Denso tape had been applied to the discharge piping on the lower level to protect against corrosion. | Denso tape had been applied to the discharge piping on the lower level to protect against corrosion. Discolouration was observed on the pipe on the lower level with localized corrosion of the pipe on the main level.
142 | HWSUR, Inlet Process Piping | 3 | fair | hwsur, inlet process piping | The inlet process piping was observed to be in fair condition. Minor discolouration was observed on the 500mm diameter stainless steel surge header and inlet piping. Denso tape had been applied to the 1200mm diameter piping from the high lift pumping station to protect against corrosion. | Minor discolouration was observed on the 500mm diameter stainless steel surge header and inlet piping. Denso tape had been applied to the 1200mm diameter piping from the high lift pumping station to protect against corrosion.
143 | HWSUR, Valve 2 Process Piping | 3 | fair | hwsur, valve 2 process piping | The valve 2 process piping was observed to be in fair condition. Discolouration was observed on the piping. Material of the pipe and valve are not consistent in the building. The pressure gauge on the piping was damaged and the piping port was clogged (DEVINE Flow Solutions, 2019). The cost estimate for the piping is based on 316 SS. | Discolouration was observed on the piping. | Material of the pipe and valve are not consistent in the building. Cost estimates is based on 316 SS. | The pressure gauge on the piping was damaged and the piping port was clogged (DEVINE Flow Solutions, 2019).
144 | HWSUR, Valve 3 Process Piping | 3 | fair | hwsur, valve 3 process piping | The valve 3 process piping was observed to be in fair condition. Discolouration was observed on the piping. Material of the pipe and valve are not consistent in the building. The pressure gauge on the piping was damaged and the piping port was clogged (DEVINE Flow Solutions, 2019). The cost estimate for the piping is based on 316 SS. | Discolouration was observed on the piping. | Material of the pipe and valve are not consistent in the building. Cost estimates is based on 316 SS. | The pressure gauge on the piping was damaged and the piping port was clogged (DEVINE Flow Solutions, 2019).
145 | Pressure Supply Header | 2 | good | pressure supply header | The pressure supply header was observed to be in good condition. The City reported that the pressure sensing line was previously tapped into an eye wash station and hot water tank in the ammonia room in the High Lift Pumping Station. This seems to be causing issues with the pilot system. DEVINE Flow Solutions recommended to modify the pilot system supply piping so that all valves receive supply pressure from the main header, not from the high lift station's discharge header. This would eliminate the buried pipe. | The City reported that the pressure sensing line was previously tapped into to install an eye wash station and hot water tank in the ammonia room in the High Lift Pumping Station. This seems to be causing issues with the pilot system. | DEVINE Flow Solutions recommended to modify the pilot system supply piping so that all valves receive supply pressure from the main header, not from the high lift station's discharge header. This would eliminate the burried pipe.

## Assetinventory
AssetID | AssetName | AssetCategory | AssessmentYear | InstallYear | AvgESL
8 | HWSUR, INLET OUTLET BUTTERFLY VALVE No.1 | Process Mechanical |  | 1950 | 30
9 | HWSUR, INLET OUTLET BUTTERFLY VALVE No.2 | Process Mechanical |  | 1950 | 30
20 | HWSUR, Inlet Butterfly Valve No.1 | Process Mechanical |  | 2000 | 30
21 | HWSUR, Inlet Butterfly Valve No.2 | Process Mechanical |  | 2000 | 30
22 | HWSUR, Inlet Butterfly Valve No.3 | Process Mechanical |  | 2000 | 30
23 | HWSUR, SURGE ANTICIPATOR VALVE NO.1 | Process Mechanical |  | 2000 | 30
24 | HWSUR, SURGE ANTICIPATOR VALVE NO.2 | Process Mechanical |  | 2000 | 30
25 | HWSUR, SURGE PRESSURE RELIEF VALVE NO.3 | Process Mechanical |  | 2000 | 30
28 | HWSUR, SURGE BUILDING HEADER PRESSURE TRANSMITTER | Process Instrumentation |  | 2016 | 15
33 | V2 Control Panel | Process Electrical |  |  | 25
47 | HWSUR, ISOLATION GATE VALVE NO.1 | Process Mechanical |  | 2000 | 30
48 | HWSUR, ISOLATION GATE VALVE NO.2 | Process Mechanical |  | 2000 | 30
49 | HWSUR, ISOLATION GATE VALVE NO.3 | Process Mechanical |  | 2000 | 30
50 | HWSUR, AIR RELEASE VALVE NO.1 | Process Mechanical |  | 2000 | 30
51 | HWSUR, AIR RELEASE VALVE NO.2 | Process Mechanical |  | 2000 | 30
52 | HWSUR, AIR RELEASE VALVE NO.3 | Process Mechanical |  | 2000 | 30
53 | HWSUR, ISOLATION GATE VALVE NO.4 | Process Mechanical |  | 2000 | 30
54 | HWSUR, AIR RELEASE VALVE NO.4 | Process Mechanical |  | 2000 | 30
55 | HWSUR, BYPASS GATE VALVE NO.1 | Process Mechanical |  | 1950 | 30
56 | HWSUR, DECOMMISSIONED GATE VALVE NO.1 | Process Mechanical |  | 1950 | 30
57 | HWSUR, Valve 1 Process Piping | Process Mechanical |  | 2000 | 60
58 | Sidewalk | Site Works |  | 2001 | 20
59 | Lighting Panel LP-A | Building Electrical |  | 2001 | 25
60 | Terminal Blocks Panel | Building Electrical |  | 2001 | 25
61 | Intrinsically Safe Relay | Process Electrical |  | 2000 | 25
62 | V2 Control Panel | Process Electrical |  |  | 25
63 | V2 Control Panel | Process Electrical |  | 2000 | 25
64 | V1 Control Panel | Process Electrical |  | 2000 | 25
65 | Interior Lighting Fixtures | Building Electrical |  | 2000 | 25
66 | Emergency Lighting Fixtures | Building Electrical |  | 2000 | 25
67 | Exterior Lighting Fixture | Building Electrical |  | 2000 | 25
68 | Unit Heater 1 (Ground Level) | Building Mechanical |  | 2000 | 30
69 | Unit Heater 2 (Lower Level) | Building Mechanical |  | 2000 | 30
70 | Unit Heater (Portable) | Building Mechanical |  | 2000 | 30
71 | Exhaust Fan EF-1 | Building Mechanical |  | 2000 | 30
72 | Roof Drain | Building Mechanical |  | 2000 | 30
73 | Fire Extinguisher | Building Mechanical |  | 2020 | 30
74 | Motorized Louvre and Ducting | Building Mechanical |  | 2000 | 30
75 | Dehumidifier (Portable) | Building Mechanical |  | 2000 | 30
80 | V2 Control Panel | Process Electrical |  |  | 25
95 | Building Architectural | Building Architectural |  |  | 30
96 | Process Structural | Process Structural |  |  | 60
98 | Building Structural | Building Structural |  |  | 60
100 | Clay Brick Walls (1950) | Building Structural |  | 1950 | 60
101 | Clay Brick Walls (2000) | Building Architectural |  | 2000 | 30
102 | Concrete Foundation Walls | Building Structural |  | 1950 | 60
103 | Clay Brick Walls (2000) | Building Architectural |  | 2000 | 30
104 | Coping Stone | Building Architectural |  | 1950 | 30
105 | Roofing | Building Architectural |  | 2000 | 30
106 | Windows | Building Architectural |  | 2000 | 30
108 | Double Steel Door | Building Architectural |  | 2000 | 30
109 | Interior Clay Brick Walls | Building Structural |  | 1950 | 60
110 | Concrete Masonry Bond Beam | Building Structural |  | 2000 | 60
111 | Precast Concrete Roof | Building Structural |  | 2000 | 60
112 | Concrete Floor Slab | Building Structural |  | 1950 | 60
113 | Concrete Floor Beams | Building Structural |  | 1950 | 60
114 | Steel Monorail Beam | Process Structural |  | 2000 | 60
115 | Steel Platform with Grating | Process Structural |  | 1950 | 60
116 | Aluminum Platform with Grating | Process Structural |  | 2000 | 60
117 | Steel Floor Beams | Building Structural |  | 1950 | 60
118 | Galvanized Steel Floor Grating | Building Structural |  | 1950 | 60
119 | Aluminum Ladder | Process Structural |  | 2000 | 60
120 | Steel Ladders | Process Structural |  | 1950 | 60
121 | Concrete Masonry Infill Wall | Building Architectural |  | 2000 | 30
122 | Aluminum Hinged Cover | Building Architectural |  | 2000 | 30
123 | Steel Platform Railings | Building Architectural |  | 1950 | 30
124 | Aluminum Platform Railings | Building Architectural |  | 2000 | 30
125 | Ground Floor Steel Railings | Building Architectural |  | 1950 | 30
126 | Concrete Foundation Walls | Building Structural |  | 1950 | 60
127 | Concrete Base Slab | Building Structural |  | 1950 | 60
128 | Aluminum Platform with Grating | Process Structural |  | 2000 | 60
129 | Aluminum Ladders | Process Structural |  | 2000 | 60
130 | Aluminum Platform Railings | Building Architectural |  | 2000 | 30
131 | Site Civil | Site Works |  | 1950 | 20
132 | Building Electrical | Building Electrical |  |  | 25
133 | Building Mechanical | Building Mechanical |  |  | 30
135 | Surge Suppression Inlet | Process Mechanical |  |  | 30
136 | Surge Anticipator Valve 1 | Process Mechanical |  |  | 30
137 | Surge Anticipator Valve 2 | Process Mechanical |  |  | 30
138 | Surge Pressure Relief Valve 3 | Process Mechanical |  |  | 30
139 | Surge Suppression Discharge | Process Mechanical |  |  | 30
140 | HWSUR, Discharge Process Piping | Process Mechanical |  | 1950 | 60
142 | HWSUR, Inlet Process Piping | Process Mechanical |  | 2000 | 60
143 | HWSUR, Valve 2 Process Piping | Process Mechanical |  | 2000 | 60
144 | HWSUR, Valve 3 Process Piping | Process Mechanical |  | 2000 | 60
145 | Pressure Supply Header | Process Mechanical |  | 2000 | 30

## condition
AssetID | AssetName | VisualCondition
8 | HWSUR, INLET OUTLET BUTTERFLY VALVE No.1 | 4
9 | HWSUR, INLET OUTLET BUTTERFLY VALVE No.2 | 4
20 | HWSUR, Inlet Butterfly Valve No.1 | 4
21 | HWSUR, Inlet Butterfly Valve No.2 | 4
22 | HWSUR, Inlet Butterfly Valve No.3 | 4
23 | HWSUR, SURGE ANTICIPATOR VALVE NO.1 | 3
24 | HWSUR, SURGE ANTICIPATOR VALVE NO.2 | 3
25 | HWSUR, SURGE PRESSURE RELIEF VALVE NO.3 | 3
28 | HWSUR, SURGE BUILDING HEADER PRESSURE TRANSMITTER | 2
33 | V2 Control Panel
47 | HWSUR, ISOLATION GATE VALVE NO.1 | 2
48 | HWSUR, ISOLATION GATE VALVE NO.2 | 2
49 | HWSUR, ISOLATION GATE VALVE NO.3 | 2
50 | HWSUR, AIR RELEASE VALVE NO.1 | 2
51 | HWSUR, AIR RELEASE VALVE NO.2 | 2
52 | HWSUR, AIR RELEASE VALVE NO.3 | 2
53 | HWSUR, ISOLATION GATE VALVE NO.4 | 2
54 | HWSUR, AIR RELEASE VALVE NO.4 | 2
55 | HWSUR, BYPASS GATE VALVE NO.1 | 4
56 | HWSUR, DECOMMISSIONED GATE VALVE NO.1 | 5
57 | HWSUR, Valve 1 Process Piping | 3
58 | Sidewalk | 3
59 | Lighting Panel LP-A | 2
60 | Terminal Blocks Panel | 2
61 | Intrinsically Safe Relay | 2
62 | V2 Control Panel
63 | V2 Control Panel | 3
64 | V1 Control Panel | 3
65 | Interior Lighting Fixtures | 3
66 | Emergency Lighting Fixtures | 2
67 | Exterior Lighting Fixture | 2
68 | Unit Heater 1 (Ground Level) | 3
69 | Unit Heater 2 (Lower Level) | 3
70 | Unit Heater (Portable) | 2
71 | Exhaust Fan EF-1 | 2
72 | Roof Drain | 2
73 | Fire Extinguisher | 2
74 | Motorized Louvre and Ducting | 2
75 | Dehumidifier (Portable) | 3
80 | V2 Control Panel
95 | Building Architectural
96 | Process Structural
98 | Building Structural
100 | Clay Brick Walls (1950) | 3
101 | Clay Brick Walls (2000) | 3
102 | Concrete Foundation Walls | 3
103 | Clay Brick Walls (2000) | 2
104 | Coping Stone | 3
105 | Roofing | 3
106 | Windows | 3
108 | Double Steel Door | 3
109 | Interior Clay Brick Walls | 3
110 | Concrete Masonry Bond Beam | 3
111 | Precast Concrete Roof | 3
112 | Concrete Floor Slab | 3
113 | Concrete Floor Beams | 3
114 | Steel Monorail Beam | 3
115 | Steel Platform with Grating | 3
116 | Aluminum Platform with Grating | 3
117 | Steel Floor Beams | 3
118 | Galvanized Steel Floor Grating | 3
119 | Aluminum Ladder | 2
120 | Steel Ladders | 4
121 | Concrete Masonry Infill Wall | 2
122 | Aluminum Hinged Cover | 2
123 | Steel Platform Railings | 4
124 | Aluminum Platform Railings | 2
125 | Ground Floor Steel Railings | 4
126 | Concrete Foundation Walls | 3
127 | Concrete Base Slab | 3
128 | Aluminum Platform with Grating | 2
129 | Aluminum Ladders | 2
130 | Aluminum Platform Railings | 2
131 | Site Civil
132 | Building Electrical
133 | Building Mechanical
135 | Surge Suppression Inlet
136 | Surge Anticipator Valve 1
137 | Surge Anticipator Valve 2
138 | Surge Pressure Relief Valve 3
139 | Surge Suppression Discharge
140 | HWSUR, Discharge Process Piping | 3
142 | HWSUR, Inlet Process Piping | 3
143 | HWSUR, Valve 2 Process Piping | 3
144 | HWSUR, Valve 3 Process Piping | 3
145 | Pressure Supply Header