## Sheet1
AssetID | ClientAssetID0 | ClientAssetID1 | ClientAssetID2 | UniformatL0 | UniformatL1 | UniformatL2 | UniformatL3 | UniformatL4 | UniformatL5 | MasterFormatX | MasterFormatX2 | FlagAsProcess | FlagAsSubProcess | FlagAsAssembly | FlagAsParent | ParentID | AssetName | AssetDescription | Owner | Status | SiteName | FacilityName | LocationName | AssetCategory | CustomClientCategory | AssetType | CustomClientAssetType | Manufacturer | Model | SerialNumber | InspectionType | AssessmentYear | InstallYear | AvgESL | ReplaceYear | PhotoName | DrawingName | VisualCondition | PerformanceCondition | CoF | PoF | RedundancyFactor | CostID | MaterialUnitCost | Quantity | UnitOfQuantity | CostYear | CostSource | MarkupEquipment | MarkupLabour | MarkupAncillary | MarkupRemoval | MarkupEngineering | MarkupAdministration | MarkupContractor | MarkupContingency | TotalReplacementMarkup | LastEditor | LastEditTime | PlannerReviewer | PlannerReviewTime | DisciplineReview | DisciplineReviewTime | PMReview | PMReviewTime | TempProcess | TempSubProcess | TempSubProcessInstance | TempComments1 | TempComments2 | TempComments3 | TempRehabComment | TempRehabYear | TempRehabCost | AssetTagNumber | SizeCapacity | DBNotes | CountCapex | CountOpex | CountComments | CountDrawings | PreventDeletion | PreventEdit
1 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE |  | Rockcliffe WWPS | Site | Hamilton |  | Rockcliffe |  |  | Site Works | Site Civil | [20 empty] | ea. | 2020 | [10 empty] | Andy Gong | 2020-06-17 11:35 | Maira Rafiq | 2020-08-06 14:10 | [6 empty] | 1 | [8 empty] | 1_primary |  |  |  |  | FALSE | FALSE
2 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Site Civil |  | Hamilton |  | Rockcliffe |  |  | Site Works | [21 empty] | ea. | 2020 | [10 empty] | Andy Gong | 2020-06-17 12:30 |  | 2020-06-09 11:28 | [6 empty] | 1 | [8 empty] | 2_primary |  |  |  |  | FALSE | FALSE
3 |  | DC015SLP0100000 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Sewage Lift Pump No.1 | Submersible Pump No.1;ITT;CP3201.180; 140 L/s @ 14m TDH, 28 kW | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Pump | [6 empty] | 2009 |  |  | COH-DC015-0282 |  |  |  | 3 |  |  |  | 137700 | 1 | ea. | 2020 | [9 empty] | 1.3625 | CAMR061927 | 2020-08-11 14:34 | Maira Rafiq | 2020-08-11 14:34 | [6 empty] | 1 | The pumps were assumed to be in good condition based on its age. No performance issues were identified during the inspection. | Good | [6 empty] | 3_primary |  |  |  |  | FALSE | FALSE
4 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | MCC | DC015, MOTOR CONTROL CENTER; Moeller; series 200; ; 4 columns + 40A breaker | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Process Electrical | Process Electrical | Motor Control Center | [6 empty] | 2000 |  | 2030 | COH-DC015-0148 |  |  |  | 3 |  |  |  | 40000 | 1 | ea. | 2020 | [9 empty] | 2 | CAMR061927 | 2020-08-10 10:32 | Maira Rafiq | 2020-08-10 14:18 | [6 empty] | 1 | good | starters and main disconnect switch are priced seperatly | CC: Missing Arc Flash labels | Conduct arc flash study and install arc flash label | 2020 | 10000 |  |  | 4_primary |  |  |  |  | FALSE | FALSE
5 |  | DC015NAC0100000 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | SCADA WAN Panel | WAN Panel, Ethernet Switch; Allen-Bradley Stratix 8000; 1783-MS10T Expansion Module;; | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Process Instrumentation | Process Instrumentation & Control | [7 empty] | 2014 |  |  | COH-DC015-0352 |  |  |  | 3 |  |  |  | 7000 | 1 | ea. | 2020 | [9 empty] | 1.3 | CAMR061927 | 2020-07-09 22:02 | Maira Rafiq | 2020-08-11 18:30 | [6 empty] | 1 | Good | [7 empty] | 5_primary |  |  |  |  | FALSE | FALSE
6 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Process Structural |  | Hamilton |  | Rockcliffe |  |  | Process Structural | Process Structural | [20 empty] | ea. | 2020 | [10 empty] | David Ip | 2020-06-15 15:33 |  | 2020-06-09 11:28 | [6 empty] | 1 | [8 empty] | 6_primary |  |  |  |  | FALSE | FALSE
7 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Unit Heater 1 | Unit Heater; Ouellet; OAS05036; ; 5KW | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Building Mechanical | Building Mechanical | Heating System | [6 empty] | 2007 |  | 2032 | COH-DC015-0305 |  |  |  | 2 |  |  |  | 760 | 1 | ea. | 2020 | [9 empty] | 2.4375 | Patryk Frankiewicz | 2020-07-10 09:10 | Maira Rafiq | 2020-08-11 10:10 | [6 empty] | 1 | CC: There was no containment for diesel fuel lines. TSSA requires all equipment containing or carrying fuel to be contained per CSA B139.1.1-15 Section 6.5.1.4. | Good conditon | [6 empty] | 7_primary |  |  |  |  | FALSE | FALSE
8 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Interior Lighting | Interior Lighting; ; ; ; 6 linear fluorescent | Hamilton | Installed | Rockcliffe |  |  | Building Electrical | Building Electrical | Lighting | [6 empty] | 2000 |  | 2030 | COH-DC015-0189 |  |  |  | 2 |  |  |  | 300 | 6 | ea. | 2020 | [9 empty] | 3.125 | CAMR061927 | 2020-08-10 11:11 | Maira Rafiq | 2020-08-10 14:18 | [6 empty] | 1 | good | replace with LED in next upgrade | [6 empty] | 8_primary |  |  |  |  | FALSE | FALSE
9 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Building Structural |  | Hamilton |  | Rockcliffe |  |  | Building Structural | [21 empty] | ea. | 2020 | [13 empty] | 2020-06-09 11:28 | [6 empty] | 1 | [8 empty] | 9_primary |  |  |  |  | FALSE | FALSE
10 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Building Architectural |  | Hamilton |  | Rockcliffe |  |  | Building Architectural | Building Architectural | [20 empty] | ea. | 2020 | [10 empty] | David Ip | 2020-06-15 15:46 |  | 2020-06-09 11:28 | [6 empty] | 1 | [8 empty] | 10_primary |  |  |  |  | FALSE | FALSE
11 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Emergency Backup Power |  | Hamilton |  | Rockcliffe |  |  | Building Electrical | [15 empty] | 3 | [5 empty] | ea. | 2020 | [13 empty] | 2020-06-09 11:29 | [6 empty] | 1 | [8 empty] | 11_primary |  |  |  |  | FALSE | FALSE
14 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 11 | Diesel Fuel Tank #1 For Generator | DC015, DIESEL FUEL TANK #1 FOR GENERATOR; DTE; Capacity 1135 Lr | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Building Mechanical |  |  |  | NA |  | 7522 C |  |  | 1992 |  | 2040 | COH-DC015-0313 |  |  |  | 3 |  |  |  | 15000 | 1 | ea. | 2020 | [9 empty] | 1.5 | CAMR061927 | 2020-08-11 10:06 | Maira Rafiq | 2020-08-11 10:10 | [6 empty] | 1 | Tanks appear to be in good condition | CC: There was no containment for diesel fuel lines. TSSA requires all equipment containing or carrying fuel to be contained per CSA B139.1.1-15 Section 6.5.1.4. | [6 empty] | 14_primary |  |  |  |  | FALSE | FALSE
15 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 11 | Diesel Fuel Tank #2 For Generator | DC015, DIESEL FUEL TANK #2 FOR GENERATOR; DTE; Capacity 1135 Lr | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Building Mechanical |  |  |  | NA |  | 7519 C |  |  | 1992 |  | 2040 | COH-DC015-0313 |  |  |  | 3 |  |  |  | 0 | 1 | ea. | 2020 | [9 empty] | 1.5 | CAMR061927 | 2020-08-11 10:06 | Maira Rafiq | 2020-08-11 10:11 | [6 empty] | 1 | Tanks appear to be in good condition | CC: There was no containment for diesel fuel lines. TSSA requires all equipment containing or carrying | [6 empty] | 15_primary |  |  |  |  | FALSE | FALSE
17 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  |  | DC015, BUILDING TEMP CONTROL | Hamilton | Withdrawn | Rockcliffe |  |  | Building Mechanical |  |  |  | HONEYWELL | T136A |  |  |  | 1912 | [12 empty] | ea. | 2020 | [20 empty] | 1 | [8 empty] | 17_primary |  |  |  |  | FALSE | FALSE
18 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  |  | DC015, WET WELL LEVEL TRANSMITTER | Hamilton | Withdrawn | Rockcliffe |  |  | Process Instrumentation |  |  |  | MILLTRONICS | MULTIRANGER | n/a |  |  | 1912 | [12 empty] | ea. | 2020 | [20 empty] | 1 | [8 empty] | 18_primary |  |  |  |  | FALSE | FALSE
20 |  | DC015GEN0100000 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  | Standby Diesel Power Generator | DC015, DIESEL STANDBY POWER GENERATOR; KLOCKNERMOELLER;SERIES 200; CDN/16/94-5513 | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Process Electrical | Process Electrical |  |  | KOHLER | 150R0ZJ91 | 359253 |  |  | 1992 | [6 empty] | 3 |  |  |  | 100000 | 1 | ea. | 2020 | [9 empty] | 2 | CAMR061927 | 2020-08-11 16:59 | Maira Rafiq | 2020-08-11 17:00 | [6 empty] | 1 | good | [7 empty] | 20_primary |  |  |  |  | FALSE | FALSE
22 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  |  | DC015, GES MONITOR | Hamilton | Withdrawn | Rockcliffe |  |  | Process Instrumentation |  |  |  | MSA | 5100 | 94BM159037 |  |  | 1912 | [12 empty] | ea. | 2020 | [20 empty] | 1 | [8 empty] | 22_primary |  |  |  |  | FALSE | FALSE
24 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  |  | DC015, LIGHTING SYSTEM | Hamilton | Installed | Rockcliffe |  |  | Building Electrical | Building Electrical | [7 empty] | 1912 | [12 empty] | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-10 16:05 | [6 empty] | 1 | [8 empty] | 24_primary |  |  |  |  | FALSE | FALSE
25 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  |  | DC015, PLC PANEL | Hamilton | Withdrawn | Rockcliffe |  |  | Process Instrumentation |  |  |  | NA | N12-483620 | NA |  |  | 2000 | [12 empty] | ea. | 2020 | [20 empty] | 1 | [8 empty] | 25_primary |  |  |  |  | FALSE | FALSE
26 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  |  | DC015, PLC | Hamilton | Withdrawn | Rockcliffe |  |  | Process Instrumentation |  |  |  | BRISTOLBABCOCK | 3330 10A 120000 | 94A11064 |  |  | 2000 | [12 empty] | ea. | 2020 | [20 empty] | 1 | [8 empty] | 26_primary |  |  |  |  | FALSE | FALSE
27 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  |  | DC015, PLC PANEL UPS | Hamilton | Withdrawn | Rockcliffe |  |  | Process Instrumentation |  |  |  | APC | BK500M | PB9923112887 |  |  | 2000 | [12 empty] | ea. | 2020 | [20 empty] | 1 | [8 empty] | 27_primary |  |  |  |  | FALSE | FALSE
30 |  | DC015WWL01LIT01 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 5 | Wet Well Level Transmitter #1 | DC015, WET WELL LEVEL TRANSMITTER #1; SIEMENS; MULTIRANGER 100 | Hamilton | Installed | Rockcliffe | Main Building | Washroom | Process Instrumentation |  |  |  | SIEMENS | MULTIRANGER 100 |  |  |  | 2016 | [6 empty] | 2 |  |  |  | 2500 | 1 | ea. | 2020 | [9 empty] | 1.8 | CAMR061927 | 2020-08-11 17:12 | Maira Rafiq | 2020-08-11 17:12 | [6 empty] | 1 | Very good | [7 empty] | 30_primary |  |  |  |  | FALSE | FALSE
31 |  | DC015WWL02LIT01 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 5 | Wet Well Level Transmitter #2 | DC015, WET WELL LEVEL TRANSMITTER #2 SIEMENS; MULTIRANGER 100 | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Process Instrumentation |  |  |  | SIEMENS | MULTIRANGER 100 |  |  |  | 2016 | [6 empty] | 2 |  |  |  | 2500 | 1 | ea. | 2020 | [9 empty] | 1.8 | CAMR061927 | 2020-08-11 17:12 | Maira Rafiq | 2020-08-11 17:12 | [6 empty] | 1 | Very Good | [7 empty] | 31_primary |  |  |  |  | FALSE | FALSE
32 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Power Meter | Power meter; Moeller; ; ; | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Process Electrical | Process Electrical | Metering | [6 empty] | 2000 |  | 2030 | COH-DC015-0153 |  |  |  | 3 |  |  |  | 11000 | 1 | ea. | 2020 | [9 empty] | 2 | Amin Norouzizadeh | 2020-07-13 12:55 | Maira Rafiq | 2020-08-10 14:20 | [6 empty] | 1 | good | [7 empty] | 32_primary |  |  |  |  | FALSE | FALSE
33 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Main Breaker | DC015, MAIN BREAKER; KLOCKNERMOELLER; MZN9-250; NZM9-250/2M9A-200;600V, 200A | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Process Electrical | Process Electrical | Main Switch | [6 empty] | 2000 |  | 2030 | COH-DC015-0152 |  |  |  | 3 |  |  |  | 3800 | 1 | ea. | 2020 | [9 empty] | 3.125 | CAMR061927 | 2020-08-10 10:33 | Maira Rafiq | 2020-08-11 16:58 | [6 empty] | 1 | Good | CC: Missing Arc Flash labels |  | Conduct arc flash study and install arc flash label | 2020 | 0 |  |  | 33_primary |  |  |  |  | FALSE | FALSE
34 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Power Factor Capacitors | Power Factor capacitos; Powerspec; ; ; 3x 600V, 15kVAr | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Process Electrical | Process Electrical | Power Factor Correction Capacitor | [6 empty] | 2013 |  | 2043 | COH-DC015-0154 |  |  |  | 2 |  |  |  | 10000 | 3 | ea. | 2020 | [9 empty] | 1.5 | Amin Norouzizadeh | 2020-07-13 12:56 | Maira Rafiq | 2020-08-10 14:20 | [6 empty] | 1 | Good | [7 empty] | 34_primary |  |  |  |  | FALSE | FALSE
35 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Unit Heater Starter | Unit Heater starter and disconnect; ; ; ; 600V, size 1 | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Electrical | Building Electrical | Starter | [6 empty] | 2000 |  | 2030 | COH-DC015-0156 |  |  |  | 2 |  |  |  | 2600 | 1 | ea. | 2020 | [9 empty] | 1.7 | CAMR061927 | 2020-08-10 11:12 | Maira Rafiq | 2020-08-10 11:46 | [6 empty] | 1 | good | CC: Missing Arc Flash labels |  | Conduct arc flash study and install arc flash label | 2020 | 0 |  |  | 35_primary |  |  |  |  | FALSE | FALSE
36 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | Hand Stop Gate No.2 | Hand Stop Gate No.2;;;;36"X 36" | Hamilton | Not In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Gate | [6 empty] | 1992 |  |  | COH-DC015-0236 |  |  |  | 2 |  |  |  | 6080 | 1 | ea. | 2020 | [9 empty] | 1.85 | Adrian Li | 2020-06-17 16:23 | [8 empty] | 1 | Poor | The gate was at three quarter of its expected life and deterioration was observed. | [6 empty] | 36_merge |  |  |  |  | FALSE | FALSE
37 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | Hand Stop Gate No.3 | Hand Stop Gate No.3;;;;36"X36" | Hamilton | Not In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Gate | [6 empty] | 1992 |  |  | COH-DC015-0236 |  |  |  | 2 |  |  |  | 6080 | 1 | ea. | 2020 | [9 empty] | 1.85 | Adrian Li | 2020-06-18 14:14 | [8 empty] | 1 | Poor | The gate was at three quarter of its expected life and deterioration was observed. | [6 empty] | 37_merge |  |  |  |  | FALSE | FALSE
38 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | Manual Bar Screen No.1 | Manual Bar Screen No.1;;;;24"X 48" | Hamilton | Obsolete and Not in Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Screen | [6 empty] | 1992 |  |  | COH-DC015-0223 |  |  |  | 2 |  |  |  | 9000 | 1 | ea. | 2020 | [9 empty] | 1.4 | CAMR061927 | 2020-07-10 10:43 | Maira Rafiq | 2020-08-11 14:23 | [6 empty] | 1 | Very Poor | Detrioration observed. Some of the bars were bent. | The operators mentioned that the screens have been removed and are no longer in use. | [5 empty] | 38_merge |  |  |  |  | FALSE | FALSE
39 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | Manual Bar Screen No.2 | Manual Bar Screen No.2;;;;24"X 48" | Hamilton | Obsolete and Not in Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Screen | [6 empty] | 1992 |  |  | COH-DC015-0223 |  |  |  | 2 |  |  |  | 9000 | 1 | ea. | 2020 | [9 empty] | 1.4 | CAMR061927 | 2020-07-10 10:43 | Maira Rafiq | 2020-08-11 14:24 | [6 empty] | 1 | Very Poor | Detrioration observed. Some of the bars were bent. | The operators mentioned that the screens have been removed and are no longer in use. | [5 empty] | 39_merge |  |  |  |  | FALSE | FALSE
40 |  | DC015SLP01CV001 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | Sewage Lift Pump No.1 Check Valve | Check Valve No.1;;;;200mm | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Valves | [6 empty] | 1992 |  |  | COH-DC015-0230 |  |  |  | 2 |  |  |  | 1990 | 1 | ea. | 2020 | [9 empty] | 2.5 | Adrian Li | 2020-06-17 17:06 | Maira Rafiq | 2020-08-11 14:24 | [6 empty] | 1 | Very Poor | Heavy corrosion and deterioration | [6 empty] | 40_merge |  |  |  |  | FALSE | FALSE
41 |  | DC015SLP02CV001 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | Sewage Lift Pump No.2 Check Valve | Check Valve No.2;;;;200mm | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Valves | [6 empty] | 1992 |  |  | COH-DC015-0244 |  |  |  | 2 |  |  |  | 1990 | 1 | ea. | 2020 | [9 empty] | 2.5 | Adrian Li | 2020-06-17 17:06 | Maira Rafiq | 2020-08-11 14:27 | [6 empty] | 1 | Very Poor | Heavy corrosion and deterioration | [6 empty] | 41_merge |  |  |  |  | FALSE | FALSE
42 |  | DC015SLP03CV001 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | Sewage Lift Pump No.3 Check Valve | Check Valve No.3;;;;200mm | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Valves | [6 empty] | 1992 |  |  | COH-DC015-0241 |  |  |  | 2 |  |  |  | 1990 | 1 | ea. | 2020 | [9 empty] | 2.5 | Adrian Li | 2020-06-17 17:37 | Maira Rafiq | 2020-08-11 14:27 | [6 empty] | 1 | Very Poor | Heavy corrosion and Deterioration | [6 empty] | 42_merge |  |  |  |  | FALSE | FALSE
43 |  | DC015SLP01DV001 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | Sewage Lift Pump No.1 Discharge Valve | Gate Valve No.1;;;;200mm | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Valves | [6 empty] | 1992 |  |  | COH-DC015-0230 |  |  |  | 2 |  |  |  | 1520 | 1 | ea. | 2020 | [9 empty] | 2.5 | Adrian Li | 2020-06-17 17:42 | Maira Rafiq | 2020-08-11 14:27 | [6 empty] | 1 | Very Poor | Heavy corrosion and deterioration | [6 empty] | 43_merge |  |  |  |  | FALSE | FALSE
44 |  | DC015SLP02DV001 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | Sewage Lift Pump No.2 Discharge Valve | Gate Valve No.2;;;;200mm | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Valves | [6 empty] | 1992 |  |  | COH-DC015-0233 |  |  |  | 2 |  |  |  | 1520 | 1 | ea. | 2020 | [9 empty] | 2.5 | Adrian Li | 2020-06-17 17:42 | Maira Rafiq | 2020-08-11 10:17 | [6 empty] | 1 | Very Poor | Heavy corrosion and Deterioration | [6 empty] | 44_merge |  |  |  |  | FALSE | FALSE
45 |  | DC015SLP03DV00 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | Sewage Lift Pump No.3 Discharge Valve | Gate Valve No.3;;;;200mm | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Valves | [6 empty] | 1992 |  |  | COH-DC015-0241 |  |  |  | 2 |  |  |  | 1520 | 1 | ea. | 2020 | [9 empty] | 2.5 | Adrian Li | 2020-06-17 18:34 | Maira Rafiq | 2020-08-11 14:27 | [6 empty] | 1 | Very Poor | Heavy corrosion and Deterioration | [6 empty] | 45_merge |  |  |  |  | FALSE | FALSE
46 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | Discharge Header Gate Valve | Gate Valve No.4;;;;300mm | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Valves | [6 empty] | 1992 |  |  | COH-DC015-0245 |  |  |  | 3 |  |  |  | 2790 | 1 | ea. | 2020 | [9 empty] | 2.5 | Adrian Li | 2020-06-18 11:32 | Maira Rafiq | 2020-08-11 14:27 | [6 empty] | 1 | Very Poor | Turn wheel is missing. Heavy corrosion and deterioration. | [6 empty] | 46_merge |  |  |  |  | FALSE | FALSE
47 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | Drain Gate Valve | Drain Gate Valve;;;;100mm | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Valves | [6 empty] | 1992 |  |  | COH-DC015-0254 |  |  |  | 2 |  |  |  | 630 | 1 | ea. | 2020 | [9 empty] | 2.5 | Adrian Li | 2020-06-18 12:37 | Maira Rafiq | 2020-08-11 14:28 | [6 empty] | 1 | Very Poor | Heavy corrosion and deterioratino | [6 empty] | 47_merge |  |  |  |  | FALSE | FALSE
48 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | Pressure Release Valve No.1 | Pressure Release Valve No.1;;;;100mm | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Valves | [6 empty] | 1992 |  |  | COH-DC015-0255 |  |  |  | 2 |  |  |  | 2280 | 1 | ea. | 2020 | [9 empty] | 2.5 | Adrian Li | 2020-06-18 15:14 | Maira Rafiq | 2020-08-11 14:28 | [6 empty] | 1 | Very Poor | Heavy corrosion and Deterioration | [6 empty] | 48_merge |  |  |  |  | FALSE | FALSE
49 |  | DC015WWL00IG001 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | Wetwell Cell Isolation Gate | Wetwell Cell Isolation Gate;;;;300mm | Hamilton | In Service | Rockcliffe | Site |  | Process Mechanical | Process Mechanical Piping and Equipment | Valves | [6 empty] | 1992 |  |  | COH-DC015-0102 |  |  |  | 3 |  |  |  | 2790 | 1 | ea. | 2020 | [9 empty] | 2.5 | Adrian Li | 2020-06-18 13:16 | Maira Rafiq | 2020-08-11 14:28 | [6 empty] | 1 | Poor | The valve was over three quarters of its expected service life. Moderate surface corrosion was observed | [6 empty] | 49_merge |  |  |  |  | FALSE | FALSE
50 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | Sluice Gate No.1 | Sluice Gate No.1;;;;900mm | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Gate | [6 empty] | 1992 |  |  | COH-DC-15-0263 |  |  |  | 2 |  |  |  | 25340 | 1 | ea. | 2020 | [9 empty] | 1.85 | Adrian Li | 2020-06-18 14:17 | Maira Rafiq | 2020-08-11 14:29 | [6 empty] | 1 | Poor | Heavy corrosion and deterioration was observed on the frame of the sluice gate | [6 empty] | 51_merge |  |  |  |  | FALSE | FALSE
51 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | Process Mechanical Piping | Process Mechanical Piping;;;; 7.5 m of 100 mm dia DI pipe, 16.5 m of 200 mm dia DI pipe, 16.5 m of 300 mm DI pipe | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Piping | [6 empty] | 1992 |  |  | COH-DC015-0206 |  |  |  | 3 |  |  |  | 142 | 8 | ea. | 2020 | [9 empty] | 1.6 | Adrian Li | 2020-06-18 14:48 | Maira Rafiq | 2020-08-11 14:29 | [6 empty] | 1 | Very Poor | Heavy corrosion and deterioration was observed on majority portion of the piping. | [6 empty] | 52_merge |  |  |  |  | FALSE | FALSE
52 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | Forcemain | Process Mechanical Piping;;;; 7.5 m of 100 mm dia DI pipe, 16.5 m of 200 mm dia DI pipe, 16.5 m of 300 mm DI pipe | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Piping | [6 empty] | 1992 |  |  | COH-DC015-0206 |  |  |  | 4 | [5 empty] | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-07-10 09:34 | [6 empty] | 1 | [8 empty] | 53_merge |  |  |  |  | FALSE | FALSE
53 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  | SCADA PANEL | PLC controller c/w all IO cards, internal wiring, PLC software programp, panel enclosure and all associated components; Allen-Bradley; 1969-L33ER, 1769-PA4, 1769-IF4I, 1769-OF4CI, 1769-IQ16; 1769-OW16, 1769-ECR; ; ; | Hamilton |  | Rockcliffe | Main Building | Generator Room | Process Instrumentation | Process Instrumentation & Control | PLC | [6 empty] | 2013 |  |  | COH-DC015-0364 |  |  |  | 3 |  |  |  | 40000 | 1 | ea. | 2020 | [9 empty] | 1 | Alex Wang | 2020-06-29 14:43 | Maira Rafiq | 2020-08-10 16:07 | [6 empty] | 1 | Good | [7 empty] | 36_merge |  |  |  |  | FALSE | FALSE
54 |  | Station Temperature Transmitter |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  | Station Temperature Transmitter | Temperature Transmitter; Pribusin: TWTS-2; ; ; | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Process Instrumentation | Process Instrumentation & Control | Transmitter | [6 empty] | 2014 |  |  | COH-DC015-0408 |  |  |  | 2 |  |  |  | 800 | 1 | ea. | 2020 | [9 empty] | 1.3 | Alex Wang | 2020-06-29 14:41 | Maira Rafiq | 2020-08-11 17:24 | [6 empty] | 1 | Good | Communication via Pribusin transmitter is old technology and will be obselete in near future. It is recommended tp replace the temperature trasmitter with a cellular transmitter or a hardwired signal from the temperature device to directly connected to th | [6 empty] | 37_merge |  |  |  |  | FALSE | FALSE
55 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  | UPS | UPS; Eaton Powerware; PW9130L2000T-XL; ; ; | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Process Instrumentation | Process Instrumentation & Control | Miscellaneous Instrumentation | [6 empty] | 2014 |  |  | COH-DC015-0366 |  |  |  | 2 |  |  |  | 3000 | 1 | ea. | 2020 | [9 empty] | 1.2 | Alex Wang | 2020-06-29 14:39 | Maira Rafiq | 2020-08-10 16:10 | [6 empty] | 1 | good | Dust | [6 empty] | 38_merge |  |  |  |  | FALSE | FALSE
56 |  | DC015WWL01LSH01 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  | Wetwell 1 High Level Float | Wetwell No.1 High Level Float; ; ; ; | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Instrumentation | Process Instrumentation & Control | [7 empty] | 2016 |  |  | COH-DC015-0269 |  |  |  | 2 |  |  |  | 500 | 1 | ea. | 2020 | [9 empty] | 1.3 | CAMR061927 | 2020-07-09 22:13 | Maira Rafiq | 2020-07-09 22:32 | [6 empty] | 1 | Good | [7 empty] | 40_merge |  |  |  |  | FALSE | FALSE
57 |  | DC015WWL02LSH01 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  | Wetwell 2 High Level Float | Wetwell No.2 High Level Float; ; ; ; | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Instrumentation | Process Instrumentation & Control | [7 empty] | 2016 |  |  | COH-DC015-0269 |  |  |  | 2 |  |  |  | 500 | 1 | ea. | 2020 | [9 empty] | 1.3 | CAMR061927 | 2020-07-09 22:13 | Maira Rafiq | 2020-07-09 22:32 | [6 empty] | 1 | Good | [7 empty] | 41_merge |  |  |  |  | FALSE | FALSE
58 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Pump 1 VFD | VFD with filter; ; ; ; 600V, size 2 | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Process Electrical | Process Electrical | Starter | [6 empty] | 2000 |  | 2030 | COH-DC015-0157 |  |  |  | 2 |  |  |  | 19000 | 1 | ea. | 2020 | [9 empty] | 1.7 | CAMR061927 | 2020-08-10 10:35 | Maira Rafiq | 2020-08-10 10:35 | [6 empty] | 1 | good | CC: Missing Arc Flash labels |  | Conduct arc flash study and install arc flash label | 2020 | 0 |  |  | 36_merge |  |  |  |  | FALSE | FALSE
59 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Wet well Fan Starter | starter and disconnect; ; ; ; 600V, size 1 | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Electrical | Building Electrical | Starter | [6 empty] | 2000 |  | 2030 | COH-DC015-0162 |  |  |  | 2 |  |  |  | 2500 | 1 | ea. | 2020 | [9 empty] | 1.7 | CAMR061927 | 2020-08-10 11:46 | Maira Rafiq | 2020-08-10 11:46 | [6 empty] | 1 | good | CC: Missing Arc Flash labels |  | Conduct arc flash study and install arc flash label | 2020 | 0 |  |  | 37_merge |  |  |  |  | FALSE | FALSE
60 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Diesel Generator Room Fan Starter | starter and disconnect; ; ; ; 600V, size 1 | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Electrical | Building Electrical | Starter | [6 empty] | 2000 |  | 2030 | COH-DC015-0163 |  |  |  | 2 |  |  |  | 2500 | 1 | ea. | 2020 | [9 empty] | 1.7 | CAMR061927 | 2020-08-10 11:45 | Maira Rafiq | 2020-08-10 14:38 | [6 empty] | 1 | good | CC: Missing Arc Flash labels |  | Conduct arc flash study and install arc flash label | 2020 | 0 |  |  | 38_merge |  |  |  |  | FALSE | FALSE
61 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Pump 2 VFD | VFD with filter; ; ; ; 600V, size 2 | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Process Electrical | Process Electrical | Starter | [6 empty] | 2000 |  | 2030 | COH-DC015-0164 |  |  |  | 2 |  |  |  | 19000 | 1 | ea. | 2020 | [9 empty] | 1.7 | CAMR061927 | 2020-08-10 10:35 | Maira Rafiq | 2020-08-10 10:35 | [6 empty] | 1 | good | CC: Missing Arc Flash labels |  | Conduct arc flash study and install arc flash label | 2020 | 0 |  |  | 39_merge |  |  |  |  | FALSE | FALSE
62 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Pump 3 VFD | VFD with filter; ; ; ; 600V, size 2 | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Process Electrical | Process Electrical | Starter | [6 empty] | 2000 |  | 2030 | COH-DC015-0170 |  |  |  | 2 |  |  |  | 19000 | 1 | ea. | 2020 | [9 empty] | 1.7 | CAMR061927 | 2020-08-10 10:35 | Maira Rafiq | 2020-08-10 10:35 | [6 empty] | 1 | good | CC: Missing Arc Flash labels |  | Conduct arc flash study and install arc flash label | 2020 | 0 |  |  | 40_merge |  |  |  |  | FALSE | FALSE
63 |  | DC015ATS0100000 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Diesel Generator Control Panel | Genreator panel with ATS ; ; ; ; 600V, 200A, 150kW | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Building Electrical | Emergency Backup Power | Standby Power Source | [6 empty] | 1992 |  | 2030 | COH-DC015-0170 |  |  |  | 3 |  |  |  | 30000 | 1 | ea. | 2020 | [9 empty] | 2.25 | CAMR061927 | 2020-08-10 11:45 | Maira Rafiq | 2020-08-10 14:21 | [6 empty] | 1 | good | CC: Missing Arc Flash labels |  | Conduct arc flash study and install arc flash label | 2020 | 0 |  |  | 41_merge |  |  |  |  | FALSE | FALSE
64 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Emergency Lighting | Battery Unit ; ; ; ; | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Electrical | Building Electrical | Emergency Lighting | [6 empty] | 2016 |  | 2043 | COH-DC015-0130 |  |  |  | 2 |  |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 1.5 | Amin Norouzizadeh | 2020-07-13 12:26 | Maira Rafiq | 2020-08-10 14:33 | [6 empty] | 1 | good | [7 empty] | 42_merge |  |  |  |  | FALSE | FALSE
65 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Lighting Panel LPA | DC015, BREAKER PANEL; Square D; NQOB; ;120/208V, 225A, | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Electrical | Building Electrical | Panelboard | [6 empty] | 2000 |  | 2030 | COH-DC015-0134 |  |  |  | 3 |  |  |  | 2000 | 1 | ea. | 2020 | [9 empty] | 3.125 | Amin Norouzizadeh | 2020-07-13 12:59 | Maira Rafiq | 2020-08-11 17:01 | [6 empty] | 1 | good | [7 empty] | 43_merge |  |  |  |  | FALSE | FALSE
66 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Lighting Trasnformer | Transformer; Square D; 33360-17112-006 ; 00J055160;600-120/208V, 30kVAr | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Electrical | Building Electrical | Distribution Transformer | [6 empty] | 1992 |  | 2030 | COH-DC015-0143 |  |  |  | 3 |  |  |  | 5100 | 1 | ea. | 2020 | [9 empty] | 3.125 | Amin Norouzizadeh | 2020-07-13 12:59 | Maira Rafiq | 2020-08-10 11:50 | [6 empty] | 1 | good | [7 empty] | 44_merge |  |  |  |  | FALSE | FALSE
67 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Exterior Lighting | Lighting; ; ; ; 1 flood light | Hamilton | In Service | Rockcliffe | Site |  | Building Electrical | Building Electrical | Lighting | [6 empty] | 2013 |  | 2030 | COH-DC015-0190 |  |  |  | 2 |  |  |  | 300 | 1 | ea. | 2020 | [9 empty] | 3.125 | Amin Norouzizadeh | 2020-07-13 12:59 | Maira Rafiq | 2020-08-10 14:29 | [6 empty] | 1 | good | [7 empty] | 45_merge |  |  |  |  | FALSE | FALSE
68 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Wet Well Lighting | Lighting; ; ; ; 3 flood light, class 1, div 1 | Hamilton | In Service | Rockcliffe | Wet Well |  | Building Electrical | Building Electrical | Lighting | [6 empty] | 2000 |  | 2025 | COH-DC015-0196 |  |  |  | 2 |  |  |  | 700 | 3 | ea. | 2020 | [9 empty] | 3.125 | CAMR061927 | 2020-08-10 11:44 | Maira Rafiq | 2020-08-10 11:44 | [6 empty] | 1 | fair | corroded | to be replaced with class 1, div 1 fixture | to be repalced with classified ficture | 0 | 0 |  |  | 46_merge |  |  |  |  | FALSE | FALSE
69 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  | Main Transformer | Main Trasnformer; ABB; ; ; 27.6kV-600V, 750KVA | Hamilton | In Service |  |  |  | Process Electrical |  | Power Transformer | [6 empty] | 2000 |  | 2030 | COH-DC015-0200 |  |  |  | 3 |  |  |  | 57000 | 1 | ea. | 2020 | [9 empty] | 2.25 | Amin Norouzizadeh | 2020-07-13 13:01 | [8 empty] | 1 | good | [7 empty] | 47_merge |  |  |  |  | FALSE | FALSE
73 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 2 | Signboards | City of Hamilton Signboards throughout the site (total of two) | Hamilton | In Service | Rockcliffe | Site |  | Site Works | Site Civil | Signboard | [6 empty] | 1992 |  |  | COH-DC015-0425 |  |  |  | 1 |  |  |  | 60 | 2 | ea. | 2020 | [9 empty] | 3.1875 | CAMR061927 | 2020-07-06 09:58 | Maira Rafiq | 2020-08-07 13:47 | [6 empty] | 1 | Good condition. Dirt on the signboard was observed |  |  | Cleaning | 2020 | 0 |  |  | 40_merge |  |  |  |  | FALSE | FALSE
75 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 2 | Station Access Road | Gravel Access Road to the Station | Hamilton | In Service | Rockcliffe | Site |  | Site Works | Site Civil | Road | [6 empty] | 1992 |  |  | COH-DC015-0529 |  |  |  | 1 |  |  |  | 55 | 30 | ea. | 2020 | [9 empty] | 1.25 | CAMR061927 | 2020-07-06 07:58 | Maira Rafiq | 2020-08-06 14:42 | [6 empty] | 1 | The access road was in fair condition. Pot holes and mud bumps were obserevd. | [7 empty] | 43_merge |  |  |  |  | FALSE | FALSE
76 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 2 | Sanitary Sewer | Sanitary Sewer Yard Piping, Approximate Length: 21 meters, Pipe Dia: 450mm, unknown material and installation year. Assumed to be reinformed concrete pipe installed in 1992 | Hamilton | In Service | Rockcliffe | Site |  | Site Works | Site Civil | Piping | [6 empty] | 1992 |  | 2072 |  |  |  |  | 3 |  |  |  | 80 | 21 | ea. | 2020 | [9 empty] | 10.7 | Andy Gong | 2020-06-17 14:03 | Maira Rafiq | 2020-08-06 14:42 | [6 empty] | 1 | The sanitary sewer piping was assumed to be in good condition bassed on age. | [7 empty] | 44_merge |  |  |  |  | FALSE | FALSE
77 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Aluminum Ladder | Aluminum ladder from lower platform to wet well | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0030 |  |  |  | 2 |  |  |  | 2500 | 1 | ea. | 2020 | [9 empty] | 1.5 | CAMR061927 | 2020-07-13 08:49 | Maira Rafiq | 2020-07-13 08:49 | [6 empty] | 1 | fair | buildup of calcium and minor pitting |  | Calcium buildup and minor pitting | 0 | 0 |  |  | 36_merge |  |  |  |  | FALSE | FALSE
78 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Aluminum Guardrail | Aluminum guardrails at lower platform level | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0008 |  |  |  | 2 |  |  |  | 200 | 20 | ea. | 2020 | [9 empty] | 2 | CAMR061927 | 2020-07-13 08:50 | Maira Rafiq | 2020-07-13 08:50 | [6 empty] | 1 | fair | buildup of calcium and minor pitting | [6 empty] | 37_merge |  |  |  |  | FALSE | FALSE
79 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Aluminum Grating | Aluminum grating at lower platform level | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0026 |  |  |  | 2 |  |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 1 | CAMR061927 | 2020-07-13 08:53 | Maira Rafiq | 2020-07-13 08:53 | [6 empty] | 1 | fair | buildup of calcium and minor pitting | HS: One section of grating was missing and should be installed/replaced | Install missing grating | 2021 | 1000 |  |  | 38_merge |  |  |  |  | FALSE | FALSE
80 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Access Hatch | Aluminum access hatch at grade level | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0067 |  |  |  | 2 |  |  |  | 5000 | 1 | ea. | 2020 | [9 empty] | 1 | David Ip | 2020-06-15 22:25 | Maira Rafiq | 2020-07-13 08:53 | [6 empty] | 1 | good | [7 empty] | 39_merge |  |  |  |  | FALSE | FALSE
81 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Pump Hatch 1 | Aluminum pump hatch at grade level | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0063 |  |  |  | 2 |  |  |  | 5000 | 1 | ea. | 2020 | [9 empty] | 1 | CAMR061927 | 2020-07-13 08:54 | Maira Rafiq | 2020-07-13 08:54 | [6 empty] | 1 | good | HS: retrofit of safety grating underneath the pump hatch is recommended to mitgate a falling hazard when hatch is open |  | Install safety grate | 2021 | 1000 |  |  | 40_merge |  |  |  |  | FALSE | FALSE
82 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Pump Hatch 2 | Aluminum pump hatch at grade level | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0063 |  |  |  | 2 |  |  |  | 6500 | 1 | ea. | 2020 | [9 empty] | 1 | CAMR061927 | 2020-07-13 08:55 | Maira Rafiq | 2020-07-13 08:55 | [6 empty] | 1 | good | retrofit of safety grating underneath the pump hatch is recommended to mitgate a falling hazard when hatch is open |  | Install safety grate | 2021 | 1000 |  |  | 41_merge |  |  |  |  | FALSE | FALSE
83 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Pump Hatch 3 | Aluminum pump hatch at grade level | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0065 |  |  |  | 2 |  |  |  | 6500 | 1 | ea. | 2020 | [9 empty] | 2 | CAMR061927 | 2020-07-13 08:55 | Maira Rafiq | 2020-07-13 08:55 | [6 empty] | 1 | good | retrofit of safety grating underneath the pump hatch is recommended to mitgate a falling hazard when hatch is open |  | Install safety grate | 2021 | 1000 |  |  | 42_merge |  |  |  |  | FALSE | FALSE
84 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Pump Hatch 4 | Aluminum pump hatch at grade level | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0065 |  |  |  | 2 |  |  |  | 6500 | 1 | ea. | 2020 | [9 empty] | 1 | CAMR061927 | 2020-07-13 11:05 | Maira Rafiq | 2020-07-13 11:05 | [6 empty] | 1 | good | retrofit of safety grating underneath the pump hatch is recommended to mitgate a falling hazard when hatch is open |  | Install safety grate | 0 | 0 |  |  | 43_merge |  |  |  |  | FALSE | FALSE
85 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Davit Base 1 | Safety davit base at grade level | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0067 |  |  |  | 2 |  |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 2 | David Ip | 2020-06-15 22:26 | Maira Rafiq | 2020-07-13 11:05 | [6 empty] | 1 | good | [7 empty] | 44_merge |  |  |  |  | FALSE | FALSE
86 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Davit Base 2 | Safety davit base at grade level | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0063 |  |  |  | 2 |  |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 2 | CAMR061927 | 2020-07-13 11:06 | Maira Rafiq | 2020-07-13 11:06 | [6 empty] | 1 | good | Missing cap |  | Install cap | 2020 | 100 |  |  | 45_merge |  |  |  |  | FALSE | FALSE
87 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Inlet Chamber 1 Concrete Structure | Reinforced concrete inlet chamber | Hamilton | In Service | Rockcliffe | Site | Inlet Chamber 1 | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0095 |  |  |  | 1 |  |  |  | 35000 | 1 | ea. | 2020 | [9 empty] | 2 | David Ip | 2020-06-15 22:27 | Maira Rafiq | 2020-07-13 11:24 | [6 empty] | 1 | good | [7 empty] | 46_merge |  |  |  |  | FALSE | FALSE
88 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Inlet Chamber 1 Aluminum Platform | Aluminum platform | Hamilton | In Service | Rockcliffe | Site | Inlet Chamber 1 | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0095 |  |  |  | 1 |  |  |  | 3000 | 1 | ea. | 2020 | [9 empty] | 2 | David Ip | 2020-06-15 22:28 | Maira Rafiq | 2020-07-13 11:24 | [6 empty] | 1 | good | [7 empty] | 47_merge |  |  |  |  | FALSE | FALSE
89 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Inlet Chamber 1 Aluminum Ladder | Aluminum Ladder | Hamilton | In Service | Rockcliffe | Site | Inlet Chamber 1 | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0095 |  |  |  | 1 |  |  |  | 5500 | 1 | ea. | 2020 | [9 empty] | 2 | CAMR061927 | 2020-07-13 11:08 | Maira Rafiq | 2020-07-13 11:24 | [6 empty] | 1 | good | [7 empty] | 48_merge |  |  |  |  | FALSE | FALSE
90 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Inlet Chamber 1 Manhole Frame and Cover | Manhole frame and cover | Hamilton | In Service | Rockcliffe | Site | Inlet Chamber 1 | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0093 |  |  |  | 1 |  |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 2 | David Ip | 2020-06-15 22:28 | Maira Rafiq | 2020-07-13 11:25 | [6 empty] | 1 | good | [7 empty] | 49_merge |  |  |  |  | FALSE | FALSE
91 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Inlet Chamber 2 Concrete Structure | Reinforced concrete inlet chamber | Hamilton | In Service | Rockcliffe | Site | Inlet Chamber 2 | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0100 |  |  |  | 1 |  |  |  | 35000 | 1 | ea. | 2020 | [9 empty] | 2 | David Ip | 2020-06-15 22:27 | Maira Rafiq | 2020-07-13 11:25 | [6 empty] | 1 | good | [7 empty] | 50_merge |  |  |  |  | FALSE | FALSE
92 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Inlet Chamber 2 Aluminum Platform | Aluminum platform | Hamilton | In Service | Rockcliffe | Site | Inlet Chamber 2 | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0100 |  |  |  | 1 |  |  |  | 3000 | 1 | ea. | 2020 | [9 empty] | 2 | David Ip | 2020-06-15 22:29 | Maira Rafiq | 2020-07-13 11:25 | [6 empty] | 1 | good | [7 empty] | 51_merge |  |  |  |  | FALSE | FALSE
93 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Inlet Chamber 2 Aluminum Ladder | Aluminum Ladder | Hamilton | In Service | Rockcliffe | Site | Inlet Chamber 2 | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0100 |  |  |  | 1 |  |  |  | 5500 | 1 | ea. | 2020 | [9 empty] | 2 | David Ip | 2020-06-15 22:29 | Maira Rafiq | 2020-07-13 11:25 | [6 empty] | 1 | good | [7 empty] | 52_merge |  |  |  |  | FALSE | FALSE
94 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Inlet Chamber 2 Manhole Frame and Cover | Manhole frame and cover | Hamilton | In Service | Rockcliffe | Site | Inlet Chamber 2 | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0097 |  |  |  | 1 |  |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 2 | David Ip | 2020-06-15 22:29 | Maira Rafiq | 2020-07-13 11:25 | [6 empty] | 1 | good | [7 empty] | 53_merge |  |  |  |  | FALSE | FALSE
95 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 9 | Generator Building Concrete Foundation | Reinforced concrete caisson and grade beam foundation | Hamilton | In Service | Rockcliffe | Main Building |  | Building Structural | Building Structural | [7 empty] | 1992 | 60 | 2052 |  |  |  |  | 3 |  |  |  | 40000 | 1 | ea. | 2020 | [9 empty] | 1 | David Ip | 2020-06-15 22:13 | Maira Rafiq | 2020-07-13 11:30 | [6 empty] | 1 | Hidden and could not be inspected. Good based on condition of other visible structural assets | [7 empty] | 54_merge |  |  |  |  | FALSE | FALSE
96 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 9 | Generator Building Concrete Floor | Reinforced concrete floor | Hamilton | In Service | Rockcliffe | Main Building |  | Building Structural | Building Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0072 |  |  |  | 3 |  |  |  | 1200 | 17 | ea. | 2020 | [9 empty] | 1.5 | David Ip | 2020-06-15 22:13 | Maira Rafiq | 2020-07-13 11:30 | [6 empty] | 1 | good | [7 empty] | 55_merge |  |  |  |  | FALSE | FALSE
97 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 9 | Generator Building Masonry Blockwall | Masonry blockwalls | Hamilton | In Service | Rockcliffe | Main Building |  | Building Structural | Building Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0072 |  |  |  | 3 |  |  |  | 150 | 76 | ea. | 2020 | [9 empty] | 2.5 | David Ip | 2020-06-15 22:14 | Maira Rafiq | 2020-07-13 11:31 | [6 empty] | 1 | good | [7 empty] | 56_merge |  |  |  |  | FALSE | FALSE
98 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 9 | Generator Building Precast Concrete Roof | Precast concrete roof slabs | Hamilton | In Service | Rockcliffe | Main Building |  | Building Structural | Building Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0074 |  |  |  | 3 |  |  |  | 250 | 42 | ea. | 2020 | [9 empty] | 2.5 | David Ip | 2020-06-15 22:15 | Maira Rafiq | 2020-07-13 11:31 | [6 empty] | 1 | good | [7 empty] | 57_merge |  |  |  |  | FALSE | FALSE
99 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Valve Chamber Manhole Frame and Cover | Manhole frame and cover | Hamilton | In Service | Rockcliffe | Site | Valve Chamber | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0101 |  |  |  | 1 |  |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 2 | David Ip | 2020-06-15 22:30 | Maira Rafiq | 2020-07-13 11:28 | [6 empty] | 1 | good | [7 empty] | 58_merge |  |  |  |  | FALSE | FALSE
100 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Valve Chamber Aluminum Ladder | Aluminum ladder | Hamilton | In Service | Rockcliffe | Site | Valve Chamber | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0103 |  |  |  | 1 |  |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 2 | David Ip | 2020-06-15 22:30 | Maira Rafiq | 2020-07-13 11:28 | [6 empty] | 1 | good | [7 empty] | 59_merge |  |  |  |  | FALSE | FALSE
101 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Valve Chamber Concrete Structure | Reinforced concrete structure | Hamilton | In Service | Rockcliffe | Site | Valve Chamber | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0103 |  |  |  | 1 |  |  |  | 9000 | 1 | ea. | 2020 | [9 empty] | 2 | David Ip | 2020-06-15 22:30 | Maira Rafiq | 2020-07-13 11:29 | [6 empty] | 1 | good | [7 empty] | 60_merge |  |  |  |  | FALSE | FALSE
102 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 10 | Generator Building Exterior Stone Veneer |  | Hamilton | In Service | Rockcliffe | Main Building |  | Building Architectural | Building Architectural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0086 |  |  |  | 3 |  |  |  | 180 | 76 | ea. | 2020 | [9 empty] | 2.5 | David Ip | 2020-06-15 21:49 | Maira Rafiq | 2020-07-13 11:31 | [6 empty] | 1 | good | [7 empty] | 61_merge |  |  |  |  | FALSE | FALSE
103 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 10 | Generator Building Asphalt Shingle Roofing |  | Hamilton | In Service | Rockcliffe | Main Building |  | Building Architectural | Building Architectural | [7 empty] | 1992 | 15 | 2025 | COH-DC015-0055 |  |  |  | 3 |  |  |  | 50 | 50 | ea. | 2020 | [9 empty] | 2 | David Ip | 2020-06-15 21:50 | Maira Rafiq | 2020-07-13 11:31 | [6 empty] | 1 | good | [7 empty] | 62_merge |  |  |  |  | FALSE | FALSE
104 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 10 | Generator Building Wood Truss Roof |  | Hamilton | In Service | Rockcliffe | Main Building |  | Building Architectural | Building Architectural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0055 |  |  |  | 3 |  |  |  | 8000 | 1 | ea. | 2020 | [9 empty] | 1 | David Ip | 2020-06-15 21:57 | Maira Rafiq | 2020-07-13 11:32 | [6 empty] | 1 | hidden under asphalt singles and precast roof. Assumed to be good based on condition of other visible assets | [7 empty] | 63_merge |  |  |  |  | FALSE | FALSE
105 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 10 | Generator Building Wall and Ceiling Paint |  | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Architectural | Building Architectural | [7 empty] | 1992 | 15 | 2025 | COH-DC015-0072 |  |  |  | 1 |  |  |  | 20 | 140 | ea. | 2020 | [9 empty] | 3.2125 | CAMR061927 | 2020-07-13 11:32 | Maira Rafiq | 2020-07-13 12:07 | [6 empty] | 1 | good | Missing/bare spot at washroom |  | Touch up paint | 2021 | 200 |  |  | 64_merge |  |  |  |  | FALSE | FALSE
106 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 10 | Generator Building Containment Coating |  | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Architectural | Building Architectural | [7 empty] | 1992 | 15 | 2025 | COH-DC015-0072 |  |  |  | 1 |  |  |  | 60 | 20 | ea. | 2020 | [9 empty] | 2 | David Ip | 2020-06-15 21:55 | Maira Rafiq | 2020-07-13 11:33 | [6 empty] | 1 | good | [7 empty] | 65_merge |  |  |  |  | FALSE | FALSE
107 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 10 | Generator Building Roof Access Hatch |  | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Architectural | Building Architectural | [7 empty] | 1992 | 15 | 2052 | COH-DC015-0081 |  |  |  | 1 |  |  |  | 500 | 1 | ea. | 2020 | [9 empty] | 1.5 | David Ip | 2020-06-15 21:56 | Maira Rafiq | 2020-07-13 11:34 | [6 empty] | 1 | good | [7 empty] | 66_merge |  |  |  |  | FALSE | FALSE
108 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 10 | Generator Building Exterior Access Door (Double) |  | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Architectural | Building Architectural | [7 empty] | 1992 | 15 | 2025 | COH-DC015-0086 |  |  |  | 2 |  |  |  | 2000 | 1 | ea. | 2020 | [9 empty] | 2.5 | CAMR061927 | 2020-07-13 11:35 | Maira Rafiq | 2020-07-13 11:35 | [6 empty] | 1 | surface corrosion and corrosion on hardware | weathered paint | [6 empty] | 67_merge |  |  |  |  | FALSE | FALSE
109 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 10 | Generator Building Interior Door (Single) |  | Hamilton | In Service | Rockcliffe | Main Building | Washroom | Building Architectural | Building Architectural | [7 empty] | 1992 | 15 | 2025 | COH-DC015-0082 |  |  |  | 2 |  |  |  | 1520 | 1 | ea. | 2020 | [9 empty] | 2.5 | David Ip | 2020-06-15 21:57 | Maira Rafiq | 2020-07-13 11:35 | [6 empty] | 1 | good | [7 empty] | 68_merge |  |  |  |  | FALSE | FALSE
110 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 9 | Generator Building Aluminum Ladder | Aluminum ladder to attic | Hamilton | In Service | Rockcliffe | Main Building |  | Building Structural | Building Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0080 |  |  |  | 2 |  |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 1.5 | David Ip | 2020-06-15 22:15 | Maira Rafiq | 2020-07-13 11:31 | [6 empty] | 1 | good | [7 empty] | 69_merge |  |  |  |  | FALSE | FALSE
111 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | Generator Exhaust | Generator Exhaust and damper | Hamilton |  | Rockcliffe |  |  | Building Mechanical | Building Mechanical | Emergency Power | [6 empty] | 1992 |  | 2045 | COH-DC015-0329 |  |  |  | 3 |  |  |  | 4500 | 1 | ea. | 2020 | [9 empty] | 1 | Patryk Frankiewicz | 2020-07-10 10:55 | [8 empty] | 1 | Good condition. | [7 empty] | 36_merge |  |  |  |  | FALSE | FALSE
112 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | Baseboard Heater | Washroom heater; ; ; ; | Hamilton |  | Rockcliffe | Main Building | Washroom | Building Mechanical | Building Mechanical | Heating System | [6 empty] | 1992 |  | 2030 | COH-DC015-0342 |  |  |  | 2 |  |  |  | 250 | 1 | ea. | 2020 | [9 empty] | 2.4375 |  | 2020-07-13 12:38 | Maira Rafiq | 2020-07-13 12:38 | [6 empty] | 1 | Fair condition | Discoloration and dust | [6 empty] | 37_merge |  |  |  |  | FALSE | FALSE
113 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | Hot Water Tank | Hot Water Tank; AO Smith; ELJF 15 910; ; 1.5kw | Hamilton | In Service | Rockcliffe |  |  | Building Mechanical | Building Mechanical | Domestic Plumbing System | [6 empty] | 1992 |  | 2021 | COH-DC015-0343 |  |  |  | 2 |  |  |  | 1200 | 1 | ea. | 2020 | [9 empty] | 2.4375 | Patryk Frankiewicz | 2020-07-10 11:00 | [8 empty] | 1 | Fair condition, typical hot water heater is at the end of its life | [7 empty] | 38_merge |  |  |  |  | FALSE | FALSE
114 |  | DC015WWL01VTF01 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | Wet Well Fan | Wet Well Fan and duct | Hamilton |  | Rockcliffe |  |  | Building Mechanical | Building Mechanical | Ventilation System | [6 empty] | 1992 |  | 2021 | COH-DC015-0348 |  |  |  | 2 |  |  |  | 5500 | 1 | ea. | 2020 | [9 empty] | 3.5 |  | 2020-07-13 12:57 | Maira Rafiq | 2020-08-11 09:50 | [6 empty] | 1 | CC: The wet well was equipped with a supply fan only. This do not conform with NFPA 820 Section 9.2.6 requirements. As per the mentioned section ventilation system serving classified locations shall maintain a minimum differential pressure relative to ambient | Moderate corrosion on the duct | Minor corrosion on fan casing | [5 empty] | 39_merge |  |  |  |  | FALSE | FALSE
115 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | Washroom Exhaust (New Asset) |  | Hamilton |  | Rockcliffe | Main Building | Washroom | Building Mechanical | Building Mechanical | Ventilation System | [9 empty] | COH-DC015-0339 |  |  |  | 2 | [5 empty] | ea. | 2020 | [9 empty] | 1 | Patryk Frankiewicz | 2020-07-10 11:28 | Maira Rafiq | 2020-08-11 10:14 | [6 empty] | 1 | CC: There was no exhaust fan installed in the washroom, which do not conform with the OBC 9.32.3.5 “Supplemental Exhaust” requirements. Additionally, as per City’s Wastewater Outstations Design Manual Ref. No. 13.1.3 one exhaust fan with an on/off switch with | [7 empty] | 40_merge |  |  |  |  | FALSE | FALSE
116 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | Backflow Preventer | Water Meter and Backflow relocation | Hamilton | Installed | Rockcliffe | Wet Well |  | Building Mechanical | Building Mechanical | Domestic Plumbing System | [6 empty] | 1912 |  |  | COH-DC015-0214 |  |  |  | 3 |  |  |  | 20000 | 1 | ea. | 2020 | [9 empty] | 1 |  | 2020-07-13 12:49 | Maira Rafiq | 2020-08-11 10:14 | [6 empty] | 1 | HS: The backflow was installed in the wet well. As per Ontario’s Design Guidelines for Sewage Works Section 7.3, backflow preventers require periodic inspection, maintenance and induce high pressure loss and therefore cannot be installed below ground level. | Fair | Minor corrosion on bolts | [5 empty] | 41_merge |  |  |  |  | FALSE | FALSE
117 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Fire Extinguisher | Total of 1 | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Mechanical | Building Mechanical | Miscellaneous Mechanical | [6 empty] | 2020 |  |  | COH-DC015-0305 |  |  |  | 3 |  |  |  | 100 | 1 | ea. | 2020 | [9 empty] | 2.5 |  | 2020-07-13 13:11 | Maira Rafiq | 2020-08-11 10:13 | [6 empty] | 1 | Very Good | [7 empty] | 42_merge |  |  |  |  | FALSE | FALSE
118 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 2 | Overflow Piping | Overflow yard piping. Unknown material. Approximate Length: 30 meters, Pipe Dia: 600mm. Assumed to be reinformed concrete pipe installed in 1992 | Hamilton | In Service | Rockcliffe | Site |  | Site Works | Site Civil | [14 empty] | 3 |  |  |  | 325 | 35 | ea. | 2020 | [9 empty] | 4 | CAMR061927 | 2020-08-06 14:40 | Maira Rafiq | 2020-08-07 13:48 | [6 empty] | 1 | The overflow piping was assumed to be in good condition based on age. The discharge of the overflow piping in equipped with a flap gate. Stones build-up at the discharge end was observed. | [8 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
119 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 2 | Asphalt Pavement | Asphalt Pavement, approximate area: 250 square meter | Hamilton | In Service | Rockcliffe | Site |  | Site Works | Site Civil |  | Road | [5 empty] | 1992 |  |  | COH-DC015-0444 |  |  |  | 1 |  |  |  | 55 | 250 | ea. | 2020 | [9 empty] | 1.25 | CAMR061927 | 2020-08-07 12:11 | Maira Rafiq | 2020-08-07 13:42 | [6 empty] | 1 | The access road was in good condition overall. Vegetation and pot holes at the site entrance were observed. Gravels and mud were noted throughout the site. | HS: The presence of gravel and dirt on the driveway adjacent to the wet well presents a trip hazard. |  | Remove the gravel and dirt | 2020 | 1000 |  |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
120 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 2 | Station Manual Perimeter Fencing Gate | Station Manual Perimeter Fencing Gate, approxiate length: 5 meters. | Hamilton |  | Rockcliffe | Site |  | Site Works | Site Civil |  | Gate | [8 empty] | COH-DC015-0424 |  |  |  | 1 |  |  |  | 3380 | 1 | ea. | 2020 | [9 empty] | 3.1875 | CAMR061927 | 2020-08-07 13:06 | Maira Rafiq | 2020-08-07 13:42 | [6 empty] | 1 | The manual perimeter fencing gate was in fair condition. Minor corrosion, broken barbed wires and deformation of the gate was observed. | It was identified by the operator that the station has experienced vandalism in the past. | [7 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
121 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 2 | Perimeter Fencing | Perimeter Fencing, installation year: 1992, Approximate Length: 110 meters | Hamilton |  | Rockcliffe | Site |  | Site Works | Site Civil |  | Fencing | [8 empty] | COH-DC015-0445 |  |  |  | 1 |  |  |  | 170 | 110 | ea. | 2020 | [9 empty] | 3.1875 | CAMR061927 | 2020-08-07 13:42 | Maira Rafiq | 2020-08-07 13:42 | [6 empty] | 1 | HS: It was identified by the operator that the station has experienced vandalism in the past. | The fencing was in fair condition. Overgrown vegetation penetrated through the fencing throughout the station was obsereved. Minor corrosion throughout the fencing, as well as broken barbed wires were observed. | It was identified by the operator that the station has experienced vandalism in the past. | Cleaning vegetation | 2020 | 1000 |  |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
122 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 2 | Overflow Flap Gate | Overflow Flap Gate | Hamilton | In Service | Rockcliffe | Site |  | Site Works | Site Civil |  | Gate | [5 empty] | 1992 |  |  | COH-DC015-0499 |  |  |  | 2 |  |  |  | 0 | 1 | ea. | 2020 | [9 empty] | 0 | CAMR061927 | 2020-08-07 13:41 | Maira Rafiq | 2020-08-07 13:41 | [6 empty] | 1 | The flap gate was in good condition overall. The flap gate was blocked by stones and dirt and would not open properly in the event of station overflow. |  |  | Remove stones and dirt to allow the flap gate to open effortlessly in the event of an overflow | 2021 | 1000 |  |  |  | 0 | 0 | 0 | 0 | FALSE | FALSE
123 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 11 | Diesel Fuel System | Diesel Storage Tanks 1&2; DTE; Capacity 1135 L | Hamilton |  | Rockcliffe | Main Building | Generator Room | Building Mechanical | Building Mechanical | [9 empty] | 2040 | COH-DC015-0313 |  |  |  | 3 |  |  |  | 15000 | 1 | ea. | 2020 | [9 empty] | 1.5 | CAMR061927 | 2020-08-07 13:55 | Maira Rafiq | 2020-08-11 10:00 | [6 empty] | 1 | Tanks appear to be in good condition | CC: There was no containment for diesel fuel lines. TSSA requires all equipment containing or carrying fuel to be contained per CSA B139.1.1-15 Section 6.5.1.4. | [7 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
124 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 11 | Generator Intake | Motorized Intake; ; ; ; | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Mechanical | Building Mechanical | [7 empty] | 1992 |  | 2045 | COH-DC015-0322 |  |  |  | 3 |  |  |  | 1430 | 1 | ea. | 2020 | [9 empty] | 2.4375 | CAMR061927 | 2020-08-07 13:59 | Maira Rafiq | 2020-08-07 13:59 | [6 empty] | 1 | Damper appears to be original | Good condition | minor surface corrosion | [6 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
125 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  | Control Room Exhaust Fan | DC015, GENERATOR/CONTROL ROOM EXHAUST FAN; Canadian Blower; 16; S218650000001; | Hamilton | In Service | Rockcliffe | Main Building |  | Building Mechanical | Building Mechanical | [7 empty] | 2010 |  | 2040 | COH-DC015-0324 |  |  |  | 2 |  |  |  | 1430 | 1 | ea. | 2020 | [9 empty] | 2.4375 | CAMR061927 | 2020-08-07 14:00 | Maira Rafiq | 2020-08-11 10:11 | [6 empty] | 1 | Summer Ventilation Exhaust Fan. Original to the building. | Good condition | [7 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
126 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  | Generator Flue Exhaust | Exhaust Silencer and Stack | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Building Mechanical | Building Mechanical | [7 empty] | 1992 |  | 2045 | COH-DC015-0329 |  |  |  | 3 |  |  |  | 20000 | 1 | ea. | 2020 | [9 empty] | 1 | CAMR061927 | 2020-08-07 14:02 | Maira Rafiq | 2020-08-11 10:06 | [6 empty] | 1 | Fully insulated silencer and exhaust piping. All original to building. | [8 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
127 |  | DC015SLP0200000 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Sewage Lift Pump No.2 | Submersible Pump No.2;ITT;CP3201.180; 140 L/s @ 14m TDH, 28 kW | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Pump | [6 empty] | 2009 |  |  | COH-DC015-0281 |  |  |  | 3 |  |  |  | 137700 | 1 | ea. | 2020 | [9 empty] | 1.3625 | CAMR061927 | 2020-08-11 14:36 | Maira Rafiq | 2020-08-11 14:36 | [6 empty] | 1 | The pumps were assumed to be in good condition based on its age. No performance issues were identified during the inspection. | Good | [7 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
128 |  | DC015SLP0300000 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Sewage Lift Pump No.3 | Submersible Pump No.3;ITT;CP3201.180; 140 L/s @ 14m TDH, 28 kW | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Pump | [6 empty] | 2009 |  |  | COH-DC015-0280 |  |  |  | 3 |  |  |  | 137700 | 1 | ea. | 2020 | [9 empty] | 1.3625 | CAMR061927 | 2020-08-11 14:36 | Maira Rafiq | 2020-08-11 14:36 | [6 empty] | 1 | Good | The pumps were assumed to be in good condition based on its age. No performance issues were identified during the inspection. | [7 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
129 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | Hand Stop Gate No.1 | Hand Stop Gate No.1;;;;36"X 36" | Hamilton | Not In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Gate | [6 empty] | 1992 |  |  | COH-DC015-0236 |  |  |  | 2 |  |  |  | 6080 | 1 | ea. | 2020 | [9 empty] | 1.85 | CAMR061927 | 2020-08-11 14:36 | Maira Rafiq | 2020-08-11 14:37 | [6 empty] | 1 | Poor | The gate was at three quarter of its expected life and deterioration was observed. | [7 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
130 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Concrete Structure | Reinforced concrete wet well structure | Hamilton |  | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 |  | 2052 | COH-DC015-0001 |  |  |  | 3 |  |  |  | 280000 | 1 | ea. | 2020 | [9 empty] | 2 | CAMR061927 | 2020-08-07 15:29 | Maira Rafiq | 2020-08-10 08:54 | [6 empty] | 1 | good | concrete was found to be hard/strong based on hammer striking and schmidt hammer test. Concrete cover at 51mm based on cover meter test | [7 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
131 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Aluminum Ladder | Aluminum ladder from exterior to intermetdiate platform (with cage) | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 |  | 2052 | COH-DC015-0039 |  |  |  | 1 |  |  |  | 3500 | 1 | ea. | 2020 | [9 empty] | 1.5 | CAMR061927 | 2020-08-10 09:14 | Maira Rafiq | 2020-08-10 09:15 | [6 empty] | 1 | fair | buildup of calcium and minor pitting | [7 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
132 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Aluminum Ladder | Aluminum ladder from intermediate platform to lower platform (with cage) | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 |  | 2052 | COH-DC015-0039 |  |  |  | 1 |  |  |  | 3500 | 1 | ea. | 2020 | [9 empty] | 1.5 | CAMR061927 | 2020-08-10 09:17 | Maira Rafiq | 2020-08-10 09:17 | [6 empty] | 1 | fair | buildup of calcium and minor pitting | [7 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
133 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Aluminum Ladder | Aluminum ladder from lower platform to wet well | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 |  | 2052 | COH-DC015-0050 |  |  |  | 1 |  |  |  | 2500 | 1 | ea. | 2020 | [9 empty] | 1.5 | CAMR061927 | 2020-08-10 09:18 | Maira Rafiq | 2020-08-10 09:18 | [6 empty] | 1 | fair | HS: buildup of calcium and minor pitting | [7 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
134 |  | DC015WWL02LSL01 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  | Wetwell 2 Low Level Float | Wetwell No.2 Low Level Float; ; ; ; | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Instrumentation | Process Instrumentation & Control | [7 empty] | 2016 |  |  | COH-DC015-0269 |  |  |  | 2 |  |  |  | 500 | 1 | ea. | 2020 | [9 empty] | 1.3 | CAMR061927 | 2020-08-11 17:13 | Maira Rafiq | 2020-08-11 17:13 | [6 empty] | 1 | [9 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
135 |  | DC015WWL01LSL01 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  | Wetwell 1 Low Level Float | Wetwell No.1 Low Level Float; ; ; ; | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Instrumentation | Process Instrumentation & Control | [7 empty] | 2016 |  |  | COH-DC015-0269 |  |  |  | 2 |  |  |  | 500 | 1 | ea. | 2020 | [9 empty] | 1.3 | CAMR061927 | 2020-08-11 17:13 | Maira Rafiq | 2020-08-11 17:13 | [6 empty] | 1 | [9 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
136 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Interior Lighting | Interior Lighting; ; ; ; 6 linear fluorescent | Hamilton |  | Rockcliffe | Main Building | Generator Room | Building Electrical | Building Electrical | Lighting | [13 empty] | 2 |  |  |  | 500 | 1 | ea. | 2020 | [9 empty] | 1.3 | CAMR061927 | 2020-08-11 17:05 | Maira Rafiq | 2020-08-11 17:06 | [6 empty] | 1 | CC: There was no exit sign installed at the station. The station needs an exit sign according to Canadian Building Code (section 3.2.7.3) and Canadian Fire Code (Section 2.7.3). | [8 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE

## Final
AssetID | ClientAssetID0 | ClientAssetID1 | ClientAssetID2 | UniformatL0 | UniformatL1 | UniformatL2 | UniformatL3 | UniformatL4 | UniformatL5 | MasterFormatX | MasterFormatX2 | FlagAsProcess | FlagAsSubProcess | FlagAsAssembly | FlagAsParent | ParentID | AssetName | AssetDescription | Owner | Status | SiteName | FacilityName | LocationName | AssetCategory | CustomClientCategory | AssetType | CustomClientAssetType | Manufacturer | Model | SerialNumber | InspectionType | AssessmentYear | InstallYear | AvgESL | ReplaceYear | PhotoName | DrawingName | VisualCondition | PerformanceCondition | CoF | PoF | RedundancyFactor | CostID | MaterialUnitCost | Quantity | UnitOfQuantity | CostYear | CostSource | MarkupEquipment | MarkupLabour | MarkupAncillary | MarkupRemoval | MarkupEngineering | MarkupAdministration | MarkupContractor | MarkupContingency | TotalReplacementMarkup | LastEditor | LastEditTime | PlannerReviewer | PlannerReviewTime | DisciplineReview | DisciplineReviewTime | PMReview | PMReviewTime | TempProcess | TempSubProcess | TempSubProcessInstance | TempComments1 | TempComments2 | TempComments3 | TempRehabComment | TempRehabYear | TempRehabCost | AssetTagNumber | SizeCapacity | DBNotes | CountCapex | CountOpex | CountComments | CountDrawings | PreventDeletion | PreventEdit
1 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE |  | Rockcliffe WWPS | Site | Hamilton |  | Rockcliffe |  |  | Site Works | Site Civil | [20 empty] | ea. | 2020 | [10 empty] | Andy Gong | 2020-06-17 11:35 | Maira Rafiq | 2020-08-06 14:10 | [6 empty] | 1 | [8 empty] | 1_primary |  |  |  |  | FALSE | FALSE
2 | 17 |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE |  | Site Civil |  | Hamilton |  | Rockcliffe |  |  | Site Works | [21 empty] | ea. | 2020 | [10 empty] | Andy Gong | 2020-06-17 12:30 | Maira Rafiq | 2020-08-19 15:48 | [6 empty] | 1 | [8 empty] | 2_primary |  |  |  |  | FALSE | FALSE
3 | 8 | DC015SLP0100000 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Sewage Lift Pump No.1 | Submersible Pump No.1;ITT;CP3201.180; 140 L/s @ 14m TDH, 28 kW | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Pump | [6 empty] | 2009 |  |  | COH-DC015-0282 |  |  |  | 3 |  |  |  | 137700 | 1 | ea. | 2020 | [9 empty] | 1.3625 | CAMR061927 | 2020-08-11 14:34 | Maira Rafiq | 2020-08-11 14:34 | [6 empty] | 1 | Good | [7 empty] | 3_primary |  |  |  |  | FALSE | FALSE
4 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 140 | MCC | DC015, MOTOR CONTROL CENTER; Moeller; series 200; ; 4 columns + 40A breaker | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Process Electrical | Process Electrical | Motor Control Center | [6 empty] | 2000 |  | 2030 | COH-DC015-0148 |  |  |  | 3 |  |  |  | 40000 | 1 | ea. | 2020 | [9 empty] | 2 | CAMR061927 | 2020-08-10 10:32 | Maira Rafiq | 2020-08-19 17:09 | [6 empty] | 1 | good | CC: Missing Arc Flash labels | [6 empty] | 4_primary |  |  |  |  | FALSE | FALSE
5 |  | DC015NAC0100000 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 145 | SCADA WAN Panel | WAN Panel, Ethernet Switch; Allen-Bradley Stratix 8000; 1783-MS10T Expansion Module;; | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Process Instrumentation | Process Instrumentation & Control | [7 empty] | 2014 |  |  | COH-DC015-0352 |  |  |  | 3 |  |  |  | 7000 | 1 | ea. | 2020 | [9 empty] | 1.3 | CAMR061927 | 2020-07-09 22:02 | Maira Rafiq | 2020-08-19 21:48 | [6 empty] | 1 | Good | [7 empty] | 5_primary |  |  |  |  | FALSE | FALSE
6 | 13 |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Wet Well |  | Hamilton |  | Rockcliffe |  |  | Process Structural | Process Structural | [20 empty] | ea. | 2020 | [10 empty] | David Ip | 2020-06-15 15:33 | Maira Rafiq | 2020-08-19 15:56 | [6 empty] | 1 | [8 empty] | 6_primary |  |  |  |  | FALSE | FALSE
7 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 147 | Unit Heater 1 | Unit Heater; Ouellet; OAS05036; ; 5KW | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Building Mechanical | Building Mechanical | Heating System | [6 empty] | 2007 |  | 2032 | COH-DC015-0305 |  |  |  | 2 |  |  |  | 760 | 1 | ea. | 2020 | [9 empty] | 2.4375 | Patryk Frankiewicz | 2020-07-10 09:10 | Maira Rafiq | 2020-08-19 21:59 | [6 empty] | 1 | CC: There was no containment for diesel fuel lines. TSSA requires all equipment containing or carrying. fuel to be contained per CSA B139.1.1-15 Section 6.5.1.4. | [7 empty] | 7_primary |  |  |  |  | FALSE | FALSE
8 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 146 | Interior Lighting | Interior Lighting; ; ; ; 6 linear fluorescent | Hamilton | Installed | Rockcliffe |  |  | Building Electrical | Building Electrical | Lighting | [6 empty] | 2000 |  | 2030 | COH-DC015-0189 |  |  |  | 2 |  |  |  | 300 | 6 | ea. | 2020 | [9 empty] | 3.125 | CAMR061927 | 2020-08-10 11:11 | Maira Rafiq | 2020-08-19 21:55 | [6 empty] | 1 | good | replace with LED in next upgrade | [6 empty] | 8_primary |  |  |  |  | FALSE | FALSE
9 | 5 |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Building Structural |  | Hamilton |  | Rockcliffe |  |  | Building Structural | [21 empty] | ea. | 2020 | [13 empty] | 2020-06-09 11:28 | [6 empty] | 1 |  |  |  | Cleaning | 2020 | 0 |  |  | 9_primary |  |  |  |  | FALSE | FALSE
10 | 1 |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Building Architectural |  | Hamilton |  | Rockcliffe |  |  | Building Architectural | Building Architectural | [20 empty] | ea. | 2020 | [10 empty] | David Ip | 2020-06-15 15:46 |  | 2020-06-09 11:28 | [6 empty] | 1 | [8 empty] | 10_primary |  |  |  |  | FALSE | FALSE
11 | 19 |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Emergency Backup Power |  | Hamilton |  | Rockcliffe |  |  | Building Electrical | [15 empty] | 3 | [5 empty] | ea. | 2020 | [13 empty] | 2020-06-09 11:29 | [6 empty] | 1 | [8 empty] | 11_primary |  |  |  |  | FALSE | FALSE
14 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 11 | Diesel Fuel Tank #1 For Generator | DC015, DIESEL FUEL TANK #1 FOR GENERATOR; DTE; Capacity 1135 Lr | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Building Mechanical |  |  |  | NA |  | 7522 C |  |  | 1992 |  | 2040 | COH-DC015-0313 |  |  |  | 3 |  |  |  | 15000 | 1 | ea. | 2020 | [9 empty] | 1.5 | CAMR061927 | 2020-08-11 10:06 | Maira Rafiq | 2020-08-11 10:10 | [6 empty] | 1 | CC: There was no containment for diesel fuel lines. TSSA requires all equipment containing or carrying fuel to be contained per CSA B139.1.1-15 Section 6.5.1.4. | [7 empty] | 14_primary |  |  |  |  | FALSE | FALSE
15 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 11 | Diesel Fuel Tank #2 For Generator | DC015, DIESEL FUEL TANK #2 FOR GENERATOR; DTE; Capacity 1135 Lr | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Building Mechanical |  |  |  | NA |  | 7519 C |  |  | 1992 |  | 2040 | COH-DC015-0313 |  |  |  | 3 |  |  |  | 0 | 1 | ea. | 2020 | [9 empty] | 1.5 | CAMR061927 | 2020-08-11 10:06 | Maira Rafiq | 2020-08-11 10:11 | [6 empty] | 1 | CC: There was no containment for diesel fuel lines. TSSA requires all equipment containing or carrying |  |  | Install safety grate | 2021 | 1000 |  |  | 15_primary |  |  |  |  | FALSE | FALSE
17 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  |  | DC015, BUILDING TEMP CONTROL | Hamilton | Withdrawn | Rockcliffe |  |  | Building Mechanical |  |  |  | HONEYWELL | T136A |  |  |  | 1912 | [12 empty] | ea. | 2020 | [20 empty] | 1 |  |  |  | Install safety grate | 2021 | 1000 |  |  | 17_primary |  |  |  |  | FALSE | FALSE
18 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  |  | DC015, WET WELL LEVEL TRANSMITTER | Hamilton | Withdrawn | Rockcliffe |  |  | Process Instrumentation |  |  |  | MILLTRONICS | MULTIRANGER | n/a |  |  | 1912 | [12 empty] | ea. | 2020 | [20 empty] | 1 |  |  |  | Install safety grate | 2020 | 0 |  |  | 18_primary |  |  |  |  | FALSE | FALSE
20 |  | DC015GEN0100000 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 11 | Standby Diesel Power Generator | DC015, DIESEL STANDBY POWER GENERATOR; KLOCKNERMOELLER;SERIES 200; CDN/16/94-5513 | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Process Electrical | Process Electrical |  |  | KOHLER | 150R0ZJ91 | 359253 |  |  | 1992 | [6 empty] | 3 |  |  |  | 100000 | 1 | ea. | 2020 | [9 empty] | 2 | CAMR061927 | 2020-08-11 16:59 | Maira Rafiq | 2020-08-19 17:08 | [6 empty] | 1 | good |  |  | Touch up paint | 2021 | 200 |  |  | 20_primary |  |  |  |  | FALSE | FALSE
22 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  |  | DC015, GES MONITOR | Hamilton | Withdrawn | Rockcliffe |  |  | Process Instrumentation |  |  |  | MSA | 5100 | 94BM159037 |  |  | 1912 | [12 empty] | ea. | 2020 | [20 empty] | 1 |  |  |  | Remove the gravel and dirt | 2020 | 1000 |  |  | 22_primary |  |  |  |  | FALSE | FALSE
24 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  |  | DC015, LIGHTING SYSTEM | Hamilton | Installed | Rockcliffe |  |  | Building Electrical | Building Electrical | [7 empty] | 1912 | [12 empty] | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-10 16:05 | [6 empty] | 1 |  |  |  | Remove stones and dirt to allow the flap gate to open effortlessly in the event of an overflow | 2021 | 1000 |  |  | 24_primary |  |  |  |  | FALSE | FALSE
25 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  |  | DC015, PLC PANEL | Hamilton | Withdrawn | Rockcliffe |  |  | Process Instrumentation |  |  |  | NA | N12-483620 | NA |  |  | 2000 | [12 empty] | ea. | 2020 | [20 empty] | 1 | [8 empty] | 25_primary |  |  |  |  | FALSE | FALSE
26 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  |  | DC015, PLC | Hamilton | Withdrawn | Rockcliffe |  |  | Process Instrumentation |  |  |  | BRISTOLBABCOCK | 3330 10A 120000 | 94A11064 |  |  | 2000 | [12 empty] | ea. | 2020 | [20 empty] | 1 | [8 empty] | 26_primary |  |  |  |  | FALSE | FALSE
27 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  |  | DC015, PLC PANEL UPS | Hamilton | Withdrawn | Rockcliffe |  |  | Process Instrumentation |  |  |  | APC | BK500M | PB9923112887 |  |  | 2000 | [12 empty] | ea. | 2020 | [20 empty] | 1 | [8 empty] | 27_primary |  |  |  |  | FALSE | FALSE
30 |  | DC015WWL01LIT01 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Level Transmitter #1 | DC015, WET WELL LEVEL TRANSMITTER #1; SIEMENS; MULTIRANGER 100 | Hamilton | Installed | Rockcliffe | Main Building | Washroom | Process Instrumentation |  |  |  | SIEMENS | MULTIRANGER 100 |  |  |  | 2016 | [6 empty] | 2 |  |  |  | 2500 | 1 | ea. | 2020 | [9 empty] | 1.8 | CAMR061927 | 2020-08-11 17:12 | Maira Rafiq | 2020-08-19 21:49 | [6 empty] | 1 | good |  |  | Conduct arc flash study and install arc flash label | 2020 | 0 |  |  | 30_primary |  |  |  |  | FALSE | FALSE
31 |  | DC015WWL02LIT01 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Level Transmitter #2 | DC015, WET WELL LEVEL TRANSMITTER #2 SIEMENS; MULTIRANGER 100 | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Process Instrumentation |  |  |  | SIEMENS | MULTIRANGER 100 |  |  |  | 2016 | [6 empty] | 2 |  |  |  | 2500 | 1 | ea. | 2020 | [9 empty] | 1.8 | CAMR061927 | 2020-08-11 17:12 | Maira Rafiq | 2020-08-19 21:49 | [6 empty] | 1 | good |  |  | Conduct arc flash study and install arc flash label | 2020 | 0 |  |  | 31_primary |  |  |  |  | FALSE | FALSE
32 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 140 | Power Meter | Power meter; Moeller; ; ; | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Process Electrical | Process Electrical | Metering | [6 empty] | 2000 |  | 2030 | COH-DC015-0153 |  |  |  | 3 |  |  |  | 11000 | 1 | ea. | 2020 | [9 empty] | 2 | Amin Norouzizadeh | 2020-07-13 12:55 | Maira Rafiq | 2020-08-19 17:08 | [6 empty] | 1 | good |  |  | Conduct arc flash study and install arc flash label | 2020 | 0 |  |  | 32_primary |  |  |  |  | FALSE | FALSE
33 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 140 | Main Breaker | DC015, MAIN BREAKER; KLOCKNERMOELLER; MZN9-250; NZM9-250/2M9A-200;600V, 200A | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Process Electrical | Process Electrical | Main Switch | [6 empty] | 2000 |  | 2030 | COH-DC015-0152 |  |  |  | 3 |  |  |  | 3800 | 1 | ea. | 2020 | [9 empty] | 3.125 | CAMR061927 | 2020-08-10 10:33 | Maira Rafiq | 2020-08-19 17:08 | [6 empty] | 1 | Good | CC: Missing Arc Flash labels |  | Conduct arc flash study and install arc flash label | 2020 | 0 |  |  | 33_primary |  |  |  |  | FALSE | FALSE
34 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 140 | Power Factor Capacitors | Power Factor capacitos; Powerspec; ; ; 3x 600V, 15kVAr | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Process Electrical | Process Electrical | Power Factor Correction Capacitor | [6 empty] | 2013 |  | 2043 | COH-DC015-0154 |  |  |  | 2 |  |  |  | 10000 | 3 | ea. | 2020 | [9 empty] | 1.5 | Amin Norouzizadeh | 2020-07-13 12:56 | Maira Rafiq | 2020-08-19 17:07 | [6 empty] | 1 | Good |  |  | Conduct arc flash study and install arc flash label | 2020 | 0 |  |  | 34_primary |  |  |  |  | FALSE | FALSE
35 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 146 | Unit Heater Starter | Unit Heater starter and disconnect; ; ; ; 600V, size 1 | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Electrical | Building Electrical | Starter | [6 empty] | 2000 |  | 2030 | COH-DC015-0156 |  |  |  | 2 |  |  |  | 2600 | 1 | ea. | 2020 | [9 empty] | 1.7 | CAMR061927 | 2020-08-10 11:12 | Maira Rafiq | 2020-08-19 21:56 | [6 empty] | 1 | good | CC: Missing Arc Flash labels |  | Conduct arc flash study and install arc flash label | 2020 | 0 |  |  | 35_primary |  |  |  |  | FALSE | FALSE
36 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 127 | Hand Stop Gate No.2 | Hand Stop Gate No.2;;;;36"X 36" | Hamilton | Not In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Gate | [6 empty] | 1992 |  |  | COH-DC015-0236 |  |  |  | 2 |  |  |  | 6080 | 1 | ea. | 2020 | [9 empty] | 1.85 | Adrian Li | 2020-06-17 16:23 | Maira Rafiq | 2020-08-19 21:31 | [6 empty] | 1 | deterioration |  |  | Conduct arc flash study and install arc flash label | 2020 | 0 |  |  | 36_merge |  |  |  |  | FALSE | FALSE
37 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 128 | Hand Stop Gate No.3 | Hand Stop Gate No.3;;;;36"X36" | Hamilton | Not In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Gate | [6 empty] | 1992 |  |  | COH-DC015-0236 |  |  |  | 2 |  |  |  | 6080 | 1 | ea. | 2020 | [9 empty] | 1.85 | Adrian Li | 2020-06-18 14:14 | Maira Rafiq | 2020-08-19 21:31 | [6 empty] | 1 | deterioration |  |  | Conduct arc flash study and install arc flash label | 2020 | 0 |  |  | 37_merge |  |  |  |  | FALSE | FALSE
38 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Manual Bar Screen No.1 | Manual Bar Screen No.1;;;;24"X 48" | Hamilton | Obsolete and Not in Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Screen | [6 empty] | 1992 |  |  | COH-DC015-0223 |  |  |  | 2 |  |  |  | 9000 | 1 | ea. | 2020 | [9 empty] | 1.4 | CAMR061927 | 2020-07-10 10:43 | Maira Rafiq | 2020-08-19 21:31 | [6 empty] | 1 | Bent bars | OM: The operators mentioned that the screens have been removed and are no longer in use. | [6 empty] | 38_merge |  |  |  |  | FALSE | FALSE
39 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Manual Bar Screen No.2 | Manual Bar Screen No.2;;;;24"X 48" | Hamilton | Obsolete and Not in Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Screen | [6 empty] | 1992 |  |  | COH-DC015-0223 |  |  |  | 2 |  |  |  | 9000 | 1 | ea. | 2020 | [9 empty] | 1.4 | CAMR061927 | 2020-07-10 10:43 | Maira Rafiq | 2020-08-19 21:31 | [6 empty] | 1 | Bent bars | OM: The operators mentioned that the screens have been removed and are no longer in use. | [6 empty] | 39_merge |  |  |  |  | FALSE | FALSE
40 |  | DC015SLP01CV001 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 3 | Sewage Lift Pump No.1 Check Valve | Check Valve No.1;;;;200mm | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Valves | [6 empty] | 1992 |  |  | COH-DC015-0230 |  |  |  | 2 |  |  |  | 1990 | 1 | ea. | 2020 | [9 empty] | 2.5 | Adrian Li | 2020-06-17 17:06 | Maira Rafiq | 2020-08-19 21:38 | [6 empty] | 1 | Heavy corrosion and deterioration | [7 empty] | 40_merge |  |  |  |  | FALSE | FALSE
41 |  | DC015SLP02CV001 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 127 | Sewage Lift Pump No.2 Check Valve | Check Valve No.2;;;;200mm | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Valves | [6 empty] | 1992 |  |  | COH-DC015-0244 |  |  |  | 2 |  |  |  | 1990 | 1 | ea. | 2020 | [9 empty] | 2.5 | Adrian Li | 2020-06-17 17:06 | Maira Rafiq | 2020-08-19 21:38 | [6 empty] | 1 | Heavy corrosion and deterioration | [7 empty] | 41_merge |  |  |  |  | FALSE | FALSE
42 |  | DC015SLP03CV001 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 128 | Sewage Lift Pump No.3 Check Valve | Check Valve No.3;;;;200mm | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Valves | [6 empty] | 1992 |  |  | COH-DC015-0241 |  |  |  | 2 |  |  |  | 1990 | 1 | ea. | 2020 | [9 empty] | 2.5 | Adrian Li | 2020-06-17 17:37 | Maira Rafiq | 2020-08-19 21:38 | [6 empty] | 1 | Heavy corrosion and Deterioration | [7 empty] | 42_merge |  |  |  |  | FALSE | FALSE
43 |  | DC015SLP01DV001 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 3 | Sewage Lift Pump No.1 Discharge Valve | Gate Valve No.1;;;;200mm | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Valves | [6 empty] | 1992 |  |  | COH-DC015-0230 |  |  |  | 2 |  |  |  | 1520 | 1 | ea. | 2020 | [9 empty] | 2.5 | Adrian Li | 2020-06-17 17:42 | Maira Rafiq | 2020-08-19 21:38 | [6 empty] | 1 | Heavy corrosion and deterioration | [7 empty] | 43_merge |  |  |  |  | FALSE | FALSE
44 |  | DC015SLP02DV001 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 127 | Sewage Lift Pump No.2 Discharge Valve | Gate Valve No.2;;;;200mm | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Valves | [6 empty] | 1992 |  |  | COH-DC015-0233 |  |  |  | 2 |  |  |  | 1520 | 1 | ea. | 2020 | [9 empty] | 2.5 | Adrian Li | 2020-06-17 17:42 | Maira Rafiq | 2020-08-19 14:23 | [6 empty] | 1 | Heavy corrosion and Deterioration | [7 empty] | 44_merge |  |  |  |  | FALSE | FALSE
45 |  | DC015SLP03DV00 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 128 | Sewage Lift Pump No.3 Discharge Valve | Gate Valve No.3;;;;200mm | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Valves | [6 empty] | 1992 |  |  | COH-DC015-0241 |  |  |  | 2 |  |  |  | 1520 | 1 | ea. | 2020 | [9 empty] | 2.5 | Adrian Li | 2020-06-17 18:34 | Maira Rafiq | 2020-08-19 14:23 | [6 empty] | 1 | Heavy corrosion and Deterioration | [7 empty] | 45_merge |  |  |  |  | FALSE | FALSE
46 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 143 | Discharge Header Gate Valve | Gate Valve No.4;;;;300mm | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Valves | [6 empty] | 1992 |  |  | COH-DC015-0245 |  |  |  | 3 |  |  |  | 2790 | 1 | ea. | 2020 | [9 empty] | 2.5 | Adrian Li | 2020-06-18 11:32 | Maira Rafiq | 2020-08-19 21:47 | [6 empty] | 1 | Heavy corrosion and deterioration | Missing Turn wheel | [6 empty] | 46_merge |  |  |  |  | FALSE | FALSE
47 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 143 | Drain Gate Valve | Drain Gate Valve;;;;100mm | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Valves | [6 empty] | 1992 |  |  | COH-DC015-0254 |  |  |  | 2 |  |  |  | 630 | 1 | ea. | 2020 | [9 empty] | 2.5 | Adrian Li | 2020-06-18 12:37 | Maira Rafiq | 2020-08-19 21:47 | [6 empty] | 1 | Heavy corrosion and deterioration | [7 empty] | 47_merge |  |  |  |  | FALSE | FALSE
48 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 143 | Pressure Release Valve No.1 | Pressure Release Valve No.1;;;;100mm | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Valves | [6 empty] | 1992 |  |  | COH-DC015-0255 |  |  |  | 2 |  |  |  | 2280 | 1 | ea. | 2020 | [9 empty] | 2.5 | Adrian Li | 2020-06-18 15:14 | Maira Rafiq | 2020-08-19 21:46 | [6 empty] | 1 | Heavy corrosion and Deterioration | [7 empty] | 48_merge |  |  |  |  | FALSE | FALSE
49 |  | DC015WWL00IG001 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 143 | Wetwell Cell Isolation Gate | Wetwell Cell Isolation Gate;;;;300mm | Hamilton | In Service | Rockcliffe | Site |  | Process Mechanical | Process Mechanical Piping and Equipment | Valves | [6 empty] | 1992 |  |  | COH-DC015-0102 |  |  |  | 3 |  |  |  | 2790 | 1 | ea. | 2020 | [9 empty] | 2.5 | Adrian Li | 2020-06-18 13:16 | Maira Rafiq | 2020-08-19 21:46 | [6 empty] | 1 | Moderate surface corrosion | [7 empty] | 49_merge |  |  |  |  | FALSE | FALSE
50 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Sluice Gate No.1 | Sluice Gate No.1;;;;900mm | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Gate | [6 empty] | 1992 |  |  | COH-DC-15-0263 |  |  |  | 2 |  |  |  | 25340 | 1 | ea. | 2020 | [9 empty] | 1.85 | Adrian Li | 2020-06-18 14:17 | Maira Rafiq | 2020-08-19 21:41 | [6 empty] | 1 | Heavy corrosion and deterioration on the frame of the sluice gate | [7 empty] | 51_merge |  |  |  |  | FALSE | FALSE
51 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 3 | Pump 1 Piping | Process Mechanical Piping;;;; 7.5 m of 100 mm dia DI pipe, 16.5 m of 200 mm dia DI pipe, 16.5 m of 300 mm DI pipe | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Piping | [6 empty] | 1992 |  |  | COH-DC015-0206 |  |  |  | 3 |  |  |  | 142 | 8 | ea. | 2020 | [9 empty] | 1.6 | Adrian Li | 2020-06-18 14:48 | Maira Rafiq | 2020-08-19 21:46 | [6 empty] | 1 | Heavy corrosion and deterioration on majority portion of the piping | [7 empty] | 52_merge |  |  |  |  | FALSE | FALSE
52 | 12 |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Forcemain |  | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Piping | [6 empty] | 1992 |  |  | COH-DC015-0206 |  |  |  | 4 | [5 empty] | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-19 21:43 | [6 empty] | 1 | [8 empty] | 53_merge |  |  |  |  | FALSE | FALSE
53 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 145 | SCADA PANEL | PLC controller c/w all IO cards, internal wiring, PLC software programp, panel enclosure and all associated components; Allen-Bradley; 1969-L33ER, 1769-PA4, 1769-IF4I, 1769-OF4CI, 1769-IQ16; 1769-OW16, 1769-ECR; ; ; | Hamilton |  | Rockcliffe | Main Building | Generator Room | Process Instrumentation | Process Instrumentation & Control | PLC | [6 empty] | 2013 |  |  | COH-DC015-0364 |  |  |  | 3 |  |  |  | 40000 | 1 | ea. | 2020 | [9 empty] | 1 | Alex Wang | 2020-06-29 14:43 | Maira Rafiq | 2020-08-19 21:49 | [6 empty] | 1 | Good | [7 empty] | 36_merge |  |  |  |  | FALSE | FALSE
54 |  | Station Temperature Transmitter |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 145 | Station Temperature Transmitter | Temperature Transmitter; Pribusin: TWTS-2; ; ; | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Process Instrumentation | Process Instrumentation & Control | Transmitter | [6 empty] | 2014 |  |  | COH-DC015-0408 |  |  |  | 2 |  |  |  | 800 | 1 | ea. | 2020 | [9 empty] | 1.3 | Alex Wang | 2020-06-29 14:41 | Maira Rafiq | 2020-08-19 21:49 | [6 empty] | 1 | Good | Communication via Pribusin transmitter is old technology and will be obselete in near future. It is recommended tp replace the temperature trasmitter with a cellular transmitter or a hardwired signal from the temperature device to directly connected to th | [6 empty] | 37_merge |  |  |  |  | FALSE | FALSE
55 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 145 | UPS | UPS; Eaton Powerware; PW9130L2000T-XL; ; ; | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Process Instrumentation | Process Instrumentation & Control | Miscellaneous Instrumentation | [6 empty] | 2014 |  |  | COH-DC015-0366 |  |  |  | 2 |  |  |  | 3000 | 1 | ea. | 2020 | [9 empty] | 1.2 | Alex Wang | 2020-06-29 14:39 | Maira Rafiq | 2020-08-19 21:49 | [6 empty] | 1 | good | Dust | [6 empty] | 38_merge |  |  |  |  | FALSE | FALSE
56 |  | DC015WWL01LSH01 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wetwell 1 High Level Float | Wetwell No.1 High Level Float; ; ; ; | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Instrumentation | Process Instrumentation & Control | [7 empty] | 2016 |  |  | COH-DC015-0269 |  |  |  | 2 |  |  |  | 500 | 1 | ea. | 2020 | [9 empty] | 1.3 | CAMR061927 | 2020-07-09 22:13 | Maira Rafiq | 2020-08-19 21:50 | [6 empty] | 1 | Good | [7 empty] | 40_merge |  |  |  |  | FALSE | FALSE
57 |  | DC015WWL02LSH01 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wetwell 2 High Level Float | Wetwell No.2 High Level Float; ; ; ; | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Instrumentation | Process Instrumentation & Control | [7 empty] | 2016 |  |  | COH-DC015-0269 |  |  |  | 2 |  |  |  | 500 | 1 | ea. | 2020 | [9 empty] | 1.3 | CAMR061927 | 2020-07-09 22:13 | Maira Rafiq | 2020-08-19 21:50 | [6 empty] | 1 | Good | [7 empty] | 41_merge |  |  |  |  | FALSE | FALSE
58 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 3 | Pump 1 VFD | VFD with filter; ; ; ; 600V, size 2 | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Process Electrical | Process Electrical | Starter | [6 empty] | 2000 |  | 2030 | COH-DC015-0157 |  |  |  | 2 |  |  |  | 19000 | 1 | ea. | 2020 | [9 empty] | 1.7 | CAMR061927 | 2020-08-10 10:35 | Maira Rafiq | 2020-08-19 17:07 | [6 empty] | 1 | CC: Missing Arc Flash labels | [7 empty] | 36_merge |  |  |  |  | FALSE | FALSE
59 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 146 | Wet well Fan Starter | starter and disconnect; ; ; ; 600V, size 1 | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Electrical | Building Electrical | Starter | [6 empty] | 2000 |  | 2030 | COH-DC015-0162 |  |  |  | 2 |  |  |  | 2500 | 1 | ea. | 2020 | [9 empty] | 1.7 | CAMR061927 | 2020-08-10 11:46 | Maira Rafiq | 2020-08-19 21:56 | [6 empty] | 1 | CC: Missing Arc Flash labels | [7 empty] | 37_merge |  |  |  |  | FALSE | FALSE
60 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 146 | Diesel Generator Room Fan Starter | starter and disconnect; ; ; ; 600V, size 1 | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Electrical | Building Electrical | Starter | [6 empty] | 2000 |  | 2030 | COH-DC015-0163 |  |  |  | 2 |  |  |  | 2500 | 1 | ea. | 2020 | [9 empty] | 1.7 | CAMR061927 | 2020-08-10 11:45 | Maira Rafiq | 2020-08-19 21:56 | [6 empty] | 1 | CC: Missing Arc Flash labels | [7 empty] | 38_merge |  |  |  |  | FALSE | FALSE
61 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 127 | Pump 2 VFD | VFD with filter; ; ; ; 600V, size 2 | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Process Electrical | Process Electrical | Starter | [6 empty] | 2000 |  | 2030 | COH-DC015-0164 |  |  |  | 2 |  |  |  | 19000 | 1 | ea. | 2020 | [9 empty] | 1.7 | CAMR061927 | 2020-08-10 10:35 | Maira Rafiq | 2020-08-19 17:06 | [6 empty] | 1 | CC: Missing Arc Flash labels | [7 empty] | 39_merge |  |  |  |  | FALSE | FALSE
62 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 128 | Pump 3 VFD | VFD with filter; ; ; ; 600V, size 2 | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Process Electrical | Process Electrical | Starter | [6 empty] | 2000 |  | 2030 | COH-DC015-0170 |  |  |  | 2 |  |  |  | 19000 | 1 | ea. | 2020 | [9 empty] | 1.7 | CAMR061927 | 2020-08-10 10:35 | Maira Rafiq | 2020-08-19 17:06 | [6 empty] | 1 | CC: Missing Arc Flash labels | [7 empty] | 40_merge |  |  |  |  | FALSE | FALSE
63 |  | DC015ATS0100000 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 11 | Diesel Generator Control Panel | Genreator panel with ATS ; ; ; ; 600V, 200A, 150kW | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Building Electrical | Emergency Backup Power | Standby Power Source | [6 empty] | 1992 |  | 2030 | COH-DC015-0170 |  |  |  | 3 |  |  |  | 30000 | 1 | ea. | 2020 | [9 empty] | 2.25 | CAMR061927 | 2020-08-10 11:45 | Maira Rafiq | 2020-08-19 21:56 | [6 empty] | 1 | CC: Missing Arc Flash labels | [7 empty] | 41_merge |  |  |  |  | FALSE | FALSE
64 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 146 | Emergency Lighting | Battery Unit ; ; ; ; | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Electrical | Building Electrical | Emergency Lighting | [6 empty] | 2016 |  | 2043 | COH-DC015-0130 |  |  |  | 2 |  |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 1.5 | Amin Norouzizadeh | 2020-07-13 12:26 | Maira Rafiq | 2020-08-19 21:56 | [6 empty] | 1 | good | [7 empty] | 42_merge |  |  |  |  | FALSE | FALSE
65 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 146 | Lighting Panel LPA | DC015, BREAKER PANEL; Square D; NQOB; ;120/208V, 225A, | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Electrical | Building Electrical | Panelboard | [6 empty] | 2000 |  | 2030 | COH-DC015-0134 |  |  |  | 3 |  |  |  | 2000 | 1 | ea. | 2020 | [9 empty] | 3.125 | Amin Norouzizadeh | 2020-07-13 12:59 | Maira Rafiq | 2020-08-19 21:56 | [6 empty] | 1 | good | [7 empty] | 43_merge |  |  |  |  | FALSE | FALSE
66 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 146 | Lighting Trasnformer | Transformer; Square D; 33360-17112-006 ; 00J055160;600-120/208V, 30kVAr | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Electrical | Building Electrical | Distribution Transformer | [6 empty] | 1992 |  | 2030 | COH-DC015-0143 |  |  |  | 3 |  |  |  | 5100 | 1 | ea. | 2020 | [9 empty] | 3.125 | Amin Norouzizadeh | 2020-07-13 12:59 | Maira Rafiq | 2020-08-19 21:57 | [6 empty] | 1 | good | [7 empty] | 44_merge |  |  |  |  | FALSE | FALSE
67 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 146 | Exterior Lighting | Lighting; ; ; ; 1 flood light | Hamilton | In Service | Rockcliffe | Site |  | Building Electrical | Building Electrical | Lighting | [6 empty] | 2013 |  | 2030 | COH-DC015-0190 |  |  |  | 2 |  |  |  | 300 | 1 | ea. | 2020 | [9 empty] | 3.125 | Amin Norouzizadeh | 2020-07-13 12:59 | Maira Rafiq | 2020-08-19 21:57 | [6 empty] | 1 | good | [7 empty] | 45_merge |  |  |  |  | FALSE | FALSE
68 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 146 | Wet Well Lighting | Lighting; ; ; ; 3 flood light, class 1, div 1 | Hamilton | In Service | Rockcliffe | Wet Well |  | Building Electrical | Building Electrical | Lighting | [6 empty] | 2000 |  | 2025 | COH-DC015-0196 |  |  |  | 2 |  |  |  | 700 | 3 | ea. | 2020 | [9 empty] | 3.125 | CAMR061927 | 2020-08-10 11:44 | Maira Rafiq | 2020-08-19 21:57 | [6 empty] | 1 | corroded | to be replaced with class 1, div 1 fixture | [6 empty] | 46_merge |  |  |  |  | FALSE | FALSE
69 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  | Main Transformer | Main Trasnformer; ABB; ; ; 27.6kV-600V, 750KVA | Hamilton | In Service |  |  |  | Process Electrical |  | Power Transformer | [6 empty] | 2000 |  | 2030 | COH-DC015-0200 |  |  |  | 3 |  |  |  | 57000 | 1 | ea. | 2020 | [9 empty] | 2.25 | Amin Norouzizadeh | 2020-07-13 13:01 | [8 empty] | 1 | good | [7 empty] | 47_merge |  |  |  |  | FALSE | FALSE
73 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 2 | Signboards | City of Hamilton Signboards throughout the site (total of two) | Hamilton | In Service | Rockcliffe | Site |  | Site Works | Site Civil | Signboard | [6 empty] | 1992 |  |  | COH-DC015-0425 |  |  |  | 1 |  |  |  | 60 | 2 | ea. | 2020 | [9 empty] | 3.1875 | CAMR061927 | 2020-07-06 09:58 | Maira Rafiq | 2020-08-19 15:48 | [6 empty] | 1 | good | [7 empty] | 40_merge |  |  |  |  | FALSE | FALSE
75 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 2 | Station Access Road | Gravel Access Road to the Station | Hamilton | In Service | Rockcliffe | Site |  | Site Works | Site Civil | Road | [6 empty] | 1992 |  |  | COH-DC015-0529 |  |  |  | 1 |  |  |  | 55 | 30 | ea. | 2020 | [9 empty] | 1.25 | CAMR061927 | 2020-07-06 07:58 | Maira Rafiq | 2020-08-18 17:30 | [6 empty] | 1 | Pot holes and mud bumps | [7 empty] | 43_merge |  |  |  |  | FALSE | FALSE
76 | 18 |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE |  | Sanitary Sewer | Sanitary Sewer Yard Piping, Approximate Length: 21 meters, Pipe Dia: 450mm, unknown material and installation year. Assumed to be reinformed concrete pipe installed in 1992 | Hamilton | In Service | Rockcliffe | Site |  | Site Works | Site Civil | Piping | [6 empty] | 1992 |  | 2072 |  |  |  |  | 3 |  |  |  | 80 | 21 | ea. | 2020 | [9 empty] | 10.7 | Andy Gong | 2020-06-17 14:03 | Maira Rafiq | 2020-08-19 15:49 | [6 empty] | 1 | good | [7 empty] | 44_merge |  |  |  |  | FALSE | FALSE
77 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Aluminum Ladder | Aluminum ladder from lower platform to wet well | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0030 |  |  |  | 2 |  |  |  | 2500 | 1 | ea. | 2020 | [9 empty] | 1.5 | CAMR061927 | 2020-07-13 08:49 | Maira Rafiq | 2020-07-13 08:49 | [6 empty] | 1 | buildup of calcium and minor pitting | [7 empty] | 36_merge |  |  |  |  | FALSE | FALSE
78 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Aluminum Guardrail | Aluminum guardrails at lower platform level | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0008 |  |  |  | 2 |  |  |  | 200 | 20 | ea. | 2020 | [9 empty] | 2 | CAMR061927 | 2020-07-13 08:50 | Maira Rafiq | 2020-07-13 08:50 | [6 empty] | 1 | buildup of calcium and minor pitting | [7 empty] | 37_merge |  |  |  |  | FALSE | FALSE
79 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Aluminum Grating | Aluminum grating at lower platform level | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0026 |  |  |  | 2 |  |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 1 | CAMR061927 | 2020-07-13 08:53 | Maira Rafiq | 2020-07-13 08:53 | [6 empty] | 1 | buildup of calcium and minor pitting | HS: One section of grating was missing and should be installed/replaced | [6 empty] | 38_merge |  |  |  |  | FALSE | FALSE
80 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Access Hatch | Aluminum access hatch at grade level | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0067 |  |  |  | 2 |  |  |  | 5000 | 1 | ea. | 2020 | [9 empty] | 1 | David Ip | 2020-06-15 22:25 | Maira Rafiq | 2020-07-13 08:53 | [6 empty] | 1 | good | [7 empty] | 39_merge |  |  |  |  | FALSE | FALSE
81 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Pump Hatch 1 | Aluminum pump hatch at grade level | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0063 |  |  |  | 2 |  |  |  | 5000 | 1 | ea. | 2020 | [9 empty] | 1 | CAMR061927 | 2020-07-13 08:54 | Maira Rafiq | 2020-07-13 08:54 | [6 empty] | 1 | good | HS: retrofit of safety grating underneath the pump hatch is recommended to mitgate a falling hazard when hatch is open | [6 empty] | 40_merge |  |  |  |  | FALSE | FALSE
82 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Pump Hatch 2 | Aluminum pump hatch at grade level | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0063 |  |  |  | 2 |  |  |  | 6500 | 1 | ea. | 2020 | [9 empty] | 1 | CAMR061927 | 2020-07-13 08:55 | Maira Rafiq | 2020-07-13 08:55 | [6 empty] | 1 | good | retrofit of safety grating underneath the pump hatch is recommended to mitgate a falling hazard when hatch is open | [6 empty] | 41_merge |  |  |  |  | FALSE | FALSE
83 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Pump Hatch 3 | Aluminum pump hatch at grade level | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0065 |  |  |  | 2 |  |  |  | 6500 | 1 | ea. | 2020 | [9 empty] | 2 | CAMR061927 | 2020-07-13 08:55 | Maira Rafiq | 2020-07-13 08:55 | [6 empty] | 1 | good | retrofit of safety grating underneath the pump hatch is recommended to mitgate a falling hazard when hatch is open | [6 empty] | 42_merge |  |  |  |  | FALSE | FALSE
84 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Pump Hatch 4 | Aluminum pump hatch at grade level | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0065 |  |  |  | 2 |  |  |  | 6500 | 1 | ea. | 2020 | [9 empty] | 1 | CAMR061927 | 2020-07-13 11:05 | Maira Rafiq | 2020-07-13 11:05 | [6 empty] | 1 | good | retrofit of safety grating underneath the pump hatch is recommended to mitgate a falling hazard when hatch is open | [6 empty] | 43_merge |  |  |  |  | FALSE | FALSE
85 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Davit Base 1 | Safety davit base at grade level | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0067 |  |  |  | 2 |  |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 2 | David Ip | 2020-06-15 22:26 | Maira Rafiq | 2020-07-13 11:05 | [6 empty] | 1 | good | [7 empty] | 44_merge |  |  |  |  | FALSE | FALSE
86 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Davit Base 2 | Safety davit base at grade level | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0063 |  |  |  | 2 |  |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 2 | CAMR061927 | 2020-07-13 11:06 | Maira Rafiq | 2020-07-13 11:06 | [6 empty] | 1 | good | Missing cap | [6 empty] | 45_merge |  |  |  |  | FALSE | FALSE
87 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 137 | Inlet Chamber 1 Concrete Structure | Reinforced concrete inlet chamber | Hamilton | In Service | Rockcliffe | Site | Inlet Chamber 1 | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0095 |  |  |  | 1 |  |  |  | 35000 | 1 | ea. | 2020 | [9 empty] | 2 | David Ip | 2020-06-15 22:27 | Maira Rafiq | 2020-08-19 17:04 | [6 empty] | 1 | good | [7 empty] | 46_merge |  |  |  |  | FALSE | FALSE
88 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 137 | Inlet Chamber 1 Aluminum Platform | Aluminum platform | Hamilton | In Service | Rockcliffe | Site | Inlet Chamber 1 | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0095 |  |  |  | 1 |  |  |  | 3000 | 1 | ea. | 2020 | [9 empty] | 2 | David Ip | 2020-06-15 22:28 | Maira Rafiq | 2020-08-19 17:04 | [6 empty] | 1 | good | [7 empty] | 47_merge |  |  |  |  | FALSE | FALSE
89 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 137 | Inlet Chamber 1 Aluminum Ladder | Aluminum Ladder | Hamilton | In Service | Rockcliffe | Site | Inlet Chamber 1 | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0095 |  |  |  | 1 |  |  |  | 5500 | 1 | ea. | 2020 | [9 empty] | 2 | CAMR061927 | 2020-07-13 11:08 | Maira Rafiq | 2020-08-19 17:04 | [6 empty] | 1 | good | [7 empty] | 48_merge |  |  |  |  | FALSE | FALSE
90 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 137 | Inlet Chamber 1 Manhole Frame and Cover | Manhole frame and cover | Hamilton | In Service | Rockcliffe | Site | Inlet Chamber 1 | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0093 |  |  |  | 1 |  |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 2 | David Ip | 2020-06-15 22:28 | Maira Rafiq | 2020-08-19 17:04 | [6 empty] | 1 | good | [7 empty] | 49_merge |  |  |  |  | FALSE | FALSE
91 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 139 | Inlet Chamber 2 Concrete Structure | Reinforced concrete inlet chamber | Hamilton | In Service | Rockcliffe | Site | Inlet Chamber 2 | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0100 |  |  |  | 1 |  |  |  | 35000 | 1 | ea. | 2020 | [9 empty] | 2 | David Ip | 2020-06-15 22:27 | Maira Rafiq | 2020-08-19 17:04 | [6 empty] | 1 | good | [7 empty] | 50_merge |  |  |  |  | FALSE | FALSE
92 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 139 | Inlet Chamber 2 Aluminum Platform | Aluminum platform | Hamilton | In Service | Rockcliffe | Site | Inlet Chamber 2 | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0100 |  |  |  | 1 |  |  |  | 3000 | 1 | ea. | 2020 | [9 empty] | 2 | David Ip | 2020-06-15 22:29 | Maira Rafiq | 2020-08-19 17:04 | [6 empty] | 1 | good | [7 empty] | 51_merge |  |  |  |  | FALSE | FALSE
93 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 139 | Inlet Chamber 2 Aluminum Ladder | Aluminum Ladder | Hamilton | In Service | Rockcliffe | Site | Inlet Chamber 2 | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0100 |  |  |  | 1 |  |  |  | 5500 | 1 | ea. | 2020 | [9 empty] | 2 | David Ip | 2020-06-15 22:29 | Maira Rafiq | 2020-08-19 17:03 | [6 empty] | 1 | good | [7 empty] | 52_merge |  |  |  |  | FALSE | FALSE
94 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 139 | Inlet Chamber 2 Manhole Frame and Cover | Manhole frame and cover | Hamilton | In Service | Rockcliffe | Site | Inlet Chamber 2 | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0097 |  |  |  | 1 |  |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 2 | David Ip | 2020-06-15 22:29 | Maira Rafiq | 2020-08-19 17:03 | [6 empty] | 1 | good | [7 empty] | 53_merge |  |  |  |  | FALSE | FALSE
95 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 9 | Generator Building Concrete Foundation | Reinforced concrete caisson and grade beam foundation | Hamilton | In Service | Rockcliffe | Main Building |  | Building Structural | Building Structural | [7 empty] | 1992 | 60 | 2052 |  |  |  |  | 3 |  |  |  | 40000 | 1 | ea. | 2020 | [9 empty] | 1 | David Ip | 2020-06-15 22:13 | Maira Rafiq | 2020-07-13 11:30 | [6 empty] | 1 | [8 empty] | 54_merge |  |  |  |  | FALSE | FALSE
96 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 9 | Generator Building Concrete Floor | Reinforced concrete floor | Hamilton | In Service | Rockcliffe | Main Building |  | Building Structural | Building Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0072 |  |  |  | 3 |  |  |  | 1200 | 17 | ea. | 2020 | [9 empty] | 1.5 | David Ip | 2020-06-15 22:13 | Maira Rafiq | 2020-07-13 11:30 | [6 empty] | 1 | good | [7 empty] | 55_merge |  |  |  |  | FALSE | FALSE
97 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 9 | Generator Building Masonry Blockwall | Masonry blockwalls | Hamilton | In Service | Rockcliffe | Main Building |  | Building Structural | Building Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0072 |  |  |  | 3 |  |  |  | 150 | 76 | ea. | 2020 | [9 empty] | 2.5 | David Ip | 2020-06-15 22:14 | Maira Rafiq | 2020-07-13 11:31 | [6 empty] | 1 | good | [7 empty] | 56_merge |  |  |  |  | FALSE | FALSE
98 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 9 | Generator Building Precast Concrete Roof | Precast concrete roof slabs | Hamilton | In Service | Rockcliffe | Main Building |  | Building Structural | Building Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0074 |  |  |  | 3 |  |  |  | 250 | 42 | ea. | 2020 | [9 empty] | 2.5 | David Ip | 2020-06-15 22:15 | Maira Rafiq | 2020-07-13 11:31 | [6 empty] | 1 | good | [7 empty] | 57_merge |  |  |  |  | FALSE | FALSE
99 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 138 | Valve Chamber Manhole Frame and Cover | Manhole frame and cover | Hamilton | In Service | Rockcliffe | Site | Valve Chamber | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0101 |  |  |  | 1 |  |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 2 | David Ip | 2020-06-15 22:30 | Maira Rafiq | 2020-08-19 16:58 | [6 empty] | 1 | good | [7 empty] | 58_merge |  |  |  |  | FALSE | FALSE
100 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 138 | Valve Chamber Aluminum Ladder | Aluminum ladder | Hamilton | In Service | Rockcliffe | Site | Valve Chamber | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0103 |  |  |  | 1 |  |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 2 | David Ip | 2020-06-15 22:30 | Maira Rafiq | 2020-08-19 16:58 | [6 empty] | 1 | good | [7 empty] | 59_merge |  |  |  |  | FALSE | FALSE
101 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 138 | Valve Chamber Concrete Structure | Reinforced concrete structure | Hamilton | In Service | Rockcliffe | Site | Valve Chamber | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0103 |  |  |  | 1 |  |  |  | 9000 | 1 | ea. | 2020 | [9 empty] | 2 | David Ip | 2020-06-15 22:30 | Maira Rafiq | 2020-08-19 16:58 | [6 empty] | 1 | good | [7 empty] | 60_merge |  |  |  |  | FALSE | FALSE
102 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 10 | Generator Building Exterior Stone Veneer |  | Hamilton | In Service | Rockcliffe | Main Building |  | Building Architectural | Building Architectural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0086 |  |  |  | 3 |  |  |  | 180 | 76 | ea. | 2020 | [9 empty] | 2.5 | David Ip | 2020-06-15 21:49 | Maira Rafiq | 2020-07-13 11:31 | [6 empty] | 1 | good | [7 empty] | 61_merge |  |  |  |  | FALSE | FALSE
103 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 10 | Generator Building Asphalt Shingle Roofing |  | Hamilton | In Service | Rockcliffe | Main Building |  | Building Architectural | Building Architectural | [7 empty] | 1992 | 15 | 2025 | COH-DC015-0055 |  |  |  | 3 |  |  |  | 50 | 50 | ea. | 2020 | [9 empty] | 2 | David Ip | 2020-06-15 21:50 | Maira Rafiq | 2020-07-13 11:31 | [6 empty] | 1 | good | [7 empty] | 62_merge |  |  |  |  | FALSE | FALSE
104 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 10 | Generator Building Wood Truss Roof |  | Hamilton | In Service | Rockcliffe | Main Building |  | Building Architectural | Building Architectural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0055 |  |  |  | 3 |  |  |  | 8000 | 1 | ea. | 2020 | [9 empty] | 1 | David Ip | 2020-06-15 21:57 | Maira Rafiq | 2020-07-13 11:32 | [6 empty] | 1 | hidden under asphalt singles and precast roof. Assumed to be good based on condition of other visible assets | [7 empty] | 63_merge |  |  |  |  | FALSE | FALSE
105 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 10 | Generator Building Wall and Ceiling Paint |  | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Architectural | Building Architectural | [7 empty] | 1992 | 15 | 2025 | COH-DC015-0072 |  |  |  | 1 |  |  |  | 20 | 140 | ea. | 2020 | [9 empty] | 3.2125 | CAMR061927 | 2020-07-13 11:32 | Maira Rafiq | 2020-07-13 12:07 | [6 empty] | 1 | Missing/bare spot at washroom | [7 empty] | 64_merge |  |  |  |  | FALSE | FALSE
106 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 10 | Generator Building Containment Coating |  | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Architectural | Building Architectural | [7 empty] | 1992 | 15 | 2025 | COH-DC015-0072 |  |  |  | 1 |  |  |  | 60 | 20 | ea. | 2020 | [9 empty] | 2 | David Ip | 2020-06-15 21:55 | Maira Rafiq | 2020-07-13 11:33 | [6 empty] | 1 | good | [7 empty] | 65_merge |  |  |  |  | FALSE | FALSE
107 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 10 | Generator Building Roof Access Hatch |  | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Architectural | Building Architectural | [7 empty] | 1992 | 15 | 2052 | COH-DC015-0081 |  |  |  | 1 |  |  |  | 500 | 1 | ea. | 2020 | [9 empty] | 1.5 | David Ip | 2020-06-15 21:56 | Maira Rafiq | 2020-07-13 11:34 | [6 empty] | 1 | good | [7 empty] | 66_merge |  |  |  |  | FALSE | FALSE
108 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 10 | Generator Building Exterior Access Door (Double) |  | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Architectural | Building Architectural | [7 empty] | 1992 | 15 | 2025 | COH-DC015-0086 |  |  |  | 2 |  |  |  | 2000 | 1 | ea. | 2020 | [9 empty] | 2.5 | CAMR061927 | 2020-07-13 11:35 | Maira Rafiq | 2020-07-13 11:35 | [6 empty] | 1 | surface corrosion on hardware | weathered paint | [6 empty] | 67_merge |  |  |  |  | FALSE | FALSE
109 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 10 | Generator Building Interior Door (Single) |  | Hamilton | In Service | Rockcliffe | Main Building | Washroom | Building Architectural | Building Architectural | [7 empty] | 1992 | 15 | 2025 | COH-DC015-0082 |  |  |  | 2 |  |  |  | 1520 | 1 | ea. | 2020 | [9 empty] | 2.5 | David Ip | 2020-06-15 21:57 | Maira Rafiq | 2020-07-13 11:35 | [6 empty] | 1 | good | [7 empty] | 68_merge |  |  |  |  | FALSE | FALSE
110 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 9 | Generator Building Aluminum Ladder | Aluminum ladder to attic | Hamilton | In Service | Rockcliffe | Main Building |  | Building Structural | Building Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0080 |  |  |  | 2 |  |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 1.5 | David Ip | 2020-06-15 22:15 | Maira Rafiq | 2020-07-13 11:31 | [6 empty] | 1 | good | [7 empty] | 69_merge |  |  |  |  | FALSE | FALSE
111 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 11 | Generator Exhaust | Generator Exhaust and damper | Hamilton |  | Rockcliffe |  |  | Building Mechanical | Building Mechanical | Emergency Power | [6 empty] | 1992 |  | 2045 | COH-DC015-0329 |  |  |  | 3 |  |  |  | 4500 | 1 | ea. | 2020 | [9 empty] | 1 | Patryk Frankiewicz | 2020-07-10 10:55 | Maira Rafiq | 2020-08-19 22:00 | [6 empty] | 1 | good | [7 empty] | 36_merge |  |  |  |  | FALSE | FALSE
112 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 147 | Baseboard Heater | Washroom heater; ; ; ; | Hamilton |  | Rockcliffe | Main Building | Washroom | Building Mechanical | Building Mechanical | Heating System | [6 empty] | 1992 |  | 2030 | COH-DC015-0342 |  |  |  | 2 |  |  |  | 250 | 1 | ea. | 2020 | [9 empty] | 2.4375 |  | 2020-07-13 12:38 | Maira Rafiq | 2020-08-19 22:00 | [6 empty] | 1 | Discoloration and dust | [7 empty] | 37_merge |  |  |  |  | FALSE | FALSE
113 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 147 | Hot Water Tank | Hot Water Tank; AO Smith; ELJF 15 910; ; 1.5kw | Hamilton | In Service | Rockcliffe |  |  | Building Mechanical | Building Mechanical | Domestic Plumbing System | [6 empty] | 1992 |  | 2021 | COH-DC015-0343 |  |  |  | 2 |  |  |  | 1200 | 1 | ea. | 2020 | [9 empty] | 2.4375 | Patryk Frankiewicz | 2020-07-10 11:00 | Maira Rafiq | 2020-08-19 22:00 | [6 empty] | 1 | Fair | [7 empty] | 38_merge |  |  |  |  | FALSE | FALSE
114 |  | DC015WWL01VTF01 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Fan | Wet Well Fan and duct | Hamilton |  | Rockcliffe |  |  | Building Mechanical | Building Mechanical | Ventilation System | [6 empty] | 1992 |  | 2021 | COH-DC015-0348 |  |  |  | 2 |  |  |  | 5500 | 1 | ea. | 2020 | [9 empty] | 3.5 |  | 2020-07-13 12:57 | Maira Rafiq | 2020-08-19 22:00 | [6 empty] | 1 | CC: The wet well was equipped with a supply fan only. This do not conform with NFPA 820 Section 9.2.6 requirements. As per the mentioned section ventilation system serving classified locations shall maintain a minimum differential pressure relative to amb | Minor corrosion on fan casing | Moderate corrosion on the duct | [5 empty] | 39_merge |  |  |  |  | FALSE | FALSE
115 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 147 | Washroom Exhaust (New Asset) |  | Hamilton |  | Rockcliffe | Main Building | Washroom | Building Mechanical | Building Mechanical | Ventilation System | [9 empty] | COH-DC015-0339 | [7 empty] | 3500 | 1 | ea. | 2020 | [9 empty] | 1 | Patryk Frankiewicz | 2020-07-10 11:28 | Maira Rafiq | 2020-08-19 22:00 | [6 empty] | 1 | CC: There was no exhaust fan installed in the washroom, which do not conform with the OBC 9.32.3.5 “Supplemental Exhaust” requirements. Additionally, as per City’s Wastewater Outstations Design Manual Ref. No. 13.1.3 one exhaust fan with an on/off switch | [7 empty] | 40_merge |  |  |  |  | FALSE | FALSE
116 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 147 | Backflow Preventer | Water Meter and Backflow relocation | Hamilton | Installed | Rockcliffe | Wet Well |  | Building Mechanical | Building Mechanical | Domestic Plumbing System | [6 empty] | 1912 |  |  | COH-DC015-0214 |  |  |  | 3 |  |  |  | 20000 | 1 | ea. | 2020 | [9 empty] | 1 |  | 2020-07-13 12:49 | Maira Rafiq | 2020-08-19 22:01 | [6 empty] | 1 | HS: The backflow was installed in the wet well. As per Ontario’s Design Guidelines for Sewage Works Section 7.3, backflow preventers require periodic inspection, maintenance and induce high pressure loss and therefore cannot be installed below ground leve | Minor corrosion on bolts | [6 empty] | 41_merge |  |  |  |  | FALSE | FALSE
117 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 147 | Fire Extinguisher | Total of 1 | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Mechanical | Building Mechanical | Miscellaneous Mechanical | [6 empty] | 2020 |  |  | COH-DC015-0305 |  |  |  | 3 |  |  |  | 100 | 1 | ea. | 2020 | [9 empty] | 2.5 |  | 2020-07-13 13:11 | Maira Rafiq | 2020-08-19 22:01 | [6 empty] | 1 | Very Good | [7 empty] | 42_merge |  |  |  |  | FALSE | FALSE
118 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Overflow Piping | Overflow yard piping. Unknown material. Approximate Length: 30 meters, Pipe Dia: 600mm. Assumed to be reinformed concrete pipe installed in 1992 | Hamilton | In Service | Rockcliffe | Site |  | Process Mechanical | Process Mechanical Piping and Equipment | [14 empty] | 3 |  |  |  | 325 | 35 | ea. | 2020 | [9 empty] | 4 | CAMR061927 | 2020-08-06 14:40 | Maira Rafiq | 2020-08-19 21:42 | [6 empty] | 1 | Stones build-up at the discharge end | [8 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
119 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 2 | Asphalt Pavement | Asphalt Pavement, approximate area: 250 square meter | Hamilton | In Service | Rockcliffe | Site |  | Site Works | Site Civil |  | Road | [5 empty] | 1992 |  |  | COH-DC015-0444 |  |  |  | 1 |  |  |  | 55 | 250 | ea. | 2020 | [9 empty] | 1.25 | CAMR061927 | 2020-08-07 12:11 | Maira Rafiq | 2020-08-18 17:03 | [6 empty] | 1 | Vegetation and pot holes at the site entrance, Gravels and mud | HS: The presence of gravel and dirt on the driveway adjacent to the wet well presents a trip hazard. | [7 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
120 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 2 | Station Manual Perimeter Fencing Gate | Station Manual Perimeter Fencing Gate, approxiate length: 5 meters. | Hamilton |  | Rockcliffe | Site |  | Site Works | Site Civil |  | Gate | [8 empty] | COH-DC015-0424 |  |  |  | 1 |  |  |  | 3380 | 1 | ea. | 2020 | [9 empty] | 3.1875 | CAMR061927 | 2020-08-07 13:06 | Maira Rafiq | 2020-08-18 17:03 | [6 empty] | 1 | Minor corrosion, broken barbed wires and deformation of the gate | OM: It was identified by the operator that the station has experienced vandalism in the past. | [7 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
121 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 2 | Perimeter Fencing | Perimeter Fencing, installation year: 1992, Approximate Length: 110 meters | Hamilton |  | Rockcliffe | Site |  | Site Works | Site Civil |  | Fencing | [8 empty] | COH-DC015-0445 |  |  |  | 1 |  |  |  | 170 | 110 | ea. | 2020 | [9 empty] | 3.1875 | CAMR061927 | 2020-08-07 13:42 | Maira Rafiq | 2020-08-18 16:56 | [6 empty] | 1 | HS: It was identified by the operator that the station has experienced vandalism in the past. | Overgrown vegetation penetrated through the fencing throughout the station | OM: It was identified by the operator that the station has experienced vandalism in the past. | [6 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
122 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 118 | Overflow Flap Gate | Overflow Flap Gate | Hamilton | In Service | Rockcliffe | Site |  | Process Mechanical | Process Mechanical Piping and Equipment |  | Gate | [5 empty] | 1992 |  |  | COH-DC015-0499 |  |  |  | 2 |  |  |  | 0 | 1 | ea. | 2020 | [9 empty] | 0 | CAMR061927 | 2020-08-07 13:41 | Maira Rafiq | 2020-08-19 21:42 | [6 empty] | 1 | blocked by stones and dirt and would not open properly in the event of station overflow. | [8 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
123 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 11 | Diesel Fuel System | Diesel Storage Tanks 1&2; DTE; Capacity 1135 L | Hamilton |  | Rockcliffe | Main Building | Generator Room | Building Mechanical | Building Mechanical | [9 empty] | 2040 | COH-DC015-0313 |  |  |  | 3 |  |  |  | 15000 | 1 | ea. | 2020 | [9 empty] | 1.5 | CAMR061927 | 2020-08-07 13:55 | Maira Rafiq | 2020-08-11 10:00 | [6 empty] | 1 | CC: There was no containment for diesel fuel lines. TSSA requires all equipment containing or carrying fuel to be contained per CSA B139.1.1-15 Section 6.5.1.4. | [8 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
124 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 11 | Generator Intake | Motorized Intake; ; ; ; | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Mechanical | Building Mechanical | [7 empty] | 1992 |  | 2045 | COH-DC015-0322 |  |  |  | 3 |  |  |  | 1430 | 1 | ea. | 2020 | [9 empty] | 2.4375 | CAMR061927 | 2020-08-07 13:59 | Maira Rafiq | 2020-08-07 13:59 | [6 empty] | 1 | Good | minor surface corrosion | [7 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
125 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 147 | Control Room Exhaust Fan | DC015, GENERATOR/CONTROL ROOM EXHAUST FAN; Canadian Blower; 16; S218650000001; | Hamilton | In Service | Rockcliffe | Main Building |  | Building Mechanical | Building Mechanical | [7 empty] | 2010 |  | 2040 | COH-DC015-0324 |  |  |  | 2 |  |  |  | 1430 | 1 | ea. | 2020 | [9 empty] | 2.4375 | CAMR061927 | 2020-08-07 14:00 | Maira Rafiq | 2020-08-19 22:01 | [6 empty] | 1 | good | good | [7 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
126 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 11 | Generator Flue Exhaust | Exhaust Silencer and Stack | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Building Mechanical | Building Mechanical | [7 empty] | 1992 |  | 2045 | COH-DC015-0329 |  |  |  | 3 |  |  |  | 20000 | 1 | ea. | 2020 | [9 empty] | 1 | CAMR061927 | 2020-08-07 14:02 | Maira Rafiq | 2020-08-19 22:01 | [6 empty] | 1 | good | [8 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
127 | 9 | DC015SLP0200000 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Sewage Lift Pump No.2 | Submersible Pump No.2;ITT;CP3201.180; 140 L/s @ 14m TDH, 28 kW | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Pump | [6 empty] | 2009 |  |  | COH-DC015-0281 |  |  |  | 3 |  |  |  | 137700 | 1 | ea. | 2020 | [9 empty] | 1.3625 | CAMR061927 | 2020-08-11 14:36 | Maira Rafiq | 2020-08-11 14:36 | [6 empty] | 1 | Good | [8 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
128 | 10 | DC015SLP0300000 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Sewage Lift Pump No.3 | Submersible Pump No.3;ITT;CP3201.180; 140 L/s @ 14m TDH, 28 kW | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Pump | [6 empty] | 2009 |  |  | COH-DC015-0280 |  |  |  | 3 |  |  |  | 137700 | 1 | ea. | 2020 | [9 empty] | 1.3625 | CAMR061927 | 2020-08-11 14:36 | Maira Rafiq | 2020-08-11 14:36 | [6 empty] | 1 | Good | [8 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
129 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 3 | Hand Stop Gate No.1 | Hand Stop Gate No.1;;;;36"X 36" | Hamilton | Not In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Gate | [6 empty] | 1992 |  |  | COH-DC015-0236 |  |  |  | 2 |  |  |  | 6080 | 1 | ea. | 2020 | [9 empty] | 1.85 | CAMR061927 | 2020-08-11 14:36 | Maira Rafiq | 2020-08-19 21:43 | [6 empty] | 1 | Deterioration | [8 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
130 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Concrete Structure | Reinforced concrete wet well structure | Hamilton |  | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 |  | 2052 | COH-DC015-0001 |  |  |  | 3 |  |  |  | 280000 | 1 | ea. | 2020 | [9 empty] | 2 | CAMR061927 | 2020-08-07 15:29 | Maira Rafiq | 2020-08-18 17:32 | [6 empty] | 1 | good | concrete was found to be hard/strong based on hammer striking and schmidt hammer test. Concrete cover at 51mm based on cover meter test | [7 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
131 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Aluminum Ladder | Aluminum ladder from exterior to intermetdiate platform (with cage) | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 |  | 2052 | COH-DC015-0039 |  |  |  | 1 |  |  |  | 3500 | 1 | ea. | 2020 | [9 empty] | 1.5 | CAMR061927 | 2020-08-10 09:14 | Maira Rafiq | 2020-08-18 17:32 | [6 empty] | 1 | buildup of calcium and minor pitting | [8 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
132 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Aluminum Ladder | Aluminum ladder from intermediate platform to lower platform (with cage) | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 |  | 2052 | COH-DC015-0039 |  |  |  | 1 |  |  |  | 3500 | 1 | ea. | 2020 | [9 empty] | 1.5 | CAMR061927 | 2020-08-10 09:17 | Maira Rafiq | 2020-08-18 17:31 | [6 empty] | 1 | buildup of calcium and minor pitting | [8 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
133 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Aluminum Ladder | Aluminum ladder from lower platform to wet well | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 |  | 2052 | COH-DC015-0050 |  |  |  | 1 |  |  |  | 2500 | 1 | ea. | 2020 | [9 empty] | 1.5 | CAMR061927 | 2020-08-10 09:18 | Maira Rafiq | 2020-08-18 17:31 | [6 empty] | 1 | HS: buildup of calcium and minor pitting | [8 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
134 |  | DC015WWL02LSL01 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wetwell 2 Low Level Float | Wetwell No.2 Low Level Float; ; ; ; | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Instrumentation | Process Instrumentation & Control | [7 empty] | 2016 |  |  | COH-DC015-0269 |  |  |  | 2 |  |  |  | 500 | 1 | ea. | 2020 | [9 empty] | 1.3 | CAMR061927 | 2020-08-11 17:13 | Maira Rafiq | 2020-08-19 21:50 | [6 empty] | 1 | [9 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
135 |  | DC015WWL01LSL01 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wetwell 1 Low Level Float | Wetwell No.1 Low Level Float; ; ; ; | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Instrumentation | Process Instrumentation & Control | [7 empty] | 2016 |  |  | COH-DC015-0269 |  |  |  | 2 |  |  |  | 500 | 1 | ea. | 2020 | [9 empty] | 1.3 | CAMR061927 | 2020-08-11 17:13 | Maira Rafiq | 2020-08-19 21:50 | [6 empty] | 1 | [9 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
136 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 146 | Exit Lighting (New Asset) |  | Hamilton |  | Rockcliffe | Main Building | Generator Room | Building Electrical | Building Electrical | Lighting | [13 empty] | 2 |  |  |  | 500 | 1 | ea. | 2020 | [9 empty] | 1.3 | CAMR061927 | 2020-08-11 17:05 | Maira Rafiq | 2020-08-19 21:58 | [6 empty] | 1 | CC: There was no exit sign installed at the station. The station needs an exit sign according to Canadian Building Code (section 3.2.7.3) and Canadian Fire Code (Section 2.7.3). | [8 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
137 | 14 |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Inlet Chamber 1 |  | Hamilton | In Service | Rockcliffe | Site | Inlet Chamber 1 | Process Structural | Process Structural | [7 empty] | 1992 |  |  | COH-DC015-0095 |  |  |  | 1 | [5 empty] | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-19 16:59 | [6 empty] | 1 | [9 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
138 | 15 |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Valve Chamber |  | Hamilton | In Service | Rockcliffe | Site | Valve Chamber | Process Structural | Process Structural | [7 empty] | 1992 |  |  | COH-DC015-0103 |  |  |  | 1 | [5 empty] | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-19 16:57 | [6 empty] | 1 | [9 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
139 | 16 |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Inlet Chamber 2 |  | Hamilton | In Service | Rockcliffe | Site | Inlet Chamber 2 | Process Structural | Process Structural | [7 empty] | 1992 |  |  | COH-DC015-0097 |  |  |  | 1 | [5 empty] | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-19 16:58 | [6 empty] | 1 | [9 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
140 | 6 |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE |  | Process Electrical |  | Hamilton |  | Rockcliffe |  |  | Process Electrical | Process Electrical | [20 empty] | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-19 17:07 | [6 empty] | 1 | [9 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
141 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 127 | Pump 2 Piping | Process Mechanical Piping;;;; 7.5 m of 100 mm dia DI pipe, 16.5 m of 200 mm dia DI pipe, 16.5 m of 300 mm DI pipe | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Piping | [6 empty] | 1992 |  |  | COH-DC015-0206 |  |  |  | 3 | [5 empty] | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-19 21:46 | [6 empty] | 1 | [9 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
142 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 128 | Pump 3 Piping | Process Mechanical Piping;;;; 7.5 m of 100 mm dia DI pipe, 16.5 m of 200 mm dia DI pipe, 16.5 m of 300 mm DI pipe | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Piping | [6 empty] | 1992 |  |  | COH-DC015-0206 |  |  |  | 3 | [5 empty] | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-19 21:46 | [6 empty] | 1 | [9 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
143 | 11 |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Discharge Header | Process Mechanical Piping;;;; 7.5 m of 100 mm dia DI pipe, 16.5 m of 200 mm dia DI pipe, 16.5 m of 300 mm DI pipe | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Piping | [6 empty] | 1992 |  |  | COH-DC015-0206 |  |  |  | 3 | [5 empty] | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-19 21:45 | [6 empty] | 1 | [9 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
144 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 143 | Drain Piping | Process Mechanical Piping;;;; 7.5 m of 100 mm dia DI pipe, 16.5 m of 200 mm dia DI pipe, 16.5 m of 300 mm DI pipe | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Piping | [6 empty] | 1992 |  |  | COH-DC015-0206 |  |  |  | 3 | [5 empty] | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-19 21:45 | [6 empty] | 1 | [9 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
145 | 7 |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE |  | Process Instrumentation & Control |  | Hamilton |  | Rockcliffe |  |  | Process Instrumentation | Process Instrumentation & Control | [20 empty] | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-19 21:48 | [6 empty] | 1 | [9 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
146 | 2 |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE |  | Building Electrical |  | Hamilton |  | Rockcliffe |  |  | Building Electrical | Building Electrical | [20 empty] | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-19 21:55 | [6 empty] | 1 | [9 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
147 | 4 |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE |  | Building Mechanical |  | Hamilton |  | Rockcliffe |  |  | Building Mechanical | Building Mechanical | [20 empty] | ea. | 2020 | [12 empty] | Maira Rafiq | 2020-08-19 21:59 | [6 empty] | 1 | [9 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE

## cof
AssetID | AssetName | CoF
1 | Rockcliffe WWPS
2 | Site Civil
3 | Sewage Lift Pump No.1 | 3
4 | MCC | 3
5 | SCADA WAN Panel | 3
6 | Process Structural
7 | Unit Heater 1 | 2
8 | Interior Lighting | 2
9 | Building Structural
10 | Building Architectural
11 | Emergency Backup Power | 3
13 | MAIN BREAKER | 3
14 | Diesel Fuel Tank #1 For Generator | 3
15 | Diesel Fuel Tank #2 For Generator | 3
17
18
20 | Standby Diesel Power Generator | 3
22
24
25
26
27
30 | Wet Well Level Transmitter #1 | 2
31 | Wet Well Level Transmitter #2 | 2
32 | Power Meter | 3
33 | Main Breaker | 3
34 | Power Factor Capacitors | 2
35 | Unit Heater Starter | 2
36 | Hand Stop Gate No.2 | 2
37 | Hand Stop Gate No.3 | 2
38 | Manual Bar Screen No.1 | 2
39 | Manual Bar Screen No.2 | 2
40 | Sewage Lift Pump No.1 Check Valve | 2
41 | Sewage Lift Pump No.2 Check Valve | 2
42 | Sewage Lift Pump No.3 Check Valve | 2
43 | Sewage Lift Pump No.1 Discharge Valve | 2
44 | Sewage Lift Pump No.2 Discharge Valve | 2
45 | Sewage Lift Pump No.3 Discharge Valve | 2
46 | Discharge Header Gate Valve | 3
47 | Drain Gate Valve | 2
48 | Pressure Release Valve No.1 | 2
49 | Wetwell Cell Isolation Gate | 3
50 | Sluice Gate No.1 | 2
51 | Process Mechanical Piping | 3
52 | Forcemain | 4
53 | SCADA PANEL | 3
54 | Station Temperature Transmitter | 2
55 | UPS | 2
56 | Wetwell 1 High Level Float | 2
57 | Wetwell 2 High Level Float | 2
58 | Pump 1 VFD | 2
59 | Wet well Fan Starter | 2
60 | Diesel Generator Room Fan Starter | 2
61 | Pump 2 VFD | 2
62 | Pump 3 VFD | 2
63 | Diesel Generator Control Panel | 3
64 | Emergency Lighting | 2
65 | Lighting Panel LPA | 3
66 | Lighting Trasnformer | 3
67 | Exterior Lighting | 2
68 | Wet Well Lighting | 2
69 | Main Transformer | 3
70 | Manhole 1
71 | Manhole 2
72 | Manhole 3
73 | Signboards | 1
75 | Station Access Road | 1
76 | Sanitary Sewer | 3
77 | Wet Well Aluminum Ladder | 2
78 | Wet Well Aluminum Guardrail | 2
79 | Wet Well Aluminum Grating | 2
80 | Wet Well Access Hatch | 2
81 | Wet Well Pump Hatch 1 | 2
82 | Wet Well Pump Hatch 2 | 2
83 | Wet Well Pump Hatch 3 | 2
84 | Wet Well Pump Hatch 4 | 2
85 | Wet Well Davit Base 1 | 2
86 | Wet Well Davit Base 2 | 2
87 | Inlet Chamber 1 Concrete Structure | 1
88 | Inlet Chamber 1 Aluminum Platform | 1
89 | Inlet Chamber 1 Aluminum Ladder | 1
90 | Inlet Chamber 1 Manhole Frame and Cover | 1
91 | Inlet Chamber 2 Concrete Structure | 1
92 | Inlet Chamber 2 Aluminum Platform | 1
93 | Inlet Chamber 2 Aluminum Ladder | 1
94 | Inlet Chamber 2 Manhole Frame and Cover | 1
95 | Generator Building Concrete Foundation | 3
96 | Generator Building Concrete Floor | 3
97 | Generator Building Masonry Blockwall | 3
98 | Generator Building Precast Concrete Roof | 3
99 | Valve Chamber Manhole Frame and Cover | 1
100 | Valve Chamber Aluminum Ladder | 1
101 | Valve Chamber Concrete Structure | 1
102 | Generator Building Exterior Stone Veneer | 3
103 | Generator Building Asphalt Shingle Roofing | 3
104 | Generator Building Wood Truss Roof | 3
105 | Generator Building Wall and Ceiling Paint | 1
106 | Generator Building Containment Coating | 1
107 | Generator Building Roof Access Hatch | 1
108 | Generator Building Exterior Access Door (Double) | 2
109 | Generator Building Interior Door (Single) | 2
110 | Generator Building Aluminum Ladder | 2
111 | Generator Exhaust | 3
112 | Baseboard Heater | 2
113 | Hot Water Tank | 2
114 | Wet Well Fan | 2
115 | Washroom Exhaust (New Asset)
116 | Backflow Preventer | 3
117 | Fire Extinguisher | 3
118 | Overflow Piping | 3
119 | Asphalt Pavement | 1
120 | Station Manual Perimeter Fencing Gate | 1
121 | Perimeter Fencing | 1
122 | Overflow Flap Gate | 2
123 | Diesel Fuel System | 3
124 | Generator Intake | 3
125 | Control Room Exhaust Fan | 2
126 | Generator Flue Exhaust | 3
127 | Sewage Lift Pump No.2 | 3
128 | Sewage Lift Pump No.3 | 3
129 | Hand Stop Gate No.1 | 2
130 | Wet Well Concrete Structure | 3
131 | Wet Well Aluminum Ladder | 1
132 | Wet Well Aluminum Ladder | 1
133 | Wet Well Aluminum Ladder | 1
134 | Wetwell 2 Low Level Float | 2
135 | Wetwell 1 Low Level Float | 2
136 | Interior Lighting | 2

## Comments
ParentID | Comment1 | Comment2 | Comment3
1
2
3 | The pumps were assumed to be in good condition based on its age. No performance issues were identified during the inspection. | Good
4 | good | starters and main disconnect switch are priced seperatly | CC: Missing Arc Flash labels
5 | Good
6
7 | CC: There was no containment for diesel fuel lines. TSSA requires all equipment containing or carrying fuel to be contained per CSA B139.1.1-15 Section 6.5.1.4. | Good conditon
8 | good | replace with LED in next upgrade
9
10
11
12
13
14 | Tanks appear to be in good condition | CC: There was no containment for diesel fuel lines. TSSA requires all equipment containing or carrying fuel to be contained per CSA B139.1.1-15 Section 6.5.1.4.
15 | Tanks appear to be in good condition | CC: There was no containment for diesel fuel lines. TSSA requires all equipment containing or carrying
16
17
18
19
20 | good
21
22
23
24
25
26
27
28
29
30 | Very good
31 | Very Good
32 | good
33 | Good | CC: Missing Arc Flash labels
34 | Good
35 | good | CC: Missing Arc Flash labels
36 | Poor | The gate was at three quarter of its expected life and deterioration was observed.
37 | Poor | The gate was at three quarter of its expected life and deterioration was observed.
38 | Very Poor | Detrioration observed. Some of the bars were bent. | The operators mentioned that the screens have been removed and are no longer in use.
39 | Very Poor | Detrioration observed. Some of the bars were bent. | The operators mentioned that the screens have been removed and are no longer in use.
40 | Very Poor | Heavy corrosion and deterioration
41 | Very Poor | Heavy corrosion and deterioration
42 | Very Poor | Heavy corrosion and Deterioration
43 | Very Poor | Heavy corrosion and deterioration
44 | Very Poor | Heavy corrosion and Deterioration
45 | Very Poor | Heavy corrosion and Deterioration
46 | Very Poor | Turn wheel is missing. Heavy corrosion and deterioration.
47 | Very Poor | Heavy corrosion and deterioratino
48 | Very Poor | Heavy corrosion and Deterioration
49 | Poor | The valve was over three quarters of its expected service life. Moderate surface corrosion was observed
50 | Poor | Heavy corrosion and deterioration was observed on the frame of the sluice gate
51 | Very Poor | Heavy corrosion and deterioration was observed on majority portion of the piping.
52
53 | Good
54 | Good | Communication via Pribusin transmitter is old technology and will be obselete in near future. It is recommended tp replace the temperature trasmitter with a cellular transmitter or a hardwired signal from the temperature device to directly connected to th
55 | good | Dust
56 | Good
57 | Good
58 | good | CC: Missing Arc Flash labels
59 | good | CC: Missing Arc Flash labels
60 | good | CC: Missing Arc Flash labels
61 | good | CC: Missing Arc Flash labels
62 | good | CC: Missing Arc Flash labels
63 | good | CC: Missing Arc Flash labels
64 | good
65 | good
66 | good
67 | good
68 | fair | corroded | to be replaced with class 1, div 1 fixture
69 | good
70 | Good Condition
71 | Good Condition
72 | Good condition
73 | Good condition. Dirt on the signboard was observed
74 | The overflow piping was assumed to be in good condition based on age. The discharge of the overflow piping is equipped with a flap gate. Stones build-up at the discharge end was observed.
75 | The access road was in fair condition. Pot holes and mud bumps were obserevd.
76 | The sanitary sewer piping was assumed to be in good condition bassed on age.
77 | fair | buildup of calcium and minor pitting
78 | fair | buildup of calcium and minor pitting
79 | fair | buildup of calcium and minor pitting | HS: One section of grating was missing and should be installed/replaced
80 | good
81 | good | HS: retrofit of safety grating underneath the pump hatch is recommended to mitgate a falling hazard when hatch is open
82 | good | retrofit of safety grating underneath the pump hatch is recommended to mitgate a falling hazard when hatch is open
83 | good | retrofit of safety grating underneath the pump hatch is recommended to mitgate a falling hazard when hatch is open
84 | good | retrofit of safety grating underneath the pump hatch is recommended to mitgate a falling hazard when hatch is open
85 | good
86 | good | Missing cap
87 | good
88 | good
89 | good
90 | good
91 | good
92 | good
93 | good
94 | good
95 | Hidden and could not be inspected. Good based on condition of other visible structural assets
96 | good
97 | good
98 | good
99 | good
100 | good
101 | good
102 | good
103 | good
104 | hidden under asphalt singles and precast roof. Assumed to be good based on condition of other visible assets
105 | good | Missing/bare spot at washroom
106 | good
107 | good
108 | surface corrosion and corrosion on hardware | weathered paint
109 | good
110 | good
111 | Good condition.
112 | Fair condition | Discoloration and dust
113 | Fair condition, typical hot water heater is at the end of its life
114 | CC: The wet well was equipped with a supply fan only. This do not conform with NFPA 820 Section 9.2.6 requirements. As per the mentioned section ventilation system serving classified locations shall maintain a minimum differential pressure relative to ambient | Moderate corrosion on the duct | Minor corrosion on fan casing
115 | CC: There was no exhaust fan installed in the washroom, which do not conform with the OBC 9.32.3.5 “Supplemental Exhaust” requirements. Additionally, as per City’s Wastewater Outstations Design Manual Ref. No. 13.1.3 one exhaust fan with an on/off switch with
116 | HS: The backflow was installed in the wet well. As per Ontario’s Design Guidelines for Sewage Works Section 7.3, backflow preventers require periodic inspection, maintenance and induce high pressure loss and therefore cannot be installed below ground level. | Fair | Minor corrosion on bolts
117 | Very Good
118 | The overflow piping was assumed to be in good condition based on age. The discharge of the overflow piping in equipped with a flap gate. Stones build-up at the discharge end was observed.
119 | The access road was in good condition overall. Vegetation and pot holes at the site entrance were observed. Gravels and mud were noted throughout the site. | HS: The presence of gravel and dirt on the driveway adjacent to the wet well presents a trip hazard.
120 | The manual perimeter fencing gate was in fair condition. Minor corrosion, broken barbed wires and deformation of the gate was observed. | It was identified by the operator that the station has experienced vandalism in the past.
121 | HS: It was identified by the operator that the station has experienced vandalism in the past. | The fencing was in fair condition. Overgrown vegetation penetrated through the fencing throughout the station was obsereved. Minor corrosion throughout the fencing, as well as broken barbed wires were observed. | It was identified by the operator that the station has experienced vandalism in the past.
122 | The flap gate was in good condition overall. The flap gate was blocked by stones and dirt and would not open properly in the event of station overflow.
123 | Tanks appear to be in good condition | CC: There was no containment for diesel fuel lines. TSSA requires all equipment containing or carrying fuel to be contained per CSA B139.1.1-15 Section 6.5.1.4.
124 | Damper appears to be original | Good condition | minor surface corrosion
125 | Summer Ventilation Exhaust Fan. Original to the building. | Good condition
126 | Fully insulated silencer and exhaust piping. All original to building.
127 | The pumps were assumed to be in good condition based on its age. No performance issues were identified during the inspection. | Good
128 | Good | The pumps were assumed to be in good condition based on its age. No performance issues were identified during the inspection.
129 | Poor | The gate was at three quarter of its expected life and deterioration was observed.
130 | good | concrete was found to be hard/strong based on hammer striking and schmidt hammer test. Concrete cover at 51mm based on cover meter test
131 | fair | buildup of calcium and minor pitting
132 | fair | buildup of calcium and minor pitting
133 | fair | HS: buildup of calcium and minor pitting
134
135
136 | CC: There was no exit sign installed at the station. The station needs an exit sign according to Canadian Building Code (section 3.2.7.3) and Canadian Fire Code (Section 2.7.3).

## Cap
WorkID | ParentID | CAPEXType | WorkShortName | WorkDescription | CostID | MaterialUnitCost | Quantity | UnitOfQuantity | CostYear | CostSource | MarkupEquipment | MarkupLabour | MarkupAncillary | MarkupRemoval | MarkupEngineering | MarkupAdministration | MarkupContractor | MarkupContingency | TotalReplacementMarkup | WorkYear | Recurring | WorkFrequency | DBNotes
1 | 3 | Replacement |  |  | 471 | 137700 | 1 | ea. | 2020 | [9 empty] | 1.3625 |  | FALSE | 0
5 | 36 | Replacement |  |  | 963 | 6080 | 1 | ea. | 2020 | [9 empty] | 1.85 |  | FALSE | 0 | 36_merge
6 | 37 | Replacement |  |  | 963 | 6080 | 1 | ea. | 2020 | [9 empty] | 1.85 |  | FALSE | 0 | 37_merge
7 | 38 | Replacement |  |  |  | 9000 | 1 | ea. | 2020 | [9 empty] | 1.4 |  | FALSE | 0 | 38_merge
8 | 39 | Replacement |  |  |  | 9000 | 1 | ea. | 2020 | [9 empty] | 1.4 |  | FALSE | 0 | 39_merge
9 | 40 | Replacement |  |  | 626 | 1990 | 1 | ea. | 2020 | [9 empty] | 2.5 |  | FALSE | 0 | 40_merge
10 | 41 | Replacement |  |  | 626 | 1990 | 1 | ea. | 2020 | [9 empty] | 2.5 |  | FALSE | 0 | 41_merge
11 | 42 | Replacement |  |  | 626 | 1990 | 1 | ea. | 2020 | [9 empty] | 2.5 |  | FALSE | 0 | 42_merge
12 | 43 | Replacement |  |  | 580 | 1520 | 1 | ea. | 2020 | [9 empty] | 2.5 |  | FALSE | 0 | 43_merge
13 | 44 | Replacement |  |  | 580 | 1520 | 1 | ea. | 2020 | [9 empty] | 2.5 |  | FALSE | 0 | 44_merge
14 | 45 |  |  |  | 580 | 1520 | 1 | ea. | 2020 | [9 empty] | 2.5 |  | FALSE | 0 | 45_merge
15 | 46 |  |  |  | 582 | 2790 | 1 | ea. | 2020 | [9 empty] | 2.5 |  | FALSE | 0 | 46_merge
16 | 47 |  |  |  | 578 | 630 | 1 | ea. | 2020 | [9 empty] | 2.5 |  | FALSE | 0 | 47_merge
17 | 48 |  |  |  | 694 | 2280 | 1 | ea. | 2020 | [9 empty] | 2.5 |  | FALSE | 0 | 48_merge
18 | 49 |  |  |  | 582 | 2790 | 1 | ea. | 2020 | [9 empty] | 2.5 |  | FALSE | 0 | 49_merge
19 | 50 |  |  |  | 951 | 25340 | 1 | ea. | 2020 | [9 empty] | 1.85 |  | FALSE | 0 | 51_merge
20 | 51 |  |  | 100 mm 316 SS |  | 142 | 8 | m | 2020 | [9 empty] | 1.6 |  | FALSE | 0 | 52_merge
21 | 51 |  |  | 200 mm 316 SS |  | 402 | 16 | m | 2020 | [9 empty] | 1.6 |  | FALSE | 0 | 52_merge
22 | 51 |  |  | 300 mm 316 SS |  | 672 | 16 | m | 2020 | [9 empty] | 1.6 |  | FALSE | 0 | 52_merge
23 | 5 | Replacement | Replacement | Replacement: like for like |  | 7000 | 1 | ea. | 2020 | [9 empty] | 1.3 |  | FALSE | 0
25 | 53 | Replacement | Replacement | Replacement: like for like |  | 40000 | 1 | ea. | 2020 | [9 empty] | 1 |  | FALSE | 0 | 36_merge
26 | 54 | Replacement | Replacement | Replacement: like for like |  | 800 | 1 | ea. | 2020 | [9 empty] | 1.3 |  | FALSE | 0 | 37_merge
27 | 55 | Replacement | Replacement | Replacement: like for like |  | 3000 | 1 | ea. | 2020 | [9 empty] | 1.2 |  | FALSE | 0 | 38_merge
28 | 56 | Replacement | Replacement | Replacement: like for like |  | 500 | 1 | ea. | 2020 | [9 empty] | 1.3 |  | FALSE | 0 | 40_merge
29 | 57 | Replacement | Replacement | Replacement: like for like |  | 500 | 1 | ea. | 2020 | [9 empty] | 1.3 |  | FALSE | 0 | 41_merge
30 | 4 | Replacement |  |  |  | 40000 | 1 | ea. | 2020 | [9 empty] | 2 | 2030 | FALSE | 0
31 | 8 | Replacement |  | Replace with LEDs |  | 300 | 6 | ea. | 2020 | [9 empty] | 3.125 | 2030 | FALSE | 0
32 | 32 | Replacement |  |  |  | 11000 | 1 | ea. | 2020 | [9 empty] | 2 | 2030 | FALSE | 0
33 | 33 | Replacement |  |  |  | 3800 | 1 | ea. | 2020 | [9 empty] | 3.125 | 2030 | FALSE | 0
34 | 34 | Replacement |  |  |  | 10000 | 3 | ea. | 2020 | [9 empty] | 1.5 | 2043 | FALSE | 0
35 | 35 | Replacement |  |  |  | 2600 | 1 | ea. | 2020 | [9 empty] | 1.7 | 2030 | FALSE | 0
36 | 58 | Replacement |  |  |  | 19000 | 1 | ea. | 2020 | [9 empty] | 1.7 | 2030 | FALSE | 0 | 36_merge
37 | 59 | Replacement |  |  |  | 2500 | 1 | ea. | 2020 | [9 empty] | 1.7 | 2030 | FALSE | 0 | 37_merge
38 | 60 | Replacement |  |  |  | 2500 | 1 | ea. | 2020 | [9 empty] | 1.7 | 2030 | FALSE | 0 | 38_merge
39 | 61 | Replacement |  |  |  | 19000 | 1 | ea. | 2020 | [9 empty] | 1.7 | 2030 | FALSE | 0 | 39_merge
40 | 62 | Replacement |  |  |  | 19000 | 1 | ea. | 2020 | [9 empty] | 1.7 | 2030 | FALSE | 0 | 40_merge
41 | 63 | Replacement |  |  |  | 30000 | 1 | ea. | 2020 | [9 empty] | 2.25 | 2030 | FALSE | 0 | 41_merge
42 | 64 | Replacement |  |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 1.5 | 2043 | FALSE | 0 | 42_merge
43 | 65 | Replacement |  |  |  | 2000 | 1 | ea. | 2020 | [9 empty] | 3.125 | 2030 | FALSE | 0 | 43_merge
44 | 66 | Replacement |  |  |  | 5100 | 1 | ea. | 2020 | [9 empty] | 3.125 | 2030 | FALSE | 0 | 44_merge
45 | 67 | Replacement |  |  |  | 300 | 1 | ea. | 2020 | [9 empty] | 3.125 | 2030 | FALSE | 0 | 45_merge
46 | 68 | Replacement |  | Replace with Class 1, Div 1 fixture |  | 700 | 3 | ea. | 2020 | [9 empty] | 3.125 | 2025 | FALSE | 0 | 46_merge
47 | 69 | Replacement |  |  |  | 57000 | 1 | ea. | 2020 | [9 empty] | 2.25 | 2030 | FALSE | 0 | 47_merge
48 | 73 | Replacement |  | Replacement: Like for Like | 51 | 60 | 2 | ea. | 2020 | [9 empty] | 3.1875 |  | FALSE | 0 | 40_merge
50 | 75 | Upgrade | Paving the Access Road | Resurfacing the access road | 30 | 55 | 30 | ea. | 2020 | [9 empty] | 1.25 | 2021 | FALSE | 0 | 43_merge
51 | 76 | Replacement | Replacement of Sanitary Yard Piping | End of service life | 71 | 80 | 21 | ea. | 2020 | [9 empty] | 10.7 | 2072 | FALSE | 0 | 44_merge
52 | 77 | Replacement |  |  |  | 2500 | 1 | ea. | 2020 | [9 empty] | 1.5 | 2052 | FALSE | 0 | 36_merge
53 | 78 | Replacement |  |  |  | 200 | 20 | ea. | 2020 | [9 empty] | 2 |  | FALSE | 0 | 37_merge
54 | 79 | Replacement |  |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 1 | 2052 | FALSE | 0 | 38_merge
55 | 80 | Replacement |  |  |  | 5000 | 1 | ea. | 2020 | [9 empty] | 1 | 2052 | FALSE | 0 | 39_merge
56 | 81 | Replacement |  |  |  | 5000 | 1 | ea. | 2020 | [9 empty] | 1 | 2052 | FALSE | 0 | 40_merge
57 | 82 | Replacement |  |  |  | 6500 | 1 | ea. | 2020 | [9 empty] | 1 | 2052 | FALSE | 0 | 41_merge
58 | 83 | Replacement |  |  |  | 6500 | 1 | ea. | 2020 | [9 empty] | 2 | 2052 | FALSE | 0 | 42_merge
59 | 84 | Replacement |  |  |  | 6500 | 1 | ea. | 2020 | [9 empty] | 1 | 2052 | FALSE | 0 | 43_merge
60 | 85 | Replacement |  |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 2 |  | FALSE | 0 | 44_merge
61 | 86 | Replacement |  |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 2 | 2052 | FALSE | 0 | 45_merge
62 | 87 | Replacement |  |  |  | 35000 | 1 | ea. | 2020 | [9 empty] | 2 | 2052 | FALSE | 0 | 46_merge
63 | 88 | Replacement |  |  |  | 3000 | 1 | ea. | 2020 | [9 empty] | 2 | 2052 | FALSE | 0 | 47_merge
64 | 89 | Replacement |  |  |  | 5500 | 1 | ea. | 2020 | [9 empty] | 2 | 2052 | FALSE | 0 | 48_merge
65 | 90 | Replacement |  |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 2 | 2052 | FALSE | 0 | 49_merge
66 | 91 | Replacement |  |  |  | 35000 | 1 | ea. | 2020 | [9 empty] | 2 | 2052 | FALSE | 0 | 50_merge
67 | 92 | Replacement |  |  |  | 3000 | 1 | ea. | 2020 | [9 empty] | 2 | 2052 | FALSE | 0 | 51_merge
68 | 93 | Replacement |  |  |  | 5500 | 1 | ea. | 2020 | [9 empty] | 2 | 2052 | FALSE | 0 | 52_merge
69 | 94 | Replacement |  |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 2 | 2052 | FALSE | 0 | 53_merge
70 | 95 | Replacement |  |  |  | 40000 | 1 | ea. | 2020 | [9 empty] | 1 | 2052 | FALSE | 0 | 54_merge
71 | 96 | Replacement |  |  |  | 1200 | 17 | ea. | 2020 | [9 empty] | 1.5 | 2052 | FALSE | 0 | 55_merge
72 | 97 | Replacement |  |  |  | 150 | 76 | ea. | 2020 | [9 empty] | 2.5 | 2052 | FALSE | 0 | 56_merge
73 | 98 | Replacement |  |  |  | 250 | 42 | ea. | 2020 | [9 empty] | 2.5 | 2052 | FALSE | 0 | 57_merge
74 | 99 | Replacement |  |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 2 |  | FALSE | 0 | 58_merge
75 | 100 | Replacement |  |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 2 | 2052 | FALSE | 0 | 59_merge
76 | 101 | Replacement |  |  |  | 9000 | 1 | ea. | 2020 | [9 empty] | 2 | 2052 | FALSE | 0 | 60_merge
77 | 102 | Replacement |  |  | 261 | 180 | 76 | ea. | 2020 | [9 empty] | 2.5 | 2052 | FALSE | 0 | 61_merge
78 | 103 | Replacement |  |  | 313 | 50 | 50 | ea. | 2020 | [9 empty] | 2 | 2025 | FALSE | 0 | 62_merge
79 | 104 | Replacement |  |  | 325 | 8000 | 1 | ea. | 2020 | [9 empty] | 1 | 2052 | FALSE | 0 | 63_merge
80 | 105 | Replacement |  |  | 244 | 20 | 140 | ea. | 2020 | [9 empty] | 3.2125 | 2025 | FALSE | 0 | 64_merge
81 | 106 | Replacement |  |  | 287 | 60 | 20 | ea. | 2020 | [9 empty] | 2 | 2025 | FALSE | 0 | 65_merge
82 | 107 | Replacement |  |  | 325 | 500 | 1 | ea. | 2020 | [9 empty] | 1.5 | 2052 | FALSE | 0 | 66_merge
83 | 108 | Replacement |  |  | 233 | 2000 | 1 | ea. | 2020 | [9 empty] | 2.5 | 2025 | FALSE | 0 | 67_merge
84 | 109 | Replacement |  |  | 234 | 1520 | 1 | ea. | 2020 | [9 empty] | 2.5 | 2025 | FALSE | 0 | 68_merge
85 | 110 | Replacement |  |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 1.5 | 2052 | FALSE | 0 | 69_merge
86 | 7 | Replacement |  |  | 890 | 760 | 1 | ea. | 2020 | [9 empty] | 2.4375 | 2032 | TRUE | 25
87 | 111 | Replacement |  |  |  | 4500 | 1 | ea. | 2020 | [9 empty] | 1 | 2045 | FALSE | 0 | 36_merge
88 | 112 | Replacement |  |  | 895 | 250 | 1 | ea. | 2020 | [9 empty] | 2.4375 | 2030 | FALSE | 0 | 37_merge
89 | 113 | Replacement |  |  | 1258 | 1200 | 1 | ea. | 2020 | [9 empty] | 2.4375 | 2021 | FALSE | 0 | 38_merge
90 | 114 | Replacement |  |  |  | 5500 | 1 | ea. | 2020 | [9 empty] | 3.5 | 2021 | FALSE | 0 | 39_merge
91 | 115 | Purchase |  |  |  | 3500 | 1 | ea. | 2020 | [9 empty] | 1 | 2021 | FALSE | 0 | 40_merge
92 | 116 | Upgrade |  | Replace the existing backflow preventor with a new backflow preventer above ground |  | 20000 | 1 | ea. | 2020 | [9 empty] | 1 | 2022 | FALSE | 0 | 41_merge
93 | 117 | Replacement |  |  |  | 100 | 1 | ea. | 2020 | [9 empty] | 2.5 |  | FALSE | 0 | 42_merge
94 | 118 | Replacement | Replacing Overflow Piping | End of service life |  | 325 | 35 | ea. | 2020 | [9 empty] | 4 |  | FALSE | 0
95 | 119 | Replacement | Asphalt Pavement | City Design Standards Compliance (1.1.4) and End of Service Life. | 30 | 55 | 250 | ea. | 2020 | [9 empty] | 1.25 |  | TRUE | 20
96 | 120 | Upgrade |  | Replace the existing gate with 2.4m high gate | 59 | 3380 | 1 | ea. | 2020 | [9 empty] | 3.1875 |  | FALSE | 0
97 | 121 | Upgrade | Replace Fence | Replace the existing fencing with a higher perimeter, anti-cut and anticlimb fence | 5 | 170 | 110 | ea. | 2020 | [9 empty] | 3.1875 |  | FALSE | 0
98 | 122 | Replacement |  |  |  |  | 1 | ea. | 2020 | [11 empty] | FALSE | 0
99 | 123 | Upgrade |  |  |  | 15000 | 1 | ea. | 2020 | [9 empty] | 1.5 | 2021 | FALSE | 0
100 | 123 | Replacement |  |  |  | 3000 | 2 | ea. | 2020 | [9 empty] | 2.5 | 2040 | FALSE | 0
101 | 124 | Replacement |  |  |  | 1430 | 1 | ea. | 2020 | [9 empty] | 2.4375 | 2045 | FALSE | 0
102 | 125 | Replacement |  |  | 915 | 1430 | 1 | ea. | 2020 | [9 empty] | 2.4375 | 2040 | FALSE | 0
103 | 126 | Replacement |  |  |  | 20000 | 1 | ea. | 2020 | [9 empty] | 1 | 2045 | FALSE | 0
104 | 130 | Replacement |  |  |  | 280000 | 1 | ea. | 2020 | [9 empty] | 2 | 2052 | FALSE | 0
105 | 131 | Replacement |  |  |  | 3500 | 1 | ea. | 2020 | [9 empty] | 1.5 | 2052 | FALSE | 0
106 | 132 | Replacement |  |  |  | 3500 | 1 | ea. | 2020 | [9 empty] | 1.5 | 2052 | FALSE | 0
107 | 133 | Replacement |  |  |  | 2500 | 1 | ea. | 2020 | [9 empty] | 1.5 | 2052 | FALSE | 0
108 | 30 | Replacement | Replacement | Replacement: like for like |  | 2500 | 1 | ea. | 2020 | [9 empty] | 1.8 |  | FALSE | 0
109 | 31 | Replacement | Replacement | Replacement: like for like |  | 2500 | 1 | ea. | 2020 | [9 empty] | 1.8 |  | FALSE | 0
110 | 134 | Replacement | Replacement | Replacement: like for like |  | 500 | 1 | ea. | 2020 | [9 empty] | 1.3 |  | FALSE | 0
111 | 135 | Replacement | Replacement | Replacement: like for like |  | 500 | 1 | ea. | 2020 | [9 empty] | 1.3 |  | FALSE | 0
112 | 14 | Upgrade |  |  |  | 15000 | 1 | ea. | 2020 | [9 empty] | 1.5 | 2021 | FALSE | 0
113 | 15 | Upgrade |  |  |  | 0 | 1 | ea. | 2020 | [9 empty] | 1.5 | 2021 | FALSE | 0
114 | 14 | Replacement |  |  |  | 3000 | 2 | ea. | 2020 | [9 empty] | 2.5 | 2040 | FALSE | 0
115 | 15 | Replacement |  |  |  | 3000 | 2 | ea. | 2020 | [9 empty] | 2.5 | 2040 | FALSE | 0
116 | 128 | Replacement |  |  | 471 | 137700 | 1 | ea. | 2020 | [9 empty] | 1.3625 |  | FALSE | 0
117 | 129 | Replacement |  |  | 963 | 6080 | 1 | ea. | 2020 | [9 empty] | 1.85 |  | FALSE | 0
118 | 127 | Replacement |  |  | 471 | 137700 | 1 | ea. | 2020 | [9 empty] | 1.3625 |  | FALSE | 0
119 | 20 | Replacement |  |  |  | 100000 | 1 | ea. | 2020 | [9 empty] | 2 |  | FALSE | 0
120 | 136 | Upgrade |  | Install an exit sign |  | 500 | 1 | ea. | 2020 | [9 empty] | 1.3 | 2021 | FALSE | 0

## defect
DefectID | ParentID | DefectType | DefectExtent | DefectComment | OPEXType | RehabComment | RehabYear | RehabUnitMaterialCost | RehabQuantity | RehabQuantityUnits | TotalRehabMarkup | Recurring | WorkFrequency | DBNotes
1 | 1 | Bugholes | Moderate |  | Maintenance |  |  |  | 1 | ea. | 1 | FALSE | 0
2 | 5 | [6 empty] | 7000 | 1 | ea. | 1.3 | FALSE | 0
3 | 53 | [6 empty] | 40000 | 1 | ea. | 1 | FALSE | 0 | 36_merge
4 | 54 | [6 empty] | 800 | 1 | ea. | 1.3 | FALSE | 0 | 37_merge
5 | 55 | [6 empty] | 3000 | 1 | ea. | 1.2 | FALSE | 0 | 38_merge
6 | 56 | [6 empty] | 500 | 1 | ea. | 1.3 | TRUE | 0 | 40_merge
7 | 57 | [6 empty] | 500 | 1 | ea. | 1.3 | FALSE | 0 | 41_merge
8 | 68 |  |  |  |  | to be repalced with classified ficture |  |  | 1 | ea. | 1 | FALSE | 0 | 46_merge
9 | 73 | Dirty / Poor Housekeeping |  | Dirt were seen on the signboard | Maintenance | Cleaning | 2020 | 0 | 1 | ea. | 1 | FALSE | 0 | 40_merge
11 | 77 | Deposits |  |  |  | Calcium buildup and minor pitting |  |  | 1 | ea. | 1 | FALSE | 0 | 36_merge
12 | 78 | Deposits |  | Calcium buildup and minor pitting |  |  |  |  | 1 | ea. | 1 | FALSE | 0 | 37_merge
13 | 79 | Missing Components |  | One section of grating was missing and should be installed/replaced |  | Install missing grating | 2021 | 1000 | 1 | ea. | 1 | FALSE | 0 | 38_merge
14 | 79 | Deposits |  | buildup of calcium and minor pitting |  |  |  |  | 1 | ea. | 1 | FALSE | 0 | 38_merge
15 | 81 | MISCELLANEOUS |  | retrofit of safety grating underneath the pump hatch to mitgate a falling hazard when hatch is open |  | Install safety grate | 2021 | 1000 | 1 | ea. | 1 | FALSE | 0 | 40_merge
16 | 82 | MISCELLANEOUS |  | retrofit of safety grating underneath the pump hatch to mitgate a falling hazard when hatch is open |  | Install safety grate | 2021 | 1000 | 1 | ea. | 1 | FALSE | 0 | 41_merge
17 | 83 | MISCELLANEOUS |  | retrofit of safety grating underneath the pump hatch to mitgate a falling hazard when hatch is open |  | Install safety grate | 2021 | 1000 | 1 | ea. | 1 | FALSE | 0 | 42_merge
18 | 84 | MISCELLANEOUS |  | retrofit of safety grating underneath the pump hatch to mitgate a falling hazard when hatch is open |  | Install safety grate |  |  | 1 | ea. | 1 | FALSE | 0 | 43_merge
19 | 86 | Missing Components |  | Missing cap |  | Install cap | 2020 | 100 | 1 | ea. | 1 | FALSE | 0 | 45_merge
20 | 105 | MISCELLANEOUS |  | Missing/bare spot at washroom |  | Touch up paint | 2021 | 200 | 1 | ea. | 1 | FALSE | 0 | 64_merge
21 | 108 |  |  | surface corrosion, corrosion on hardware and weathered paint |  |  |  |  | 1 | ea. | 1 | FALSE | 0 | 67_merge
22 | 119 | Uneven / Rough Surfaces |  | Gravel and dirt | Maintenance | Remove the gravel and dirt | 2020 | 1000 | 1 | ea. | 1 | FALSE | 0
23 | 121 | Dirty / Poor Housekeeping |  | Vegetation on or penetrate the fencing | Maintenance | Cleaning vegetation | 2020 | 1000 | 1 | ea. | 1 | FALSE | 0
24 | 122 | Performance Issues | Moderate | Flap gate will not operate properly due to presence of dirt and stones around | Maintenance | Remove stones and dirt to allow the flap gate to open effortlessly in the event of an overflow | 2021 | 1000 | 1 | ea. | 1 | FALSE | 0
25 | 122 | [7 empty] | 1 | ea. | 1 | FALSE | 0
26 | 131 | Deposits | Minor | Calcium buildup and minor pitting |  |  |  |  | 1 | ea. | 1 | FALSE | 0
27 | 132 | Deposits | Minor | Calcium buildup and minor pitting |  |  |  |  | 1 | ea. | 1 | FALSE | 0
28 | 133 | Deposits | Minor | buildup of calcium and minor pitting |  |  |  |  | 1 | ea. | 1 | FALSE | 0
29 | 4 | MISCELLANEOUS | N/A | Missing arc flash label | Study | Conduct arc flash study and install arc flash label | 2020 | 10000 | 1 | ea. | 1 | FALSE | 0
30 | 33 | MISCELLANEOUS |  | Missing arc flash label |  | Conduct arc flash study and install arc flash label | 2020 |  | 1 | ea. | 1 | FALSE | 0
31 | 58 | MISCELLANEOUS |  | Missing arc flash label |  | Conduct arc flash study and install arc flash label | 2020 |  | 1 | ea. | 1 | FALSE | 0
32 | 61 | MISCELLANEOUS |  | Missing arc flash label |  | Conduct arc flash study and install arc flash label | 2020 |  | 1 | ea. | 1 | FALSE | 0
33 | 62 | MISCELLANEOUS |  | Missing arc flash label |  | Conduct arc flash study and install arc flash label | 2020 |  | 1 | ea. | 1 | FALSE | 0
34 | 35 | MISCELLANEOUS |  | Missing arc flash label |  | Conduct arc flash study and install arc flash label | 2020 |  | 1 | ea. | 1 | FALSE | 0
35 | 63 | MISCELLANEOUS |  | Missing arc flash label |  | Conduct arc flash study and install arc flash label | 2020 |  | 1 | ea. | 1 | FALSE | 0
36 | 60 | MISCELLANEOUS |  | Missing arc flash label |  | Conduct arc flash study and install arc flash label | 2020 |  | 1 | ea. | 1 | FALSE | 0
37 | 59 | MISCELLANEOUS |  | Missing arc flash label |  | Conduct arc flash study and install arc flash label | 2020 |  | 1 | ea. | 1 | FALSE | 0