## Sheet1
AssetID | ClientAssetID0 | ClientAssetID1 | ClientAssetID2 | UniformatL0 | UniformatL1 | UniformatL2 | UniformatL3 | UniformatL4 | UniformatL5 | MasterFormatX | MasterFormatX2 | FlagAsProcess | FlagAsSubProcess | FlagAsAssembly | FlagAsParent | ParentID | AssetName | AssetDescription | Owner | Status | SiteName | FacilityName | LocationName | AssetCategory | CustomClientCategory | AssetType | CustomClientAssetType | Manufacturer | Model | SerialNumber | InspectionType | AssessmentYear | InstallYear | AvgESL | ReplaceYear | PhotoName | DrawingName | VisualCondition | PerformanceCondition | CoF | PoF | RedundancyFactor | CostID | MaterialUnitCost | Quantity | UnitOfQuantity | CostYear | CostSource | MarkupEquipment | MarkupLabour | MarkupAncillary | MarkupRemoval | MarkupEngineering | MarkupAdministration | MarkupContractor | MarkupContingency | TotalReplacementMarkup | LastEditor | LastEditTime | PlannerReviewer | PlannerReviewTime | DisciplineReview | DisciplineReviewTime | PMReview | PMReviewTime | TempProcess | TempSubProcess | TempSubProcessInstance | TempComments1 | TempComments2 | TempComments3 | TempRehabComment | TempRehabYear | TempRehabCost | AssetTagNumber | SizeCapacity | DBNotes | CountCapex | CountOpex | CountComments | CountDrawings | PreventDeletion | PreventEdit
1 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | TRUE |  | Rockcliffe WWPS | Site , | Hamilton |  | Rockcliffe |  |  | Site Works | Site Civil | [8 empty] | 20 |  |  |  | 3 |  |  | 3 |  |  |  |  | ea. | 2020 | [10 empty] | Andy Gong | 1.5924e+18 | Maira Rafiq | 1.5967e+18 | [6 empty] | 1 | [8 empty] | 1_primary |  |  |  |  | FALSE | FALSE
2 | 17 |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE |  | Site Civil | , | Hamilton |  | Rockcliffe |  |  | Site Works | [9 empty] | 20 |  |  |  | 3 |  |  | 3 |  |  |  |  | ea. | 2020 | [10 empty] | Andy Gong | 1.5924e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | [8 empty] | 2_primary |  |  |  |  | FALSE | FALSE
3 | 8 | DC015SLP0100000 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Sewage Lift Pump No.1 | Submersible Pump No.1 , | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Pump |  | ITT | CP3201.180 | 140 L/s @ 14m TDH, 28 kW |  |  | 2009 | 30 |  | COH-DC015-0282 |  | 2 |  | 3 | 2 |  |  | 137700 | 1 | ea. | 2020 | [9 empty] | 1.3625 | CAMR061927 | 1.5972e+18 | Maira Rafiq | 1.5972e+18 | [6 empty] | 1 | Good | [7 empty] | 3_primary |  |  |  |  | FALSE | FALSE
4 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 140 | MCC | DC015, MOTOR CONTROL CENTER , 4 columns + 40A breaker | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Process Electrical | Process Electrical | Motor Control Center |  | Moeller | series 200 |  |  |  | 2000 | 25 | 2030 | COH-DC015-0148 |  | 4 |  | 3 | 4 |  |  | 40000 | 1 | ea. | 2020 | [9 empty] | 2 | CAMR061927 | 1.5971e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | good | CC: Missing Arc Flash labels | [5 empty] | 4 columns + 40A breaker | 4_primary |  |  |  |  | FALSE | FALSE
5 |  | DC015NAC0100000 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 145 | SCADA WAN Panel | WAN Panel, Ethernet Switch , | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Process Instrumentation | Process Instrumentation & Control |  |  | Allen-Bradley Stratix 8000 | 1783-MS10T Expansion Module |  |  |  | 2014 | 15 |  | COH-DC015-0352 |  | 2 |  | 3 | 2 |  |  | 7000 | 1 | ea. | 2020 | [9 empty] | 1.3 | CAMR061927 | 1.5943e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | Good | [7 empty] | 5_primary |  |  |  |  | FALSE | FALSE
6 | 13 |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Wet Well | , | Hamilton |  | Rockcliffe |  |  | Process Structural | Process Structural | [8 empty] | 60 |  |  |  | 3 |  |  | 3 |  |  |  |  | ea. | 2020 | [10 empty] | David Ip | 1.5922e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | [8 empty] | 6_primary |  |  |  |  | FALSE | FALSE
7 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 147 | Unit Heater 1 | Unit Heater , 5KW | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Building Mechanical | Building Mechanical | Heating System |  | Ouellet | OAS05036 |  |  |  | 2007 | 30 | 2032 | COH-DC015-0305 |  | 4 |  | 2 | 4 |  |  | 760 | 1 | ea. | 2020 | [9 empty] | 2.4375 | Patryk Frankiewicz | 1.5944e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | CC: There was no containment for diesel fuel lines. TSSA requires all equipment containing or carrying. fuel to be contained per CSA B139.1.1-15 Section 6.5.1.4. | [6 empty] | 5KW | 7_primary |  |  |  |  | FALSE | FALSE
8 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 146 | Interior Lighting | Interior Lighting , 6 linear fluorescent | Hamilton | Installed | Rockcliffe |  |  | Building Electrical | Building Electrical | Lighting | [6 empty] | 2000 | 25 | 2030 | COH-DC015-0189 |  | 2 |  | 2 | 2 |  |  | 300 | 6 | ea. | 2020 | [9 empty] | 3.125 | CAMR061927 | 1.5971e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | good | replace with LED in next upgrade | [5 empty] | 6 linear fluorescent | 8_primary |  |  |  |  | FALSE | FALSE
9 | 5 |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Building Structural | , | Hamilton |  | Rockcliffe |  |  | Building Structural | [9 empty] | 60 |  |  |  | 3 |  |  | 3 |  |  |  |  | ea. | 2020 | [13 empty] | 1.5917e+18 | [6 empty] | 1 |  |  |  | Cleaning | 2020 | 0 |  |  | 9_primary |  |  |  |  | FALSE | FALSE
10 | 1 |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Building Architectural | , | Hamilton |  | Rockcliffe |  |  | Building Architectural | Building Architectural | [8 empty] | 30 |  |  |  | 3 |  |  | 3 |  |  |  |  | ea. | 2020 | [10 empty] | David Ip | 1.5922e+18 |  | 1.5917e+18 | [6 empty] | 1 | [8 empty] | 10_primary |  |  |  |  | FALSE | FALSE
11 | 19 |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Emergency Backup Power | , | Hamilton |  | Rockcliffe |  |  | Building Electrical | [9 empty] | 25 |  |  |  | 3 |  | 3 | 3 |  |  |  |  | ea. | 2020 | [13 empty] | 1.5917e+18 | [6 empty] | 1 | [8 empty] | 11_primary |  |  |  |  | FALSE | FALSE
14 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 11 | Diesel Fuel Tank #1 For Generator | DC015, DIESEL FUEL TANK #1 FOR GENERATOR , | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Building Mechanical |  |  |  | DTE | Capacity 1135 Lr |  |  |  | 1992 | 30 | 2040 | COH-DC015-0313 |  | 4 |  | 3 | 4 |  |  | 15000 | 1 | ea. | 2020 | [9 empty] | 1.5 | CAMR061927 | 1.5971e+18 | Maira Rafiq | 1.5971e+18 | [6 empty] | 1 | CC: There was no containment for diesel fuel lines. TSSA requires all equipment containing or carrying fuel to be contained per CSA B139.1.1-15 Section 6.5.1.4. | [7 empty] | 14_primary |  |  |  |  | FALSE | FALSE
15 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 11 | Diesel Fuel Tank #2 For Generator | DC015, DIESEL FUEL TANK #2 FOR GENERATOR , | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Building Mechanical |  |  |  | DTE | Capacity 1135 Lr |  |  |  | 1992 | 30 | 2040 | COH-DC015-0313 |  | 4 |  | 3 | 4 |  |  | 0 | 1 | ea. | 2020 | [9 empty] | 1.5 | CAMR061927 | 1.5971e+18 | Maira Rafiq | 1.5971e+18 | [6 empty] | 1 | CC: There was no containment for diesel fuel lines. TSSA requires all equipment containing or carrying |  |  | Install safety grate | 2021 | 1000 |  |  | 15_primary |  |  |  |  | FALSE | FALSE
17 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  |  | DC015, BUILDING TEMP CONTROL | Hamilton | Withdrawn | Rockcliffe |  |  | Building Mechanical |  |  |  | HONEYWELL | T136A |  |  |  | 1912 | [12 empty] | ea. | 2020 | [20 empty] | 1 |  |  |  | Install safety grate | 2021 | 1000 |  |  | 17_primary |  |  |  |  | FALSE | FALSE
18 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  |  | DC015, WET WELL LEVEL TRANSMITTER | Hamilton | Withdrawn | Rockcliffe |  |  | Process Instrumentation |  |  |  | MILLTRONICS | MULTIRANGER |  |  |  | 1912 | [12 empty] | ea. | 2020 | [20 empty] | 1 |  |  |  | Install safety grate | 2020 | 0 |  |  | 18_primary |  |  |  |  | FALSE | FALSE
20 |  | DC015GEN0100000 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 11 | Standby Diesel Power Generator | DC015, DIESEL STANDBY POWER GENERATOR , | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Process Electrical | Process Electrical |  |  | KLOCKNERMOELLER | SERIES 200 | CDN/16/94-5513 |  |  | 1992 | 25 |  |  |  | 2 |  | 3 | 2 |  |  | 100000 | 1 | ea. | 2020 | [9 empty] | 2 | CAMR061927 | 1.5972e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | good |  |  | Touch up paint | 2021 | 200 |  |  | 20_primary |  |  |  |  | FALSE | FALSE
22 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  |  | DC015, GES MONITOR | Hamilton | Withdrawn | Rockcliffe |  |  | Process Instrumentation |  |  |  | MSA | 5100 | 94BM159037 |  |  | 1912 | [12 empty] | ea. | 2020 | [20 empty] | 1 |  |  |  | Remove the gravel and dirt | 2020 | 1000 |  |  | 22_primary |  |  |  |  | FALSE | FALSE
24 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  |  | DC015, LIGHTING SYSTEM | Hamilton | Installed | Rockcliffe |  |  | Building Electrical | Building Electrical | [7 empty] | 1912 | [12 empty] | ea. | 2020 | [12 empty] | Maira Rafiq | 1.5971e+18 | [6 empty] | 1 |  |  |  | Remove stones and dirt to allow the flap gate to open effortlessly in the event of an overflow | 2021 | 1000 |  |  | 24_primary |  |  |  |  | FALSE | FALSE
25 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  |  | DC015, PLC PANEL | Hamilton | Withdrawn | Rockcliffe |  |  | Process Instrumentation |  |  |  |  | N12-483620 |  |  |  | 2000 | [12 empty] | ea. | 2020 | [20 empty] | 1 | [8 empty] | 25_primary |  |  |  |  | FALSE | FALSE
26 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  |  | DC015, PLC | Hamilton | Withdrawn | Rockcliffe |  |  | Process Instrumentation |  |  |  | BRISTOLBABCOCK | 3330 10A 120000 | 94A11064 |  |  | 2000 | [12 empty] | ea. | 2020 | [20 empty] | 1 | [8 empty] | 26_primary |  |  |  |  | FALSE | FALSE
27 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  |  | DC015, PLC PANEL UPS | Hamilton | Withdrawn | Rockcliffe |  |  | Process Instrumentation |  |  |  | APC | BK500M | PB9923112887 |  |  | 2000 | [12 empty] | ea. | 2020 | [20 empty] | 1 | [8 empty] | 27_primary |  |  |  |  | FALSE | FALSE
30 |  | DC015WWL01LIT01 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Level Transmitter #1 | DC015, WET WELL LEVEL TRANSMITTER #1 , | Hamilton | Installed | Rockcliffe | Main Building | Washroom | Process Instrumentation |  |  |  | SIEMENS | MULTIRANGER 100 |  |  |  | 2016 | 15 |  |  |  | 2 |  | 2 | 2 |  |  | 2500 | 1 | ea. | 2020 | [9 empty] | 1.8 | CAMR061927 | 1.5972e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | good |  |  | Conduct arc flash study and install arc flash label | 2020 | 0 |  |  | 30_primary |  |  |  |  | FALSE | FALSE
31 |  | DC015WWL02LIT01 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Level Transmitter #2 | DC015, WET WELL LEVEL TRANSMITTER #2 SIEMENS , | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Process Instrumentation |  |  |  | MULTIRANGER 100 |  |  |  |  | 2016 | 15 |  |  |  | 2 |  | 2 | 2 |  |  | 2500 | 1 | ea. | 2020 | [9 empty] | 1.8 | CAMR061927 | 1.5972e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | good |  |  | Conduct arc flash study and install arc flash label | 2020 | 0 |  |  | 31_primary |  |  |  |  | FALSE | FALSE
32 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 140 | Power Meter | Power meter , | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Process Electrical | Process Electrical | Metering |  | Moeller |  |  |  |  | 2000 | 25 | 2030 | COH-DC015-0153 |  | 2 |  | 3 | 2 |  |  | 11000 | 1 | ea. | 2020 | [9 empty] | 2 | Amin Norouzizadeh | 1.5946e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | good |  |  | Conduct arc flash study and install arc flash label | 2020 | 0 |  |  | 32_primary |  |  |  |  | FALSE | FALSE
33 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 140 | Main Breaker | DC015, MAIN BREAKER ,600V, 200A | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Process Electrical | Process Electrical | Main Switch |  | KLOCKNERMOELLER | MZN9-250 | NZM9-250/2M9A-200 |  |  | 2000 | 25 | 2030 | COH-DC015-0152 |  | 4 |  | 3 | 4 |  |  | 3800 | 1 | ea. | 2020 | [9 empty] | 3.125 | CAMR061927 | 1.5971e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | Good | CC: Missing Arc Flash labels |  | Conduct arc flash study and install arc flash label | 2020 | 0 |  | 600V, 200A | 33_primary |  |  |  |  | FALSE | FALSE
34 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 140 | Power Factor Capacitors | Power Factor capacitos , 3x 600V, 15kVAr | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Process Electrical | Process Electrical | Power Factor Correction Capacitor |  | Powerspec |  |  |  |  | 2013 | 25 | 2043 | COH-DC015-0154 |  | 2 |  | 2 | 2 |  |  | 10000 | 3 | ea. | 2020 | [9 empty] | 1.5 | Amin Norouzizadeh | 1.5946e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | Good |  |  | Conduct arc flash study and install arc flash label | 2020 | 0 |  | 3x 600V, 15kVAr | 34_primary |  |  |  |  | FALSE | FALSE
35 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 146 | Unit Heater Starter | Unit Heater starter and disconnect , 600V, size 1 | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Electrical | Building Electrical | Starter | [6 empty] | 2000 | 25 | 2030 | COH-DC015-0156 |  | 4 |  | 2 | 4 |  |  | 2600 | 1 | ea. | 2020 | [9 empty] | 1.7 | CAMR061927 | 1.5971e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | good | CC: Missing Arc Flash labels |  | Conduct arc flash study and install arc flash label | 2020 | 0 |  | 600V, size 1 | 35_primary |  |  |  |  | FALSE | FALSE
36 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 127 | Hand Stop Gate No.2 | Hand Stop Gate No.2 ,36"X 36" | Hamilton | Not In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Gate | [6 empty] | 1992 | 30 |  | COH-DC015-0236 |  | 3 |  | 2 | 3 |  |  | 6080 | 1 | ea. | 2020 | [9 empty] | 1.85 | Adrian Li | 1.5924e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | deterioration |  |  | Conduct arc flash study and install arc flash label | 2020 | 0 |  | 36"X 36" | 36_merge |  |  |  |  | FALSE | FALSE
37 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 128 | Hand Stop Gate No.3 | Hand Stop Gate No.3 ,36"X36" | Hamilton | Not In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Gate | [6 empty] | 1992 | 30 |  | COH-DC015-0236 |  | 3 |  | 2 | 3 |  |  | 6080 | 1 | ea. | 2020 | [9 empty] | 1.85 | Adrian Li | 1.5925e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | deterioration |  |  | Conduct arc flash study and install arc flash label | 2020 | 0 |  | 36"X36" | 37_merge |  |  |  |  | FALSE | FALSE
38 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Manual Bar Screen No.1 | Manual Bar Screen No.1 ,24"X 48" | Hamilton | Obsolete and Not in Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Screen | [6 empty] | 1992 | 30 |  | COH-DC015-0223 |  | 3 |  | 2 | 3 |  |  | 9000 | 1 | ea. | 2020 | [9 empty] | 1.4 | CAMR061927 | 1.5944e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | Bent bars | OM: The operators mentioned that the screens have been removed and are no longer in use. | [5 empty] | 24"X 48" | 38_merge |  |  |  |  | FALSE | FALSE
39 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Manual Bar Screen No.2 | Manual Bar Screen No.2 ,24"X 48" | Hamilton | Obsolete and Not in Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Screen | [6 empty] | 1992 | 30 |  | COH-DC015-0223 |  | 3 |  | 2 | 3 |  |  | 9000 | 1 | ea. | 2020 | [9 empty] | 1.4 | CAMR061927 | 1.5944e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | Bent bars | OM: The operators mentioned that the screens have been removed and are no longer in use. | [5 empty] | 24"X 48" | 39_merge |  |  |  |  | FALSE | FALSE
40 |  | DC015SLP01CV001 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 3 | Sewage Lift Pump No.1 Check Valve | Check Valve No.1 ,200mm | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Valves | [6 empty] | 1992 | 30 |  | COH-DC015-0230 |  | 3 |  | 2 | 3 |  |  | 1990 | 1 | ea. | 2020 | [9 empty] | 2.5 | Adrian Li | 1.5924e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | Heavy corrosion and deterioration | [6 empty] | 200mm | 40_merge |  |  |  |  | FALSE | FALSE
41 |  | DC015SLP02CV001 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 127 | Sewage Lift Pump No.2 Check Valve | Check Valve No.2 ,200mm | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Valves | [6 empty] | 1992 | 30 |  | COH-DC015-0244 |  | 3 |  | 2 | 3 |  |  | 1990 | 1 | ea. | 2020 | [9 empty] | 2.5 | Adrian Li | 1.5924e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | Heavy corrosion and deterioration | [6 empty] | 200mm | 41_merge |  |  |  |  | FALSE | FALSE
42 |  | DC015SLP03CV001 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 128 | Sewage Lift Pump No.3 Check Valve | Check Valve No.3 ,200mm | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Valves | [6 empty] | 1992 | 30 |  | COH-DC015-0241 |  | 3 |  | 2 | 3 |  |  | 1990 | 1 | ea. | 2020 | [9 empty] | 2.5 | Adrian Li | 1.5924e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | Heavy corrosion and Deterioration | [6 empty] | 200mm | 42_merge |  |  |  |  | FALSE | FALSE
43 |  | DC015SLP01DV001 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 3 | Sewage Lift Pump No.1 Discharge Valve | Gate Valve No.1 ,200mm | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Valves | [6 empty] | 1992 | 30 |  | COH-DC015-0230 |  | 3 |  | 2 | 3 |  |  | 1520 | 1 | ea. | 2020 | [9 empty] | 2.5 | Adrian Li | 1.5924e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | Heavy corrosion and deterioration | [6 empty] | 200mm | 43_merge |  |  |  |  | FALSE | FALSE
44 |  | DC015SLP02DV001 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 127 | Sewage Lift Pump No.2 Discharge Valve | Gate Valve No.2 ,200mm | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Valves | [6 empty] | 1992 | 30 |  | COH-DC015-0233 |  | 3 |  | 2 | 3 |  |  | 1520 | 1 | ea. | 2020 | [9 empty] | 2.5 | Adrian Li | 1.5924e+18 | Maira Rafiq | 1.5978e+18 | [6 empty] | 1 | Heavy corrosion and Deterioration | [6 empty] | 200mm | 44_merge |  |  |  |  | FALSE | FALSE
45 |  | DC015SLP03DV00 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 128 | Sewage Lift Pump No.3 Discharge Valve | Gate Valve No.3 ,200mm | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Valves | [6 empty] | 1992 | 30 |  | COH-DC015-0241 |  | 3 |  | 2 | 3 |  |  | 1520 | 1 | ea. | 2020 | [9 empty] | 2.5 | Adrian Li | 1.5924e+18 | Maira Rafiq | 1.5978e+18 | [6 empty] | 1 | Heavy corrosion and Deterioration | [6 empty] | 200mm | 45_merge |  |  |  |  | FALSE | FALSE
46 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 143 | Discharge Header Gate Valve | Gate Valve No.4 ,300mm | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Valves | [6 empty] | 1992 | 30 |  | COH-DC015-0245 |  | 3 |  | 3 | 3 |  |  | 2790 | 1 | ea. | 2020 | [9 empty] | 2.5 | Adrian Li | 1.5925e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | Heavy corrosion and deterioration | Missing Turn wheel | [5 empty] | 300mm | 46_merge |  |  |  |  | FALSE | FALSE
47 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 143 | Drain Gate Valve | Drain Gate Valve ,100mm | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Valves | [6 empty] | 1992 | 30 |  | COH-DC015-0254 |  | 3 |  | 2 | 3 |  |  | 630 | 1 | ea. | 2020 | [9 empty] | 2.5 | Adrian Li | 1.5925e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | Heavy corrosion and deterioration | [6 empty] | 100mm | 47_merge |  |  |  |  | FALSE | FALSE
48 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 143 | Pressure Release Valve No.1 | Pressure Release Valve No.1 ,100mm | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Valves | [6 empty] | 1992 | 30 |  | COH-DC015-0255 |  | 3 |  | 2 | 3 |  |  | 2280 | 1 | ea. | 2020 | [9 empty] | 2.5 | Adrian Li | 1.5925e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | Heavy corrosion and Deterioration | [6 empty] | 100mm | 48_merge |  |  |  |  | FALSE | FALSE
49 |  | DC015WWL00IG001 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 143 | Wetwell Cell Isolation Gate | Wetwell Cell Isolation Gate ,300mm | Hamilton | In Service | Rockcliffe | Site |  | Process Mechanical | Process Mechanical Piping and Equipment | Valves | [6 empty] | 1992 | 30 |  | COH-DC015-0102 |  | 3 |  | 3 | 3 |  |  | 2790 | 1 | ea. | 2020 | [9 empty] | 2.5 | Adrian Li | 1.5925e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | Moderate surface corrosion | [6 empty] | 300mm | 49_merge |  |  |  |  | FALSE | FALSE
50 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Sluice Gate No.1 | Sluice Gate No.1 ,900mm | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Gate | [6 empty] | 1992 | 30 |  | COH-DC-15-0263 |  | 3 |  | 2 | 3 |  |  | 25340 | 1 | ea. | 2020 | [9 empty] | 1.85 | Adrian Li | 1.5925e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | Heavy corrosion and deterioration on the frame of the sluice gate | [6 empty] | 900mm | 51_merge |  |  |  |  | FALSE | FALSE
51 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 3 | Pump 1 Piping | Process Mechanical Piping , 7.5 m of 100 mm dia DI pipe, 16.5 m of 200 mm dia DI pipe, 16.5 m of 300 mm DI pipe | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Piping | [6 empty] | 1992 | 30 |  | COH-DC015-0206 |  | 3 |  | 3 | 3 |  |  | 142 | 8 | ea. | 2020 | [9 empty] | 1.6 | Adrian Li | 1.5925e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | Heavy corrosion and deterioration on majority portion of the piping | [6 empty] | 7.5 m of 100 mm dia DI pipe, 16.5 m of 200 mm dia DI pipe, 16.5 m of 300 mm DI pipe | 52_merge |  |  |  |  | FALSE | FALSE
52 | 12 |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Forcemain | , | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Piping | [6 empty] | 1992 | 30 |  | COH-DC015-0206 |  | 3 |  | 4 | 3 |  |  |  |  | ea. | 2020 | [12 empty] | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | [8 empty] | 53_merge |  |  |  |  | FALSE | FALSE
53 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 145 | SCADA PANEL | PLC controller c/w all IO cards, internal wiring, PLC software programp, panel enclosure and all associated components , | Hamilton |  | Rockcliffe | Main Building | Generator Room | Process Instrumentation | Process Instrumentation & Control | PLC |  | Allen-Bradley | 1969-L33ER, 1769-PA4, 1769-IF4I, 1769-OF4CI, 1769-IQ16 | 1769-OW16, 1769-ECR |  |  | 2013 | 15 |  | COH-DC015-0364 |  | 2 |  | 3 | 2 |  |  | 40000 | 1 | ea. | 2020 | [9 empty] | 1 | Alex Wang | 1.5934e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | Good | [7 empty] | 36_merge |  |  |  |  | FALSE | FALSE
54 |  | Station Temperature Transmitter |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 145 | Station Temperature Transmitter | Temperature Transmitter , | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Process Instrumentation | Process Instrumentation & Control | Transmitter |  | Pribusin: TWTS-2 |  |  |  |  | 2014 | 15 |  | COH-DC015-0408 |  | 3 |  | 2 | 3 |  |  | 800 | 1 | ea. | 2020 | [9 empty] | 1.3 | Alex Wang | 1.5934e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | Good | Communication via Pribusin transmitter is old technology and will be obselete in near future. It is recommended tp replace the temperature trasmitter with a cellular transmitter or a hardwired signal from the temperature device to directly connected to th | [6 empty] | 37_merge |  |  |  |  | FALSE | FALSE
55 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 145 | UPS | UPS , | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Process Instrumentation | Process Instrumentation & Control | Miscellaneous Instrumentation |  | Eaton Powerware | PW9130L2000T-XL |  |  |  | 2014 | 15 |  | COH-DC015-0366 |  | 2 |  | 2 | 2 |  |  | 3000 | 1 | ea. | 2020 | [9 empty] | 1.2 | Alex Wang | 1.5934e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | good | Dust | [6 empty] | 38_merge |  |  |  |  | FALSE | FALSE
56 |  | DC015WWL01LSH01 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wetwell 1 High Level Float | Wetwell No.1 High Level Float , | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Instrumentation | Process Instrumentation & Control | [7 empty] | 2016 | 15 |  | COH-DC015-0269 |  | 2 |  | 2 | 2 |  |  | 500 | 1 | ea. | 2020 | [9 empty] | 1.3 | CAMR061927 | 1.5943e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | Good | [7 empty] | 40_merge |  |  |  |  | FALSE | FALSE
57 |  | DC015WWL02LSH01 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wetwell 2 High Level Float | Wetwell No.2 High Level Float , | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Instrumentation | Process Instrumentation & Control | [7 empty] | 2016 | 15 |  | COH-DC015-0269 |  | 2 |  | 2 | 2 |  |  | 500 | 1 | ea. | 2020 | [9 empty] | 1.3 | CAMR061927 | 1.5943e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | Good | [7 empty] | 41_merge |  |  |  |  | FALSE | FALSE
58 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 3 | Pump 1 VFD | VFD with filter , 600V, size 2 | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Process Electrical | Process Electrical | Starter | [6 empty] | 2000 | 25 | 2030 | COH-DC015-0157 |  | 4 |  | 2 | 4 |  |  | 19000 | 1 | ea. | 2020 | [9 empty] | 1.7 | CAMR061927 | 1.5971e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | CC: Missing Arc Flash labels | [6 empty] | 600V, size 2 | 36_merge |  |  |  |  | FALSE | FALSE
59 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 146 | Wet well Fan Starter | starter and disconnect , 600V, size 1 | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Electrical | Building Electrical | Starter | [6 empty] | 2000 | 25 | 2030 | COH-DC015-0162 |  | 4 |  | 2 | 4 |  |  | 2500 | 1 | ea. | 2020 | [9 empty] | 1.7 | CAMR061927 | 1.5971e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | CC: Missing Arc Flash labels | [6 empty] | 600V, size 1 | 37_merge |  |  |  |  | FALSE | FALSE
60 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 146 | Diesel Generator Room Fan Starter | starter and disconnect , 600V, size 1 | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Electrical | Building Electrical | Starter | [6 empty] | 2000 | 25 | 2030 | COH-DC015-0163 |  | 4 |  | 2 | 4 |  |  | 2500 | 1 | ea. | 2020 | [9 empty] | 1.7 | CAMR061927 | 1.5971e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | CC: Missing Arc Flash labels | [6 empty] | 600V, size 1 | 38_merge |  |  |  |  | FALSE | FALSE
61 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 127 | Pump 2 VFD | VFD with filter , 600V, size 2 | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Process Electrical | Process Electrical | Starter | [6 empty] | 2000 | 25 | 2030 | COH-DC015-0164 |  | 4 |  | 2 | 4 |  |  | 19000 | 1 | ea. | 2020 | [9 empty] | 1.7 | CAMR061927 | 1.5971e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | CC: Missing Arc Flash labels | [6 empty] | 600V, size 2 | 39_merge |  |  |  |  | FALSE | FALSE
62 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 128 | Pump 3 VFD | VFD with filter , 600V, size 2 | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Process Electrical | Process Electrical | Starter | [6 empty] | 2000 | 25 | 2030 | COH-DC015-0170 |  | 4 |  | 2 | 4 |  |  | 19000 | 1 | ea. | 2020 | [9 empty] | 1.7 | CAMR061927 | 1.5971e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | CC: Missing Arc Flash labels | [6 empty] | 600V, size 2 | 40_merge |  |  |  |  | FALSE | FALSE
63 |  | DC015ATS0100000 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 11 | Diesel Generator Control Panel | Genreator panel with ATS , 600V, 200A, 150kW | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Building Electrical | Emergency Backup Power | Standby Power Source | [6 empty] | 1992 | 25 | 2030 | COH-DC015-0170 |  | 4 |  | 3 | 4 |  |  | 30000 | 1 | ea. | 2020 | [9 empty] | 2.25 | CAMR061927 | 1.5971e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | CC: Missing Arc Flash labels | [6 empty] | 600V, 200A, 150kW | 41_merge |  |  |  |  | FALSE | FALSE
64 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 146 | Emergency Lighting | Battery Unit , | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Electrical | Building Electrical | Emergency Lighting | [6 empty] | 2016 | 25 | 2043 | COH-DC015-0130 |  | 2 |  | 2 | 2 |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 1.5 | Amin Norouzizadeh | 1.5946e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | good | [7 empty] | 42_merge |  |  |  |  | FALSE | FALSE
65 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 146 | Lighting Panel LPA | DC015, BREAKER PANEL ,120/208V, 225A, | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Electrical | Building Electrical | Panelboard |  | Square D | NQOB |  |  |  | 2000 | 25 | 2030 | COH-DC015-0134 |  | 2 |  | 3 | 2 |  |  | 2000 | 1 | ea. | 2020 | [9 empty] | 3.125 | Amin Norouzizadeh | 1.5946e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | good | [6 empty] | 120/208V, 225A, | 43_merge |  |  |  |  | FALSE | FALSE
66 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 146 | Lighting Trasnformer | Transformer ,600-120/208V, 30kVAr | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Electrical | Building Electrical | Distribution Transformer |  | Square D | 33360-17112-006 | 00J055160 |  |  | 1992 | 25 | 2030 | COH-DC015-0143 |  | 2 |  | 3 | 2 |  |  | 5100 | 1 | ea. | 2020 | [9 empty] | 3.125 | Amin Norouzizadeh | 1.5946e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | good | [6 empty] | 600-120/208V, 30kVAr | 44_merge |  |  |  |  | FALSE | FALSE
67 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 146 | Exterior Lighting | Lighting , 1 flood light | Hamilton | In Service | Rockcliffe | Site |  | Building Electrical | Building Electrical | Lighting | [6 empty] | 2013 | 25 | 2030 | COH-DC015-0190 |  | 2 |  | 2 | 2 |  |  | 300 | 1 | ea. | 2020 | [9 empty] | 3.125 | Amin Norouzizadeh | 1.5946e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | good | [6 empty] | 1 flood light | 45_merge |  |  |  |  | FALSE | FALSE
68 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 146 | Wet Well Lighting | Lighting , 3 flood light, class 1, div 1 | Hamilton | In Service | Rockcliffe | Wet Well |  | Building Electrical | Building Electrical | Lighting | [6 empty] | 2000 | 25 | 2025 | COH-DC015-0196 |  | 3 |  | 2 | 3 |  |  | 700 | 3 | ea. | 2020 | [9 empty] | 3.125 | CAMR061927 | 1.5971e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | corroded | to be replaced with class 1, div 1 fixture | [5 empty] | 3 flood light, class 1, div 1 | 46_merge |  |  |  |  | FALSE | FALSE
69 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE |  | Main Transformer | Main Trasnformer , 27.6kV-600V, 750KVA | Hamilton | In Service |  |  |  | Process Electrical |  | Power Transformer |  | ABB |  |  |  |  | 2000 | 25 | 2030 | COH-DC015-0200 |  | 2 |  | 3 | 2 |  |  | 57000 | 1 | ea. | 2020 | [9 empty] | 2.25 | Amin Norouzizadeh | 1.5946e+18 | [8 empty] | 1 | good | [6 empty] | 27.6kV-600V, 750KVA | 47_merge |  |  |  |  | FALSE | FALSE
73 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 2 | Signboards | City of Hamilton Signboards throughout the site (total of two) , | Hamilton | In Service | Rockcliffe | Site |  | Site Works | Site Civil | Signboard | [6 empty] | 1992 | 20 |  | COH-DC015-0425 |  | 2 |  | 1 | 2 |  |  | 60 | 2 | ea. | 2020 | [9 empty] | 3.1875 | CAMR061927 | 1.594e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | good | [7 empty] | 40_merge |  |  |  |  | FALSE | FALSE
75 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 2 | Station Access Road | Gravel Access Road to the Station , | Hamilton | In Service | Rockcliffe | Site |  | Site Works | Site Civil | Road | [6 empty] | 1992 | 20 |  | COH-DC015-0529 |  | 3 |  | 1 | 3 |  |  | 55 | 30 | ea. | 2020 | [9 empty] | 1.25 | CAMR061927 | 1.594e+18 | Maira Rafiq | 1.5978e+18 | [6 empty] | 1 | Pot holes and mud bumps | [7 empty] | 43_merge |  |  |  |  | FALSE | FALSE
76 | 18 |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE |  | Sanitary Sewer | Sanitary Sewer Yard Piping, Approximate Length: 21 meters, Pipe Dia: 450mm, unknown material and installation year. Assumed to be reinformed concrete pipe installed in 1992 , | Hamilton | In Service | Rockcliffe | Site |  | Site Works | Site Civil | Piping | [6 empty] | 1992 | 20 | 2072 |  |  | 2 |  | 3 | 2 |  |  | 80 | 21 | ea. | 2020 | [9 empty] | 10.7 | Andy Gong | 1.5924e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | good | [7 empty] | 44_merge |  |  |  |  | FALSE | FALSE
77 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Aluminum Ladder | Aluminum ladder from lower platform to wet well , | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0030 |  | 3 |  | 2 | 3 |  |  | 2500 | 1 | ea. | 2020 | [9 empty] | 1.5 | CAMR061927 | 1.5946e+18 | Maira Rafiq | 1.5946e+18 | [6 empty] | 1 | buildup of calcium and minor pitting | [7 empty] | 36_merge |  |  |  |  | FALSE | FALSE
78 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Aluminum Guardrail | Aluminum guardrails at lower platform level , | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0008 |  | 3 |  | 2 | 3 |  |  | 200 | 20 | ea. | 2020 | [9 empty] | 2 | CAMR061927 | 1.5946e+18 | Maira Rafiq | 1.5946e+18 | [6 empty] | 1 | buildup of calcium and minor pitting | [7 empty] | 37_merge |  |  |  |  | FALSE | FALSE
79 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Aluminum Grating | Aluminum grating at lower platform level , | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0026 |  | 4 |  | 2 | 4 |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 1 | CAMR061927 | 1.5946e+18 | Maira Rafiq | 1.5946e+18 | [6 empty] | 1 | buildup of calcium and minor pitting | HS: One section of grating was missing and should be installed/replaced | [6 empty] | 38_merge |  |  |  |  | FALSE | FALSE
80 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Access Hatch | Aluminum access hatch at grade level , | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0067 |  | 2 |  | 2 | 2 |  |  | 5000 | 1 | ea. | 2020 | [9 empty] | 1 | David Ip | 1.5923e+18 | Maira Rafiq | 1.5946e+18 | [6 empty] | 1 | good | [7 empty] | 39_merge |  |  |  |  | FALSE | FALSE
81 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Pump Hatch 1 | Aluminum pump hatch at grade level , | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0063 |  | 4 |  | 2 | 4 |  |  | 5000 | 1 | ea. | 2020 | [9 empty] | 1 | CAMR061927 | 1.5946e+18 | Maira Rafiq | 1.5946e+18 | [6 empty] | 1 | good | HS: retrofit of safety grating underneath the pump hatch is recommended to mitgate a falling hazard when hatch is open | [6 empty] | 40_merge |  |  |  |  | FALSE | FALSE
82 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Pump Hatch 2 | Aluminum pump hatch at grade level , | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0063 |  | 3 |  | 2 | 3 |  |  | 6500 | 1 | ea. | 2020 | [9 empty] | 1 | CAMR061927 | 1.5946e+18 | Maira Rafiq | 1.5946e+18 | [6 empty] | 1 | good | retrofit of safety grating underneath the pump hatch is recommended to mitgate a falling hazard when hatch is open | [6 empty] | 41_merge |  |  |  |  | FALSE | FALSE
83 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Pump Hatch 3 | Aluminum pump hatch at grade level , | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0065 |  | 3 |  | 2 | 3 |  |  | 6500 | 1 | ea. | 2020 | [9 empty] | 2 | CAMR061927 | 1.5946e+18 | Maira Rafiq | 1.5946e+18 | [6 empty] | 1 | good | retrofit of safety grating underneath the pump hatch is recommended to mitgate a falling hazard when hatch is open | [6 empty] | 42_merge |  |  |  |  | FALSE | FALSE
84 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Pump Hatch 4 | Aluminum pump hatch at grade level , | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0065 |  | 3 |  | 2 | 3 |  |  | 6500 | 1 | ea. | 2020 | [9 empty] | 1 | CAMR061927 | 1.5946e+18 | Maira Rafiq | 1.5946e+18 | [6 empty] | 1 | good | retrofit of safety grating underneath the pump hatch is recommended to mitgate a falling hazard when hatch is open | [6 empty] | 43_merge |  |  |  |  | FALSE | FALSE
85 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Davit Base 1 | Safety davit base at grade level , | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0067 |  | 2 |  | 2 | 2 |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 2 | David Ip | 1.5923e+18 | Maira Rafiq | 1.5946e+18 | [6 empty] | 1 | good | [7 empty] | 44_merge |  |  |  |  | FALSE | FALSE
86 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Davit Base 2 | Safety davit base at grade level , | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0063 |  | 2 |  | 2 | 2 |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 2 | CAMR061927 | 1.5946e+18 | Maira Rafiq | 1.5946e+18 | [6 empty] | 1 | good | Missing cap | [6 empty] | 45_merge |  |  |  |  | FALSE | FALSE
87 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 137 | Inlet Chamber 1 Concrete Structure | Reinforced concrete inlet chamber , | Hamilton | In Service | Rockcliffe | Site | Inlet Chamber 1 | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0095 |  | 2 |  | 1 | 2 |  |  | 35000 | 1 | ea. | 2020 | [9 empty] | 2 | David Ip | 1.5923e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | good | [7 empty] | 46_merge |  |  |  |  | FALSE | FALSE
88 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 137 | Inlet Chamber 1 Aluminum Platform | Aluminum platform , | Hamilton | In Service | Rockcliffe | Site | Inlet Chamber 1 | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0095 |  | 2 |  | 1 | 2 |  |  | 3000 | 1 | ea. | 2020 | [9 empty] | 2 | David Ip | 1.5923e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | good | [7 empty] | 47_merge |  |  |  |  | FALSE | FALSE
89 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 137 | Inlet Chamber 1 Aluminum Ladder | Aluminum Ladder , | Hamilton | In Service | Rockcliffe | Site | Inlet Chamber 1 | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0095 |  | 2 |  | 1 | 2 |  |  | 5500 | 1 | ea. | 2020 | [9 empty] | 2 | CAMR061927 | 1.5946e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | good | [7 empty] | 48_merge |  |  |  |  | FALSE | FALSE
90 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 137 | Inlet Chamber 1 Manhole Frame and Cover | Manhole frame and cover , | Hamilton | In Service | Rockcliffe | Site | Inlet Chamber 1 | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0093 |  | 2 |  | 1 | 2 |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 2 | David Ip | 1.5923e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | good | [7 empty] | 49_merge |  |  |  |  | FALSE | FALSE
91 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 139 | Inlet Chamber 2 Concrete Structure | Reinforced concrete inlet chamber , | Hamilton | In Service | Rockcliffe | Site | Inlet Chamber 2 | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0100 |  | 2 |  | 1 | 2 |  |  | 35000 | 1 | ea. | 2020 | [9 empty] | 2 | David Ip | 1.5923e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | good | [7 empty] | 50_merge |  |  |  |  | FALSE | FALSE
92 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 139 | Inlet Chamber 2 Aluminum Platform | Aluminum platform , | Hamilton | In Service | Rockcliffe | Site | Inlet Chamber 2 | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0100 |  | 2 |  | 1 | 2 |  |  | 3000 | 1 | ea. | 2020 | [9 empty] | 2 | David Ip | 1.5923e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | good | [7 empty] | 51_merge |  |  |  |  | FALSE | FALSE
93 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 139 | Inlet Chamber 2 Aluminum Ladder | Aluminum Ladder , | Hamilton | In Service | Rockcliffe | Site | Inlet Chamber 2 | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0100 |  | 2 |  | 1 | 2 |  |  | 5500 | 1 | ea. | 2020 | [9 empty] | 2 | David Ip | 1.5923e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | good | [7 empty] | 52_merge |  |  |  |  | FALSE | FALSE
94 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 139 | Inlet Chamber 2 Manhole Frame and Cover | Manhole frame and cover , | Hamilton | In Service | Rockcliffe | Site | Inlet Chamber 2 | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0097 |  | 2 |  | 1 | 2 |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 2 | David Ip | 1.5923e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | good | [7 empty] | 53_merge |  |  |  |  | FALSE | FALSE
95 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 9 | Generator Building Concrete Foundation | Reinforced concrete caisson and grade beam foundation , | Hamilton | In Service | Rockcliffe | Main Building |  | Building Structural | Building Structural | [7 empty] | 1992 | 60 | 2052 |  |  | 3 |  | 3 | 3 |  |  | 40000 | 1 | ea. | 2020 | [9 empty] | 1 | David Ip | 1.5923e+18 | Maira Rafiq | 1.5946e+18 | [6 empty] | 1 | [8 empty] | 54_merge |  |  |  |  | FALSE | FALSE
96 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 9 | Generator Building Concrete Floor | Reinforced concrete floor , | Hamilton | In Service | Rockcliffe | Main Building |  | Building Structural | Building Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0072 |  | 2 |  | 3 | 2 |  |  | 1200 | 17 | ea. | 2020 | [9 empty] | 1.5 | David Ip | 1.5923e+18 | Maira Rafiq | 1.5946e+18 | [6 empty] | 1 | good | [7 empty] | 55_merge |  |  |  |  | FALSE | FALSE
97 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 9 | Generator Building Masonry Blockwall | Masonry blockwalls , | Hamilton | In Service | Rockcliffe | Main Building |  | Building Structural | Building Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0072 |  | 2 |  | 3 | 2 |  |  | 150 | 76 | ea. | 2020 | [9 empty] | 2.5 | David Ip | 1.5923e+18 | Maira Rafiq | 1.5946e+18 | [6 empty] | 1 | good | [7 empty] | 56_merge |  |  |  |  | FALSE | FALSE
98 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 9 | Generator Building Precast Concrete Roof | Precast concrete roof slabs , | Hamilton | In Service | Rockcliffe | Main Building |  | Building Structural | Building Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0074 |  | 2 |  | 3 | 2 |  |  | 250 | 42 | ea. | 2020 | [9 empty] | 2.5 | David Ip | 1.5923e+18 | Maira Rafiq | 1.5946e+18 | [6 empty] | 1 | good | [7 empty] | 57_merge |  |  |  |  | FALSE | FALSE
99 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 138 | Valve Chamber Manhole Frame and Cover | Manhole frame and cover , | Hamilton | In Service | Rockcliffe | Site | Valve Chamber | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0101 |  | 2 |  | 1 | 2 |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 2 | David Ip | 1.5923e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | good | [7 empty] | 58_merge |  |  |  |  | FALSE | FALSE
100 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 138 | Valve Chamber Aluminum Ladder | Aluminum ladder , | Hamilton | In Service | Rockcliffe | Site | Valve Chamber | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0103 |  | 2 |  | 1 | 2 |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 2 | David Ip | 1.5923e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | good | [7 empty] | 59_merge |  |  |  |  | FALSE | FALSE
101 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 138 | Valve Chamber Concrete Structure | Reinforced concrete structure , | Hamilton | In Service | Rockcliffe | Site | Valve Chamber | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0103 |  | 2 |  | 1 | 2 |  |  | 9000 | 1 | ea. | 2020 | [9 empty] | 2 | David Ip | 1.5923e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | good | [7 empty] | 60_merge |  |  |  |  | FALSE | FALSE
102 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 10 | Generator Building Exterior Stone Veneer | , | Hamilton | In Service | Rockcliffe | Main Building |  | Building Architectural | Building Architectural | [7 empty] | 1992 | 30 | 2052 | COH-DC015-0086 |  | 2 |  | 3 | 2 |  |  | 180 | 76 | ea. | 2020 | [9 empty] | 2.5 | David Ip | 1.5923e+18 | Maira Rafiq | 1.5946e+18 | [6 empty] | 1 | good | [7 empty] | 61_merge |  |  |  |  | FALSE | FALSE
103 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 10 | Generator Building Asphalt Shingle Roofing | , | Hamilton | In Service | Rockcliffe | Main Building |  | Building Architectural | Building Architectural | [7 empty] | 1992 | 30 | 2025 | COH-DC015-0055 |  | 2 |  | 3 | 2 |  |  | 50 | 50 | ea. | 2020 | [9 empty] | 2 | David Ip | 1.5923e+18 | Maira Rafiq | 1.5946e+18 | [6 empty] | 1 | good | [7 empty] | 62_merge |  |  |  |  | FALSE | FALSE
104 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 10 | Generator Building Wood Truss Roof | , | Hamilton | In Service | Rockcliffe | Main Building |  | Building Architectural | Building Architectural | [7 empty] | 1992 | 30 | 2052 | COH-DC015-0055 |  | 3 |  | 3 | 3 |  |  | 8000 | 1 | ea. | 2020 | [9 empty] | 1 | David Ip | 1.5923e+18 | Maira Rafiq | 1.5946e+18 | [6 empty] | 1 | hidden under asphalt singles and precast roof. Assumed to be good based on condition of other visible assets | [7 empty] | 63_merge |  |  |  |  | FALSE | FALSE
105 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 10 | Generator Building Wall and Ceiling Paint | , | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Architectural | Building Architectural | [7 empty] | 1992 | 30 | 2025 | COH-DC015-0072 |  | 3 |  | 1 | 3 |  |  | 20 | 140 | ea. | 2020 | [9 empty] | 3.2125 | CAMR061927 | 1.5946e+18 | Maira Rafiq | 1.5946e+18 | [6 empty] | 1 | Missing/bare spot at washroom | [7 empty] | 64_merge |  |  |  |  | FALSE | FALSE
106 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 10 | Generator Building Containment Coating | , | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Architectural | Building Architectural | [7 empty] | 1992 | 30 | 2025 | COH-DC015-0072 |  | 2 |  | 1 | 2 |  |  | 60 | 20 | ea. | 2020 | [9 empty] | 2 | David Ip | 1.5923e+18 | Maira Rafiq | 1.5946e+18 | [6 empty] | 1 | good | [7 empty] | 65_merge |  |  |  |  | FALSE | FALSE
107 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 10 | Generator Building Roof Access Hatch | , | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Architectural | Building Architectural | [7 empty] | 1992 | 30 | 2052 | COH-DC015-0081 |  | 2 |  | 1 | 2 |  |  | 500 | 1 | ea. | 2020 | [9 empty] | 1.5 | David Ip | 1.5923e+18 | Maira Rafiq | 1.5946e+18 | [6 empty] | 1 | good | [7 empty] | 66_merge |  |  |  |  | FALSE | FALSE
108 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 10 | Generator Building Exterior Access Door (Double) | , | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Architectural | Building Architectural | [7 empty] | 1992 | 30 | 2025 | COH-DC015-0086 |  | 3 |  | 2 | 3 |  |  | 2000 | 1 | ea. | 2020 | [9 empty] | 2.5 | CAMR061927 | 1.5946e+18 | Maira Rafiq | 1.5946e+18 | [6 empty] | 1 | surface corrosion on hardware | weathered paint | [6 empty] | 67_merge |  |  |  |  | FALSE | FALSE
109 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 10 | Generator Building Interior Door (Single) | , | Hamilton | In Service | Rockcliffe | Main Building | Washroom | Building Architectural | Building Architectural | [7 empty] | 1992 | 30 | 2025 | COH-DC015-0082 |  | 2 |  | 2 | 2 |  |  | 1520 | 1 | ea. | 2020 | [9 empty] | 2.5 | David Ip | 1.5923e+18 | Maira Rafiq | 1.5946e+18 | [6 empty] | 1 | good | [7 empty] | 68_merge |  |  |  |  | FALSE | FALSE
110 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 9 | Generator Building Aluminum Ladder | Aluminum ladder to attic , | Hamilton | In Service | Rockcliffe | Main Building |  | Building Structural | Building Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0080 |  | 2 |  | 2 | 2 |  |  | 1500 | 1 | ea. | 2020 | [9 empty] | 1.5 | David Ip | 1.5923e+18 | Maira Rafiq | 1.5946e+18 | [6 empty] | 1 | good | [7 empty] | 69_merge |  |  |  |  | FALSE | FALSE
111 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 11 | Generator Exhaust | Generator Exhaust and damper , | Hamilton |  | Rockcliffe |  |  | Building Mechanical | Building Mechanical | Emergency Power | [6 empty] | 1992 | 30 | 2045 | COH-DC015-0329 |  | 2 |  | 3 | 2 |  |  | 4500 | 1 | ea. | 2020 | [9 empty] | 1 | Patryk Frankiewicz | 1.5944e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | good | [7 empty] | 36_merge |  |  |  |  | FALSE | FALSE
112 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 147 | Baseboard Heater | Washroom heater , | Hamilton |  | Rockcliffe | Main Building | Washroom | Building Mechanical | Building Mechanical | Heating System | [6 empty] | 1992 | 30 | 2030 | COH-DC015-0342 |  | 3 |  | 2 | 3 |  |  | 250 | 1 | ea. | 2020 | [9 empty] | 2.4375 |  | 1.5946e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | Discoloration and dust | [7 empty] | 37_merge |  |  |  |  | FALSE | FALSE
113 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 147 | Hot Water Tank | Hot Water Tank , 1.5kw | Hamilton | In Service | Rockcliffe |  |  | Building Mechanical | Building Mechanical | Domestic Plumbing System |  | AO Smith | ELJF 15 910 |  |  |  | 1992 | 30 | 2021 | COH-DC015-0343 |  | 3 |  | 2 | 3 |  |  | 1200 | 1 | ea. | 2020 | [9 empty] | 2.4375 | Patryk Frankiewicz | 1.5944e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | Fair | [6 empty] | 1.5kw | 38_merge |  |  |  |  | FALSE | FALSE
114 |  | DC015WWL01VTF01 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Fan | Wet Well Fan and duct , | Hamilton |  | Rockcliffe |  |  | Building Mechanical | Building Mechanical | Ventilation System | [6 empty] | 1992 | 30 | 2021 | COH-DC015-0348 |  | 4 |  | 2 | 4 |  |  | 5500 | 1 | ea. | 2020 | [9 empty] | 3.5 |  | 1.5946e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | CC: The wet well was equipped with a supply fan only. This do not conform with NFPA 820 Section 9.2.6 requirements. As per the mentioned section ventilation system serving classified locations shall maintain a minimum differential pressure relative to amb | Minor corrosion on fan casing | Moderate corrosion on the duct | [5 empty] | 39_merge |  |  |  |  | FALSE | FALSE
115 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 147 | Washroom Exhaust (New Asset) | , | Hamilton |  | Rockcliffe | Main Building | Washroom | Building Mechanical | Building Mechanical | Ventilation System | [7 empty] | 30 |  | COH-DC015-0339 |  | 4 |  |  | 4 |  |  | 3500 | 1 | ea. | 2020 | [9 empty] | 1 | Patryk Frankiewicz | 1.5944e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | CC: There was no exhaust fan installed in the washroom, which do not conform with the OBC 9.32.3.5 “Supplemental Exhaust” requirements. Additionally, as per City’s Wastewater Outstations Design Manual Ref. No. 13.1.3 one exhaust fan with an on/off switch | [7 empty] | 40_merge |  |  |  |  | FALSE | FALSE
116 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 147 | Backflow Preventer | Water Meter and Backflow relocation , | Hamilton | Installed | Rockcliffe | Wet Well |  | Building Mechanical | Building Mechanical | Domestic Plumbing System | [6 empty] | 1912 | 30 |  | COH-DC015-0214 |  | 4 |  | 3 | 4 |  |  | 20000 | 1 | ea. | 2020 | [9 empty] | 1 |  | 1.5946e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | HS: The backflow was installed in the wet well. As per Ontario’s Design Guidelines for Sewage Works Section 7.3, backflow preventers require periodic inspection, maintenance and induce high pressure loss and therefore cannot be installed below ground leve | Minor corrosion on bolts | [6 empty] | 41_merge |  |  |  |  | FALSE | FALSE
117 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 147 | Fire Extinguisher | Total of 1 , | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Mechanical | Building Mechanical | Miscellaneous Mechanical | [6 empty] | 2020 | 30 |  | COH-DC015-0305 |  | 1 |  | 3 | 1 |  |  | 100 | 1 | ea. | 2020 | [9 empty] | 2.5 |  | 1.5946e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | Very Good | [7 empty] | 42_merge |  |  |  |  | FALSE | FALSE
118 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Overflow Piping | Overflow yard piping. Unknown material. Approximate Length: 30 meters, Pipe Dia: 600mm. Assumed to be reinformed concrete pipe installed in 1992 , | Hamilton | In Service | Rockcliffe | Site |  | Process Mechanical | Process Mechanical Piping and Equipment | [8 empty] | 30 |  |  |  | 3 |  | 3 | 3 |  |  | 325 | 35 | ea. | 2020 | [9 empty] | 4 | CAMR061927 | 1.5967e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | Stones build-up at the discharge end | [8 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
119 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 2 | Asphalt Pavement | Asphalt Pavement, approximate area: 250 square meter , | Hamilton | In Service | Rockcliffe | Site |  | Site Works | Site Civil |  | Road | [5 empty] | 1992 | 20 |  | COH-DC015-0444 |  | 4 |  | 1 | 4 |  |  | 55 | 250 | ea. | 2020 | [9 empty] | 1.25 | CAMR061927 | 1.5968e+18 | Maira Rafiq | 1.5978e+18 | [6 empty] | 1 | Vegetation and pot holes at the site entrance, Gravels and mud | HS: The presence of gravel and dirt on the driveway adjacent to the wet well presents a trip hazard. | [7 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
120 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 2 | Station Manual Perimeter Fencing Gate | Station Manual Perimeter Fencing Gate, approxiate length: 5 meters. , | Hamilton |  | Rockcliffe | Site |  | Site Works | Site Civil |  | Gate | [6 empty] | 20 |  | COH-DC015-0424 |  | 3 |  | 1 | 3 |  |  | 3380 | 1 | ea. | 2020 | [9 empty] | 3.1875 | CAMR061927 | 1.5968e+18 | Maira Rafiq | 1.5978e+18 | [6 empty] | 1 | Minor corrosion, broken barbed wires and deformation of the gate | OM: It was identified by the operator that the station has experienced vandalism in the past. | [7 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
121 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 2 | Perimeter Fencing | Perimeter Fencing, installation year: 1992, Approximate Length: 110 meters , | Hamilton |  | Rockcliffe | Site |  | Site Works | Site Civil |  | Fencing | [6 empty] | 20 |  | COH-DC015-0445 |  | 4 |  | 1 | 4 |  |  | 170 | 110 | ea. | 2020 | [9 empty] | 3.1875 | CAMR061927 | 1.5968e+18 | Maira Rafiq | 1.5978e+18 | [6 empty] | 1 | HS: It was identified by the operator that the station has experienced vandalism in the past. | Overgrown vegetation penetrated through the fencing throughout the station | OM: It was identified by the operator that the station has experienced vandalism in the past. | [6 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
122 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 118 | Overflow Flap Gate | Overflow Flap Gate , | Hamilton | In Service | Rockcliffe | Site |  | Process Mechanical | Process Mechanical Piping and Equipment |  | Gate | [5 empty] | 1992 | 30 |  | COH-DC015-0499 |  | 3 |  | 2 | 3 |  |  | 0 | 1 | ea. | 2020 | [9 empty] | 0 | CAMR061927 | 1.5968e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | blocked by stones and dirt and would not open properly in the event of station overflow. | [8 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
123 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 11 | Diesel Fuel System | Diesel Storage Tanks 1&2 , | Hamilton |  | Rockcliffe | Main Building | Generator Room | Building Mechanical | Building Mechanical |  |  | DTE | Capacity 1135 L |  |  |  |  | 30 | 2040 | COH-DC015-0313 |  | 4 |  | 3 | 4 |  |  | 15000 | 1 | ea. | 2020 | [9 empty] | 1.5 | CAMR061927 | 1.5968e+18 | Maira Rafiq | 1.5971e+18 | [6 empty] | 1 | CC: There was no containment for diesel fuel lines. TSSA requires all equipment containing or carrying fuel to be contained per CSA B139.1.1-15 Section 6.5.1.4. | [8 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
124 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 11 | Generator Intake | Motorized Intake , | Hamilton | In Service | Rockcliffe | Main Building | Generator Room | Building Mechanical | Building Mechanical | [7 empty] | 1992 | 30 | 2045 | COH-DC015-0322 |  | 3 |  | 3 | 3 |  |  | 1430 | 1 | ea. | 2020 | [9 empty] | 2.4375 | CAMR061927 | 1.5968e+18 | Maira Rafiq | 1.5968e+18 | [6 empty] | 1 | Good | minor surface corrosion | [7 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
125 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 147 | Control Room Exhaust Fan | DC015, GENERATOR/CONTROL ROOM EXHAUST FAN , | Hamilton | In Service | Rockcliffe | Main Building |  | Building Mechanical | Building Mechanical |  |  | Canadian Blower | 16 | S218650000001 |  |  | 2010 | 30 | 2040 | COH-DC015-0324 |  | 2 |  | 2 | 2 |  |  | 1430 | 1 | ea. | 2020 | [9 empty] | 2.4375 | CAMR061927 | 1.5968e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | good | good | [7 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
126 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 11 | Generator Flue Exhaust | Exhaust Silencer and Stack , | Hamilton | Installed | Rockcliffe | Main Building | Generator Room | Building Mechanical | Building Mechanical | [7 empty] | 1992 | 30 | 2045 | COH-DC015-0329 |  | 2 |  | 3 | 2 |  |  | 20000 | 1 | ea. | 2020 | [9 empty] | 1 | CAMR061927 | 1.5968e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | good | [8 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
127 | 9 | DC015SLP0200000 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Sewage Lift Pump No.2 | Submersible Pump No.2 , | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Pump |  | ITT | CP3201.180 | 140 L/s @ 14m TDH, 28 kW |  |  | 2009 | 30 |  | COH-DC015-0281 |  | 2 |  | 3 | 2 |  |  | 137700 | 1 | ea. | 2020 | [9 empty] | 1.3625 | CAMR061927 | 1.5972e+18 | Maira Rafiq | 1.5972e+18 | [6 empty] | 1 | Good | [8 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
128 | 10 | DC015SLP0300000 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Sewage Lift Pump No.3 | Submersible Pump No.3 , | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Pump |  | ITT | CP3201.180 | 140 L/s @ 14m TDH, 28 kW |  |  | 2009 | 30 |  | COH-DC015-0280 |  | 2 |  | 3 | 2 |  |  | 137700 | 1 | ea. | 2020 | [9 empty] | 1.3625 | CAMR061927 | 1.5972e+18 | Maira Rafiq | 1.5972e+18 | [6 empty] | 1 | Good | [8 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
129 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 3 | Hand Stop Gate No.1 | Hand Stop Gate No.1 ,36"X 36" | Hamilton | Not In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Gate | [6 empty] | 1992 | 30 |  | COH-DC015-0236 |  | 3 |  | 2 | 3 |  |  | 6080 | 1 | ea. | 2020 | [9 empty] | 1.85 | CAMR061927 | 1.5972e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | Deterioration | [6 empty] | 36"X 36" |  | 0 | 0 | 0 | 0 | FALSE | FALSE
130 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Concrete Structure | Reinforced concrete wet well structure , | Hamilton |  | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0001 |  | 2 |  | 3 | 2 |  |  | 280000 | 1 | ea. | 2020 | [9 empty] | 2 | CAMR061927 | 1.5968e+18 | Maira Rafiq | 1.5978e+18 | [6 empty] | 1 | good | concrete was found to be hard/strong based on hammer striking and schmidt hammer test. Concrete cover at 51mm based on cover meter test | [7 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
131 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Aluminum Ladder | Aluminum ladder from exterior to intermetdiate platform (with cage) , | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0039 |  | 3 |  | 1 | 3 |  |  | 3500 | 1 | ea. | 2020 | [9 empty] | 1.5 | CAMR061927 | 1.5971e+18 | Maira Rafiq | 1.5978e+18 | [6 empty] | 1 | buildup of calcium and minor pitting | [8 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
132 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Aluminum Ladder | Aluminum ladder from intermediate platform to lower platform (with cage) , | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0039 |  | 3 |  | 1 | 3 |  |  | 3500 | 1 | ea. | 2020 | [9 empty] | 1.5 | CAMR061927 | 1.5971e+18 | Maira Rafiq | 1.5978e+18 | [6 empty] | 1 | buildup of calcium and minor pitting | [8 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
133 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wet Well Aluminum Ladder | Aluminum ladder from lower platform to wet well , | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Structural | Process Structural | [7 empty] | 1992 | 60 | 2052 | COH-DC015-0050 |  | 4 |  | 1 | 4 |  |  | 2500 | 1 | ea. | 2020 | [9 empty] | 1.5 | CAMR061927 | 1.5971e+18 | Maira Rafiq | 1.5978e+18 | [6 empty] | 1 | HS: buildup of calcium and minor pitting | [8 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
134 |  | DC015WWL02LSL01 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wetwell 2 Low Level Float | Wetwell No.2 Low Level Float , | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Instrumentation | Process Instrumentation & Control | [7 empty] | 2016 | 15 |  | COH-DC015-0269 |  | 3 |  | 2 | 3 |  |  | 500 | 1 | ea. | 2020 | [9 empty] | 1.3 | CAMR061927 | 1.5972e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | [9 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
135 |  | DC015WWL01LSL01 |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 6 | Wetwell 1 Low Level Float | Wetwell No.1 Low Level Float , | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Instrumentation | Process Instrumentation & Control | [7 empty] | 2016 | 15 |  | COH-DC015-0269 |  | 3 |  | 2 | 3 |  |  | 500 | 1 | ea. | 2020 | [9 empty] | 1.3 | CAMR061927 | 1.5972e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | [9 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
136 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 146 | Exit Lighting (New Asset) | , | Hamilton |  | Rockcliffe | Main Building | Generator Room | Building Electrical | Building Electrical | Lighting | [7 empty] | 25 |  |  |  | 4 |  | 2 | 4 |  |  | 500 | 1 | ea. | 2020 | [9 empty] | 1.3 | CAMR061927 | 1.5972e+18 | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | CC: There was no exit sign installed at the station. The station needs an exit sign according to Canadian Building Code (section 3.2.7.3) and Canadian Fire Code (Section 2.7.3). | [8 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
137 | 14 |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Inlet Chamber 1 | , | Hamilton | In Service | Rockcliffe | Site | Inlet Chamber 1 | Process Structural | Process Structural | [7 empty] | 1992 | 60 |  | COH-DC015-0095 |  | 3 |  | 1 | 3 |  |  |  |  | ea. | 2020 | [12 empty] | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | [9 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
138 | 15 |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Valve Chamber | , | Hamilton | In Service | Rockcliffe | Site | Valve Chamber | Process Structural | Process Structural | [7 empty] | 1992 | 60 |  | COH-DC015-0103 |  | 3 |  | 1 | 3 |  |  |  |  | ea. | 2020 | [12 empty] | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | [9 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
139 | 16 |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Inlet Chamber 2 | , | Hamilton | In Service | Rockcliffe | Site | Inlet Chamber 2 | Process Structural | Process Structural | [7 empty] | 1992 | 60 |  | COH-DC015-0097 |  | 3 |  | 1 | 3 |  |  |  |  | ea. | 2020 | [12 empty] | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | [9 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
140 | 6 |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE |  | Process Electrical | , | Hamilton |  | Rockcliffe |  |  | Process Electrical | Process Electrical | [8 empty] | 25 |  |  |  | 3 |  |  | 3 |  |  |  |  | ea. | 2020 | [12 empty] | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | [9 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
141 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 127 | Pump 2 Piping | Process Mechanical Piping , 7.5 m of 100 mm dia DI pipe, 16.5 m of 200 mm dia DI pipe, 16.5 m of 300 mm DI pipe | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Piping | [6 empty] | 1992 | 30 |  | COH-DC015-0206 |  | 3 |  | 3 | 3 |  |  |  |  | ea. | 2020 | [12 empty] | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | [7 empty] | 7.5 m of 100 mm dia DI pipe, 16.5 m of 200 mm dia DI pipe, 16.5 m of 300 mm DI pipe |  | 0 | 0 | 0 | 0 | FALSE | FALSE
142 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 128 | Pump 3 Piping | Process Mechanical Piping , 7.5 m of 100 mm dia DI pipe, 16.5 m of 200 mm dia DI pipe, 16.5 m of 300 mm DI pipe | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Piping | [6 empty] | 1992 | 30 |  | COH-DC015-0206 |  | 3 |  | 3 | 3 |  |  |  |  | ea. | 2020 | [12 empty] | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | [7 empty] | 7.5 m of 100 mm dia DI pipe, 16.5 m of 200 mm dia DI pipe, 16.5 m of 300 mm DI pipe |  | 0 | 0 | 0 | 0 | FALSE | FALSE
143 | 11 |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE | 1 | Discharge Header | Process Mechanical Piping , 7.5 m of 100 mm dia DI pipe, 16.5 m of 200 mm dia DI pipe, 16.5 m of 300 mm DI pipe | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Piping | [6 empty] | 1992 | 30 |  | COH-DC015-0206 |  | 3 |  | 3 | 3 |  |  |  |  | ea. | 2020 | [12 empty] | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | [7 empty] | 7.5 m of 100 mm dia DI pipe, 16.5 m of 200 mm dia DI pipe, 16.5 m of 300 mm DI pipe |  | 0 | 0 | 0 | 0 | FALSE | FALSE
144 |  |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | FALSE | FALSE | 143 | Drain Piping | Process Mechanical Piping , 7.5 m of 100 mm dia DI pipe, 16.5 m of 200 mm dia DI pipe, 16.5 m of 300 mm DI pipe | Hamilton | In Service | Rockcliffe | Wet Well |  | Process Mechanical | Process Mechanical Piping and Equipment | Piping | [6 empty] | 1992 | 30 |  | COH-DC015-0206 |  | 3 |  | 3 | 3 |  |  |  |  | ea. | 2020 | [12 empty] | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | [7 empty] | 7.5 m of 100 mm dia DI pipe, 16.5 m of 200 mm dia DI pipe, 16.5 m of 300 mm DI pipe |  | 0 | 0 | 0 | 0 | FALSE | FALSE
145 | 7 |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE |  | Process Instrumentation & Control | , | Hamilton |  | Rockcliffe |  |  | Process Instrumentation | Process Instrumentation & Control | [8 empty] | 15 |  |  |  | 3 |  |  | 3 |  |  |  |  | ea. | 2020 | [12 empty] | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | [9 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
146 | 2 |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE |  | Building Electrical | , | Hamilton |  | Rockcliffe |  |  | Building Electrical | Building Electrical | [8 empty] | 25 |  |  |  | 3 |  |  | 3 |  |  |  |  | ea. | 2020 | [12 empty] | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | [9 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE
147 | 4 |  |  | 0 |  |  |  |  | 0 |  |  | FALSE | FALSE | TRUE | TRUE |  | Building Mechanical | , | Hamilton |  | Rockcliffe |  |  | Building Mechanical | Building Mechanical | [8 empty] | 30 |  |  |  | 3 |  |  | 3 |  |  |  |  | ea. | 2020 | [12 empty] | Maira Rafiq | 1.5979e+18 | [6 empty] | 1 | [9 empty] | 0 | 0 | 0 | 0 | FALSE | FALSE

## comment
| 0 | 1 | 2 | 3
0 | ParentID | AssetName | Comment Type | Comment
9 | 3 | Sewage Lift Pump No.1 | Condition Comment | The asset was observed to be in good condition.
13 | 4 | MCC | Condition Comment | The asset was observed to be in good condition, however it did not have arc flash labels.
14 | 4 | MCC | Code Concern Comment | Missing arc flash labels
17 | 5 | SCADA WAN Panel | Condition Comment | The asset was observed to be in good condition.
21 | 6 | Wet Well | Condition Comment | The asset was assumed to be in fair condition.
25 | 7 | Unit Heater 1 | Condition Comment | The asset was observed to be in good condition, however, there was no containment for diesel fuel lines. TSSA requires all equipment containing or carrying.Fuel to be contained per csa b139.1.1-15 section 6.5.1.4.
26 | 7 | Unit Heater 1 | Code Concern Comment | There was no containment for diesel fuel lines. tssa requires all equipment containing or carrying. fuel to be contained per csa b139.1.1-15 section 6.5.1.4.
29 | 8 | Interior Lighting | Condition Comment | The asset was observed to be in good condition. It is recommended to replace the lighting with LED in the next upgrade project.
33 | 9 | Building Structural | Condition Comment | The asset was assumed to be in fair condition.
37 | 10 | Building Architectural | Condition Comment | The asset was assumed to be in fair condition.
41 | 11 | Emergency Backup Power | Condition Comment | The asset was assumed to be in fair condition.
45 | 14 | Diesel Fuel Tank #1 For Generator | Condition Comment | The asset was observed to be in good condition, however, there was no containment for diesel fuel lines. TSSA requires all equipment containing or carrying.Fuel to be contained per csa b139.1.1-15 section 6.5.1.4.
46 | 14 | Diesel Fuel Tank #1 For Generator | Code Concern Comment | There was no containment for diesel fuel lines. tssa requires all equipment containing or carrying fuel to be contained per csa b139.1.1-15 section 6.5.1.4.
49 | 15 | Diesel Fuel Tank #2 For Generator | Condition Comment | The asset was observed to be in good condition, however, there was no containment for diesel fuel lines. TSSA requires all equipment containing or carrying.Fuel to be contained per csa b139.1.1-15 section 6.5.1.4.
50 | 15 | Diesel Fuel Tank #2 For Generator | Code Concern Comment | There was no containment for diesel fuel lines. tssa requires all equipment containing or carrying
53 | 20 | Standby Diesel Power Generator | Condition Comment | The asset was observed to be in good condition.
57 | 30 | Wet Well Level Transmitter #1 | Condition Comment | The asset was observed to be in good condition.
61 | 31 | Wet Well Level Transmitter #2 | Condition Comment | The asset was observed to be in good condition.
65 | 32 | Power Meter | Condition Comment | The asset was observed to be in good condition.
69 | 33 | Main Breaker | Condition Comment | The asset was observed to be in good condition, however it did not have arc flash labels.
70 | 33 | Main Breaker | Code Concern Comment | Missing arc flash labels
73 | 34 | Power Factor Capacitors | Condition Comment | The asset was observed to be in good condition.
77 | 35 | Unit Heater Starter | Condition Comment | The asset was observed to be in good condition, however it did not have arc flash labels.
78 | 35 | Unit Heater Starter | Code Concern Comment | Missing arc flash labels
81 | 36 | Hand Stop Gate No.2 | Condition Comment | The asset was observed to be in fair condition. Deterioration was observed.
85 | 37 | Hand Stop Gate No.3 | Condition Comment | The asset was observed to be in fair condition. Deterioration was observed.
89 | 38 | Manual Bar Screen No.1 | Condition Comment | The asset was observed to be in fair condition. Bent bars were observed. The operators mentioned that the screens had been removed and were no longer in use.
92 | 38 | Manual Bar Screen No.1 | Client Comment | The operators mentioned that the screens have been removed and are no longer in use.
93 | 39 | Manual Bar Screen No.2 | Condition Comment | The asset was observed to be in fair condition. Bent bars were observed. The operators mentioned that the screens had been removed and were no longer in use.
96 | 39 | Manual Bar Screen No.2 | Client Comment | The operators mentioned that the screens have been removed and are no longer in use.
97 | 40 | Sewage Lift Pump No.1 Check Valve | Condition Comment | The asset was observed to be in fair condition. Heavy corrosion and deterioration were observed.
101 | 41 | Sewage Lift Pump No.2 Check Valve | Condition Comment | The asset was observed to be in fair condition. Heavy corrosion and deterioration were observed.
105 | 42 | Sewage Lift Pump No.3 Check Valve | Condition Comment | The asset was observed to be in fair condition. Heavy corrosion and deterioration were observed.
109 | 43 | Sewage Lift Pump No.1 Discharge Valve | Condition Comment | The asset was observed to be in fair condition. Heavy corrosion and deterioration were observed.
113 | 44 | Sewage Lift Pump No.2 Discharge Valve | Condition Comment | The asset was observed to be in fair condition. Heavy corrosion and deterioration were observed.
117 | 45 | Sewage Lift Pump No.3 Discharge Valve | Condition Comment | The asset was observed to be in fair condition. Heavy corrosion and deterioration were observed.
121 | 46 | Discharge Header Gate Valve | Condition Comment | The asset was observed to be in fair condition. Heavy corrosion and deterioration was observed. Turn wheel appeared to be missing
125 | 47 | Drain Gate Valve | Condition Comment | The asset was observed to be in fair condition. Heavy corrosion and deterioration were observed.
129 | 48 | Pressure Release Valve No.1 | Condition Comment | The asset was observed to be in fair condition. Heavy corrosion and deterioration were observed.
133 | 49 | Wetwell Cell Isolation Gate | Condition Comment | The asset was observed to be in fair condition. Moderate surface corrosion was observed.
137 | 50 | Sluice Gate No.1 | Condition Comment | The asset was observed to be in fair condition. Heavy corrosion and deterioration on the frame of the sluice gate were observed.
141 | 51 | Pump 1 Piping | Condition Comment | The asset was observed to be in fair condition. Heavy corrosion and deterioration on majority portion of the piping were observed.
145 | 52 | Forcemain | Condition Comment | The asset was assumed to be in fair condition.
149 | 53 | SCADA PANEL | Condition Comment | The asset was observed to be in good condition.
153 | 54 | Station Temperature Transmitter | Condition Comment | The asset was observed to be in fair condition. Communication via pribusin transmitter is old technology and will be obselete in near future. It is recommended tp replace the temperature trasmitter with a cellular transmitter or a hardwired signal from the temperature device to directly connected to th.
157 | 55 | UPS | Condition Comment | The asset was observed to be in good condition. Dust was observed.
161 | 56 | Wetwell 1 High Level Float | Condition Comment | The asset was observed to be in good condition.
165 | 57 | Wetwell 2 High Level Float | Condition Comment | The asset was observed to be in good condition.
169 | 58 | Pump 1 VFD | Condition Comment | The asset was observed to be in good condition, however it did not have arc flash labels.
170 | 58 | Pump 1 VFD | Code Concern Comment | Missing arc flash labels
173 | 59 | Wet well Fan Starter | Condition Comment | The asset was observed to be in good condition, however it did not have arc flash labels.
174 | 59 | Wet well Fan Starter | Code Concern Comment | Missing arc flash labels
177 | 60 | Diesel Generator Room Fan Starter | Condition Comment | The asset was observed to be in good condition, however it did not have arc flash labels.
178 | 60 | Diesel Generator Room Fan Starter | Code Concern Comment | Missing arc flash labels
181 | 61 | Pump 2 VFD | Condition Comment | The asset was observed to be in good condition, however it did not have arc flash labels.
182 | 61 | Pump 2 VFD | Code Concern Comment | Missing arc flash labels
185 | 62 | Pump 3 VFD | Condition Comment | The asset was observed to be in good condition, however it did not have arc flash labels.
186 | 62 | Pump 3 VFD | Code Concern Comment | Missing arc flash labels
189 | 63 | Diesel Generator Control Panel | Condition Comment | The asset was observed to be in good condition, however it did not have arc flash labels.
190 | 63 | Diesel Generator Control Panel | Code Concern Comment | Missing arc flash labels
193 | 64 | Emergency Lighting | Condition Comment | The asset was observed to be in good condition.
197 | 65 | Lighting Panel LPA | Condition Comment | The asset was observed to be in good condition.
201 | 66 | Lighting Trasnformer | Condition Comment | The asset was observed to be in good condition.
205 | 67 | Exterior Lighting | Condition Comment | The asset was observed to be in good condition.
209 | 68 | Wet Well Lighting | Condition Comment | The asset was observed to be in fair condition. It was observed to be corroded. It is recommended to replace it with class 1, div 1 fixture.
213 | 69 | Main Transformer | Condition Comment | The asset was observed to be in good condition.
217 | 73 | Signboards | Condition Comment | The asset was observed to be in good condition.
221 | 75 | Station Access Road | Condition Comment | The asset was observed to be in fair condition. Pot holes and mud bumps were observed.
225 | 76 | Sanitary Sewer | Condition Comment | The asset was observed to be in good condition.
229 | 77 | Wet Well Aluminum Ladder | Condition Comment | The asset was observed to be in fair condition. Buildup of calcium and minor pitting were observed.
233 | 78 | Wet Well Aluminum Guardrail | Condition Comment | The asset was observed to be in fair condition. Buildup of calcium and minor pitting were observed.
237 | 79 | Wet Well Aluminum Grating | Condition Comment | The asset was observed to be in poor condition. Buildup of calcium and minor pitting were observed. One section of grating was missing and should be installed/replaced
239 | 79 | Wet Well Aluminum Grating | H&S Concern Comment | One section of grating was missing and should be installed/replaced
241 | 80 | Wet Well Access Hatch | Condition Comment | The asset was observed to be in good condition.
245 | 81 | Wet Well Pump Hatch 1 | Condition Comment | The asset was observed to be in fair condition. Retrofit of safety grating underneath the pump hatch is recommended to mitgate a falling hazard when hatch is open.
247 | 81 | Wet Well Pump Hatch 1 | H&S Concern Comment | Retrofit of safety grating underneath the pump hatch is recommended to mitgate a falling hazard when hatch is open
249 | 82 | Wet Well Pump Hatch 2 | Condition Comment | The asset was observed to be in fair condition. Retrofit of safety grating underneath the pump hatch is recommended to mitgate a falling hazard when hatch is open.
253 | 83 | Wet Well Pump Hatch 3 | Condition Comment | The asset was observed to be in fair condition. Retrofit of safety grating underneath the pump hatch is recommended to mitgate a falling hazard when hatch is open.
257 | 84 | Wet Well Pump Hatch 4 | Condition Comment | The asset was observed to be in fair condition. Retrofit of safety grating underneath the pump hatch is recommended to mitgate a falling hazard when hatch is open.
261 | 85 | Wet Well Davit Base 1 | Condition Comment | The asset was observed to be in good condition.
265 | 86 | Wet Well Davit Base 2 | Condition Comment | The asset was observed to be in fair condition. Observed cap was missing.
269 | 87 | Inlet Chamber 1 Concrete Structure | Condition Comment | The asset was observed to be in good condition.
273 | 88 | Inlet Chamber 1 Aluminum Platform | Condition Comment | The asset was observed to be in good condition.
277 | 89 | Inlet Chamber 1 Aluminum Ladder | Condition Comment | The asset was observed to be in good condition.
281 | 90 | Inlet Chamber 1 Manhole Frame and Cover | Condition Comment | The asset was observed to be in good condition.
285 | 91 | Inlet Chamber 2 Concrete Structure | Condition Comment | The asset was observed to be in good condition.
289 | 92 | Inlet Chamber 2 Aluminum Platform | Condition Comment | The asset was observed to be in good condition.
293 | 93 | Inlet Chamber 2 Aluminum Ladder | Condition Comment | The asset was observed to be in good condition.
297 | 94 | Inlet Chamber 2 Manhole Frame and Cover | Condition Comment | The asset was observed to be in good condition.
301 | 95 | Generator Building Concrete Foundation | Condition Comment | The asset was assumed to be in fair condition.
305 | 96 | Generator Building Concrete Floor | Condition Comment | The asset was observed to be in good condition.
309 | 97 | Generator Building Masonry Blockwall | Condition Comment | The asset was observed to be in good condition.
313 | 98 | Generator Building Precast Concrete Roof | Condition Comment | The asset was observed to be in good condition.
317 | 99 | Valve Chamber Manhole Frame and Cover | Condition Comment | The asset was observed to be in good condition.
321 | 100 | Valve Chamber Aluminum Ladder | Condition Comment | The asset was observed to be in good condition.
325 | 101 | Valve Chamber Concrete Structure | Condition Comment | The asset was observed to be in good condition.
329 | 102 | Generator Building Exterior Stone Veneer | Condition Comment | The asset was observed to be in good condition.
333 | 103 | Generator Building Asphalt Shingle Roofing | Condition Comment | The asset was observed to be in good condition.
337 | 104 | Generator Building Wood Truss Roof | Condition Comment | As it was hidden under asphalt singles and precast roof, the asset was assumed to be good based on condition of other visible assets.
341 | 105 | Generator Building Wall and Ceiling Paint | Condition Comment | The asset was observed to be in fair condition. Missing/bare spot at washroom.
345 | 106 | Generator Building Containment Coating | Condition Comment | The asset was observed to be in good condition.
349 | 107 | Generator Building Roof Access Hatch | Condition Comment | The asset was observed to be in good condition.
353 | 108 | Generator Building Exterior Access Door (Double) | Condition Comment | The asset was observed to be in fair condition. Surface corrosion on hardware and weathered paint were observed.
357 | 109 | Generator Building Interior Door (Single) | Condition Comment | The asset was observed to be in good condition.
361 | 110 | Generator Building Aluminum Ladder | Condition Comment | The asset was observed to be in good condition.
365 | 111 | Generator Exhaust | Condition Comment | The asset was observed to be in good condition.
369 | 112 | Baseboard Heater | Condition Comment | The asset was observed to be in fair condition. Discoloration and dust were observed.
373 | 113 | Hot Water Tank | Condition Comment | The asset was observed to be in fair condition.
377 | 114 | Wet Well Fan | Condition Comment | The asset was observed to be in poor condition. Minor corrosion was observed on fan casing and moderate corrosion was observed on the duct. The wet well was equipped with a supply fan only. This does not conform with NFPA 820 section 9.2.6 requirements. As per the mentioned section ventilation system serving classified locations shall maintain a minimum differential pressure relative to o ambient pressure of -25 Pa (−0.1 in. water column) under all operating conditions.
378 | 114 | Wet Well Fan | Code Concern Comment | The wet well was equipped with a supply fan only. this do not conform with nfpa 820 section 9.2.6 requirements. as per the mentioned section ventilation system serving classified locations shall maintain a minimum differential pressure relative to amb
381 | 115 | Washroom Exhaust (New Asset) | Condition Comment | There was no exhaust fan installed in the washroom, which do not conform with the OBC 9.32.3.5 “supplemental exhaust” requirements. additionally, as per city’s wastewater outstations design manual ref. no. 13.1.3 one exhaust fan with an on/off switch with a timer at the entrance to the washroom is required.
382 | 115 | Washroom Exhaust (New Asset) | Code Concern Comment | There was no exhaust fan installed in the washroom, which do not conform with the obc 9.32.3.5 “supplemental exhaust” requirements. additionally, as per city’s wastewater outstations design manual ref. no. 13.1.3 one exhaust fan with an on/off switch
385 | 116 | Backflow Preventer | Condition Comment | The asset was observed to be in fair condition. Minor corrosion was observed on bolts.The backflow was installed in the wet well. As per Ontario’s Design Guidelines for Sewage Works Section 7.3, backflow preventers require periodic inspection, maintenance and induce high pressure loss and therefore cannot be installed below ground level.
387 | 116 | Backflow Preventer | H&S Concern Comment | The backflow was installed in the wet well. as per ontario’s design guidelines for sewage works section 7.3, backflow preventers require periodic inspection, maintenance and induce high pressure loss and therefore cannot be installed below ground leve
389 | 117 | Fire Extinguisher | Condition Comment | The asset was observed to be in very good condition.
393 | 118 | Overflow Piping | Condition Comment | The asset was observed to be in fair condition. Stones build-up at the discharge end was observed.
397 | 119 | Asphalt Pavement | Condition Comment | The asset was observed to be in poor condition. Vegetation was observed and pot holes at the site entrance, gravels and mud.The presence of gravel and dirt on the driveway adjacent to the wet well presents a trip hazard.
399 | 119 | Asphalt Pavement | H&S Concern Comment | The presence of gravel and dirt on the driveway adjacent to the wet well presents a trip hazard.
401 | 120 | Station Manual Perimeter Fencing Gate | Condition Comment | The asset was observed to be in fair condition. Minor corrosion, broken barbed wires and deformation of the gate were observed.It was identified by the operator that the station has experienced vandalism in the past.
404 | 120 | Station Manual Perimeter Fencing Gate | Client Comment | It was identified by the operator that the station has experienced vandalism in the past.
405 | 121 | Perimeter Fencing | Condition Comment | The asset was observed to be in fair condition. Overgrown vegetation penetrated through the fencing throughout the station was observed.It was identified by the operator that the station has experienced vandalism in the past.
407 | 121 | Perimeter Fencing | H&S Concern Comment | It was identified by the operator that the station has experienced vandalism in the past.
408 | 121 | Perimeter Fencing | Client Comment | It was identified by the operator that the station has experienced vandalism in the past.
409 | 122 | Overflow Flap Gate | Condition Comment | The asset was observed to be in fair condition. Blocked by stones and dirt and would not open properly in the event of station overflow was observed.
413 | 123 | Diesel Fuel System | Condition Comment | The asset was observed to be in good condition, however, there was no containment for diesel fuel lines. TSSA requires all equipment containing or carrying.Fuel to be contained per csa b139.1.1-15 section 6.5.1.4.
414 | 123 | Diesel Fuel System | Code Concern Comment | There was no containment for diesel fuel lines. tssa requires all equipment containing or carrying fuel to be contained per csa b139.1.1-15 section 6.5.1.4.
417 | 124 | Generator Intake | Condition Comment | The asset was observed to be in fair condition. Minor surface corrosion was observed.
421 | 125 | Control Room Exhaust Fan | Condition Comment | The asset was observed to be in good condition.
425 | 126 | Generator Flue Exhaust | Condition Comment | The asset was observed to be in good condition.
429 | 127 | Sewage Lift Pump No.2 | Condition Comment | The asset was observed to be in good condition.
433 | 128 | Sewage Lift Pump No.3 | Condition Comment | The asset was observed to be in good condition.
437 | 129 | Hand Stop Gate No.1 | Condition Comment | The asset was observed to be in fair condition. Deterioration was observed.
441 | 130 | Wet Well Concrete Structure | Condition Comment | The asset was observed to be in good condition. Concrete was found to be hard/strong based on hammer striking and schmidt hammer test. concrete cover at 51mm based on cover meter test was observed.
445 | 131 | Wet Well Aluminum Ladder | Condition Comment | The asset was observed to be in fair condition. Buildup of calcium and minor pitting was observed.
449 | 132 | Wet Well Aluminum Ladder | Condition Comment | The asset was observed to be in fair condition. Buildup of calcium and minor pitting was observed.
453 | 133 | Wet Well Aluminum Ladder | Condition Comment | The asset was observed to be in poor condition. Buildup of calcium and minor pitting
455 | 133 | Wet Well Aluminum Ladder | H&S Concern Comment | Buildup of calcium and minor pitting
457 | 134 | Wetwell 2 Low Level Float | Condition Comment | The asset was assumed to be in fair condition.
461 | 135 | Wetwell 1 Low Level Float | Condition Comment | The asset was assumed to be in fair condition.
465 | 136 | Exit Lighting (New Asset) | Condition Comment | There was no exit sign installed at the station. The station needs an exit sign according to Canadian Building Code (section 3.2.7.3) and Canadian Fire Code (section 2.7.3).
466 | 136 | Exit Lighting (New Asset) | Code Concern Comment | There was no exit sign installed at the station. the station needs an exit sign according to canadian building code (section 3.2.7.3) and canadian fire code (section 2.7.3).
469 | 137 | Inlet Chamber 1 | Condition Comment | The asset was assumed to be in fair condition.
473 | 138 | Valve Chamber | Condition Comment | The asset was assumed to be in fair condition.
477 | 139 | Inlet Chamber 2 | Condition Comment | The asset was assumed to be in fair condition.
481 | 140 | Process Electrical | Condition Comment | The asset was assumed to be in fair condition.
485 | 141 | Pump 2 Piping | Condition Comment | The asset was assumed to be in fair condition.
489 | 142 | Pump 3 Piping | Condition Comment | The asset was assumed to be in fair condition.
493 | 143 | Discharge Header | Condition Comment | The asset was assumed to be in fair condition.
497 | 144 | Drain Piping | Condition Comment | The asset was assumed to be in fair condition.
501 | 145 | Process Instrumentation & Control | Condition Comment | The asset was assumed to be in fair condition.
505 | 146 | Building Electrical | Condition Comment | The asset was assumed to be in fair condition.
509 | 147 | Building Mechanical | Condition Comment | The asset was assumed to be in fair condition.

## replacement
| 0 | 1 | 2 | 3 | 4
0 | ParentID | AssetName | WorkYear | Recurring | WorkFrequency
1 | 1 | Rockcliffe WWPS | 2026 | True | 20
2 | 2 | Site Civil | 2026 | True | 20
3 | 3 | Sewage Lift Pump No.1 | 2039 | True | 30
4 | 4 | MCC | 2025 | True | 25
5 | 5 | SCADA WAN Panel | 2029 | True | 15
6 | 6 | Wet Well | 2047 | True | 60
7 | 7 | Unit Heater 1 | 2037 | True | 30
8 | 8 | Interior Lighting | 2031 | True | 25
9 | 9 | Building Structural | 2047 | True | 60
10 | 10 | Building Architectural | 2026 | True | 30
11 | 11 | Emergency Backup Power | 2022 | True | 25
12 | 14 | Diesel Fuel Tank #1 For Generator | 2022 | True | 30
13 | 15 | Diesel Fuel Tank #2 For Generator | 2022 | True | 30
14 | 20 | Standby Diesel Power Generator | 2026 | True | 25
15 | 30 | Wet Well Level Transmitter #1 | 2031 | True | 15
16 | 31 | Wet Well Level Transmitter #2 | 2031 | True | 15
17 | 32 | Power Meter | 2031 | True | 25
18 | 33 | Main Breaker | 2025 | True | 25
19 | 34 | Power Factor Capacitors | 2038 | True | 25
20 | 35 | Unit Heater Starter | 2031 | True | 25
21 | 36 | Hand Stop Gate No.2 | 2028 | True | 30
22 | 37 | Hand Stop Gate No.3 | 2028 | True | 30
23 | 38 | Manual Bar Screen No.1 | 2028 | True | 30
24 | 39 | Manual Bar Screen No.2 | 2028 | True | 30
25 | 40 | Sewage Lift Pump No.1 Check Valve | 2028 | True | 30
26 | 41 | Sewage Lift Pump No.2 Check Valve | 2028 | True | 30
27 | 42 | Sewage Lift Pump No.3 Check Valve | 2028 | True | 30
28 | 43 | Sewage Lift Pump No.1 Discharge Valve | 2028 | True | 30
29 | 44 | Sewage Lift Pump No.2 Discharge Valve | 2028 | True | 30
30 | 45 | Sewage Lift Pump No.3 Discharge Valve | 2028 | True | 30
31 | 46 | Discharge Header Gate Valve | 2022 | True | 30
32 | 47 | Drain Gate Valve | 2028 | True | 30
33 | 48 | Pressure Release Valve No.1 | 2028 | True | 30
34 | 49 | Wetwell Cell Isolation Gate | 2022 | True | 30
35 | 50 | Sluice Gate No.1 | 2028 | True | 30
36 | 51 | Pump 1 Piping | 2022 | True | 30
37 | 52 | Forcemain | 2022 | True | 30
38 | 53 | SCADA PANEL | 2028 | True | 15
39 | 54 | Station Temperature Transmitter | 2029 | True | 15
40 | 55 | UPS | 2029 | True | 15
41 | 56 | Wetwell 1 High Level Float | 2031 | True | 15
42 | 57 | Wetwell 2 High Level Float | 2031 | True | 15
43 | 58 | Pump 1 VFD | 2031 | True | 25
44 | 59 | Wet well Fan Starter | 2031 | True | 25
45 | 60 | Diesel Generator Room Fan Starter | 2031 | True | 25
46 | 61 | Pump 2 VFD | 2031 | True | 25
47 | 62 | Pump 3 VFD | 2031 | True | 25
48 | 63 | Diesel Generator Control Panel | 2022 | True | 25
49 | 64 | Emergency Lighting | 2041 | True | 25
50 | 65 | Lighting Panel LPA | 2031 | True | 25
51 | 66 | Lighting Trasnformer | 2026 | True | 25
52 | 67 | Exterior Lighting | 2038 | True | 25
53 | 68 | Wet Well Lighting | 2031 | True | 25
54 | 69 | Main Transformer | 2031 | True | 25
55 | 73 | Signboards | 2026 | True | 20
56 | 75 | Station Access Road | 2026 | True | 20
57 | 76 | Sanitary Sewer | 2026 | True | 20
58 | 77 | Wet Well Aluminum Ladder | 2052 | True | 60
59 | 78 | Wet Well Aluminum Guardrail | 2052 | True | 60
60 | 79 | Wet Well Aluminum Grating | 2052 | True | 60
61 | 80 | Wet Well Access Hatch | 2052 | True | 60
62 | 81 | Wet Well Pump Hatch 1 | 2052 | True | 60
63 | 82 | Wet Well Pump Hatch 2 | 2052 | True | 60
64 | 83 | Wet Well Pump Hatch 3 | 2052 | True | 60
65 | 84 | Wet Well Pump Hatch 4 | 2052 | True | 60
66 | 85 | Wet Well Davit Base 1 | 2052 | True | 60
67 | 86 | Wet Well Davit Base 2 | 2052 | True | 60
68 | 87 | Inlet Chamber 1 Concrete Structure | 2052 | True | 60
69 | 88 | Inlet Chamber 1 Aluminum Platform | 2052 | True | 60
70 | 89 | Inlet Chamber 1 Aluminum Ladder | 2052 | True | 60
71 | 90 | Inlet Chamber 1 Manhole Frame and Cover | 2052 | True | 60
72 | 91 | Inlet Chamber 2 Concrete Structure | 2052 | True | 60
73 | 92 | Inlet Chamber 2 Aluminum Platform | 2052 | True | 60
74 | 93 | Inlet Chamber 2 Aluminum Ladder | 2052 | True | 60
75 | 94 | Inlet Chamber 2 Manhole Frame and Cover | 2052 | True | 60
76 | 95 | Generator Building Concrete Foundation | 2052 | True | 60
77 | 96 | Generator Building Concrete Floor | 2052 | True | 60
78 | 97 | Generator Building Masonry Blockwall | 2052 | True | 60
79 | 98 | Generator Building Precast Concrete Roof | 2052 | True | 60
80 | 99 | Valve Chamber Manhole Frame and Cover | 2052 | True | 60
81 | 100 | Valve Chamber Aluminum Ladder | 2052 | True | 60
82 | 101 | Valve Chamber Concrete Structure | 2052 | True | 60
83 | 102 | Generator Building Exterior Stone Veneer | 2028 | True | 30
84 | 103 | Generator Building Asphalt Shingle Roofing | 2028 | True | 30
85 | 104 | Generator Building Wood Truss Roof | 2022 | True | 30
86 | 105 | Generator Building Wall and Ceiling Paint | 2028 | True | 30
87 | 106 | Generator Building Containment Coating | 2028 | True | 30
88 | 107 | Generator Building Roof Access Hatch | 2028 | True | 30
89 | 108 | Generator Building Exterior Access Door (Double) | 2028 | True | 30
90 | 109 | Generator Building Interior Door (Single) | 2028 | True | 30
91 | 110 | Generator Building Aluminum Ladder | 2052 | True | 60
92 | 111 | Generator Exhaust | 2028 | True | 30
93 | 112 | Baseboard Heater | 2028 | True | 30
94 | 113 | Hot Water Tank | 2028 | True | 30
95 | 114 | Wet Well Fan | 2028 | True | 30
96 | 115 | Washroom Exhaust (New Asset) | 2026 | True | 30
97 | 116 | Backflow Preventer | 2022 | True | 30
98 | 117 | Fire Extinguisher | 2050 | True | 30
99 | 118 | Overflow Piping | 2022 | True | 30
100 | 119 | Asphalt Pavement | 2026 | True | 20
101 | 120 | Station Manual Perimeter Fencing Gate | 2026 | True | 20
102 | 121 | Perimeter Fencing | 2026 | True | 20
103 | 122 | Overflow Flap Gate | 2028 | True | 30
104 | 123 | Diesel Fuel System | 2022 | True | 30
105 | 124 | Generator Intake | 2022 | True | 30
106 | 125 | Control Room Exhaust Fan | 2040 | True | 30
107 | 126 | Generator Flue Exhaust | 2028 | True | 30
108 | 127 | Sewage Lift Pump No.2 | 2039 | True | 30
109 | 128 | Sewage Lift Pump No.3 | 2039 | True | 30
110 | 129 | Hand Stop Gate No.1 | 2028 | True | 30
111 | 130 | Wet Well Concrete Structure | 2052 | True | 60
112 | 131 | Wet Well Aluminum Ladder | 2052 | True | 60
113 | 132 | Wet Well Aluminum Ladder | 2052 | True | 60
114 | 133 | Wet Well Aluminum Ladder | 2052 | True | 60
115 | 134 | Wetwell 2 Low Level Float | 2031 | True | 15
116 | 135 | Wetwell 1 Low Level Float | 2031 | True | 15
117 | 136 | Exit Lighting (New Asset) | 2026 | True | 25
118 | 137 | Inlet Chamber 1 | 2052 | True | 60
119 | 138 | Valve Chamber | 2052 | True | 60
120 | 139 | Inlet Chamber 2 | 2052 | True | 60
121 | 140 | Process Electrical | 2026 | True | 25
122 | 141 | Pump 2 Piping | 2022 | True | 30
123 | 142 | Pump 3 Piping | 2022 | True | 30
124 | 143 | Discharge Header | 2022 | True | 30
125 | 144 | Drain Piping | 2022 | True | 30
126 | 145 | Process Instrumentation & Control | 2026 | True | 15
127 | 146 | Building Electrical | 2026 | True | 25
128 | 147 | Building Mechanical | 2026 | True | 30

## rehab
| 0 | 1 | 2 | 3 | 4
0 | ParentID | AssetName | RehabComment | Rehabyear | RehabUnitMaterialCost
1 | 9 | Building Structural | Cleaning | 2020 | 0
2 | 15 | Diesel Fuel Tank #2 For Generator | Install safety grate | 2021 | 1000
5 | 20 | Standby Diesel Power Generator | Touch up paint | 2021 | 200
6 | 30 | Wet Well Level Transmitter #1 | Conduct arc flash study and install arc flash label | 2020 | 0
7 | 31 | Wet Well Level Transmitter #2 | Conduct arc flash study and install arc flash label | 2020 | 0
8 | 32 | Power Meter | Conduct arc flash study and install arc flash label | 2020 | 0
9 | 33 | Main Breaker | Conduct arc flash study and install arc flash label | 2020 | 0
10 | 34 | Power Factor Capacitors | Conduct arc flash study and install arc flash label | 2020 | 0
11 | 35 | Unit Heater Starter | Conduct arc flash study and install arc flash label | 2020 | 0
12 | 36 | Hand Stop Gate No.2 | Conduct arc flash study and install arc flash label | 2020 | 0
13 | 37 | Hand Stop Gate No.3 | Conduct arc flash study and install arc flash label | 2020 | 0
14 | 87 | Inlet Chamber 1 Concrete Structure | Provision for structural repairs every 10 years. | 2030 | 0
15 | 87 | Inlet Chamber 1 Concrete Structure | Provision for structural repairs every 10 years. | 2040 | 0
16 | 91 | Inlet Chamber 2 Concrete Structure | Provision for structural repairs every 10 years. | 2030 | 0
17 | 91 | Inlet Chamber 2 Concrete Structure | Provision for structural repairs every 10 years. | 2040 | 0
18 | 95 | Generator Building Concrete Foundation | Structural repairs to address asset defects. | 2026 | 0
19 | 95 | Generator Building Concrete Foundation | Provision for structural repairs every 10 years. | 2036 | 0
20 | 96 | Generator Building Concrete Floor | Provision for structural repairs every 10 years. | 2030 | 0
21 | 96 | Generator Building Concrete Floor | Provision for structural repairs every 10 years. | 2040 | 0
22 | 97 | Generator Building Masonry Blockwall | Provision for structural repairs every 10 years. | 2030 | 0
23 | 97 | Generator Building Masonry Blockwall | Provision for structural repairs every 10 years. | 2040 | 0
24 | 98 | Generator Building Precast Concrete Roof | Provision for structural repairs every 10 years. | 2030 | 0
25 | 98 | Generator Building Precast Concrete Roof | Provision for structural repairs every 10 years. | 2040 | 0
26 | 101 | Valve Chamber Concrete Structure | Provision for structural repairs every 10 years. | 2030 | 0
27 | 101 | Valve Chamber Concrete Structure | Provision for structural repairs every 10 years. | 2040 | 0
28 | 130 | Wet Well Concrete Structure | Provision for structural repairs every 10 years. | 2030 | 0
29 | 130 | Wet Well Concrete Structure | Provision for structural repairs every 10 years. | 2040 | 0