## Sheet1
facility | CategoryCode | assetName | repCost | seqNum | assetTag | Description | Process | building | inspectorName | installYear | LocationORIGINAL | LocationTag | manufacturer | TransmitterModel | TransducerModel | TransducerSerial | InstMeva | installationDate | InstType | ServiceArea | FacilityType | LifeCycleCategory | SerialNo | Parent | RotatingItem | Status | Site | condition | COF | defect1 | defect2 | defect3 | observations | RehabRepairCost | RehabRepairYear | RehabRepairCost2 | RehabRepairYear2 | photoName | remainingESL | repProjectName | rehabProjectName | rehab2ProjectName | InspectionYear | rehabComment1 | rehabCost1 | rehabComment2 | rehabCost2 | defect1Input | defect2Input | defect3Input
NRH | HSS | Emergency Shower Station | 2500 | 5627 | 00041014 |  |  |  |  | 2011 | Vestibule | 101118 | M00074 | [6 empty] | Central | W - Storage Elevated Tank | Health and Safety |  |  |  | OPERATING | W-WW | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3128 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | PM | Elevated Tank Pressure Relief Line Pressure Reducing Valve | 3000 | 5628 | 00040932 | Diameter: 100mm, Cla-Val Model 52 |  |  |  | 2011 | Valve Room | 101111 | M00038 | [6 empty] | Central | W - Storage Elevated Tank | Process Mechanical | 442515K |  |  | OPERATING | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3601 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | BM | Gas Chlorination Room Electric Heater | 3000 | 5629 | 00041008 | Wall-mounted unit heater by Ouellet, 3.0KW/600V/3p |  |  |  | 2011 | Gas Chlorination Room | 101112 | M00111 | [6 empty] | Central | W - Storage Elevated Tank | Building Mechanical |  |  |  | OPERATING | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3759 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | SIC | Elevated Tank Inlet/Outlet Line Pressure Gauge | 700 | 5630 | 00040933 | NRETCR_TWR_PIT1 |  |  |  | 2011 | Valve Room | 101111 | M00125 | Sitrans P-300 |  |  | Pressure |  |  | Central | W - Storage Elevated Tank | Instrumentation and Control | 7MF8023-1DA14-1MJ7-Z |  |  | OPERATING | W-WW | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3219 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | SIC | PAC Control Panel Network Connection Switch | 2000 | 5631 | 00086797 | NRETCR_PCS_NAC1_X1,inside PAC Control Panel |  |  |  | 2011 | Electrical and SCADA Room | 101111 | [7 empty] | Central | W - Storage Elevated Tank |  |  |  |  | OPERATING | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3302 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | PM | Elevated Tank Outlet Line Butterfly Valve | 5000 | 5632 | 00040942 | Diameter: 450mm, Mueller Model Lineseal III |  |  |  | 2011 | Valve Room | 101111 | M00671 | [6 empty] | Central | W - Storage Elevated Tank | Process Mechanical | 1375102-5-1-MS |  |  | OPERATING | W-WW | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3558 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | PM | Elevated Tank Circulation Line Centrifugal Circulation Pump and Motor | 12000 | 5633 | 00040950 | Goulds G&L Series 22SSH4K, Imp. diameter: 8.25", 7.5HP, 575V/3/60Hz |  |  |  | 2011 | Valve Room | 101111 | M00465 | [6 empty] | Central | W - Storage Elevated Tank | Process Mechanical | 22SH4K72D0 |  |  | OPERATING | W-WW | 2 | 4 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3497 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | SIC | PAC Control Panel Router | 2000 | 5634 | 00089687 | Catalyst IR1101 Rugged Series Router, inside Network Area Panel |  |  |  | 2011 | Electrical and SCADA Room | 101114 | M01002 | [6 empty] | Central | W - Storage Elevated Tank |  |  |  |  | OPERATING | W-WW | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3303 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | BM | Vestibule Supply Fan | 6000 | 5635 | 00040987 | Cook square inline fan model SQN-B60: 1/10HP, 120V/1/60Hz, 1458rpm |  |  |  | 2011 | Vestibule | 101118 | M00327 | [6 empty] | Central | W - Storage Elevated Tank | Building Mechanical | 401SD38093-00/005201 |  |  | OPERATING | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3727 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | BM | Valve Room Electric Heater 1 | 3000 | 5636 | 00040960 | Ceiling-mounted unit heater by Ouellet, 7.5KW/600V/3p |  |  |  | 2011 | Valve Room | 101111 | M00111 | [6 empty] | Central | W - Storage Elevated Tank | Building Mechanical |  |  |  | OPERATING | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3640 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | SIC | Electrical & SCADA Room Low Temperature Switch | 700 | 5637 | 00040982 | NRETCR_BLDS_TSL3 |  |  |  | 2011 | Electrical and SCADA Room | 101114 | M00076 | [6 empty] | Central | W - Storage Elevated Tank | Instrumentation and Control |  |  |  | OPERATING | W-WW | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_1465 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | SIC | Ammonium Sulphate Room Low Temperature Switch | 700 | 5638 | 00041001 | Instrumentation,Switch,Temperature,Low, NRETCR_BLDS_TSL4 |  |  |  | 2011 | Ammonium Sulphate Room | 101113 | M00076 |  |  |  | Temperature |  |  | Central | W - Storage Elevated Tank | Instrumentation and Control | T631A1063 |  |  | OPERATING | W-WW | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3151 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | PM | Elevated Tank Inlet Line Butterfly Valve | 5000 | 5641 | 00040939 | Diameter: 450mm, Mueller Model Lineseal III |  |  |  | 2011 | Valve Room | 101111 | M00671 | [6 empty] | Central | W - Storage Elevated Tank | Process Mechanical | 1120689-25-1-MS |  |  | OPERATING | W-WW | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3520 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | HSS | Gas Chlorination Room Chlorine Gas Remote Unit | 3000 | 5642 | 00040999 | NRETCR_SCRB_GCL21 |  |  |  | 2011 | Gas Chlorination Room | 101112 | M10086 | A-ULTIMAX-PL-A-28-0-3-2-D-H-0-0-1-1-0-0 (3-WIRE) |  |  | Cl2 Gas |  |  | Central | W - Storage Elevated Tank | Health and Safety |  |  |  | OPERATING | W-WW | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3163 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | ES | Main Fused Disconnect Switch | 5000 | 5643 |  | Fused, 600V, 200A |  |  |  | 2011 |  | 101114 | [10 empty] | 85-624342 |  |  |  |  | 2 | 2 | Arc flash label to be reviewed and replaced if necessary. |  |  | The asset was observed to be in good condition. Review arc flash label and replace if necessary. Asset to be replaced in the long term. | 500 | 2023 | 0 |  | PXL_20210929_131726628 | 15 | North Richmond Hill Coons Road ET Capital Project 2 | North Richmond Hill Coons Road ET Capital Project 1 |  | 0 | Review arc flash label and replace if necessary. | 500 |  | 0 | good | Arc flash label to be reviewed and replaced if necessary.
NRH | SIC | PAC Control Panel Radio 1 | 2000 | 5644 | 00086798 | NRETCR_PCS_NAC1_RAD1, inside PAC Control Panel |  |  |  | 2011 | Electrical and SCADA Room | 101114 | [7 empty] | Central | W - Storage Elevated Tank |  |  |  |  | OPERATING | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3303 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | PM | Elevated Tank Inlet/Outlet Line Air Release Valve | 2500 | 5645 | 00040930 | Diameter: 50mm, Val-matic Model 201C |  |  |  | 2011 | Valve Room | 101111 | M00926 | [6 empty] | Central | W - Storage Elevated Tank | Process Mechanical | SERIES 100S |  |  | OPERATING | W-WW | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3609 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | PM | Elevated Tank Outlet Line Butterfly Valve | 5000 | 5646 | 00040945 | Diameter: 450mm, Mueller Model Lineseal III |  |  |  | 2011 | Valve Room | 101111 | M00671 | [6 empty] | Central | W - Storage Elevated Tank | Process Mechanical |  |  |  | OPERATING | W-WW | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3569 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | SIC | Outlet Total Chlorine Analyzer | 28000 | 5647 | 00040957 | NRETCR_TWR_AIT2 |  |  |  | 2011 | Valve Room | 101111 | M00482 | CL-17 |  |  | Chlorine |  |  | Central | W - Storage Elevated Tank | Instrumentation and Control | 1.012003774E+011 |  |  | OPERATING | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3201 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | BM | Electrical & SCADA Room Exhaust Fan | 6000 | 5648 | 00040985 | Cook square inline fan model SQN-B60: 1/10HP, 120V/1/60Hz, 1787rpm |  |  |  | 2011 | Electrical and SCADA Room | 101114 | M00327 | [6 empty] | Central | W - Storage Elevated Tank | Building Mechanical | 401SD38093-00/001801 |  |  | OPERATING | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3314 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | BM | Vestibule Electric Heater | 3000 | 5649 | 00041013 | Wall-mounted unit heater by Ouellet, 3.0KW/600V/3p |  |  |  | 2011 | Vestibule | 101118 | M00111 | [6 empty] | Central | W - Storage Elevated Tank | Architectural |  |  |  | OPERATING | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3721 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | ES | Power Meter | 6000 | 5650 | [5 empty] | 2011 |  | 101117 | [15 empty] | 4 | 3 | The hydro meter enclosure was observed to be severely damaged to the point that one of the doors was out of hinge. | Arc flash label for the enclosure is outdated and severely damaged was observed. |  | The asset was observed to be in poor condition. Install arc flash label for the enclosure and replace the power meter enclosure. | 3000 | 2023 | 0 |  | PXL_20210929_130237499 | 15 | North Richmond Hill Coons Road ET Capital Project 2 | North Richmond Hill Coons Road ET Capital Project 1 |  | 0 | Install arc flash label for the enclosure | 500 |  | 0 | Poor | The hydro meter enclosure was observed to be severely damaged to the point that one of the doors is out of hinge. | Arc flash label for the enclosure is outdated and severely damaged.
NRH | SIC | Elevated Tank Level Transmitter and Gauge | 4500 | 5652 | 00040943 | NRETCR_TWR_LIT1 |  |  |  | 2011 | Valve Room | 101111 | M00125 | Sitrans P-300 |  |  | Level |  |  | Central | W - Storage Elevated Tank | Instrumentation and Control | 7MF8023-1DA14-1MJ7-Z |  |  | OPERATING | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3271 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | SIC | Gas Chlorination Room Low Temperature Switch | 700 | 5653 | 00041007 | NRETCR_BLDS_TSL2 |  |  |  | 2011 | Gas Chlorination Room | 101112 | M00076 |  |  |  | Temperature |  |  | Central | W - Storage Elevated Tank | Instrumentation and Control | T631A 1063 |  |  | OPERATING | W-WW | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3151 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | PM | Elevated Tank Outlet Line Check Valve | 7500 | 5654 | 00040941 | Diameter: 450mm, Val-matic Swing-Flex Model No. 518A |  |  |  | 2011 | Valve Room | 101111 | M00926 | [6 empty] | Central | W - Storage Elevated Tank | Process Mechanical | MODEL 518A |  |  | OPERATING | W-WW | 2 | 3 | Very minor corrosion was observed. |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3548 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | minor corrosion
NRH | PM | Elevated Tank Drain Line Gate Valve | 3000 | 5655 | 00040947 | Diameter: 200mm, Mueller Model |  |  |  | 2011 | Valve Room | 101111 | M00671 | [6 empty] | Central | W - Storage Elevated Tank | Process Mechanical | FIG 2360 |  |  | OPERATING | W-WW | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3584 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | BM | Vestibule Exhaust Fan | 6000 | 5656 | 00040988 | Cook square inline fan model SQN-B60: 1/10HP, 120V/1/60Hz, 1615rpm |  |  |  | 2011 | Vestibule | 101118 | M00327 | [6 empty] | Central | W - Storage Elevated Tank | Building Mechanical | 401SD38093-00/002901 |  |  | OPERATING | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3729 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | ES | Indoor Lighting | 42000 | 5657 |  | Summary: 12 small wall-mounted lights, 11 remote head, 3 exit, 19 linear lights |  |  |  | 2011 |  | 101119 | [10 empty] | 85-624342 |  |  |  |  | 2 | 2 |  |  |  | The asset was observed to be in good condition. Non-LED fixtures to be replaced with LED fixture in the next capital upgrade. Asset to be replaced in the long term. | 10000 | 2023 | 0 |  | PXL_20210929_132550293 | 15 | North Richmond Hill Coons Road ET Capital Project 2 | North Richmond Hill Coons Road ET Capital Project 1 |  | 0 | Non-LED fixtures to be replaced with LED fixture in the next capital upgrade. | 20000 |  | 0 | good
NRH | ES | Emergency Gas Scrubber System Panel | 12000 | 5658 | [5 empty] | 2011 |  | 101115 | [10 empty] | 85-624342 |  |  |  |  | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | PXL_20210929_130707737 | 15 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | SIC | PAC Control Panel | 75000 | 5659 | 00040971 | NRETCR_PCS_CP1 |  |  |  | 2011 | Electrical and SCADA Room | 101114 | [7 empty] | Central | W - Storage Elevated Tank | SCADA |  |  |  | OPERATING | W-WW | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3303 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | PM | Elevated Tank Inlet/Outlet Line Butterfly Valve | 3500 | 5660 | 00040935 | Diameter: 300mm, Mueller Model FL, electric actuator by Rotork |  |  |  | 2011 | Valve Room | 101111 | M00114 | [6 empty] | Central | W - Storage Elevated Tank | Process Mechanical | 1375738-1-1 MS |  |  | OPERATING | W-WW | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3597 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | PM | Elevated Tank Inlet/Outlet Line Butterfly Valve Electric Actuator | 5000 | 5661 | 00040936 | Rotork electric actuator, 30-120rpm, 0.45V motor rating, 575-3-60 motor supply |  |  |  | 2011 | Valve Room | 101111 | M00120 | [6 empty] | Central | W - Storage Elevated Tank | Process Mechanical | D144230101 |  |  | OPERATING | W-WW | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3597 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | PM | Elevated Tank Drain Line Reduced Pressure Principle Backflow Preventer | 3500 | 5662 | 00040955 | Diameter: 63mm, Watts Model 909 |  |  |  | 2011 | Valve Room | 101111 | M00145 | [6 empty] | Central | W - Storage Elevated Tank | Process Mechanical | 125711 |  |  | OPERATING | W-WW | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3508 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | BM | Valve Room Electric Heater 2 | 3000 | 5663 | 00040961 | Ceiling-mounted unit heater by Ouellet, 7.5KW/600V/3p |  |  |  | 2011 | Valve Room | 101111 | M00111 | [6 empty] | Central | W - Storage Elevated Tank | Building Mechanical |  |  |  | OPERATING | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3639 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | SIC | Atrium Ammonia Gas Monitor | 3000 | 5664 | 00040994 | Instrumentation, Gas Detectors, Chlorine, NRETCR_CL2D_GCL22 |  |  |  | 2011 | Gas Chlorination Room | 101113 | M10086 | A-ULTIMAX-PL-A-28-0-3-2-D-H-0-0-1-1-0-0 (3-WIRE) |  |  | Cl2 Gas |  |  | Central | W - Storage Elevated Tank | Health and Safety | A11-3642386-10-001 |  |  | OPERATING | W-WW | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3179 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | SIC | Elevated Tank Inlet/Outlet Line Flowmeter Transmitter | 4500 | 5665 | 00040937 | NRETCR_TWR_FIT1 |  |  |  | 2011 | Valve Room | 101111 | M00125 | MAG6000 |  |  | Flow |  |  | Central | W - Storage Elevated Tank | Process Mechanical | 092502H500 |  |  | OPERATING | W-WW | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3202 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | SIC | Tank Inlet Line Flow Sensor | 700 | 5666 | 00086800 | NRETCR_TWR_FIT1 |  |  |  | 2011 | Valve Room | 101111 | [7 empty] | Central | W - Storage Elevated Tank |  |  |  |  | OPERATING | W-WW | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3220 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | SIC | PAC Control Panel UPS | 3500 | 5667 | 00086795 | inside PAC Control Panel |  |  |  | 2011 | Electrical and SCADA Room | 101114 | [7 empty] | Central | W - Storage Elevated Tank |  |  |  |  | OPERATING | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3304 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | BM | Valve Room Exhaust Fan | 6000 | 5668 | 00040986 | Cook square inline fan model SQN-B80: 1/3HP, 120V/1/60Hz, 2262rpm |  |  |  | 2011 | Valve Room | 101111 | M00327 | [6 empty] | Central | W - Storage Elevated Tank | Building Mechanical | 401SD38093-00/000701 |  |  | OPERATING | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3316 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | PM | Elevated Tank Circulation Line Gate Valve 3 | 2000 | 5669 | 00040954 | Diameter: 75mm, Mueller Model |  |  |  | 2011 | Valve Room | 101111 | M00671 | [6 empty] | Central | W - Storage Elevated Tank | Process Mechanical | FIG 2360 |  |  | OPERATING | W-WW | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3516 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | BM | Ammonium Sulphate Room Exhaust Fan | 6000 | 5670 | 00040989 | Cook square inline fan model SQN-B60: 1/10HP, 120V/1/60Hz, 1615rpm |  |  |  | 2011 | Ammonium Sulphate Room | 101113 | M00327 | [6 empty] | Central | W - Storage Elevated Tank | Building Mechanical | 401SD38093-00/002902 |  |  | OPERATING | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3326 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | SIC | PAC Control Panel CPU | 2000 | 5671 | 00086794 | inside PAC Control Panel |  |  |  | 2011 | Electrical and SCADA Room | 101114 | [7 empty] | Central | W - Storage Elevated Tank |  |  |  |  | OPERATING | W-WW | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3304 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | SIC | PAC Control Panel OIT | 2000 | 5672 | 00086793 | NRETCR_PCS_OIT1 |  |  |  | 2011 | Electrical and SCADA Room | 101114 | [7 empty] | Central | W - Storage Elevated Tank |  |  |  |  | OPERATING | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3304 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | PM | Elevated Tank Inlet Line Flow Control Altitude & Check Valve | 10000 | 5673 | 00040938 | Diameter: 450mm, Cla-Val Model 631-06BCDNSYKCX |  |  |  | 2011 | Valve Room | 101111 | M00038 | [6 empty] | Central | W - Storage Elevated Tank | Process Mechanical | 20802001E |  |  | OPERATING | W-WW | 3 | 4 | Very minor corrosion was observed. |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3526 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | minor corrosion
NRH | SIC | PAC Control Panel Radio 2 | 2000 | 5674 | 00086799 | NRETCR_PCS_NAC1_RAD2, inside PAC Control Panel |  |  |  | 2011 | Electrical and SCADA Room | 101114 | [7 empty] | Central | W - Storage Elevated Tank |  |  |  |  | OPERATING | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3303 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | BM | Vestibule Tankless Water Heater | 1000 | 5675 | 00041019 | Eemax model SP3012: 3KW, 120VAC |  |  |  | 2011 | Vestibule | 101118 | M01078 | [6 empty] | Central | W - Storage Elevated Tank | Building Mechanical | 1001048 |  |  | OPERATING | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3732 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | PM | Elevated Tank Circulation Line Gate Valve 1 | 2000 | 5676 | 00040948 | Diameter: 100mm, Mueller Model |  |  |  | 2011 | Valve Room | 101111 | M00671 | [6 empty] | Central | W - Storage Elevated Tank | Process Mechanical | FIG 2360 |  |  | OPERATING | W-WW | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3555 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | PM | Elevated Tank Pressure Relief Line Gate Valve | 2000 | 5677 | 00040931 | Diameter: 100mm, Mueller Model |  |  |  | 2011 | Valve Room | 101111 | M00671 | [6 empty] | Central | W - Storage Elevated Tank | Process Mechanical | FIG. 2360 |  |  | OPERATING | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3602 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | SIC | Valve Room Lower Temperature Switch | 700 | 5678 | 00040962 | NRETCR_BLDS_TSL1 |  |  |  | 2011 | Valve Room | 101111 | M00076 |  |  |  | Temperature |  |  | Central | W - Storage Elevated Tank | Instrumentation and Control | T631A 1063 |  |  | OPERATING | W-WW | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3185 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | SIC | Eyewash Station & Emergency Shower Flow Sensor | 700 | 5679 | 00041015 | NRETCR_HS_EYEW1_FSH1 |  |  |  | 2011 | Vestibule | 101118 | [7 empty] | Central | W - Storage Elevated Tank | Instrumentation and Control |  |  |  | OPERATING | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3130 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | PM | Elevated Tank Potable Cold Water Line Double Check Valve Backflow Preventer | 2000 | 5681 | 00047862 | Diameter: 38mm backflow preventer, Watts Model 007QTS |  |  |  | 2011 | Valve Room | 101111 | M00145 | [6 empty] | Central | W - Storage Elevated Tank | Process Mechanical | 107514 |  |  | OPERATING | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3476 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | BM | Valve Room Tankless Water Heater | 4000 | 5682 | 00040963 | Eemax model EX240T2T EE: 24KW, 120/208 |  |  |  | 2011 | Valve Room | 101118 | M01078 | [6 empty] | Central | W - Storage Elevated Tank | Building Mechanical | 995248 |  |  | OPERATING | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3480 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | PM | Elevated Tank Circulation Line Gate Valve 2 | 2000 | 5683 | 00040953 | Diameter: 75mm, Mueller Model |  |  |  | 2011 | Valve Room | 101111 | M00671 | [6 empty] | Central | W - Storage Elevated Tank | Process Mechanical | FIG 2360 |  |  | OPERATING | W-WW | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3503 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | PM | Elevated Tank Potable Cold Water Line Reduced Pressure Principle Backflow Prevente | 2000 | 5684 | 00047861 | Diameter: 50mm, Watts Model 909-S |  |  |  | 2011 | Valve Room | 101111 | M00145 | [6 empty] | Central | W - Storage Elevated Tank | Process Mechanical | 459528 |  |  | OPERATING | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3478 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | BM | Ammonium Sulphate Room Electric Heater | 3000 | 5685 | 00041003 | Wall-mounted unit heater by Ouellet, 3.0KW/600V/3p |  |  |  | 2011 | Ammonium Sulphate Room | 101113 | M00111 | [6 empty] | Central | W - Storage Elevated Tank | Building Mechanical |  |  |  | OPERATING | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3786 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | PM | Elevated Tank Circulation Line Check Valve | 3000 | 5686 | 00040952 | Diameter: 75mm, Val-matic Swing-Flex Model No. 503A |  |  |  | 2011 | Valve Room | 101111 | M00926 | [6 empty] | Central | W - Storage Elevated Tank | Process Mechanical | 503A |  |  | OPERATING | W-WW | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3499 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | BM | Electrical & SCADA Room Electric Heater | 3000 | 5687 | 00040983 | Wall-mounted unit heater by Ouellet, 5KW/600V/3p |  |  |  | 2011 | Electrical and SCADA Room | 101114 | M00111 | [6 empty] | Central | W - Storage Elevated Tank | Building Mechanical |  |  |  | OPERATING | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3456 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | SIC | Gas Chlorination Room Sump Level Switch | 1500 | 5688 | 00086808 | NRETCR_BLDS_SU1_LSHH1 |  |  |  | 2011 | Gas Chlorination Room | 101112 | [7 empty] | Central | W - Storage Elevated Tank |  |  |  |  | OPERATING | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3779 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | ES | Circulating Pump Starter | 5000 | 5689 | [5 empty] | 2011 |  | 101111 | [15 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | PXL_20210929_132252439 | 15 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | PM | Backflow Preventer | 1200 | 5690 | 00087414 | Diameter: 13 mm, Watts Model 007QT |  |  |  | 2011 | Ammonium Sulphate Room | 101118 | [7 empty] | Central | W - Storage Elevated Tank |  |  |  |  | OPERATING | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3760 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | SIC | Inlet Total Chlorine Analyzer | 28000 | 5691 | 00040956 | Instrumentation,Analysers,Chlorine,Total Chlorine,CL17, NRETCR_TWR_AIT1 |  |  |  | 2011 | Valve Room | 101111 | M00482 | CL-17 |  |  | Chlorine |  |  | Central | W - Storage Elevated Tank | Instrumentation and Control | 1.0120037737E+012 |  |  | OPERATING | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3204 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | ES | Outdoor Lighting | 12000 | 5692 |  | 2 flood light, 2 pole lights |  |  |  | 2011 |  | 101117 | [10 empty] | 85-624342 |  |  |  |  | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | PXL_20210929_130211337 | 15 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | ES | Water Heater Fused Disconnect Switch | 4000 | 5693 |  | 600V, 100A |  |  |  | 2010 |  | 101114 | [15 empty] | 2 | 2 | The arc flash label was missing. |  |  | The asset was observed to be in good condition. Install arc flash label. Asset to be replaced in the long term. | 500 | 2023 | 0 |  | PXL_20210929_132246213 | 14 | North Richmond Hill Coons Road ET Capital Project 2 | North Richmond Hill Coons Road ET Capital Project 1 |  | 0 | Install arc flash label. | 500 | 2 | 0 | good | missing arc flash label
NRH | BM | Chlorine Scrubber Blower | 20000 | 5694 | 00040990 | FRP Radial Fume Exhauster |  |  |  | 2011 | Gas Chlorination Room | 101115 | M00742 | [6 empty] | Central | W - Storage Elevated Tank | Building Mechanical | F10-1920 |  |  | OPERATING | W-WW | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3690 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | SIC | Tank Inlet Line Attitude Valve Controller and Transmitter | 15000 | 5695 | 00045455 | NRETCR_TWR_LCV1_POS1 |  |  |  | 2011 | Valve Room | 101111 | [13 empty] | OPERATING | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3252 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | BM | Floor Drain | 30000 | 5698 |  | floor drain within the facility |  |  |  | 2011 |  | 101111 | [15 empty] | 3 | 2 | Floor water condensation near sampling drain was observed. |  |  | The asset was observed to be in fair condition. Repair the funnel drain. Asset to be replaced in the long term. | 500 | 2021 | 0 |  | IMG_3207 | 20 | North Richmond Hill Coons Road ET Capital Project 2 | North Richmond Hill Coons Road ET Capital Project 1 |  | 0 |  | 0 |  | 0 | Floor water condensation near sampling drain.
NRH | HSS | Ammonia Gas Detector Remote Unit | 3000 | 5699 |  | Not in service. |  |  |  | 2011 |  | 101113 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3140 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | HSS | Ammonium Sulphate Room Smoke Detector | 800 | 5700 | [5 empty] | 2011 |  | 101119 | [15 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3145 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | HSS | Gas Chlorination Room Smoke Detector | 800 | 5701 | [5 empty] | 2011 |  | 101112 | [15 empty] | 2 | 3 | The smoke detector was covered. |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3154 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | The smoke detector was covered.
NRH | SIC | Facility Security System Panel | 42000 | 5702 |  | Manufacturer: Bosch |  |  |  | 2011 |  | 101119 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3169 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | SIC | Facility Security System Touchpad | 2500 | 5703 |  | Manufacturer: Bosch |  |  |  | 2011 |  | 101119 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3171 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | HSS | Gas Chlorination Room Chlorine Gas Detector | 3000 | 5704 | 00040994 |  |  |  |  | 2011 |  | 101112 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3181 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | HSS | Valve Room Smoke Detector | 800 | 5706 | [5 empty] | 2011 |  | 101111 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3210 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | HSS | Ammonia Gas Detector | 3000 | 5707 | 00040995 |  |  |  |  | 2011 |  | 101118 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3179 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | HSS | Fire Extinguishers | 500 | 5708 |  | Total of 3. |  |  |  | 2011 |  | 101119 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3187 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | SC | Elevated Tank Steel Tank | 2500000 | 5860 | [5 empty] | 2011 |  | 101119 | [15 empty] | 2 | 5 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_9027 | 50 |  |  |  | 0 |  | 0 |  | 0 | Good
NRH | SCS | Elevated Tank Exterior Coating | 1140000 | 5857 | [5 empty] | 2011 |  | 101119 | [15 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Replace the exterior coating at the end of the service life. |  |  | 0 |  | IMG_9027 | 15 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | SC | Elevated Tank Concrete Pedestal | 1100000 | 5856 | [5 empty] | 2011 |  | 101119 | [15 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 50000 | 2031 | 0 |  | IMG_9028 | 50 |  | North Richmond Hill Coons Road ET Capital Project 2 |  | 0 |  | 0 |  | 0 | Good
NRH | SCS | Elevated Tank Interior Coating | 660000 | 5858 | [5 empty] | 2011 |  | 101119 | [15 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Replace the interior coating at the end of the service life. | 0 |  | 0 |  |  | 15 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | SC | Elevated Tank Concrete Foundation | 600000 | 5855 | [5 empty] | 2011 |  | 101119 | [15 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 50000 | 2031 | 0 |  |  | 50 |  | North Richmond Hill Coons Road ET Capital Project 2 |  | 0 |  | 0 |  | 0 | Good
NRH | SC | Valve Room Composite Roof Slab | 80000 | 5862 | [5 empty] | 2011 |  | 101111 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_9046 | 50 |  |  |  | 0 |  | 0 |  | 0 | Good
NRH | SC | Valve Room Concrete Floor Slab | 72000 | 5861 | [5 empty] | 2011 |  | 101111 | [15 empty] | 2 | 3 | Minor hairline cracking was noted. |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 7200 | 2031 | 0 |  | IMG_9047 | 50 |  | North Richmond Hill Coons Road ET Capital Project 2 |  | 0 |  | 0 |  | 0 | Good | Minor hairline cracking noted
NRH | SC | Valve Room Masonry Block Wall | 50000 | 5863 | [5 empty] | 2011 |  | 101111 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 5000 | 2031 | 0 |  | IMG_9048 | 50 |  | North Richmond Hill Coons Road ET Capital Project 2 |  | 0 |  | 0 |  | 0 | Good
NRH | SC | Elevated Tank Platform | 50000 | 5881 | [5 empty] | 2011 |  | 101119 | [15 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_9095 | 50 |  |  |  | 0 |  | 0 |  | 0 | Good
NRH | SC | Elevated Tank Guardrail | 40000 | 5859 | [5 empty] | 2011 |  | 101119 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_9111 | 50 |  |  |  | 0 |  | 0 |  | 0 | Good
NRH | SC | Ammonium Sulphate Room Masonry Blockwall Ammonium Sulphate Room Masonry Block Wall | 30000 | 5843 | [5 empty] | 2011 |  | 101113 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 0 | 2031 | 0 |  | IMG_9039 | 50 |  | North Richmond Hill Coons Road ET Capital Project 2 |  | 0 |  | 0 |  | 0 | Good
NRH | SC | Elevated Tank Ladder (Base to Platform) | 30000 | 5870 |  | Ground to platform |  |  |  | 2011 |  | 101119 | [15 empty] | 2 | 4 | The fail arrest system was not compliant to current CSA standard. |  |  | The asset was observed to be in good condition. The fail arrest system was not compliant to current CSA standard. Replace the fail arrest system immediately. Asset to be replaced at the end of remaining service life. | 5000 | 2021 | 0 |  | IMG_9068 | 50 |  | North Richmond Hill Coons Road ET Capital Project 1 |  | 0 |  | 0 |  | 0 | Good
NRH | SC | Ammonium Sulphate Room Composite Roof Slab | 25000 | 5842 | [5 empty] | 2011 |  | 101113 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_9040 | 50 |  |  |  | 0 |  | 0 |  | 0 | Good
NRH | SC | Atrium Concrete Floor Slab Floor Slab | 25000 | 5844 | [5 empty] | 2011 |  | 101115 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 2500 | 2031 | 0 |  | IMG_9044 | 50 |  | North Richmond Hill Coons Road ET Capital Project 2 |  | 0 |  | 0 |  | 0 | Good
NRH | SC | Atrium Masonry Block Wall | 25000 | 5845 | [5 empty] | 2011 |  | 101115 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 2500 | 2031 | 0 |  | IMG_9044 | 50 |  | North Richmond Hill Coons Road ET Capital Project 2 |  | 0 |  | 0 |  | 0 | Good
NRH | SC | Electrical and SCADA Room Composite Roof Slab | 23000 | 5852 | [5 empty] | 2011 |  | 101114 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_9051 | 50 |  |  |  | 0 |  | 0 |  | 0 | Good
NRH | SC | Electrical and SCADA Room Masonry Blockwall | 23000 | 5853 | [5 empty] | 2011 |  | 101114 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 2300 | 2031 | 0 |  | IMG_9053 | 50 |  | North Richmond Hill Coons Road ET Capital Project 2 |  | 0 |  | 0 |  | 0 | Good
NRH | SC | Electrical and SCADA Room Concrete Floor Slab | 21000 | 5851 | [5 empty] | 2011 |  | 101114 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 2100 | 2031 | 0 |  | IMG_9050 | 50 |  | North Richmond Hill Coons Road ET Capital Project 2 |  | 0 |  | 0 |  | 0 | Good
NRH | SC | Ammonium Sulphate Room Concrete Floor Slab | 20000 | 5841 | [5 empty] | 2011 |  | 101113 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 2000 | 2031 | 0 |  | IMG_9038 | 50 |  | North Richmond Hill Coons Road ET Capital Project 2 |  | 0 |  | 0 |  | 0 | Good
NRH | SC | Gas Chlorination Masonry Blockwall | 15000 | 5850 | [5 empty] | 2011 |  | 101112 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 1500 | 2031 | 0 |  | IMG_9041 | 50 |  | North Richmond Hill Coons Road ET Capital Project 2 |  | 0 |  | 0 |  | 0 | Good
NRH | SC | Vestibule Masonry Blockwall | 15000 | 5866 | [5 empty] | 2011 |  | 101118 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 1500 | 2031 | 0 |  | IMG_9034 | 50 |  | North Richmond Hill Coons Road ET Capital Project 2 |  | 0 |  | 0 |  | 0 | Good
NRH | SC | Atrium Aluminum Staircase | 15000 | 5882 | [5 empty] | 2011 |  | 101115 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_9045 | 50 |  |  |  | 0 |  | 0 |  | 0 | Good
NRH | SC | Elevated Tank Ladder (Platform to Roof) | 10000 | 5871 |  | Platform to tank exterior |  |  |  | 2011 |  | 101119 | [15 empty] | 2 | 4 | The fail arrest system was not compliant to current CSA standard. |  |  | The asset was observed to be in good condition. The fail arrest system was not compliant to current CSA standard. Replace the fail arrest system immediately. Asset to be replaced at the end of remaining service life. | 5000 | 2021 | 0 |  | IMG_9130 | 50 |  | North Richmond Hill Coons Road ET Capital Project 1 |  | 0 |  | 0 |  | 0 | Good
NRH | SC | Elevated Tank Interior Ladder (Roof to Tank) | 10000 | 5974 | [5 empty] | 2011 |  | 101119 | [15 empty] | 2 | 4 | The fail arrest system was not compliant to current CSA standard. |  |  | The asset was observed to be in good condition. The fail arrest system was not compliant to current CSA standard. Replace the fail arrest system immediately. Asset to be replaced at the end of remaining service life. | 5000 | 2021 | 0 |  |  | 50 |  | North Richmond Hill Coons Road ET Capital Project 1 |  | 0 |  | 0 |  | 0
NRH | SC | Atrium Aluminum Guardrail | 8000 | 5847 | [5 empty] | 2011 |  | 101115 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_9045 | 50 |  |  |  | 0 |  | 0 |  | 0 | Good
NRH | SC | Vestibule Composite Roof Slab | 8000 | 5865 | [5 empty] | 2011 |  | 101118 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_9034 | 50 |  |  |  | 0 |  | 0 |  | 0 | Good
NRH | SC | Gas Chlorination Concrete Roof Slab | 7000 | 5849 | [5 empty] | 2011 |  | 101112 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 1000 | 2031 | 0 |  | IMG_9042 | 50 |  | North Richmond Hill Coons Road ET Capital Project 2 |  | 0 |  | 0 |  | 0 | Good
NRH | SC | Vestibule Concrete Floor Slab | 7000 | 5864 | [5 empty] | 2011 |  | 101118 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 1000 | 2031 | 0 |  | IMG_9036 | 50 |  | North Richmond Hill Coons Road ET Capital Project 2 |  | 0 |  | 0 |  | 0 | Good
NRH | SC | Gas Chlorination Room Concrete Floor Slab | 6000 | 5846 | [5 empty] | 2011 |  | 101112 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Provision for structural repairs every 10 years. Asset to be replaced at the end of remaining service life. | 1000 | 2031 | 0 |  | IMG_9041 | 50 |  | North Richmond Hill Coons Road ET Capital Project 2 |  | 0 |  | 0 |  | 0 | Good
NRH | SC | Elevated Tank Roof Hatch 1 | 5000 | 5873 | [5 empty] | 2011 |  | 101119 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_9129 | 50 |  |  |  | 0 |  | 0 |  | 0 | Good
NRH | HSS | Elevated Tank Davit Arm Base | 5000 | 5876 | [5 empty] | 2011 |  | 101119 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_9131 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | SC | Elevated Tank Roof Hatch 2 | 5000 | 5874 | [5 empty] | 2011 |  | 101119 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_9127 | 50 |  |  |  | 0 |  | 0 |  | 0 | Good
NRH | SW | Dechlorination Chamber Access Ladder | 2000 | 5878 | [5 empty] | 2011 |  | 101117 | [15 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. | 0 |  | 0 |  | IMG_9091 | 22 |  |  |  | 0 |  | 0 |  | 0 | Good
NRH | SW | Dechlorination Chamber Concrete Structure | 10000 | 5879 | [5 empty] | 2011 |  | 101117 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. | 0 |  | 0 |  | IMG_9091 | 50 |  |  |  | 0 |  | 0 |  | 0 | Good
NRH | SW | Dechlorination Chamber Manhole Frame and Cover | 3000 | 5880 | [5 empty] | 2011 |  | 101117 | [15 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. | 0 |  | 0 |  | IMG_9090 | 50 |  |  |  | 0 |  | 0 |  | 0 | Good
NRH | SC | Elevated Tank Roof Hatch/Vent | 5000 | 5875 | [5 empty] | 2011 |  | 101119 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_9128 | 50 |  |  |  | 0 |  | 0 |  | 0 | Good
NRH | SC | Elevated Tank Tank Hatch | 5000 | 5877 | [5 empty] | 2011 |  | 101119 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_9099 | 50 |  |  |  | 0 |  | 0 |  | 0 | Good
NRH | AC | Ammonium Sulphate Room Access Door (Single) | 3500 | 5883 | [5 empty] | 2011 |  | 101113 | [15 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_9037 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | AC | Ammonium Sulphate Room Protective Floor Coating | 12000 | 5884 | [5 empty] | 2011 |  | 101113 | [15 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_9039 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | AC | Ammonium Sulphate Room Wall Paint | 2500 | 5885 | [5 empty] | 2011 |  | 101113 | [15 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_9039 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | AC | Ammonium Sulphate Room Interior Window | 3000 | 5886 | [5 empty] | 2011 |  | 101113 | [15 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_9039 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | AC | Vestibule Access Door (Single) | 3500 | 5887 | [5 empty] | 2011 |  | 101118 | [15 empty] | 3 | 1 | Corrosion on hardware was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_9031 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | corrosion on hardware
NRH | AC | Vestibule Protective Floor Coating | 5000 | 5888 | [5 empty] | 2011 |  | 101118 | [15 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_9035 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | AC | Vestibule Wall Paint | 1500 | 5889 | [5 empty] | 2011 |  | 101118 | [15 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_9035 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | AC | Gas Chlorination Room Access Door (Single) | 3500 | 5890 | [5 empty] | 2011 |  | 101112 | [15 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_9034 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | AC | Gas Chlorination Room Interior Window | 6000 | 5891 | [5 empty] | 2011 |  | 101112 | [15 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_9034 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | AC | Gas Chlorination Room Protective Floor Coating | 5000 | 5892 | [5 empty] | 2011 |  | 101112 | [15 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_9041 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | AC | Gas Chlorination Room Wall Paint | 1500 | 5893 | [5 empty] | 2011 |  | 101112 | [15 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_9041 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | AC | Atrium Protective Floor Coating | 15000 | 5894 | [5 empty] | 2011 |  | 101115 | [15 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_9045 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | AC | Atrium Wall Paint | 2500 | 5895 | [5 empty] | 2011 |  | 101115 | [15 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_9045 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | AC | Atrium Access Door (Double) | 5500 | 5896 | [5 empty] | 2011 |  | 101115 | [15 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_9043 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | AC | Valve Room Access Door (Double) | 5500 | 5897 | [5 empty] | 2011 |  | 101111 | [15 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_9045 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | AC | Valve Room Protective Floor Coating | 45000 | 5898 | [5 empty] | 2011 |  | 101111 | [15 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_9046 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | AC | Valve Room Wall Paint | 5000 | 5899 | [5 empty] | 2011 |  | 101111 | [15 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_9046 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | AC | Electrical and SCADA Room Access Door (Single) | 3500 | 5900 | [5 empty] | 2011 |  | 101114 | [15 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_9054 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | AC | Electrical and SCADA Room Wall Paint | 2500 | 5901 | [5 empty] | 2011 |  | 101114 | [15 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_9050 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | AC | Electrical and SCADA Room Protective Floor Coating | 13000 | 5902 | [5 empty] | 2011 |  | 101114 | [15 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_9050 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | SC | Ammonium Sulphate Room FRP Grating | 5000 | 5904 | [5 empty] | 2011 |  | 101113 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_9038 | 50 |  |  |  | 0 |  | 0 |  | 0 | Good
NRH | SC | Elevated Tank Ladder (Platform to U/S Tank) | 3000 | 5872 |  | Platform to u/s tank |  |  |  | 2011 |  | 101119 | [15 empty] | 2 | 4 | The fail arrest system was not compliant to current CSA standard. |  |  | The asset was observed to be in good condition. The fail arrest system was not compliant to current CSA standard. Replace the fail arrest system immediately. Asset to be replaced at the end of remaining service life. | 2000 | 2021 | 0 |  | IMG_9099 | 50 |  | North Richmond Hill Coons Road ET Capital Project 1 |  | 0 |  | 0 |  | 0 | Good
NRH | SIC | Elevated Tank Antennas and Communication System | 100000 | 5905 |  | around 6 antenna posts including a RFS microwave antenna. |  |  |  | 2011 |  | 101119 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_9125 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | BM | Valve Room Exhaust Fan Damper and Louver | 3000 | 5906 |  | 600mm x 600mm x 100mm |  |  |  | 2011 |  | 101111 | [15 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3628 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | BM | Valve Room Air Intake Damper and Louver | 3000 | 5907 |  | 600mm x 600mm x 100mm |  |  |  | 2011 |  | 101111 | [15 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3209 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | BM | Electrical & SCADA Room Air Intake Damper and Louver | 3000 | 5908 |  | 450mm x 450mm x 100mm |  |  |  | 2011 |  | 101114 | [15 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3300 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | BM | Electrical & SCADA Room Exhaust Fan Damper and Louver | 6000 | 5909 |  | 450mm x 450mm x 100mm |  |  |  | 2011 |  | 101114 | [15 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_9053 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | BM | Gas Chlorination Room Air Intake Damper and Louver | 3000 | 5910 |  | 450mm x 450mm x 100mm |  |  |  | 2011 |  | 101112 | [15 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_9042 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | BM | Gas Chlorination Room Scrubber Damper and Louver | 3000 | 5911 |  | 450mm x 450mm x 100mm |  |  |  | 2011 |  | 101112 | [15 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_9042 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | BM | Ammonium Sulphate Room Air Intake Damper and Louver | 3000 | 5912 |  | 450mm x 450mm x 100mm |  |  |  | 2011 |  | 101113 | [15 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_9040 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | BM | Ammonium Sulphate Room Exhaust Fan Damper and Louver | 3000 | 5913 |  | 450mm x 450mm x 100mm |  |  |  | 2011 |  | 101113 | [15 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_9040 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | BM | Vestibule Room Air Intake Damper and Louver | 3000 | 5914 |  | 450mm x 450mm x 100mm |  |  |  | 2011 |  | 101118 | [15 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3123 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | BM | Upper Platform Louver | 6000 | 5916 |  | 900mm x 600mm x 150mm |  |  |  | 2011 |  | 101119 | [15 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_9106 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | BM | Gas Chlorination Room Exhaust Fan | 6000 | 5918 |  | Cook square inline fan model SQN-B60: 1/10HP, 120V/1/60Hz, 1615rpm |  |  |  | 2011 |  | 101112 | [15 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3153 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | BM | Chlorine Scrubber | 50000 | 5919 | 00040990 |  |  |  |  | 2011 |  | 101115 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3690 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | Good
NRH | BM | Sampling Sink | 1000 | 5920 | [5 empty] | 2011 |  | 101111 | [15 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3205 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | BM | Vestibule Sink | 1000 | 5921 | [5 empty] | 2011 |  | 101118 | [15 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_3125 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | HSS | Elevated Tank Anchor Point (Platform Level) | 2500 | 5922 | [5 empty] | 2011 |  | 101119 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_9100 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | HSS | Elevated Tank Davit Socket Base (Roof Level) | 4500 | 5923 | [5 empty] | 2011 |  | 101119 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_9109 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | ES | Inlet Pipe Heat Trace Panel | 10000 | 5924 | 00040958 | NRETCR_TWR_HTRC1 |  |  |  | 2011 | Elevated Tank Pedestal | 101111 | [7 empty] | Central | W - Storage Elevated Tank | Building Mechanical | 24901 |  |  | OPERATING | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | PXL_20210929_132951242 | 15 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | ES | Outlet Heat Trace Panel | 5000 | 5925 | 00040959 | NRETCR_TWR_HTRC3 |  |  |  | 2011 | Valve Room | 101111 | [7 empty] | Central | W - Storage Elevated Tank | Building Mechanical | 24901 |  |  | OPERATING | W-WW | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | PXL_20210929_132958677 | 15 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | ES | Distribution Panel DPA | 16000 | 5926 | 00040975 | 600V, 250A, 36CCT, 200kA SPD |  |  |  | 2011 | Electrical and SCADA Room | 101114 | M00044 | [6 empty] | Central | W - Storage Elevated Tank | Electrical System | 85-624342 |  |  | OPERATING | W-WW | 2 | 2 | Arc flash label to be reviewed and replaced if necessary. |  |  | The asset was observed to be in good condition. Review arc flash label and replace if necessary. Asset to be replaced in the long term. | 500 | 2023 | 0 |  | PXL_20210929_131301523 | 15 | North Richmond Hill Coons Road ET Capital Project 2 | North Richmond Hill Coons Road ET Capital Project 1 |  | 0 | Review arc flash label and replace if necessary. | 500 |  | 0 | good | arc flash label to be reviewed and replaced if necessary
NRH | ES | Lighting Panel LPA | 10000 | 5927 | 00040976 | 120/208V, 150A, 60CCT |  |  |  | 2011 | Electrical and SCADA Room | 101114 | M00044 | [6 empty] | Central | W - Storage Elevated Tank | Electrical System | 85-624342 |  |  | OPERATING | W-WW | 2 | 2 | Arc flash label to be reviewed and replaced if necessary. |  |  | The asset was observed to be in good condition. Review arc flash label and replace if necessary. Asset to be replaced in the long term. | 500 | 2023 | 0 |  | PXL_20210929_130857780 | 15 | North Richmond Hill Coons Road ET Capital Project 2 | North Richmond Hill Coons Road ET Capital Project 1 |  | 0 | Review arc flash label and replace if necessary. | 500 |  | 0 | good | arc flash label to be reviewed and replaced if necessary
NRH | ES | Transformer #1 | 9000 | 5928 | 00040978 | NRETCR_ELEC_TX1 |  |  |  | 2011 | Electrical and SCADA Room | 101114 | M00488 | [6 empty] | Central | W - Storage Elevated Tank | Siteworks | NMK045PBC |  |  | OPERATING | W-WW | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | PXL_20210929_131216304 | 15 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | ES | Transformer #2 | 11000 | 5929 | 00040979 | NRETCR_ELEC_TX2, 45kVA, 600-208V |  |  |  | 2011 | Electrical and SCADA Room | 101114 | M00488 | [6 empty] | Central | W - Storage Elevated Tank | Siteworks | NMK030PBCN |  |  | OPERATING | W-WW | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | PXL_20210929_131245455 | 15 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | ES | Fan Control Panel 2 | 5000 | 5930 | 00040985 |  |  |  |  | 2011 |  | 101113 | [15 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | PXL_20210929_131759973 | 15 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | ES | Fan Control Panel 2 | 5000 | 5931 | 00040986 |  |  |  |  | 2011 |  | 101113 | [15 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | PXL_20210929_133006471 | 15 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | ES | Fan Control Panel 3 | 5000 | 5932 | 00040987 |  |  |  |  | 2011 |  | 101112 | [15 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | PXL_20210929_133955195 | 14 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | ES | Fan Control Panel 4 | 5000 | 5933 | 00040988 |  |  |  |  | 2010 |  | 101118 | [15 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | PXL_20210929_134029516 | 14 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | ES | Fan Control Panel 5 | 5000 | 5934 | 00040989 |  |  |  |  | 2010 |  | 101112 | [15 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | PXL_20210929_134115354 | 14 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | ES | Generator Transfer Panel | 5000 | 5935 | 00086792 | with manual transfer switch, NRETCR_GEN_MTS1, 30A, 120/240V |  |  |  | 2011 | Vestibule | 101114 | [7 empty] | Central | W - Storage Elevated Tank |  |  |  |  | OPERATING | W-WW | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  | PXL_20210929_131918544 | 15 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | good
NRH | ES | Elevated Tank Lightning Protection System | 7000 | 5937 | [5 empty] | 2010 |  | 101119 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. |  |  | 0 |  | IMG_9125 | 14 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 2019 |  |  |  | 0 | good
NRH | ES | Elevated Tank Grounding | 10000 | 5938 | [5 empty] | 2011 |  | 101116 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. |  |  |  |  | IMG_9062 | 15 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  |  |  |  | good
NRH | ES | Electrical Duct System and Conduit System | 75000 | 5939 | [5 empty] | 2011 |  | 101119 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. |  |  | 0 |  | IMG_9068 | 15 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 2019 |  |  |  | 0 | good
NRH | ES | Aircraft Obstruction Lights | 2000 | 5940 |  | Two warning lights, assumed installation year: 2010 |  |  |  | 2011 |  | 101119 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. |  |  |  |  | IMG_9116 | 15 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 2019 |  |  |  |  | Good
NRH | ES | Elevated Tank Piping Heat Tracing | 30000 | 5941 | 00043008 |  |  |  |  | 2011 |  | 101119 | [10 empty] | R1-050-DP |  |  |  |  | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. |  |  |  |  | IMG_3277 | 15 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  |  |  |  | good
NRH | SW | Watermain | 85000 | 5942 |  | 450mm CCP watermain. Approx. total length 60 meters |  |  |  | 2011 |  | 101117 | [15 empty] | 2 | 5 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. | [5 empty] | 50 |  |  |  | 0 |  |  |  |  | good
NRH | SW | Valve Chamber No. 1 Concrete Structure | 65000 | 5943 | [5 empty] | 2011 |  | 101117 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. |  |  |  |  | IMG_9071 | 50 |  |  |  | 0 |  |  |  |  | good
NRH | SW | Valve Chamber No. 1 Ladder | 3000 | 5944 | [5 empty] | 2011 |  | 101117 | [15 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. |  |  |  |  | IMG_9071 | 22 |  |  |  | 0 |  |  |  |  | good
NRH | SW | Valve Chamber No. 1 Access Hatch | 5000 | 5945 | [5 empty] | 2011 |  | 101117 | [15 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. |  |  |  |  | IMG_9075 | 22 |  |  |  | 0 |  |  |  |  | good
NRH | SW | Sanitary Service | 150000 | 5946 |  | Approximate 200m 250mm PVC Sanitary pipe |  |  |  | 2011 |  | 101117 | [15 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. | [5 empty] | 50 |  |  |  | 0 |  |  |  |  | good
NRH | SW | Overflow Pipe | 280000 | 5947 |  | 450mm PCV, length: 200 meters |  |  |  | 1984 |  | 101117 | [15 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. | [5 empty] | 23 |  |  |  | 0 |  |  |  |  | good
NRH | SW | Valve Chamber No.2 Concrete Structure | 10000 | 5948 | [5 empty] | 2011 |  | 101117 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. |  |  |  |  | IMG_3106 | 50 |  |  |  | 0 |  |  |  |  | good
NRH | SW | Valve Chamber No.2 Concrete Structure | 2000 | 5949 | [5 empty] | 2011 |  | 101117 | [15 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. |  |  |  |  | IMG_9077 | 50 |  |  |  | 0 |  |  |  |  | good
NRH | SW | Valve Chamber No.2 Access Hatch | 5000 | 5950 | [5 empty] | 2011 |  | 101117 | [15 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. |  |  |  |  | IMG_3106 | 50 |  |  |  | 0 |  |  |  |  | good
NRH | SW | Concrete Pads (at entrance) | 6000 | 5952 |  | 3 in total |  |  |  | 2011 |  | 101117 | [15 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. |  |  |  |  | IMG_3115 | 50 |  |  |  | 0 |  |  |  |  | good
NRH | SW | Chainlink Fence | 23000 | 5953 |  | 1.8m hight chainlink fence around site. Approx. length 230m |  |  |  | 2011 |  | 101117 | [15 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. |  |  |  |  | IMG_3086 | 23 |  |  |  | 0 |  |  |  |  | good
NRH | SW | Asphalt Driveway | 50000 | 5954 |  | Asphalt driveway |  |  |  | 2011 |  | 101117 | [15 empty] | 3 | 2 | Minor surface cracks was observed. |  |  | The asset was observed to be in good condition. Resurface the asphalt driveway. Asset to be replaced at the end of the service life. | 20000 | 2033 | 0 |  | IMG_3097 | 23 |  | North Richmond Hill Coons Road ET Capital Project 2 |  | 0 |  |  |  | 0 | Minor surface cracks
NRH | SW | Double Lockable Swing Gate | 4000 | 5955 | 00008866 |  |  |  |  | 2011 | King City Fisher Elevated Tank | 101117 | [7 empty] | Area 1S Linear Water & Wells | W - Storage Elevated Tank | Siteworks |  |  |  |  | W-WW | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. |  |  |  |  | IMG_3103 | 23 |  |  |  | 0 |  |  |  |  | Good
NRH | SW | Site Drainage (soft surfaces) | 75000 | 5956 | 00008870 | including swale |  |  |  | 2011 | King City FS ET Valve Room | 101117 | [7 empty] | Area 2N Linear Water & Wells |  | Siteworks |  |  |  |  | W-WW | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. |  |  |  |  | IMG_3097 | 50 |  |  |  | 0 |  |  |  |  | good
NRH | PM | Valve Chamber No. 1 Butterfly Valve | 10000 | 5957 |  | diameter: 450mm |  |  |  | 1997 |  | 101117 | [15 empty] | 3 | 3 | Surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_9072 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | surface corrosion
NRH | PM | Valve Chamber No. 1 Watermain Drain Valve | 2000 | 5958 |  | diameter: 100mm |  |  |  | 1997 |  | 101117 | [15 empty] | 3 | 3 | Surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term. | 0 |  | 0 |  | IMG_9074 | 11 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0 | surface corrosion
NRH | SW | PRV Valve Chamber Ladder | 3000 | 5959 | [5 empty] | 2011 |  | 101117 | [15 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. |  |  |  |  | IMG_9132 | 50 |  |  |  | 0 |  |  |  |  | good
NRH | SW | PRV Valve Chamber Concrete Structure | 65000 | 5960 | [5 empty] | 2011 |  | 101117 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. |  |  |  |  | IMG_9132 | 50 |  |  |  | 0 |  |  |  |  | good
NRH | SW | PRV Valve Chamber Access Hatch | 5000 | 5961 | [5 empty] | 2011 |  | 101117 | [15 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. |  |  |  |  | IMG_9138 | 50 |  |  |  | 0 |  |  |  |  | good
NRH | SW | Bollards | 2000 | 5962 |  | 4 in total |  |  |  | 2011 |  | 101117 | [15 empty] | 2 | 1 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. |  |  |  |  | IMG_3115 | 50 |  |  |  | 0 |  |  |  |  | good
NRH | PM | Elevated Tank Inlet/Outlet Line | 10000 | 5963 |  | 450mm ss, approximate length: 15 meters |  |  |  | 2011 | King City FS ET Valve Room | 101111 | [15 empty] | 2 | 5 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. |  |  |  |  | IMG_3214 | 50 |  |  |  | 0 |  |  |  |  | good
NRH | PM | Elevated Tank Bypass Line | 5000 | 5964 |  | Diameter: 200mm, with a gate valve |  |  |  | 2011 | King City FS ET Valve Room | 101111 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. |  |  |  |  | IMG_3273 | 50 |  |  |  | 0 |  |  |  |  | Good
NRH | PM | Elevated Tank Inlet Line | 66000 | 5966 |  | Diameter: 450mm, approximate length: 40 meters |  |  |  | 2011 | King City FS ET Valve Room | 101111 | [15 empty] | 2 | 5 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. |  |  |  |  | IMG_3234 | 50 |  |  |  | 0 |  |  |  |  | good
NRH | PM | Elevated Tank Outlet Line | 41000 | 5967 |  | Diameter: 450mm, approximate length: 25 meters |  |  |  | 2011 | King City FS ET Valve Room | 101111 | [15 empty] | 2 | 5 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. |  |  |  |  | IMG_3263 | 50 |  |  |  | 0 |  |  |  |  | good
NRH | PM | Elevated Tank Circulation Line | 7000 | 5968 |  | Diameter: 100mm, approximate length: 20 meters |  |  |  | 2011 | King City FS ET Valve Room | 101111 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. |  |  |  |  | DSCN4033 | 50 |  |  |  | 0 |  |  |  |  | good
NRH | PM | Elevated Tank Overflow Line | 73000 | 5969 |  | Diameter: 400mm, approximate length: 50 meters |  |  |  | 2011 | King City FS ET Valve Room | 101111 | [15 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. |  |  |  |  | IMG_3262 | 50 |  |  |  | 0 |  |  |  |  | good
NRH | PM | PRV Valve Chamber Process Mechanical Equipment | 30000 | 5970 |  | Two PRV valves |  |  |  | 2011 | King City FS ET Valve Room | 101117 | [15 empty] | 3 | 3 | Minor surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced in the long term. |  |  |  |  | IMG_9133 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  |  |  |  | minor surface corrosion
NRH | PM | Elevated Tank Mixing System | 85000 | 5971 | [5 empty] | 2011 |  | 101119 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. | 0 |  | 0 |  |  | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 2019 |  | 0 |  | 0 | good
NRH | PM | Elevated Tank Frostproof Vent/Vacuum Relief Unit | 6000 | 5972 | [5 empty] | 2011 | King City FS ET Valve Room | 101119 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. |  |  |  |  | IMG_9108 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 2019 |  |  |  |  | good
NRH | SW | Sanitary Manholes | 50000 | 5973 |  | total of 3 |  |  |  | 2011 |  | 101117 | [15 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of the service life. | 0 |  | 0 |  | IMG_9085 | 50 |  |  |  | 0 |  | 0 |  | 0 | good
NRH | SC | Gas Chlorination Room FRP Grating | 500 | 5903 | [5 empty] | 2011 |  | 101112 | [15 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of remaining service life. | 0 |  | 0 |  | IMG_9041 | 50 |  |  |  | 0 |  | 0 |  | 0 | Good
NRH | PM | Dechlorination Chamber Overflow Pipe Tideflex Check Valve | 5000 | 5975 |  | Tideflex Check Valve, 450mm |  |  |  | 2011 |  | 101117 | [15 empty] | 2 | 3 |  |  |  | The asset was in good condition. Asset to be replaced in the long term. | 0 | 0 | 0 | 0 | IMG_9091 | 20 | North Richmond Hill Coons Road ET Capital Project 2 |  |  | 0 |  | 0 |  | 0