## 03 Preston - BA
Barcode | Asset Description | Physical Location | Building Name | Condition Rating | Inspector Comments | Year of Installation | Asset Photo | Name Plate Photo | Barcode Photo | Existing ID | Category | Location | Date
| UV System Bank Lifting Device | UV Disinfection System UV Disinfection System Outdoor East of Secondary Clarifier 5 | UV Disinfection System |  |  | 2000-12-12 |  |  |  | PRE-000136 | BA
| Aeration Cell David Crane | Aeration Tank Cell 2 | Aeration Tank Cell 2 |  |  | 2000-04-01 |  |  |  | PRE-000353 | BA
| Gantry Crane | Site Unknown | Site |  |  | 1972-01-01 |  |  |  | PRE-000354 | BA
| Hoist Crane | Site Unknwon | Site |  |  | 1972-01-01 |  |  |  | PRE-000355 | BA
| Storage Building Davit Material Handling | Storage Building | Storage Building |  |  | 2004-01-01 |  |  |  | PRE-000603 | BA
| Storage Building Davit Material Handling | Storage Building | Storage Building |  |  | 2004-01-01 |  |  |  | PRE-000604 | BA
| Storage Room Chain Fall Winch | Storage Building Storage Room | Storage Building |  |  | 2004-01-01 |  |  |  | PRE-000614 | BA
| Main Gate Door Opener | Site Main Gate | Site |  |  | 1972-01-01 |  |  |  | PRE-000615 | BA
| Return Sludge PS 1 Material Handling | Return Sludge PS 1 | Return Sludge PS 1 |  |  | 1972-01-01 |  |  |  | PRE-000893 | BA
| Return Sludge PS 1 Material Handling | Return Sludge PS 1 | Return Sludge PS 1 |  |  | 1972-01-01 |  |  |  | PRE-000894 | BA
| Return Sludge PS 1 Material Handling | Return Sludge PS 1 | Return Sludge PS 1 |  |  | 1972-01-01 |  |  |  | PRE-000895 | BA
| Return Sludge PS 1 Material Handling | Return Sludge PS 1 | Return Sludge PS 1 |  |  | 1972-01-01 |  |  |  | PRE-000896 | BA
| Davit | Aeration Tank Cell 1 | Aeration Tank Cell 1 |  |  | 2000-04-01 |  |  |  | PRE-000919 | BA
| 3000X3000 Sectional Overhead Door | Headworks Building Mechanical Room Headworks | Headworks Building |  |  | 2000-01-01 |  |  |  | PRE-000931 | BA
| Headworks Building Mechanical Room Headworks Doors (Total of 4) | Headworks Building Mechanical Room Headworks | Headworks Building |  |  | 1999-01-01 |  |  |  | WSP-000022 | BA
| Primary Clarifier 2 Electrical Room Electrical Room Roof and Structure | Primary Clarifier 2 Electrical Room Electrical Room | Primary Clarifier 2 |  |  | 1972-01-01 |  |  |  | WSP-000028 | BA
| Raw Sludge Pump Station 1 Door | Raw Sludge Pumping Station 1 Raw Sludge Pump Station 1 Room Ground Level | Raw Sludge Pumping Station 1 |  |  | 1972-01-01 |  |  |  | WSP-000034 | BA
| Raw Sludge Pump Station 1 Door | Raw Sludge Pumping Station 2 Raw Sludge Pump Station 2 Room Ground Level | Raw Sludge Pumping Station 2 |  |  | 1972-01-01 |  |  |  | WSP-000040 | BA
| Roof Guard Rail | Secondary Clarifier 1 On Top of Clarifier | Secondary Clarifier 1 |  |  | 2000-01-20 |  |  |  | WSP-000043 | BA
| Secondary Clarifier 2 Guard Rail | Secondary Clarifier 2 On Top of Clarifier | Secondary Clarifier 2 |  |  | 2000-01-20 |  |  |  | WSP-000044 | BA
| Secondary Clarifier 3 Guard Rail | Secondary Clarifier 3 On Top of Clarifier | Secondary Clarifier 3 |  |  | 2000-01-20 |  |  |  | WSP-000045 | BA
| Secondary Clarifier 4 Guard Rail | Secondary Clarifier 4 On Top of Clarifier | Secondary Clarifier 4 |  |  | 2000-01-20 |  |  |  | WSP-000046 | BA
| Secondary Clarifier 5 Guard Rail | Secondary Clarifier 5 On Top of Clarifier | Secondary Clarifier 5 |  |  | 2000-01-20 |  |  |  | WSP-000047 | BA
| Secondary Clarifier 6 Guard Rail | Secondary Clarifier 6 On Top of Clarifier | Secondary Clarifier 6 |  |  | 2000-01-20 |  |  |  | WSP-000048 | BA
| Stairs With Rail | Secondary Clarifier 1 Secondary Clarifier 1 and 2 | Secondary Clarifier 1 |  |  | 2000-01-20 |  |  |  | WSP-000049 | BA
| Stairs With Rail | Secondary Clarifier 3 Secondary Clarifier 3 and 4 | Secondary Clarifier 3 |  |  | 2000-01-20 |  |  |  | WSP-000050 | BA
| Stairs With Rail | Secondary Clarifier 5 Secondary Clarifier 5 and 6 | Secondary Clarifier 5 |  |  | 2000-01-20 |  |  |  | WSP-000051 | BA
| Secondary Clarifier 5 Electrical Room Electrical Room Roof and Structure | Secondary Clarifier 5 Electrical Room Electrical Room Ceiling | Secondary Clarifier 5 |  |  | 2000-01-20 |  |  |  | WSP-000053 | BA
| Secondary Clarifier Distribution Chamber Guard Rail | Middle of Secondary Clarifier 1-4 | Secondary Clarifier 1 |  |  | 2000-01-20 |  |  |  | WSP-000056 | BA
| Aeration WAS Pump Room Roof and Structure | Aeration Tank Cell 1 Aeration Tank Waste Activated Sludge Pump and Control Room | Aeration Tank Cell 1 |  |  | 2000-01-20 |  |  |  | WSP-000059 | BA
| Aeration Waste Activited Sludge Pump and Control Room Stairs With Rail | Aeration Tank Cell 1 Aeration Tank Waste Activated Sludge Pump and Control Room | Aeration Tank Cell 1 |  |  | 2000-01-20 |  |  |  | WSP-000062 | BA
| Aeration Waste Activited Sludge Pump and Control Room Double Swing Doors | Aeration Tank Cell 1 Aeration Tank Waste Activated Sludge Pump and Control Room | Aeration Tank Cell 1 |  |  | 2000-01-20 |  |  |  | WSP-000063 | BA
| Aeration Tank Cell 1 Roof Guard Rail | Aeration Tank Cell 1 On Top of Aeration Tank | Aeration Tank Cell 1 |  |  | 2000-01-20 |  |  |  | WSP-000065 | BA
| Aeration Tank Cell 3 Roof Guard Rail | Aeration Tank Cell 3 On Top of Aeration Tank | Aeration Tank Cell 3 |  |  | 2000-01-20 |  |  |  | WSP-000066 | BA
| Aeration Tank Cell 1 Exterior Stairs | Aeration Tank Cell 1 On Top of Aeration Tank | Aeration Tank Cell 1 |  |  | 2000-01-20 |  |  |  | WSP-000067 | BA
| Exterior Stairs | Aeration Tank Cell 4 On Top of Aeration Tank | Aeration Tank Cell 4 |  |  | 2000-01-20 |  |  |  | WSP-000068 | BA
| Return Sludge Pumping Station Room Exterior Door | Return Sludge Pumping Station Room Entrance Beside Rectangular Secondary Clarifiers | Return Sludge Pumping Station |  |  | 2000-01-20 |  |  |  | WSP-000069 | BA
| Return Sludge Pumping Station Room Stairs With Rail | Return Sludge Pumping Station Room Entrance Beside Rectangular Secondary Clarifiers | Return Sludge Pumping Station |  |  | 2000-01-20 |  |  |  | WSP-000070 | BA
| Bio-Rem Room Exterior Door | Bio Rem Building Bio Rem Room | Bio-Rem Building |  |  | 2017-01-01 |  |  |  | WSP-000075 | BA
| Bio-Rem Room Roof Structure | Bio Rem Building Bio Rem Room | Bio-Rem Building |  |  | 2017-01-01 |  |  |  | WSP-000076 | BA
| Bio-Rem Room Interior Concrete Veneer Wall | Bio Rem Building Bio Rem Room | Bio-Rem Building |  |  | 2017-01-01 |  |  |  | WSP-000077 | BA
| Bio-Rem Room Ceiling Finishes | Bio Rem Building Bio Rem Room | Bio-Rem Building |  |  | 2017-01-01 |  |  |  | WSP-000078 | BA
| Bio-Rem Room Concrete Flooring | Bio Rem Building Bio Rem Room | Bio-Rem Building |  |  | 2017-01-01 |  |  |  | WSP-000079 | BA
| Storage Room Interior Concrete Veneer Wall | Storage Building Storage Room | Storage Building |  |  | 2004-01-01 |  |  |  | WSP-000081 | BA
| Storage Room Roof Structure | Storage Building Storage Room | Storage Building |  |  | 2004-01-01 |  |  |  | WSP-000083 | BA
| Storage Room Interior Door | Storage Building Storage Room | Storage Building |  |  | 2004-01-01 |  |  |  | WSP-000084 | BA
| Storage Room Exterior Door | Storage Building Storage Room | Storage Building |  |  | 2004-01-01 |  |  |  | WSP-000085 | BA
| Storage Room Overhead Door | Storage Building Storage Room | Storage Building |  |  | 2004-01-01 |  |  |  | WSP-000086 | BA
| Storage Room Exterior Windows (3 Total) | Storage Building Storage Room | Storage Building |  |  | 2004-01-01 |  |  |  | WSP-000087 | BA
| Storage Room Ceiling | Storage Building Storage Room | Storage Building |  |  | 2004-01-01 |  |  |  | WSP-000088 | BA
| Storage Room Concrete Flooring | Storage Building Storage Room | Storage Building |  |  | 2004-01-01 |  |  |  | WSP-000089 | BA
| Storage Room Industrial Shelving (8 Total) | Storage Building Storage Room | Storage Building |  |  | 2004-01-01 |  |  |  | WSP-000090 | BA
| Storage Room Steel Storage Cabinets (4 Total) | Storage Building Storage Room | Storage Building |  |  | 2004-01-01 |  |  |  | WSP-000091 | BA
| UV System Roof Guard Rail | UV Disinfection System Room Outdoor East of Secondary Clarifier 5 | UV Disinfection System |  |  | 2000-12-12 |  |  |  | WSP-000094 | BA
| UV System Vertical Ladder | UV Disinfection System Room Outdoor East of Secondary Clarifier 5 | UV Disinfection System |  |  | 2000-12-12 |  |  |  | WSP-000095 | BA
| Digestor Control Building Exterior Door | Digester Control Building Boiler Room | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000096 | BA
| Digestor Control Building Exterior Windows (3 Total) | Digester Control Building Boiler Room | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000097 | BA
| Digestor Control Building Interior Door | Digester Control Building Boiler Room | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000098 | BA
| Digestor Control Building Interior Concrete Veneer Wall | Digester Control Building Boiler Room | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000099 | BA
| Digestor Control Building Ceiling | Digester Control Building Boiler Room | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000101 | BA
| Digestor Control Building Concrete Flooring | Digester Control Building Boiler Room | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000102 | BA
| Digestor Control Building Indoor Metal Floor Hatch | Digester Control Building Boiler Room | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000103 | BA
| Digestor Control Building Indoor Metal Trench Cover | Digester Control Building Boiler Room | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000104 | BA
| Digestor Boiler Room Roof Structure | Digester Control Building Boiler Room | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000105 | BA
| Digestor Control Building Exterior Door | Digester Control Building Electrical Room | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000106 | BA
| Digestor Control Building Interior Concrete Veneer Wall | Digester Control Building Electrical Room | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000107 | BA
| Digestor Control Building Ceiling | Digester Control Building Electrical Room | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000109 | BA
| Digestor Control Building Concrete Flooring | Digester Control Building Electrical Room | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000110 | BA
| Digestor Control Building Exterior Window (1 Total) | Digester Control Building Electrical Room | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000111 | BA
| Digestor Control Building Steel Storage Cabinet | Digester Control Building Electrical Room | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000112 | BA
| Digestor Electrical Room Roof Structure | Digester Control Building Electrical Room | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000113 | BA
| Digestor Control Building Exterior Door | Digester Control Building Gas Booster Room | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000114 | BA
| Digestor Control Building Interior Concrete Veneer Wall | Digester Control Building Gas Booster Room | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000115 | BA
| Digestor Control Building Ceiling | Digester Control Building Gas Booster Room | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000117 | BA
| Digestor Control Building Concrete Flooring | Digester Control Building Gas Booster Room | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000118 | BA
| Digestor Gas Booster Room Roof Structure | Digester Control Building Gas Booster Room | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000120 | BA
| Digestor Control Building Exterior Doors (2 Total) | Digester Control Building Gas Safety Room | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000121 | BA
| Digestor Control Building Interior Concrete Veneer Wall | Digester Control Building Gas Safety Room | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000122 | BA
| Digestor Control Building Ceiling | Digester Control Building Gas Safety Room | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000124 | BA
| Digestor Control Building Concrete Flooring | Digester Control Building Gas Safety Room | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000125 | BA
| Digestor Control Building Stairs With Rail | Digester Control Building Gas Safety Room (Outside) Between Gas Safety Room and Sludge Mixing Room | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000127 | BA
| Digestor Control Building Outdoor Stairs With Rail | Digester Control Building Sludge Mixing Pump Room (Outside) West and South Side of the Sludge Mixing Pump Room | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000128 | BA
| Digestor Control Building Exterior Doors (3 Total) | Digester Control Building Sludge Mixing Pump Room Sludge Mixing Pump Room First Floor | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000129 | BA
| Digestor Control Building Interior Concrete Veneer Wall | Digester Control Building Sludge Mixing Pump Room Sludge Mixing Pump Room First Floor | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000130 | BA
| Digestor Control Building Ceiling | Digester Control Building Sludge Mixing Pump Room Sludge Mixing Pump Room First Floor | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000132 | BA
| Digestor Control Building Concrete Flooring | Digester Control Building Sludge Mixing Pump Room Sludge Mixing Pump Room First Floor | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000133 | BA
| Digestor Sludge Mixing Pump Room Roof Structure | Digester Control Building Sludge Mixing Pump Room Sludge Mixing Pump Room First Floor | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000134 | BA
| Digestor Control Building Interior Doors (2 Total) | Digester Control Building Sludge Mixing Pump Room Sludge Mixing Pump Room First Floor, For WAShroom and Staircase | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000135 | BA
| Digestor Control Building Exterior Windows (2 Total) | Digester Control Building Sludge Mixing Pump Room Sludge Mixing Pump Room First Floor, Near WAShroom and Staircase | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000136 | BA
| Digestor Control Building Indoor Stairs | Digester Control Building Sludge Mixing Pump Room South Side of the Sludge Mixing Pump Room | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000137 | BA
| Digestor Control Building Exterior Window | Digester Control Building Sludge Mixing Pump Room Sludge Mixing Pump Room Second Floor | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000139 | BA
| Digestor Control Building Interior Concrete Veneer Wall | Digester Control Building Sludge Mixing Pump Room Sludge Mixing Pump Room Second Floor | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000140 | BA
| Digestor Control Building Ceiling | Digester Control Building Sludge Mixing Pump Room Sludge Mixing Pump Room Second Floor | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000142 | BA
| Digestor Control Building Concrete Flooring | Digester Control Building Sludge Mixing Pump Room Sludge Mixing Pump Room Second Floor | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000143 | BA
| Digestor Sludge Mixing Pump Roof Hatch | Digester Control Building Sludge Mixing Pump Room Sludge Mixing Pump Room Second Floor | Digester Control Building |  |  | 1972-01-01 |  |  |  | WSP-000144 | BA
| O&M Building Interior Concrete Veneer Wall | Ops & Maintenance Building Electrical Room | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000148 | BA
| O&M Building Ceiling | Ops & Maintenance Building Electrical Room | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000149 | BA
| O&M Building Concrete Flooring | Ops & Maintenance Building Electrical Room | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000150 | BA
| O&M Building Interior Doors (4 Total) | Ops & Maintenance Building Electrical Room | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000151 | BA
| O&M Building Interior Concrete Veneer Wall | Ops & Maintenance Building Garage | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000152 | BA
| O&M Building Ceiling | Ops & Maintenance Building Garage | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000153 | BA
| O&M Building Concrete Flooring | Ops & Maintenance Building Garage | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000154 | BA
| O&M Building Metal Storage Cabinets (4 Total) | Ops & Maintenance Building Garage | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000155 | BA
| O&M Building Electrical Chain Hoist | Ops & Maintenance Building Garage | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000156 | BA
| O&M Building Electrical Monorail Beam | Ops & Maintenance Building Garage | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000157 | BA
| O&M Building Interior Doors (2 Total) | Ops & Maintenance Building Garage | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000158 | BA
| O&M Building Metal Wall Panelling | Ops & Maintenance Building Garage | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000159 | BA
| O&M Building Overhead Door | Ops & Maintenance Building Garage | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000160 | BA
| O&M Building Exterior Door | Ops & Maintenance Building Garage | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000161 | BA
| O&M Building Exterior Windows (2 Total) | Ops & Maintenance Building Garage | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000162 | BA
| O&M Building Interior Concrete Veneer Wall | Ops & Maintenance Building Laboratory | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000163 | BA
| O&M Building Ceiling | Ops & Maintenance Building Laboratory | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000164 | BA
| O&M Building Plastic Flooring | Ops & Maintenance Building Laboratory | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000165 | BA
| O&M Building Exterior Windows (2 Total) | Ops & Maintenance Building Laboratory | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000167 | BA
| O&M Building Interior Door | Ops & Maintenance Building Laboratory | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000168 | BA
| O&M Building Interior Door | Ops & Maintenance Building Scada Room | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000169 | BA
| O&M Building Interior Concrete Veneer Wall | Ops & Maintenance Building Scada Room | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000170 | BA
| O&M Building Ceiling | Ops & Maintenance Building Scada Room | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000171 | BA
| O&M Building Plastic Flooring | Ops & Maintenance Building Scada Room | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000172 | BA
| O&M Building Metal Storage Cabinets (2 Total) | Ops & Maintenance Building Scada Room | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000173 | BA
| O&M Building Tables (3 Total) | Ops & Maintenance Building Scada Room | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000174 | BA
| O&M Building Interior Window | Ops & Maintenance Building Scada Room | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000175 | BA
| O&M Building Interior Concrete Veneer Wall | Ops & Maintenance Building Blower Room | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000176 | BA
| O&M Building Ceiling | Ops & Maintenance Building Blower Room | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000177 | BA
| O&M Building Concrete Flooring | Ops & Maintenance Building Blower Room | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000178 | BA
| O&M Building Storage Cabinets (3 Total) | Ops & Maintenance Building Blower Room | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000179 | BA
| O&M Building Exterior Door | Ops & Maintenance Building Blower Room | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000180 | BA
| O&M Building Building Interior Doors (2 Total) | Ops & Maintenance Building Blower Room | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000181 | BA
| O&M Building Tables (3 Total) | Ops & Maintenance Building Blower Room | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000182 | BA
| O&M Building Electrical Chain Hoist | Ops & Maintenance Building Blower Room | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000183 | BA
| O&M Building Electrical Monorail Beam | Ops & Maintenance Building Blower Room | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000184 | BA
| O&M Building Interior Concrete Veneer Wall | Ops & Maintenance Building Generator Room | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000185 | BA
| O&M Building Ceiling | Ops & Maintenance Building Generator Room | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000186 | BA
| O&M Building Concrete Flooring | Ops & Maintenance Building Generator Room | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000187 | BA
| O&M Building Indoor Metal Trench Cover | Ops & Maintenance Building Generator Room | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000189 | BA
| O&M Building Interior Wall | Ops & Maintenance Building Hallway | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000190 | BA
| O&M Building Ceiling | Ops & Maintenance Building Hallway | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000191 | BA
| O&M Building Plastic Flooring | Ops & Maintenance Building Hallway | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000192 | BA
| O&M Building Interior Wall | Ops & Maintenance Building Office | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000194 | BA
| O&M Building Ceiling | Ops & Maintenance Building Office | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000195 | BA
| O&M Building Carpet Flooring | Ops & Maintenance Building Office | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000196 | BA
| O&M Building Exterior Windows (2 Total) | Ops & Maintenance Building Office | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000197 | BA
| O&M Building Cabinet | Ops & Maintenance Building Office | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000198 | BA
| O&M Building Interior Door | Ops & Maintenance Building Office | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000199 | BA
| Return Sludge PS 1 Roof | Return Sludge PS 1 between Secondary Clarifier 1&2 | Return Sludge PS 1 |  |  | 1972-01-01 |  |  |  | WSP-000236 | BA
| Return Sludge PS 2 Roof | Return Sludge PS 2 between Secondary Clarifier 3&4 | Return Sludge PS 2 |  |  | 1972-01-01 |  |  |  | WSP-000237 | BA
| Return Sludge Pumping Station Roof | Return Sludge Pumping Station at Secondary Clarifier 5&6 | Return Sludge Pumping Station |  |  | 1972-01-01 |  |  |  | WSP-000238 | BA
| Headworks Building Roof | Headworks Building and Chemical Storage Room | Headworks Building |  |  | 1972-01-01 |  |  |  | WSP-000239 | BA
| Ops & Maintenance Building Main Building Roof | Ops & Maintenance Building Main Building | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000240 | BA
| Ops & Maintenance Building Blower and Generator Room Roof | Ops & Maintenance Building Blower and Generator Room | Ops & Maintenance Building |  |  | 1972-01-01 |  |  |  | WSP-000241 | BA
| Wastewater Pumping station Concrete Roof and Structure | Wastewater Pumping station | Wastewater Pumping station |  |  | 1999-01-01 |  |  |  | WSP-000242 | BA
| Primary Sludge Pumping Station 1 Roof | Primary Sludge Pumping Station 1 between Clarifier 1&2 | Primary Clarifier Dist Chamber |  |  | 1972-01-01 |  |  |  | WSP-000243 | BA
| Primary Sludge Pumping Station 2 Roof | Primary Sludge Pumping Station 2 between Clarifier 3&4 | Primary Clarifier Dist Chamber |  |  | 1972-01-01 |  |  |  | WSP-000244 | BA
| Primary Digester Roof | Primary Digester | Primary Digester |  |  | 1972-01-01 |  |  |  | WSP-000245 | BA
| Secondary Digester Roof | Secondary Digester | Secondary Digester |  |  | 1972-01-01 |  |  |  | WSP-000246 | BA
okvcfc25g0000476dwrqras7s | Roof AssemblyAsphalt shingles | Storage buiodimg at entrance | Storage Building | Very Good |  |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617bfaa21e7d393e03000000/asset-photo/eUaq+kLiNI2EKIbvIMJ6Q.jpg |  |  |  |  | 43.3886145, -80.3519489 | 2021-10-29 13:40
okvcfft6m0001476d8nl0qox1 | Roof Accessories Soffit fascia and evestrough | Storage building at entrance | Storage Building | Good | Minor pealing paint on evestrough.Minir warpijg if fascia boards.Localized Loose alum, soffit |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617bfbbc1e7d393e03000001/asset-photo/GPgNAt+nBeJaZZuXhUw.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617bfbbc1e7d393e03000001/name-plate-photo/JERVPGDMHAJMYYSuOGlzcg.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617bfbbc1e7d393e03000001/barcode-photo/O54A5cako0Twfrb14DjfPQ.jpg |  |  | 43.3885544, -80.3520110 | 2021-10-29 13:44
okvcfn9f80002476dkj2fks09 | Exterior WallMasonry Veneer | Storage Building | Storage Building | Very Good |  |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617bfc651e7d393e03000002/asset-photo/N+eFK9aHpt7TEcj+l3H0xA.jpg |  |  |  |  | 43.3885576, -80.3518248 | 2021-10-29 13:50
okvcfpor20003476dhx1k8162 | Exterior windows, aluminum | Storagebuikding by front entrance | Storage Building | Fair | Deformed glazing gasket Cracked perimeter caulking |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617bfd5b1e7d393e03000003/asset-photo/DQ53MXcvDt+xxYocvAP7A.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617bfd5b1e7d393e03000003/name-plate-photo/3+KAJl8QrIhPCPj65nMNWw.jpg |  |  |  | 43.3886498, -80.3519148 | 2021-10-29 13:52
okvcfum2k0004476d9oipreyq | Exterior DoorsHollow Metal | Front entrance | Storage Building | Fair | Rust at base of door.Chalking paint |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617bfde61e7d393e03000004/asset-photo/YuUSurntCv1EX61bn8UsVw.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617bfde61e7d393e03000004/name-plate-photo/LNi2IL72sjhUMAtv8A6lg.jpg |  |  |  | 43.3886116, -80.3519661 | 2021-10-29 13:56
okvcfxnil0005476dbx2kon2z | Manual Chain Operated, Sectional Overhead Door | Front entrance | Storage Building | Good | General wear and tareChaulking paint |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617bfe461e7d393e03000005/asset-photo/4tzT2c8Icdp7qqFNJLH6gg.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617bfe461e7d393e03000005/name-plate-photo/l2Sox4FLLF9cNZAlV78JQ.jpg |  |  |  | 43.3885825, -80.3518706 | 2021-10-29 13:58
okvcg8tii0006476d2ujhp64t | Interior DoorsHollow Metal Door | Frint entrance | Storage Building | Very Good | Hollow metal door |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c003c1e7d393e03000006/asset-photo/Ju3NI+EKpRLJ7WzNopE7w.jpg |  |  |  |  | 43.3886509, -80.3518651 | 2021-10-29 14:07
okvcgehuw0007476d34mtnluv | Ceiling finishGypsum, Painted | Front entrance | Storage Building | Good |  |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c01681e7d393e03000007/asset-photo/GLPtJGOjuffCLCWthA0KTw.jpg |  |  |  |  | 43.3886529, -80.3518401 | 2021-10-29 14:11
okvcgh31h0008476dp0o9juek | Wall Finish,Concrete Block, Painted | Front entrance | Storage Building | Very Good |  |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c01ec1e7d393e03000008/asset-photo/dR5DZjoD9MmOcDmTR9Sm3w.jpg |  |  |  |  | 43.3886788, -80.3518720 | 2021-10-29 14:13
okvcgvaeh0009476dg2kwoivs | Roof AssemblyMetal Panels, prefinished, surface fastened |  | Headworks Building | Good | Closure strip missing (multiple locations) |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c05271e7d393e03000009/asset-photo/UuuF5uMWC+adVdav4+3v5A.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c05271e7d393e03000009/name-plate-photo/am3MECwfCh7NSxQn1qsB1w.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c05271e7d393e03000009/barcode-photo/Um7UStXwFLXSNiLIlobX9w.jpg |  |  | 43.3878508, -80.3523415 | 2021-10-29 14:23
okvch2hl3000a476dp7hgxcde | Exterior Wall Assembly,Masonry, Brick and conc, blk,Control joint not concrete |  | Headworks Building | Good | Minor mortar joint deficiency |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c06261e7d393e0300000a/asset-photo/hBoMiqyrddzlMwluZCBs1w.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c06261e7d393e0300000a/name-plate-photo/K2Q6POwIjIjJneNSQMqxCg.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c06261e7d393e0300000a/barcode-photo/WL5H4rHXL6jTxK0LdA6VHQ.jpg |  |  | 43.3880657, -80.3524825 | 2021-10-29 14:30
okvchbqgw000b476dfkybid77 | Roof Accessories Soffit Fascia Evestrough |  | Headworks Building | Good | Evidence of leak at evestrough seam |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c07a41e7d393e0300000b/asset-photo/+aTgDIBj2L1Y05KUpSGfgg.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c07a41e7d393e0300000b/name-plate-photo/y12ahGKtJfwNitpRSmArg.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c07a41e7d393e0300000b/barcode-photo/QtHvRg8Pw6eWsvOzeEH9gg.jpg |  |  | 43.3879980, -80.3521729 | 2021-10-29 14:37
okvchgzbi000c476d5bswjbrt | Exterior DoorsHollow Metal, Painted |  | Headworks Building | Poor | Single and double door into headworks room extensive rust on frame. Need replacement. Other doors of headworks building, good condition |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c0aad1e7d393e0300000c/asset-photo/nJpPKWrnyPfQ8mIe5GB7EA.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c0aad1e7d393e0300000c/name-plate-photo/XYMWXk9zQmLirlin67gF+A.jpg |  |  |  | 43.3881126, -80.3522414 | 2021-10-29 14:41
okvchw0st000d476dk524md3i | Overhead Doors |  | Headworks Building | Poor | Motor operated, sectional doors. Door 1 (West): interiorExtensive locallized rust. Cracked window pane. Motor operated ( cant confirm if it's running)exterior side: paint flaking and corrosion Door 2 (South): fair with minor corrosion |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c0c651e7d393e0300000d/asset-photo/S70X+cV92g9TMOrgAmEgAg.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c0c651e7d393e0300000d/name-plate-photo/f4nP7GIiLPOd4AU4TJzc3Q.jpg |  |  |  | 43.3878951, -80.3524266 | 2021-10-29 14:53
okvci6b66000e476ddwhbaqzf | Ceiling Assembly:Vinyl Clad Gypsum board, Joint Strips |  | Headworks Building | Fair | General wear &tare |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c0eb11e7d393e0300000e/asset-photo/7dtINZpP6oR52Tj3lcMVtg.jpg |  |  |  |  | 43.3880041, -80.3524572 | 2021-10-29 15:01
okvcij8n6000f476dmcks66ci | Firestopping Concrete Block Walls |  | Headworks Building | Very Good |  |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c0f7b1e7d393e0300000f/asset-photo/zz8+ITR4npGleCHxQDB7wQ.jpg |  |  |  |  | 43.3880337, -80.3524423 | 2021-10-29 15:11
okvcinsul000g476dbc5mljdm | Floor Coating Sulphur Hypochlorite |  | Headworks Building | Fair | Localized coating flaking |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c10ca1e7d393e03000010/asset-photo/NaX8eRh4knJrfkjQ3XouMA.jpg |  |  |  |  | 43.3879703, -80.3521911 | 2021-10-29 15:14
okvcitm52000h476dgi2w0d0h | Interior RailingsAluminum |  | Headworks Building | Very Good | C: safety chains are not code complaint and require a swing gate |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c118e1e7d393e03000011/asset-photo/o4CdSYlEBcF1LnrKy6CTOw.jpg |  |  |  |  | 43.3878703, -80.3521928 | 2021-10-29 15:19
okvcj04cl000i476dktyokonl | Exterior Louvres |  | Headworks Building | Good | Chalking paint, deteriorating caulking |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c12721e7d393e03000012/asset-photo/RDvmfNnHIn5PQf1knL4Xg.jpg |  |  |  |  | 43.3882036, -80.3521809 | 2021-10-29 15:24
okvcjbtgx0001406d8vuxuu2k | Roof accessoriesCoping, metal, prefinished |  | Bio-Rem Building | Very Good |  |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c14b9d170114b06000001/asset-photo/bwr+L6k2uyhr5J3iZMNRoQ.jpg |  |  |  |  | 43.3878174, -80.3521882 | 2021-10-29 15:33
okvcjzox80007406dezc7lm21 | Roof assembly | W bldg | Aeration Tank Cell 1 |  | Not visible, comdition unknown |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c18e7d170114b06000007/asset-photo/k+InQ8g7RvVihNaYJEXRg.jpg |  |  |  |  | 43.3880492, -80.3520691 | 2021-10-29 15:52
okvck9rba000a406dkkcz25vn | Ext doorHollow metal, paintedOne double door | W bldg | Aeration Tank Cell 1 |  | Rust in several locations, paint flaking |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c1bf0d170114b0600000a/asset-photo/5hC6uZkRlazkcER73Imohg.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c1bf0d170114b0600000a/name-plate-photo/f+bG5FoiCzCyisqmjgDg.jpg |  |  |  | 43.3880238, -80.3520460 | 2021-10-29 16:00
okvcl4vyy0000476darw3wagy | Roof AssemblyConventional flat roof, pea gravel | South building | Aeration Tank Cell 1 | Poor | Ponding, roof not draining |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c20bc1e7d396121000000/asset-photo/WvUu+ZbYLFET4AHgDbN48g.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c20bc1e7d396121000000/name-plate-photo/ziMqycNkomPqDvfxg0H6yw.jpg |  |  |  | 43.3879808, -80.3520746 | 2021-10-29 16:24
okvcl8wkw0001476d6lmd2vse | Roof Accessories Coping , prefin. Scupper drqin with downspout | South building | Aeration Tank Cell 1 | Very Poor | N |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c21421e7d396121000001/asset-photo/+anrSHODBcnMhLYrjlob0A.jpg |  |  |  |  | 43.3877215, -80.3522438 | 2021-10-29 16:27
okvclbjuz0002476dhbtenevv | Exterior Wall AssemblyEIFS | Sputh building | Aeration Tank Cell 1 | Good | D |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c21a01e7d396121000002/asset-photo/xfUddPFt32L9Jz8o59skSQ.jpg |  |  |  |  | 43.3877992, -80.3521780 | 2021-10-29 16:29
okvcldqxs0003476dz64u8uc3 | Exterior DoorHMU double door | South | Aeration Tank Cell 1 | Poor | Localized moderate corrosion, flak8ng paint. Damaged weatherstripping. |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c22631e7d396121000003/asset-photo/uCYVepsFHKNDcoKmYd2BqQ.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c22631e7d396121000003/name-plate-photo/PWfAwnGIQW2EBYFkGrb7RA.jpg |  |  |  | 43.3878224, -80.3522571 | 2021-10-29 16:31
okvclif9d0004476dzx0gamjc | Aluminum, Railings | South building | Aeration Tank Cell 1 | Very Good | C: one railing missing bottom extension |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c23101e7d396121000004/asset-photo/QOwCs1XrB2ahYUllJXKOg.jpg |  |  |  |  | 43.3878438, -80.3522263 | 2021-10-29 16:34
okvclphk50000476dbga0587d | Exterior Railings | South building | Aeration Tank Cell 1 | Good | Minor pitting |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c24251e7d393aeb000000/asset-photo/ewEdz3OBjidm7n+iAzgwKQ.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c24251e7d393aeb000000/name-plate-photo/XVNTzMURk8uMcczCBoDMaw.jpg |  |  |  | 43.3878153, -80.3521666 | 2021-10-29 16:40
okvclsrz50001476dz9wr4p97 | Exterior Wall AssemblyEiFS | South building | Aeration Tank Cell 1 | Poor | Physical damage to multiple locations |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c25301e7d393aeb000001/asset-photo/SR3wpEXqw7OKnTWUBYPM7w.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c25301e7d393aeb000001/name-plate-photo/bwqwWACw3YawzJm80XYwYw.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c25301e7d393aeb000001/barcode-photo/zQ3PZxt8i+C0pP3SOlHQPg.jpg |  |  | 43.3877395, -80.3521264 | 2021-10-29 16:42
okvcm0nqd0002476dc4djeupf | Roof Accessories Metal Coping prefinished metalExposed roof fascia | Near entrance | Raw Sludge Pumping Station 2 | Good | Deteriorating wood and flaking paint |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c26871e7d393aeb000002/asset-photo/oKn+saWadDAl6C6hSJUsng.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c26871e7d393aeb000002/name-plate-photo/UWvNUt6N5tLt5DgTuWBI7Q.jpg |  |  |  | 43.3883566, -80.3520087 | 2021-10-29 16:48
okvcm4hzn0003476duvozgd4d | Exterior Wall AssemblyConcrete, paint | Entrance | Raw Sludge Pumping Station 2 | Good |  |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c279d1e7d393aeb000003/asset-photo/+0ME4cpAba8doK5mISTJRg.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c279d1e7d393aeb000003/name-plate-photo/1lhTXQfmrXQ1NCmB0zzgg.jpg |  |  |  | 43.3882637, -80.3520657 | 2021-10-29 16:51
okvcmam4g0004476dubt4p5mx | Exterior DoorHollow Metal Frame | Entrance | Raw Sludge Pumping Station 2 | Good | C: Height of door opening is 1970mm. |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c28101e7d393aeb000004/asset-photo/aKIihy8hTbXxk7CzEawWrQ.jpg |  |  |  |  | 43.3882604, -80.3520410 | 2021-10-29 16:56
okvcmd11r0005476de8ztc4ak | Interior CeilingConcrete, painted | Entrance | Raw Sludge Pumping Station 2 | Good |  |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c28c21e7d393aeb000005/asset-photo/egwwGGBjGbJIzmu1lhDCUQ.jpg |  |  |  |  | 43.3882648, -80.3520634 | 2021-10-29 16:58
okvcmhobl0006476d1ycqmmx7 | Interior Concrete WallPaint |  | Raw Sludge Pumping Station 2 | Very Good |  |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c29671e7d393aeb000006/asset-photo/iwQ+AmZuoC1YHOPwx6Uew.jpg |  |  |  |  | 43.3883103, -80.3520937 | 2021-10-29 17:01
okvcmko2r0007476d31ktcpsx | Interior Floor, Concrete, painted |  | Raw Sludge Pumping Station 2 | Good | Minor staining |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c2a131e7d393aeb000007/asset-photo/2an9x6mpNg7AHkf2Oa3YUA.jpg |  |  |  |  | 43.3883260, -80.3521013 | 2021-10-29 17:04
okvcmo5290008476daa1auz5h | Exterior WindowSingle-pane aluminum frame | Emtrance | Raw Sludge Pumping Station 2 | Poor | Middle window pane , temprred glass brokenGlazing gasket has failed on inside and outside |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c2b661e7d393aeb000008/asset-photo/+d82irj+RkWd0KrYHUXAkQ.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c2b661e7d393aeb000008/name-plate-photo/qu0ovNE+XHW4v2jY46BZ1A.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c2b661e7d393aeb000008/barcode-photo/grCKnXhbtu229BvlXX7aQ.jpg |  |  | 43.3883029, -80.3521171 | 2021-10-29 17:07
okvcmvs560009476d2xoun6fp | Aluminum louver | Entrance | Raw Sludge Pumping Station 2 | Very Good |  |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c2c0a1e7d393aeb000009/asset-photo/3FH+OC5AjTrQX83q499oMA.jpg |  |  |  |  | 43.3883794, -80.3520661 | 2021-10-29 17:12
okvcmz109000a476d13eg32hu | RailingsAluminum | C: no kick plate at top of stairs, missing handrail extension at base of stairs. Guardrail at stairs is kes than 920mm | Raw Sludge Pumping Station 2 | Good | General Ware &Tare |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c2d261e7d393aeb00000a/asset-photo/+imCMc6gAhUHD8QWYssQA.jpg |  |  |  |  | 43.3883255, -80.3520736 | 2021-10-29 17:15
Exterior Roof Assemmbly | Conventioal Roof Assembly Pea Gravel |  | Raw Sludge Pumping Station 2 | Poor | Excessive roof pooling |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c2e361e7d393aeb00000b/asset-photo/m2MT5rBYwr91pjNSSq6BSA.jpg |  |  |  |  | 43.3882436, -80.3520712 | 2021-10-29 17:22
okvcnmgrm000b476d7c45ityt | Exterior Traffic Topping |  | Raw Sludge Pumping Station 2 | Very Good |  |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c30951e7d393aeb00000c/asset-photo/RWYi+gqZLRPM6DGS4n9jDA.jpg |  |  |  |  | 43.3883610, -80.3521101 | 2021-10-29 17:33
okvcnrb99000c476d1ko8pf2j | Interior Floor finishEpoxy coating, slip resistant |  | Raw Sludge Pumping Station 1 | Fair | Chipped coating. New coating on 1/2of floor onlyWare and tear on the stairs |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c32051e7d393aeb00000d/asset-photo/bewFFNGGWKhqdXgenZZXA.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c32051e7d393aeb00000d/name-plate-photo/EqQtcHOF0GtbEM7RHxoKwQ.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c32051e7d393aeb00000d/barcode-photo/mLeGQCqxVZ3YYtwjyrBtxg.jpg |  |  | 43.3882502, -80.3519499 | 2021-10-29 17:37
okvcnvn7f000d476dvhlfjbj8 | Interior Wall FinishPoured concrete, paint |  | Raw Sludge Pumping Station 1 | Good | Evidence of leaks at pedestrians and other locations. |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c32901e7d393aeb00000e/asset-photo/i4a6nSO8H+1GJ+qXJ6yIRg.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c32901e7d393aeb00000e/name-plate-photo/Frq+drDHUFmsQFDNNsCMgg.jpg |  |  |  | 43.3882300, -80.3519056 | 2021-10-29 17:40
okvco3dsn0000476d6g8tkppx | Interior Ceiling, Concrete Slab, paint |  | Raw Sludge Pumping Station 1 | Good | Evidence of leaks |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c33821e7d3976fb000000/asset-photo/QFvEac76IILuQ8TNjHOYw.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c33821e7d3976fb000000/name-plate-photo/g1O381Lz5iHZ7LI2cco9IA.jpg |  |  |  | 43.3882330, -80.3519007 | 2021-10-29 17:45
okvco4h370001476d0mt39tmh | Interior Door,Hollow metal frame, painted, louver |  | Raw Sludge Pumping Station 1 | Very Good |  |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c33fd1e7d3976fb000001/asset-photo/b51pD6zM02twbdGrXFBzhA.jpg |  |  |  |  | 43.3884046, -80.3518846 | 2021-10-29 17:47
okvco7cu80002476dxtcpe811 | Aluminum Railing |  | Raw Sludge Pumping Station 1 | Good | Ware and tearC: no stair extension |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c34ab1e7d3976fb000002/asset-photo/YgVrDuYLjZ6M8szOMCOQow.jpg |  |  |  |  | 43.3883646, -80.3518965 | 2021-10-29 17:49
okvcoatz70003476dvbg57k5c | Exterior Door |  | Raw Sludge Pumping Station 1 | Fair | Rusted hinges, chipping paint |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c358b1e7d3976fb000003/asset-photo/Ftv4rPB6jkbzMRQXZp2Q0Q.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c358b1e7d3976fb000003/name-plate-photo/Kqc95AUf3nGehxonMqIdJw.jpg |  |  |  | 43.3881246, -80.3519104 | 2021-10-29 17:52
okvcoeyd20004476dv22f3ryl | Louvers |  | Raw Sludge Pumping Station 2 | Very Good |  |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c36361e7d3976fb000004/asset-photo/w5ZtjVnHGbaXx6LvG+Z4Tg.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c36361e7d3976fb000004/name-plate-photo/+HelWI06xsjWFi1jUDoNHA.jpg |  |  |  | 43.3881167, -80.3519621 | 2021-10-29 17:55
okvcoo8ud0005476dkdo3ctdd | Metal copingPrefin, metal,Wooden Fascia |  | Raw Sludge Pumping Station 1 | Fair | Missing scu00er downspoutPaint chipping and wood decomposing |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c37ae1e7d3976fb000005/asset-photo/KbJXsYj6KjdhO9g5on1e1Q.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c37ae1e7d3976fb000005/name-plate-photo/Xa9h4FYFBoGRNZ03kgjERw.jpg |  |  |  | 43.3881566, -80.3519496 | 2021-10-29 17:59
okvcor8q10006476dxiov2mkn | Conventional Roof Assembly, pea gravel |  | Raw Sludge Pumping Station 2 | Poor | Excessive pooling |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c3ae51e7d3976fb000006/asset-photo/H3Eg1tjQ5NRKqwkhDESxTw.jpg |  |  |  |  | 43.3881850, -80.3518916 | 2021-10-29 18:05
okvcq58il0007476d8bhfuk2w | Interior Wall FinishPoured Concrete, paint |  | Return Sludge PS 2 | Fair | Extensivw evidence of leaks, stains |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c41e71e7d3976fb000007/asset-photo/xXw9MdsDCJHKmUkmYDk3Q.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c41e71e7d3976fb000007/name-plate-photo/aAVw68jnk1+DeCnoWJV7w.jpg |  |  |  | 43.3878340, -80.3509769 | 2021-10-29 18:43
okvcqap4z0008476dhos9cjxr | Interior Ceiling finisheConcrete, paint |  | Return Sludge PS 2 | Fair | Evidence ofmleakain multiple locations. |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c42761e7d3976fb000008/asset-photo/x9IPluh2vBRiG56+lmaiCQ.jpg |  |  |  |  | 43.3877957, -80.3510800 | 2021-10-29 18:48
okvcqdvbo0009476dfaxtdhyi | Aluminum Stairs |  | Return Sludge PS 2 | Good | C: height of guardrail is less than 920mmNo extension of railing at landing |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c430c1e7d3976fb000009/asset-photo/2Medbmp07YwLRdWGBMUSjw.jpg |  |  |  |  | 43.3877978, -80.3510950 | 2021-10-29 18:51
okvcqhfz4000a476dflkeubco | Exterior hollow metal Door, painted |  | Return Sludge PS 2 | Very Good |  |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c43781e7d3976fb00000a/asset-photo/foNk6rllYpi0JNuJhjdmw.jpg |  |  |  |  | 43.3877696, -80.3510491 | 2021-10-29 18:53
okvcqk7jl000b476dpkcit035 | Louver, stainless steel |  | Return Sludge PS 2 | Good | General ware and tearoò22 |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c44781e7d3976fb00000b/asset-photo/PeIixPDC0pjuhyOZCbc4sg.jpg |  |  |  |  | 43.3877640, -80.3510415 | 2021-10-29 18:56
okvcqovyw000c476dq3ui2rmg | Traffic topping |  | Return Sludge PS 2 | Fair | Ponding , cracks, and minor flaking |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c44e91e7d3976fb00000c/asset-photo/HhDusYovWoRO6GQ9BK+8Ug.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c44e91e7d3976fb00000c/name-plate-photo/VoIaXXkFBMc7zsYVYDXFQ.jpg |  |  |  | 43.3877819, -80.3510040 | 2021-10-29 18:59
okvcqw65m000d476dtbw2y4mn | Foot Traffic Topping, |  | Raw Sludge Pumping Station 1 | Good | General ware and tear and staining |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c46961e7d3976fb00000d/asset-photo/Zg00w4KFkFgxNEmgQwPE3w.jpg |  |  |  |  | 43.3881516, -80.3519344 | 2021-10-29 19:05
okvcr0eer000e476d0q99l8yi | Domed Skylight Aluminum , fall protection grating |  | Raw Sludge Pumping Station 1 | Good |  |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c47091e7d3976fb00000e/asset-photo/kAIWVERYbT3qbqpqMASGlg.jpg |  |  |  |  | 43.3882012, -80.3519222 | 2021-10-29 19:08
okvcj4s780000406dpst0000h | Roof assemblyModified bitumen roofing |  | Bio-Rem Building | Good | Debris on roof |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617fff887d917700b596332f/asset-photo/B1qEKn2iH6r8BGqJvQmAA.jpg |  |  |  |  | 43.3886293, -80.3520035 | 2021-10-29 13:41
okvcjf9e70002406dla0uhejo | Ext. Wall assemblyMasonry veneer, brick and conc block |  | Bio-Rem Building | Good | Staining on wall from duct penetrarion on s wall |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617fff8d097cfe00b5ab5661/asset-photo/y4UC982yUXa5O6qTjXlV+Q.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617fff8d097cfe00b5ab5661/name-plate-photo/gVK8OPuTWQVnpSmUaNbJw.jpg |  |  |  | 43.3878203, -80.3521891 | 2021-10-29 15:36
okvcjjw6s0003406d9ixofdfr | Ext doorHollow metal, painted |  | Bio-Rem Building | Good | Minor rust, weathered paint |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617fff900679ae00b5e74d19/asset-photo/U2NJrwxnguFSpd7fGzmvQ.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617fff900679ae00b5e74d19/name-plate-photo/zgchY0DOiHkADr7I4fc2SQ.jpg |  |  |  | 43.3879354, -80.3521778 | 2021-10-29 15:39
okvcjne520004406dhrizxx3w | Ext. LouverPrefinished |  | Bio-Rem Building | Very Good |  |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617fff916ef76800b5521aae/asset-photo/47c9T7X6nuiE8FsiZuFvew.jpg |  |  |  |  | 43.3879299, -80.3521601 | 2021-10-29 15:42
okvcjph820005406d8j7rsmig | Ceiling finishesPaint, coreslab |  | Bio-Rem Building | Very Good |  |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617fff920679ae00b5e74d1c/asset-photo/zTWKgFC3DpL7t4CHmFmCg.jpg |  |  |  |  | 43.3879030, -80.3521444 | 2021-10-29 15:44
okvcju77u0006406dtonjvg27 | Wall finishesPaint, conc block |  | Bio-Rem Building | Very Good |  |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617fff937d917700b5963332/asset-photo/7GysABJCu90dAHxlRLj0tA.jpg |  |  |  |  | 43.3879040, -80.3520816 | 2021-10-29 15:47
okvck28xr0008406d08ajxntb | Roof accessories Coping, prefinishef | W bldg | Aeration Tank Cell 1 |  |  |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c1952d170114b06000008/asset-photo/EwoyxnpG+8hdFTtwiOIYag.jpg |  |  |  |  | 43.3880043, -80.3521336 | 2021-10-29 15:54
okvck3zgi0009406drl0mofwh | Ext wall assemblyEIFS | W bldg | Aeration Tank Cell 1 |  | Damaged stucco at base, corners and other locations |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c1a45d170114b06000009/asset-photo/LNvrqzullKJU52Uo0GuM1w.jpg | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c1a45d170114b06000009/name-plate-photo/ajd930gk32vftG+ZNfci6A.jpg |  |  |  | 43.3880804, -80.3519805 | 2021-10-29 15:55
okvckic6j000b406djcpk7hqp | Ext louver | W bldg | Aeration Tank Cell 1 |  |  |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617c1ca0d170114b0600000b/asset-photo/0d9rljNpEQYLctKtkKOIag.jpg |  |  |  |  | 43.3880126, -80.3520567 | 2021-10-29 16:06
okvckxbxn000c406dzpoj1wwu | Roof assemblyGravel ballast | S bldg |  |  | Ponding, roof not draining |  | https://cdn.orca.storage/6178141a8b51f600b5891a30/617fffb22e8faa00b5a2f7ae/asset-photo/LAJlHJzRQCiP7UZvRvFmHw.jpg |  |  |  |  | 43.3878233, -80.3522121 | 2021-10-29 16:18