## Sheet1
seqNum | assetTag | facility | Description | Process | building | inspectorName | CategoryCode | installYear | LocationORIGINAL | LocationTag | assetName | manufacturer | TransmitterModel | TransducerModel | TransducerSerial | InstMeva | installationDate | remainingESL | InstType | ServiceArea | FacilityType | LifeCycleCategory | SerialNo | Parent | RotatingItem | Status | Site | condition | COF | defect1 | defect2 | defect3 | observations | RehabRepairCost | RehabRepairYear | RehabRepairCost2 | RehabRepairYear2 | repCost | photoName | repProjectName | rehabProjectName | rehab2ProjectName | InspectionYear | rehabComment1 | rehabCost1 | rehabComment2 | rehabCost2 | defect1Input | defect2Input | defect3Input
5627 | 00041014 | NRH |  |  |  |  | HSS | 2011 | Vestibule | 101118 | Emergency Shower Station | M00074 | [5 empty] | 0 |  | Central | W - Storage Elevated Tank | Health and Safety | N/A |  |  | OPERATING | W-WW | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 2500 | IMG_3128 |  |  |  | 0 |  | 0 |  | 0 | good
5628 | 00040932 | NRH | Diameter: 100mm, Cla-Val Model 52 |  |  |  | PM | 2011 | Valve Room | 101111 | Elevated Tank Pressure Relief Line Pressure Reducing Valve | M00038 | [5 empty] | 15 |  | Central | W - Storage Elevated Tank | Process Mechanical | 442515K |  |  | OPERATING | W-WW | 2 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 3000 | IMG_3601 |  |  |  | 0 |  | 0 |  | 0 | Good
5629 | 00041008 | NRH | Wall-mounted unit heater by Ouellet, 3.0KW/600V/3p |  |  |  | BM | 2011 | Gas Chlorination Room | 101112 | Gas Chlorination Room Electric Heater | M00111 | [5 empty] | 10 |  | Central | W - Storage Elevated Tank | Building Mechanical | N/A |  |  | OPERATING | W-WW | 2 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 3000 | IMG_3759 |  |  |  | 0 |  | 0 |  | 0 | Good
5630 | 00040933 | NRH | NRETCR_TWR_PIT1 |  |  |  | SIC | 2011 | Valve Room | 101111 | Elevated Tank Inlet/Outlet Line Pressure Gauge | M00125 | Sitrans P-300 | N/A | N/A | Pressure |  | 0 |  | Central | W - Storage Elevated Tank | Instrumentation and Control | 7MF8023-1DA14-1MJ7-Z |  |  | OPERATING | W-WW | 0 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 700 | IMG_3219 |  |  |  | 0 |  | 0 |  | 0 | good
5631 | 00086797 | NRH | NRETCR_PCS_NAC1_X1,inside PAC Control Panel |  |  |  | SIC | 2011 | Electrical and SCADA Room | 101114 | PAC Control Panel Network Connection Switch | [6 empty] | 0 |  | Central | W - Storage Elevated Tank |  |  |  |  | OPERATING | W-WW | 0 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 2000 | IMG_3302 |  |  |  | 0 |  | 0 |  | 0 | good
5632 | 00040942 | NRH | Diameter: 450mm, Mueller Model Lineseal III |  |  |  | PM | 2011 | Valve Room | 101111 | Elevated Tank Outlet Line Butterfly Valve | M00671 | [5 empty] | 15 |  | Central | W - Storage Elevated Tank | Process Mechanical | 1375102-5-1-MS |  |  | OPERATING | W-WW | 2 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 5000 | IMG_3558 |  |  |  | 0 |  | 0 |  | 0 | Good
5633 | 00040950 | NRH | Goulds G&L Series 22SSH4K, Imp. diameter: 8.25", 7.5HP, 575V/3/60Hz |  |  |  | PM | 2011 | Valve Room | 101111 | Elevated Tank Circulation Line Centrifugal Circulation Pump and Motor | M00465 | [5 empty] | 15 |  | Central | W - Storage Elevated Tank | Process Mechanical | 22SH4K72D0 |  |  | OPERATING | W-WW | 2 | 4 |  |  |  |  | 0 | 0 | 0 | 0 | 12000 | IMG_3497 |  |  |  | 0 |  | 0 |  | 0 | Good
5634 | 00089687 | NRH | Catalyst IR1101 Rugged Series Router, inside Network Area Panel |  |  |  | SIC | 2011 | Electrical and SCADA Room | 101114 | PAC Control Panel Router | M01002 | [5 empty] | 0 |  | Central | W - Storage Elevated Tank |  | N/A |  |  | OPERATING | W-WW | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 2000 | IMG_3303 |  |  |  | 0 |  | 0 |  | 0 | good
5635 | 00040987 | NRH | Cook square inline fan model SQN-B60: 1/10HP, 120V/1/60Hz, 1458rpm |  |  |  | BM | 2011 | Vestibule | 101118 | Vestibule Supply Fan | M00327 | [5 empty] | 0 |  | Central | W - Storage Elevated Tank | Building Mechanical | 401SD38093-00/005201 |  |  | OPERATING | W-WW | 2 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 6000 | IMG_3727 |  |  |  | 0 |  | 0 |  | 0 | Good
5636 | 00040960 | NRH | Ceiling-mounted unit heater by Ouellet, 7.5KW/600V/3p |  |  |  | BM | 2011 | Valve Room | 101111 | Valve Room Electric Heater 1 | M00111 | [5 empty] | 10 |  | Central | W - Storage Elevated Tank | Building Mechanical | N/A |  |  | OPERATING | W-WW | 2 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 3000 | IMG_3640 |  |  |  | 0 |  | 0 |  | 0 | Good
5637 | 00040982 | NRH | NRETCR_BLDS_TSL3 |  |  |  | SIC | 2011 | Electrical and SCADA Room | 101114 | Electrical & SCADA Room Low Temperature Switch | M00076 | [5 empty] | 0 |  | Central | W - Storage Elevated Tank | Instrumentation and Control | N/A |  |  | OPERATING | W-WW | 0 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 700 | IMG_1465 |  |  |  | 0 |  | 0 |  | 0 | good
5638 | 00041001 | NRH | Instrumentation,Switch,Temperature,Low, NRETCR_BLDS_TSL4 |  |  |  | SIC | 2011 | Ammonium Sulphate Room | 101113 | Ammonium Sulphate Room Low Temperature Switch | M00076 |  |  |  | Temperature |  | 0 |  | Central | W - Storage Elevated Tank | Instrumentation and Control | T631A1063 |  |  | OPERATING | W-WW | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 700 | IMG_3151 |  |  |  | 0 |  | 0 |  | 0 | good
5641 | 00040939 | NRH | Diameter: 450mm, Mueller Model Lineseal III |  |  |  | PM | 2011 | Valve Room | 101111 | Elevated Tank Inlet Line Butterfly Valve | M00671 | [5 empty] | 15 |  | Central | W - Storage Elevated Tank | Process Mechanical | 1120689-25-1-MS |  |  | OPERATING | W-WW | 2 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 5000 | IMG_3520 |  |  |  | 0 |  | 0 |  | 0 | Good
5642 | 00040999 | NRH | NRETCR_SCRB_GCL21 |  |  |  | HSS | 2011 | Gas Chlorination Room | 101112 | Gas Chlorination Room Chlorine Gas Remote Unit | M10086 | A-ULTIMAX-PL-A-28-0-3-2-D-H-0-0-1-1-0-0 (3-WIRE) |  |  | Cl2 Gas |  | 0 |  | Central | W - Storage Elevated Tank | Health and Safety | N/A |  |  | OPERATING | W-WW | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 3000 | IMG_3163 |  |  |  | 0 |  | 0 |  | 0 | good
5643 |  | NRH | Fused, 600V, 200A |  |  |  | ES | 2011 |  | 101114 | Main Fused Disconnect Switch | [6 empty] | 0 |  |  |  |  | 85-624342 |  |  |  |  | 0 | 2 |  |  |  |  | 0 | 2023 | 0 | 0 | 5000 | PXL_20210929_131726628 |  |  |  | 0 | Review arc flash label and replace if necessary. | 500 |  | 0 | good | Arc flash label to be reviewed and replaced if necessary.
5644 | 00086798 | NRH | NRETCR_PCS_NAC1_RAD1, inside PAC Control Panel |  |  |  | SIC | 2011 | Electrical and SCADA Room | 101114 | PAC Control Panel Radio 1 | [6 empty] | 0 |  | Central | W - Storage Elevated Tank |  |  |  |  | OPERATING | W-WW | 0 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 2000 | IMG_3303 |  |  |  | 0 |  | 0 |  | 0 | good
5645 | 00040930 | NRH | Diameter: 50mm, Val-matic Model 201C |  |  |  | PM | 2011 | Valve Room | 101111 | Elevated Tank Inlet/Outlet Line Air Release Valve | M00926 | [5 empty] | 15 |  | Central | W - Storage Elevated Tank | Process Mechanical | SERIES 100S |  |  | OPERATING | W-WW | 2 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 2500 | IMG_3609 |  |  |  | 0 |  | 0 |  | 0 | Good
5646 | 00040945 | NRH | Diameter: 450mm, Mueller Model Lineseal III |  |  |  | PM | 2011 | Valve Room | 101111 | Elevated Tank Outlet Line Butterfly Valve | M00671 | [5 empty] | 15 |  | Central | W - Storage Elevated Tank | Process Mechanical | N/A |  |  | OPERATING | W-WW | 2 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 5000 | IMG_3569 |  |  |  | 0 |  | 0 |  | 0 | Good
5647 | 00040957 | NRH | NRETCR_TWR_AIT2 |  |  |  | SIC | 2011 | Valve Room | 101111 | Outlet Total Chlorine Analyzer | M00482 | CL-17 |  |  | Chlorine |  | 0 |  | Central | W - Storage Elevated Tank | Instrumentation and Control | 1.012003774E+011 |  |  | OPERATING | W-WW | 0 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 28000 | IMG_3201 |  |  |  | 0 |  | 0 |  | 0 | good
5648 | 00040985 | NRH | Cook square inline fan model SQN-B60: 1/10HP, 120V/1/60Hz, 1787rpm |  |  |  | BM | 2011 | Electrical and SCADA Room | 101114 | Electrical & SCADA Room Exhaust Fan | M00327 | [5 empty] | 10 |  | Central | W - Storage Elevated Tank | Building Mechanical | 401SD38093-00/001801 |  |  | OPERATING | W-WW | 2 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 6000 | IMG_3314 |  |  |  | 0 |  | 0 |  | 0 | Good
5649 | 00041013 | NRH | Wall-mounted unit heater by Ouellet, 3.0KW/600V/3p |  |  |  | BM | 2011 | Vestibule | 101118 | Vestibule Electric Heater | M00111 | [5 empty] | 10 |  | Central | W - Storage Elevated Tank | Architectural | N/A |  |  | OPERATING | W-WW | 2 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 3000 | IMG_3721 |  |  |  | 0 |  | 0 |  | 0 | Good
5650 |  | NRH |  |  |  |  | ES | 2010 |  | 101117 | Power Meter | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 2023 | 0 | 0 | 6000 | PXL_20210929_130237499 |  |  |  | 0 | Install arc flash label for the enclosure | 500 |  | 0 | Poor | The hydro meter enclosure was observed to be severly damaged to the point that one of the doors is out of hinge. | Arc flash label for the enclosure is outdated and severly damaged.
5652 | 00040943 | NRH | NRETCR_TWR_LIT1 |  |  |  | SIC | 2011 | Valve Room | 101111 | Elevated Tank Level Transmitter and Gauge | M00125 | Sitrans P-300 |  |  | Level |  | 0 |  | Central | W - Storage Elevated Tank | Instrumentation and Control | 7MF8023-1DA14-1MJ7-Z |  |  | OPERATING | W-WW | 0 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 4500 | IMG_3271 |  |  |  | 0 |  | 0 |  | 0 | good
5653 | 00041007 | NRH | NRETCR_BLDS_TSL2 |  |  |  | SIC | 2011 | Gas Chlorination Room | 101112 | Gas Chlorination Room Low Temperature Switch | M00076 |  |  |  | Temperature |  | 0 |  | Central | W - Storage Elevated Tank | Instrumentation and Control | T631A 1063 |  |  | OPERATING | W-WW | 0 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 700 | IMG_3151 |  |  |  | 0 |  | 0 |  | 0 | good
5654 | 00040941 | NRH | Diameter: 450mm, Val-matic Swing-Flex Model No. 518A |  |  |  | PM | 2011 | Valve Room | 101111 | Elevated Tank Outlet Line Check Valve | M00926 | [5 empty] | 15 |  | Central | W - Storage Elevated Tank | Process Mechanical | MODEL 518A |  |  | OPERATING | W-WW | 2 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 7500 | IMG_3548 |  |  |  | 0 |  | 0 |  | 0 | minor corrosion
5655 | 00040947 | NRH | Diameter: 200mm, Mueller Model |  |  |  | PM | 2011 | Valve Room | 101111 | Elevated Tank Drain Line Gate Valve | M00671 | [5 empty] | 15 |  | Central | W - Storage Elevated Tank | Process Mechanical | FIG 2360 |  |  | OPERATING | W-WW | 2 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 3000 | IMG_3584 |  |  |  | 0 |  | 0 |  | 0 | Good
5656 | 00040988 | NRH | Cook square inline fan model SQN-B60: 1/10HP, 120V/1/60Hz, 1615rpm |  |  |  | BM | 2011 | Vestibule | 101118 | Vestibule Exhaust Fan | M00327 | [5 empty] | 10 |  | Central | W - Storage Elevated Tank | Building Mechanical | 401SD38093-00/002901 |  |  | OPERATING | W-WW | 2 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 6000 | IMG_3729 |  |  |  | 0 |  | 0 |  | 0 | Good
5657 |  | NRH | Summary: 12 small wall-mounted lights, 11 remote head, 3 exit, 19 linear lights |  |  |  | ES | 2011 |  | 101119 | Indoor Lighting | [6 empty] | 0 |  |  |  |  | 85-624342 |  |  |  |  | 0 | 2 |  |  |  |  | 0 | 2027 | 0 | 0 | 42000 | PXL_20210929_132550293 |  |  |  | 0 | Non-LED fixtures to be replaced with LED fixture in the next capital upgrade. | 20000 |  | 0 | good
5658 |  | NRH |  |  |  |  | ES | 2011 |  | 101115 | Emergency Gas Scurbber System Panel | [6 empty] | 0 |  |  |  |  | 85-624342 |  |  |  |  | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 12000 | PXL_20210929_130707737 |  |  |  | 0 |  | 0 |  | 0 | good
5659 | 00040971 | NRH | NRETCR_PCS_CP1 |  |  |  | SIC | 2011 | Electrical and SCADA Room | 101114 | PAC Control Panel | [6 empty] | 0 |  | Central | W - Storage Elevated Tank | SCADA | N/A |  |  | OPERATING | W-WW | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 75000 | IMG_3303 |  |  |  | 0 |  | 0 |  | 0 | good
5660 | 00040935 | NRH | Diameter: 300mm, Mueller Model FL, electric actuator by Rotork |  |  |  | PM | 2011 | Valve Room | 101111 | Elevated Tank Inlet/Outlet Line Butterfly Valve | M00114 | [5 empty] | 15 |  | Central | W - Storage Elevated Tank | Process Mechanical | 1375738-1-1 MS |  |  | OPERATING | W-WW | 2 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 3500 | IMG_3597 |  |  |  | 0 |  | 0 |  | 0 | Good
5661 | 00040936 | NRH | Rotork electric actuator, 30-120rpm, 0.45V motor rating, 575-3-60 motor supply |  |  |  | PM | 2011 | Valve Room | 101111 | Elevated Tank Inlet/Outlet Line Butterfly Valve Electric Actuator | M00120 | [5 empty] | 15 |  | Central | W - Storage Elevated Tank | Process Mechanical | D144230101 |  |  | OPERATING | W-WW | 2 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 5000 | IMG_3597 |  |  |  | 0 |  | 0 |  | 0 | Good
5662 | 00040955 | NRH | Diameter: 63mm, Watts Model 909 |  |  |  | PM | 2011 | Valve Room | 101111 | Elevated Tank Drain Line Reduced Pressure Principle Backflow Preventer | M00145 | [5 empty] | 15 |  | Central | W - Storage Elevated Tank | Process Mechanical | 125711 |  |  | OPERATING | W-WW | 2 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 3500 | IMG_3508 |  |  |  | 0 |  | 0 |  | 0 | Good
5663 | 00040961 | NRH | Ceiling-mounted unit heater by Ouellet, 7.5KW/600V/3p |  |  |  | BM | 2011 | Valve Room | 101111 | Valve Room Electric Heater 2 | M00111 | [5 empty] | 10 |  | Central | W - Storage Elevated Tank | Building Mechanical | N/A |  |  | OPERATING | W-WW | 2 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 3000 | IMG_3639 |  |  |  | 0 |  | 0 |  | 0 | Good
5664 | 00040994 | NRH | Instrumentation,Gas Detectors,Chlorine, NRETCR_CL2D_GCL22 |  |  |  | SIC | 2011 | Gas Chlorination Room | 101112 | Atrium Ammonia Gas Monitor | M10086 | A-ULTIMAX-PL-A-28-0-3-2-D-H-0-0-1-1-0-0 (3-WIRE) |  |  | Cl2 Gas |  | 0 |  | Central | W - Storage Elevated Tank | Health and Safety | A11-3642386-10-001 |  |  | OPERATING | W-WW | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 3000 | IMG_3179 |  |  |  | 0 |  | 0 |  | 0 | good
5665 | 00040937 | NRH | NRETCR_TWR_FIT1 |  |  |  | SIC | 2011 | Valve Room | 101111 | Elevated Tank Inlet/Outlet Line Flowmeter Transmitter | M00125 | MAG6000 |  |  | Flow |  | 0 |  | Central | W - Storage Elevated Tank | Process Mechanical | 092502H500 |  |  | OPERATING | W-WW | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 4500 | IMG_3202 |  |  |  | 0 |  | 0 |  | 0 | good
5666 | 00086800 | NRH | NRETCR_TWR_FIT1 |  |  |  | SIC | 2011 | Valve Room | 101111 | Tank Inlet Line Flow Sensor | [6 empty] | 0 |  | Central | W - Storage Elevated Tank |  |  |  |  | OPERATING | W-WW | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 700 | IMG_3220 |  |  |  | 0 |  | 0 |  | 0 | good
5667 | 00086795 | NRH | inside PAC Control Panel |  |  |  | SIC | 2011 | Electrical and SCADA Room | 101114 | PAC Control Panel UPS | [6 empty] | 0 |  | Central | W - Storage Elevated Tank |  |  |  |  | OPERATING | W-WW | 0 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 3500 | IMG_3304 |  |  |  | 0 |  | 0 |  | 0 | good
5668 | 00040986 | NRH | Cook square inline fan model SQN-B80: 1/3HP, 120V/1/60Hz, 2262rpm |  |  |  | BM | 2011 | Valve Room | 101111 | Valve Room Exhaust Fan | M00327 | [5 empty] | 10 |  | Central | W - Storage Elevated Tank | Building Mechanical | 401SD38093-00/000701 |  |  | OPERATING | W-WW | 2 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 6000 | IMG_3316 |  |  |  | 0 |  | 0 |  | 0 | Good
5669 | 00040954 | NRH | Diameter: 75mm, Mueller Model |  |  |  | PM | 2011 | Valve Room | 101111 | Elevated Tank Circulation Line Gate Valve 3 | M00671 | [5 empty] | 15 |  | Central | W - Storage Elevated Tank | Process Mechanical | FIG 2360 |  |  | OPERATING | W-WW | 2 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 2000 | IMG_3516 |  |  |  | 0 |  | 0 |  | 0 | Good
5670 | 00040989 | NRH | Cook square inline fan model SQN-B60: 1/10HP, 120V/1/60Hz, 1615rpm |  |  |  | BM | 2011 | Ammonium Sulphate Room | 101113 | Ammonium Sulphate Room Exhaust Fan | M00327 | [5 empty] | 10 |  | Central | W - Storage Elevated Tank | Building Mechanical | 401SD38093-00/002902 |  |  | OPERATING | W-WW | 2 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 6000 | IMG_3326 |  |  |  | 0 |  | 0 |  | 0 | Good
5671 | 00086794 | NRH | inside PAC Control Panel |  |  |  | SIC | 2011 | Electrical and SCADA Room | 101114 | PAC Control Panel CPU | [6 empty] | 0 |  | Central | W - Storage Elevated Tank |  |  |  |  | OPERATING | W-WW | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 2000 | IMG_3304 |  |  |  | 0 |  | 0 |  | 0 | good
5672 | 00086793 | NRH | NRETCR_PCS_OIT1 |  |  |  | SIC | 2011 | Electrical and SCADA Room | 101114 | PAC Control Panel OIT | [6 empty] | 0 |  | Central | W - Storage Elevated Tank |  |  |  |  | OPERATING | W-WW | 0 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 2000 | IMG_3304 |  |  |  | 0 |  | 0 |  | 0 | good
5673 | 00040938 | NRH | Diameter: 450mm, Cla-Val Model 631-06BCDNSYKCX |  |  |  | PM | 2011 | Valve Room | 101111 | Elevated Tank Inlet Line Flow Control, Altitude & Check Valve | M00038 | [5 empty] | 15 |  | Central | W - Storage Elevated Tank | Process Mechanical | 20802001E |  |  | OPERATING | W-WW | 2 | 4 | Needs maintenance for leaking seal on the valve top |  |  |  | 0 | 0 | 0 | 0 | 10000 | IMG_3526 |  |  |  | 0 |  | 0 |  | 0 | minor corrosion
5674 | 00086799 | NRH | NRETCR_PCS_NAC1_RAD2, inside PAC Control Panel |  |  |  | SIC | 2011 | Electrical and SCADA Room | 101114 | PAC Control Panel Radio 2 | [6 empty] | 0 |  | Central | W - Storage Elevated Tank |  |  |  |  | OPERATING | W-WW | 0 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 2000 | IMG_3303 |  |  |  | 0 |  | 0 |  | 0 | good
5675 | 00041019 | NRH | Eemax model SP3012: 3KW, 120VAC |  |  |  | BM | 2011 | Vestibule | 101118 | Vestibule Tankless Water Heater | M01078 | [5 empty] | 10 |  | Central | W - Storage Elevated Tank | Building Mechanical | 1001048 |  |  | OPERATING | W-WW | 2 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 1000 | IMG_3732 |  |  |  | 0 |  | 0 |  | 0 | Good
5676 | 00040948 | NRH | Diameter: 100mm, Mueller Model |  |  |  | PM | 2011 | Valve Room | 101111 | Elevated Tank Circulation Line Gate Valve 1 | M00671 | [5 empty] | 15 |  | Central | W - Storage Elevated Tank | Process Mechanical | FIG 2360 |  |  | OPERATING | W-WW | 2 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 2000 | IMG_3555 |  |  |  | 0 |  | 0 |  | 0 | Good
5677 | 00040931 | NRH | Diameter: 100mm, Mueller Model |  |  |  | PM | 2011 | Valve Room | 101111 | Elevated Tank Pressure Relief Line Gate Valve | M00671 | [5 empty] | 15 |  | Central | W - Storage Elevated Tank | Process Mechanical | FIG. 2360 |  |  | OPERATING | W-WW | 2 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 2000 | IMG_3602 |  |  |  | 0 |  | 0 |  | 0 | Good
5678 | 00040962 | NRH | NRETCR_BLDS_TSL1 |  |  |  | SIC | 2011 | Valve Room | 101111 | Valve Room Lower Temperature Switch | M00076 |  |  |  | Temperature |  | 0 |  | Central | W - Storage Elevated Tank | Instrumentation and Control | T631A 1063 |  |  | OPERATING | W-WW | 0 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 700 | IMG_3185 |  |  |  | 0 |  | 0 |  | 0 | good
5679 | 00041015 | NRH | NRETCR_HS_EYEW1_FSH1 |  |  |  | SIC | 2011 | Vestibule | 101118 | Eyewash Station & Emergency Shower Flow Sensor | [6 empty] | 0 |  | Central | W - Storage Elevated Tank | Instrumentation and Control | N/A |  |  | OPERATING | W-WW | 0 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 700 | IMG_3130 |  |  |  | 0 |  | 0 |  | 0 | good
5681 | 00047862 | NRH | Diameter: 38mm backflow preventer, Watts Model 007QTS |  |  |  | PM | 2011 | Valve Room | 101111 | Elevated Tank Potable Cold Water Line Double Check Valve Bacfklow Preventer | M00145 | [5 empty] | 15 |  | Central | W - Storage Elevated Tank | Process Mechanical | 107514 |  |  | OPERATING | W-WW | 2 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 2000 | IMG_3476 |  |  |  | 0 |  | 0 |  | 0 | Good
5682 | 00040963 | NRH | Eemax model EX240T2T EE: 24KW, 120/208 |  |  |  | BM | 2011 | Valve Room | 101111 | Valve Room Tankless Water Heater | M01078 | [5 empty] | 10 |  | Central | W - Storage Elevated Tank | Building Mechanical | 995248 |  |  | OPERATING | W-WW | 2 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 4000 | IMG_3480 |  |  |  | 0 |  | 0 |  | 0 | Good
5683 | 00040953 | NRH | Diameter: 75mm, Mueller Model |  |  |  | PM | 2011 | Valve Room | 101111 | Elevated Tank Circulation Line Gate Valve 2 | M00671 | [5 empty] | 15 |  | Central | W - Storage Elevated Tank | Process Mechanical | FIG 2360 |  |  | OPERATING | W-WW | 2 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 2000 | IMG_3503 |  |  |  | 0 |  | 0 |  | 0 | Good
5684 | 00047861 | NRH | Diameter: 50mm, Watts Model 909-S |  |  |  | PM | 2011 | Valve Room | 101111 | Elevated Tank Potable Cold Water Line Reduced Pressure Principle Backflow Preventer Potable Cold Water Line Reduced Pressure Principle Backflow Preventer | M00145 | [5 empty] | 15 |  | Central | W - Storage Elevated Tank | Process Mechanical | 459528 |  |  | OPERATING | W-WW | 2 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 2000 | IMG_3478 |  |  |  | 0 |  | 0 |  | 0 | Good
5685 | 00041003 | NRH | Wall-mounted unit heater by Ouellet, 3.0KW/600V/3p |  |  |  | BM | 2011 | Ammonium Sulphate Room | 101113 | Ammonium Sulphate Room Electric Heater | M00111 | [5 empty] | 10 |  | Central | W - Storage Elevated Tank | Building Mechanical | N/A |  |  | OPERATING | W-WW | 2 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 3000 | IMG_3786 |  |  |  | 0 |  | 0 |  | 0 | Good
5686 | 00040952 | NRH | Diameter: 75mm, Val-matic Swing-Flex Model No. 503A |  |  |  | PM | 2011 | Valve Room | 101111 | Elevated Tank Circulation Line Check Valve | M00926 | [5 empty] | 15 |  | Central | W - Storage Elevated Tank | Process Mechanical | 503A |  |  | OPERATING | W-WW | 2 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 3000 | IMG_3499 |  |  |  | 0 |  | 0 |  | 0 | Good
5687 | 00040983 | NRH | Wall-mounted unit heater by Ouellet, 5KW/600V/3p |  |  |  | BM | 2011 | Electrical and SCADA Room | 101114 | Electrical & SCADA Room Electric Heater | M00111 | [5 empty] | 10 |  | Central | W - Storage Elevated Tank | Building Mechanical | N/A |  |  | OPERATING | W-WW | 2 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 3000 | IMG_3456 |  |  |  | 0 |  | 0 |  | 0 | Good
5688 | 00086808 | NRH | NRETCR_BLDS_SU1_LSHH1 |  |  |  | SIC | 2011 | Gas Chlorination Room | 101112 | Gas Chlorination Room Sump Level Switch | [6 empty] | 0 |  | Central | W - Storage Elevated Tank |  |  |  |  | OPERATING | W-WW | 0 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 1500 | IMG_3779 |  |  |  | 0 |  | 0 |  | 0 | good
5689 |  | NRH |  |  |  |  | ES | 2010 |  | 101111 | Circulating Pump Starter | [6 empty] | 0 | [9 empty] | 0 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 5000 | PXL_20210929_132252439 |  |  |  | 0 |  | 0 |  | 0 | good
5690 | 00087414 | NRH | Diameter: 13 mm, Watts Model 007QT |  |  |  | PM | 2011 | Ammonium Sulphate Room | 101113 | Backflow Preventer | [6 empty] | 15 |  | Central | W - Storage Elevated Tank |  |  |  |  | OPERATING | W-WW | 2 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 1200 | IMG_3760 |  |  |  | 0 |  | 0 |  | 0 | Good
5691 | 00040956 | NRH | Instrumentation,Analysers,Chlorine,Total Chlorine,CL17, NRETCR_TWR_AIT1 |  |  |  | SIC | 2011 | Valve Room | 101111 | Inlet Total Chlorine Analyzer | M00482 | CL-17 |  |  | Chlorine |  | 0 |  | Central | W - Storage Elevated Tank | Instrumentation and Control | 1.0120037737E+012 |  |  | OPERATING | W-WW | 0 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 28000 | IMG_3204 |  |  |  | 0 |  | 0 |  | 0 | good
5692 |  | NRH | 2 flood light, 2 pole lights |  |  |  | ES | 2011 |  | 101119 | Outdoor Lighting | [6 empty] | 0 |  |  |  |  | 85-624342 |  |  |  |  | 0 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 12000 | PXL_20210929_130211337 |  |  |  | 0 |  | 0 |  | 0 | good
5693 |  | NRH | 600V, 100A |  |  |  | ES | 2010 |  | 101111 | Water Heater Fused Disconnect Switch | [6 empty] | 0 | [9 empty] | 0 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 4000 | PXL_20210929_132246213 |  |  |  | 0 | Install arc flash label. | 500 | 2 | 0 | good | missing arc flash label
5694 | 00040990 | NRH | FRP Radial Fume Exhauster |  |  |  | BM | 2011 | Gas Chlorination Room | 101115 | Chlorine Scrubber Blower | M00742 | [5 empty] | 15 |  | Central | W - Storage Elevated Tank | Building Mechanical | F10-1920 |  |  | OPERATING | W-WW | 2 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 20000 | IMG_3690 |  |  |  | 0 |  | 0 |  | 0 | Good
5695 | 00045455 | NRH | NRETCR_TWR_LCV1_POS1 |  |  |  | SIC | 2011 | Valve Room | 101111 | Tank Inlet Line Attitude Valve Controller and Transmitter | [6 empty] | 0 | [7 empty] | OPERATING | W-WW | 0 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 15000 | IMG_3252 |  |  |  | 0 |  | 0 |  | 0 | good
5698 |  | NRH | floor drain within the facility |  |  |  | BM | 2011 |  | 101111 | Floor Drain | [6 empty] | 0 | [9 empty] | 5 | 2 | Brocken cover and potentially clogged sewer; need repair and cleaning |  |  |  | 0 | 0 | 0 | 0 | 30000 | IMG_3207 |  |  |  | 0 |  | 0 |  | 0 | Floor water condensation near sampling drain.
5699 |  | NRH | Not in service. |  |  |  | HSS | 2011 |  | 101113 | Ammonia Gas Detector Remote Unit | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 3000 | IMG_3140 |  |  |  | 0 |  | 0 |  | 0 | good
5700 |  | NRH |  |  |  |  | HSS | 2011 |  | 101113 | Ammonium Sulphate Room Smoke Detector | [6 empty] | 0 | [9 empty] | 0 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 800 | IMG_3145 |  |  |  | 0 |  | 0 |  | 0 | good
5701 |  | NRH |  |  |  |  | HSS | 2011 |  | 101112 | Gas Chlorination Room Smoke Detector | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 800 | IMG_3154 |  |  |  | 0 |  | 0 |  | 0 | The smoke detector was covered.
5702 |  | NRH | Manufacturer: Bosch |  |  |  | SIC | 2011 |  |  | Facility Security System Panel | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 42000 | IMG_3169 |  |  |  | 0 |  | 0 |  | 0 | good
5703 |  | NRH | Manufacturer: Bosch |  |  |  | SIC | 2011 |  |  | Facility Security System Touchpad | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 2500 | IMG_3171 |  |  |  | 0 |  | 0 |  | 0 | good
5704 | 00040994 | NRH |  |  |  |  | HSS | 2011 |  | 101112 | Gas Chlorination Room Chlorine Gas Detector | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 3000 | IMG_3181 |  |  |  | 0 |  | 0 |  | 0 | good
5706 |  | NRH |  |  |  |  | HSS | 2011 |  | 101111 | Valve Room Smoke Detector | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 800 | IMG_3210 |  |  |  | 0 |  | 0 |  | 0 | good
5707 | 00040995 | NRH | Not in service. |  |  |  | HSS | 2011 |  | 101113 | Ammonia Gas Detector | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 3000 | IMG_3179 |  |  |  | 0 |  | 0 |  | 0 | good
5708 |  | NRH | Total of 3. |  |  |  | HSS | 2010 |  | 101116 | Fire Extinguisers | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 500 | IMG_3187 |  |  |  | 0 |  | 0 |  | 0 | good
5841 |  | NRH |  |  |  |  | SC | 2011 |  | 101113 | Ammonium Sulphate Room Concrete Floor Slab | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 20000 | IMG_9038 |  |  |  | 0 |  | 0 |  | 0 | Good
5842 |  | NRH |  |  |  |  | SC | 2011 |  | 101113 | Ammonium Sulphate Room Composite Roof Slab | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 25000 | IMG_9040 |  |  |  | 0 |  | 0 |  | 0 | Good
5843 |  | NRH |  |  |  |  | SC | 2011 |  | 101113 | Ammonium Sulphate Room Masonry Blockwall Ammonium Sulphate Room Masonry Block Wall | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 30000 | IMG_9039 |  |  |  | 0 |  | 0 |  | 0 | Good
5844 |  | NRH |  |  |  |  | SC | 2011 |  | 101115 | Atrium Concrete Floor Slab Floor Slab | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 25000 | IMG_9044 |  |  |  | 0 |  | 0 |  | 0 | Good
5845 |  | NRH |  |  |  |  | SC | 2011 |  | 101115 | Atrium Masonry Block Wall Atrium Masonry Block Wall | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 25000 | IMG_9044 |  |  |  | 0 |  | 0 |  | 0 | Good
5846 |  | NRH |  |  |  |  | SC | 2011 |  | 101112 | Gas Chlorination Room Concrete Floor Slab | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 6000 | IMG_9041 |  |  |  | 0 |  | 0 |  | 0 | Good
5847 |  | NRH |  |  |  |  | SC | 2011 |  | 101115 | Atrium Aluminum Guardrail | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 8000 | IMG_9045 |  |  |  | 0 |  | 0 |  | 0 | Good
5849 |  | NRH |  |  |  |  | SC | 2011 |  | 101112 | Gas Chlorination Concrete Roof Slab | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 7000 | IMG_9042 |  |  |  | 0 |  | 0 |  | 0 | Good
5850 |  | NRH |  |  |  |  | SC | 2011 |  | 101112 | Gas Chlorination Masonry Blockwall | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 15000 | IMG_9041 |  |  |  | 0 |  | 0 |  | 0 | Good
5851 |  | NRH |  |  |  |  | SC | 2011 |  | 101114 | Electrical and SCADA Room Concrete Floor Slab | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 21000 | IMG_9050 |  |  |  | 0 |  | 0 |  | 0 | Good
5852 |  | NRH |  |  |  |  | SC | 2011 |  | 101114 | Electrical and SCADA Room Composite Roof Slab | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 23000 | IMG_9051 |  |  |  | 0 |  | 0 |  | 0 | Good
5853 |  | NRH |  |  |  |  | SC | 2011 |  | 101114 | Electrical and SCADA Room Masonry Blockwall | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 23000 | IMG_9053 |  |  |  | 0 |  | 0 |  | 0 | Good
5855 |  | NRH |  |  |  |  | SC | 2011 |  | 101119 | Elevated Tank Concrete Foundation | [6 empty] | 0 | [9 empty] | 0 | 4 |  |  |  |  | 0 | 0 | 0 | 0 | 600000 |  |  |  |  | 0 |  | 0 |  | 0 | Good
5856 |  | NRH |  |  |  |  | SC | 2011 |  | 101116 | Elevated Tank Concrete Pedestal | [6 empty] | 0 | [9 empty] | 0 | 4 |  |  |  |  | 0 | 0 | 0 | 0 | 1100000 | IMG_9028 |  |  |  | 0 |  | 0 |  | 0 | Good
5857 |  | NRH |  |  |  |  | SC | 2011 |  | 101119 | Elevated Tank Exterior Coating | [6 empty] | 0 | [9 empty] | 0 | 4 |  |  |  |  | 0 | 0 | 0 | 0 | 1000000 | IMG_9027 |  |  |  | 0 |  | 0 |  | 0 | Good
5858 |  | NRH |  |  |  |  | SC | 2011 |  | 101119 | Elevated Tank Interior Coating | [6 empty] | 0 | [9 empty] | 0 | 4 |  |  |  |  | 0 | 0 | 0 | 0 | 550000 |  |  |  |  | 0 |  | 0 |  | 0 | Good
5859 |  | NRH |  |  |  |  | SC | 2011 |  | 101119 | Elevated Tank Guardrail Elevated Tank Roof Guardrail | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 40000 | IMG_9111 |  |  |  | 0 |  | 0 |  | 0 | Good
5860 |  | NRH |  |  |  |  | SC | 2011 |  | 101119 | Elevated Tank Steel Tank | [6 empty] | 0 | [9 empty] | 0 | 5 |  |  |  |  | 0 | 0 | 0 | 0 | 1100000 | IMG_9027 |  |  |  | 0 |  | 0 |  | 0 | Good
5861 |  | NRH |  |  |  |  | SC | 2011 |  | 101111 | Valve Room Concrete Floor Slab | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 72000 | IMG_9047 |  |  |  | 0 |  | 0 |  | 0 | Good | Minor harilne cracking noted
5862 |  | NRH |  |  |  |  | SC | 2011 |  | 101111 | Valve Room Composite Roof Slab | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 80000 | IMG_9046 |  |  |  | 0 |  | 0 |  | 0 | Good
5863 |  | NRH |  |  |  |  | SC | 2011 |  | 101111 | Valve Room Mansonry Block Wall | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 50000 | IMG_9048 |  |  |  | 0 |  | 0 |  | 0 | Good
5864 |  | NRH |  |  |  |  | SC | 2011 |  | 101118 | Vestibule Concrete Floor Slab | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 7000 | IMG_9036 |  |  |  | 0 |  | 0 |  | 0 | Good
5865 |  | NRH |  |  |  |  | SC | 2011 |  | 101118 | Vestibule Composite Roof Slab | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 8000 | IMG_9034 |  |  |  | 0 |  | 0 |  | 0 | Good
5866 |  | NRH |  |  |  |  | SC | 2011 |  | 101118 | Vestibule Masonry Blockwall | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 15000 | IMG_9034 |  |  |  | 0 |  | 0 |  | 0 | Good
5867 |  | NRH |  |  |  |  | SC | 2011 |  | 101117 | Valve Chamber Access Hatch | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 5000 | IMG_9075 |  |  |  | 0 |  | 0 |  | 0 | Good
5868 |  | NRH |  |  |  |  | SC | 2011 |  | 101117 | Valve Chamber Access Ladder | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 5000 | IMG_9071 |  |  |  | 0 |  | 0 |  | 0 | Good
5869 |  | NRH |  |  |  |  | SC | 2011 |  | 101117 | Valve Chamber Concrete Structure | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 100000 | IMG_9073 |  |  |  | 0 |  | 0 |  | 0 | Good
5870 |  | NRH | Ground to platform |  |  |  | SC | 2011 |  | 101116 | Elevated Tank Ladder (Base to Platform) | [6 empty] | 0 | [9 empty] | 0 | 4 |  |  |  |  | 0 | 0 | 0 | 0 | 20000 | IMG_9068 |  |  |  | 0 |  | 0 |  | 0 | Good
5871 |  | NRH | Platform to tank exterior |  |  |  | SC | 2011 |  | 101116 | Elevated Tank Ladder (Platform to Roof) | [6 empty] | 0 | [9 empty] | 0 | 4 |  |  |  |  | 0 | 0 | 0 | 0 | 8000 | IMG_9130 |  |  |  | 0 |  | 0 |  | 0 | Good
5872 |  | NRH | Platform to u/s tank |  |  |  | SC | 2011 |  | 101116 | Elevated Tank Ladder (Platform to U/S Tank) | [6 empty] | 0 | [9 empty] | 0 | 4 |  |  |  |  | 0 | 0 | 0 | 0 | 3000 | IMG_9099 |  |  |  | 0 |  | 0 |  | 0 | Good
5873 |  | NRH |  |  |  |  | SC | 2011 |  | 101116 | Elevated Tank Roof Hatch 1 | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 5000 | IMG_9129 |  |  |  | 0 |  | 0 |  | 0 | Good
5874 |  | NRH |  |  |  |  | SC | 2011 |  | 101116 | Elevated Tank Roof Hatch 2 | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 5000 | IMG_9127 |  |  |  | 0 |  | 0 |  | 0 | Good
5875 |  | NRH |  |  |  |  | SC | 2011 |  | 101116 | Elevated Tank Roof Hatch/Vent | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 5000 | IMG_9128 |  |  |  | 0 |  | 0 |  | 0 | Good
5876 |  | NRH |  |  |  |  | HSS | 2011 |  | 101116 | Elevated Tank Davit Arm Base | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 5000 | IMG_9131 |  |  |  | 0 |  | 0 |  | 0 | Good
5877 |  | NRH |  |  |  |  | SC | 2011 |  | 101116 | Elevated Tank Tank Hatch | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 5000 | IMG_9099 |  |  |  | 0 |  | 0 |  | 0 | Good
5878 |  | NRH |  |  |  |  | SW | 2011 |  | 101117 | Dechlorination Chamber Access Ladder | [6 empty] | 0 | [9 empty] | 0 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 2000 | IMG_9091 |  |  |  | 0 |  | 0 |  | 0 | Good
5879 |  | NRH |  |  |  |  | SW | 2011 |  | 101117 | Dechlorination Chamber Concrete Structure | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 10000 | IMG_9091 |  |  |  | 0 |  | 0 |  | 0 | Good
5880 |  | NRH |  |  |  |  | SW | 2011 |  | 101117 | Dechlorination Chamber Manhole Frame and Cover | [6 empty] | 0 | [9 empty] | 0 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 3000 | IMG_9090 |  |  |  | 0 |  | 0 |  | 0 | Good
5881 |  | NRH |  |  |  |  | SC | 2011 |  | 101116 | Elevated Tank Platform | [6 empty] | 0 | [9 empty] | 0 | 4 |  |  |  |  | 0 | 0 | 0 | 0 | 50000 | IMG_9095 |  |  |  | 0 |  | 0 |  | 0 | Good
5882 |  | NRH |  |  |  |  | SC | 2011 |  | 101115 | Atrium Aluminum Staircase | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 15000 | IMG_9045 |  |  |  | 0 |  | 0 |  | 0 | Good
5883 |  | NRH |  |  |  |  | AC | 2011 |  | 101113 | Ammonium Sulphate Room Access Door (Single) | [6 empty] | 0 | [9 empty] | 0 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 3500 | IMG_9037 |  |  |  | 0 |  | 0 |  | 0 | good
5884 |  | NRH |  |  |  |  | AC | 2011 |  | 101113 | Ammonium Sulphate Room Protective Floor Coating | [6 empty] | 0 | [9 empty] | 0 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 12000 | IMG_9039 |  |  |  | 0 |  | 0 |  | 0 | good
5885 |  | NRH |  |  |  |  | AC | 2011 |  | 101113 | Ammonium Sulphate Room Wall Paint | [6 empty] | 0 | [9 empty] | 0 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 2500 | IMG_9039 |  |  |  | 0 |  | 0 |  | 0 | good
5886 |  | NRH |  |  |  |  | AC | 2011 |  | 101113 | Ammonium Sulphate Room Interior Window | [6 empty] | 0 | [9 empty] | 0 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 3000 | IMG_9039 |  |  |  | 0 |  | 0 |  | 0 | good
5887 |  | NRH |  |  |  |  | AC | 2011 |  | 101118 | Vestibule Access Door (Single) | [6 empty] | 0 | [9 empty] | 0 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 3500 | IMG_9031 |  |  |  | 0 |  | 0 |  | 0 | corrosion on hardware
5888 |  | NRH |  |  |  |  | AC | 2011 |  | 101118 | Vestibule Protective Floor Coating | [6 empty] | 0 | [9 empty] | 0 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 5000 | IMG_9035 |  |  |  | 0 |  | 0 |  | 0 | good
5889 |  | NRH |  |  |  |  | AC | 2011 |  | 101118 | Vestibule Wall Paint | [6 empty] | 0 | [9 empty] | 0 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 1500 | IMG_9035 |  |  |  | 0 |  | 0 |  | 0 | good
5890 |  | NRH |  |  |  |  | AC | 2011 |  | 101112 | Gas Chlorination Room Access Door (Single) | [6 empty] | 0 | [9 empty] | 0 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 3500 | IMG_9034 |  |  |  | 0 |  | 0 |  | 0 | good
5891 |  | NRH |  |  |  |  | AC | 2011 |  | 101112 | Gas Chlorination Room Interior Window | [6 empty] | 0 | [9 empty] | 0 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 6000 | IMG_9034 |  |  |  | 0 |  | 0 |  | 0 | good
5892 |  | NRH |  |  |  |  | AC | 2011 |  | 101112 | Gas Chlorination Room Protective Floor Coating | [6 empty] | 0 | [9 empty] | 0 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 5000 | IMG_9041 |  |  |  | 0 |  | 0 |  | 0 | good
5893 |  | NRH |  |  |  |  | AC | 2011 |  | 101112 | Gas Chlorination Room Wall Paint | [6 empty] | 0 | [9 empty] | 0 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 1500 | IMG_9041 |  |  |  | 0 |  | 0 |  | 0 | good
5894 |  | NRH |  |  |  |  | AC | 2011 |  | 101115 | Atrium Protective Floor Coating | [6 empty] | 0 | [9 empty] | 0 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 15000 | IMG_9045 |  |  |  | 0 |  | 0 |  | 0 | good
5895 |  | NRH |  |  |  |  | AC | 2011 |  | 101115 | Atrium Wall Paint | [6 empty] | 0 | [9 empty] | 0 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 2500 | IMG_9045 |  |  |  | 0 |  | 0 |  | 0 | good
5896 |  | NRH |  |  |  |  | AC | 2011 |  | 101115 | Atrium Access Door (Double) | [6 empty] | 0 | [9 empty] | 0 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 5500 | IMG_9043 |  |  |  | 0 |  | 0 |  | 0 | good
5897 |  | NRH |  |  |  |  | AC | 2011 |  | 101111 | Valve Room Access Door (Double) | [6 empty] | 0 | [9 empty] | 0 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 5500 | IMG_9045 |  |  |  | 0 |  | 0 |  | 0 | good
5898 |  | NRH |  |  |  |  | AC | 2011 |  | 101111 | Valve Room Protective Floor Coating | [6 empty] | 0 | [9 empty] | 0 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 45000 | IMG_9046 |  |  |  | 0 |  | 0 |  | 0 | good
5899 |  | NRH |  |  |  |  | AC | 2011 |  | 101111 | Valve Room Wall Paint | [6 empty] | 0 | [9 empty] | 0 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 5000 | IMG_9046 |  |  |  | 0 |  | 0 |  | 0 | good
5900 |  | NRH |  |  |  |  | AC | 2011 |  | 101114 | Electrical and SCADA Room Access Door (Single) | [6 empty] | 0 | [9 empty] | 0 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 3500 | IMG_9054 |  |  |  | 0 |  | 0 |  | 0 | good
5901 |  | NRH |  |  |  |  | AC | 2011 |  | 101114 | Electrical and SCADA Room Wall Paint | [6 empty] | 0 | [9 empty] | 0 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 2500 | IMG_9050 |  |  |  | 0 |  | 0 |  | 0 | good
5902 |  | NRH |  |  |  |  | AC | 2011 |  | 101114 | Electrical and SCADA Room Protective Floor Coating | [6 empty] | 0 | [9 empty] | 0 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 13000 | IMG_9050 |  |  |  | 0 |  | 0 |  | 0 | good
5903 |  | NRH |  |  |  |  | SC | 2011 |  | 101112 | Gas Chlorination Room FRP Grating | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 500 | IMG_9041 |  |  |  | 0 |  | 0 |  | 0 | Good
5904 |  | NRH |  |  |  |  | SC | 2011 |  | 101113 | Ammonium Sulphate Room FRP Grating | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 5000 | IMG_9038 |  |  |  | 0 |  | 0 |  | 0 | Good
5905 |  | NRH | around 6 antenna posts including a RFS microwave antenna. |  |  |  | SIC | 2011 |  | 101119 | Elevated Tank Antennas and Communication System | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 100000 | IMG_9125 |  |  |  | 0 |  | 0 |  | 0 | good
5906 |  | NRH | 600mm x 600mm x 100mm |  |  |  | BM | 2011 |  | 101111 | Valve Room Exhaust Fan Damper and Louver | [6 empty] | 0 | [9 empty] | 0 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 3000 | IMG_3628 |  |  |  | 0 |  | 0 |  | 0 | Good
5907 |  | NRH | 600mm x 600mm x 100mm |  |  |  | BM | 2011 |  | 101111 | Valve Room Air Intake Damper and Louver | [6 empty] | 0 | [9 empty] | 0 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 3000 | IMG_3209 |  |  |  | 0 |  | 0 |  | 0 | Good
5908 |  | NRH | 450mm x 450mm x 100mm |  |  |  | BM | 2011 |  | 101114 | Electrical & SCADA Room Air Intake Damper and Louver | [6 empty] | 0 | [9 empty] | 0 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 3000 | IMG_3300 |  |  |  | 0 |  | 0 |  | 0 | Good
5909 |  | NRH | 450mm x 450mm x 100mm |  |  |  | BM | 2011 |  | 101114 | Electrical & SCADA Room Exhaust Fan Damper and Louver | [6 empty] | 0 | [9 empty] | 0 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 6000 | IMG_9053 |  |  |  | 0 |  | 0 |  | 0 | Good
5910 |  | NRH | 450mm x 450mm x 100mm |  |  |  | BM | 2011 |  | 101112 | Gas Chlorination Room Air Intake Damper and Louver | [6 empty] | 0 | [9 empty] | 0 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 3000 | IMG_9042 |  |  |  | 0 |  | 0 |  | 0 | Good
5911 |  | NRH | 450mm x 450mm x 100mm |  |  |  | BM | 2011 |  | 101112 | Gas Chlorination Room Scrubber Damper and Louver | [6 empty] | 0 | [9 empty] | 0 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 3000 | IMG_9042 |  |  |  | 0 |  | 0 |  | 0 | Good
5912 |  | NRH | 450mm x 450mm x 100mm |  |  |  | BM | 2011 |  | 101113 | Ammonium Sulphate Room Air Intake Damper and Louver | [6 empty] | 0 | [9 empty] | 0 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 3000 | IMG_9040 |  |  |  | 0 |  | 0 |  | 0 | Good
5913 |  | NRH | 450mm x 450mm x 100mm |  |  |  | BM | 2011 |  | 101113 | Ammonium Sulphate Room Exhaust Fan Damper and Louver | [6 empty] | 0 | [9 empty] | 0 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 3000 | IMG_9040 |  |  |  | 0 |  | 0 |  | 0 | Good
5914 |  | NRH | 450mm x 450mm x 100mm |  |  |  | BM | 2011 |  | 101118 | Vestibule Room Air Intake Damper and Louver | [6 empty] | 0 | [9 empty] | 0 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 3000 | IMG_3123 |  |  |  | 0 |  | 0 |  | 0 | Good
5916 |  | NRH | 900mm x 600mm x 150mm |  |  |  | BM | 2011 |  | 101116 | Upper Platform Louver | [6 empty] | 0 | [9 empty] | 0 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 6000 | IMG_9106 |  |  |  | 0 |  | 0 |  | 0 | Good
5918 |  | NRH | Cook square inline fan model SQN-B60: 1/10HP, 120V/1/60Hz, 1615rpm |  |  |  | BM | 2011 |  | 101112 | Gas Chlorination Room Exhaust Fan | [6 empty] | 0 | [9 empty] | 0 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 6000 | IMG_3153 |  |  |  | 0 |  | 0 |  | 0 | Good
5919 | 00040990 | NRH |  |  |  |  | BM | 2011 |  | 101116 | Chlorine Scrubber | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 50000 | IMG_3690 |  |  |  | 0 |  | 0 |  | 0 | Good
5920 |  | NRH |  |  |  |  | BM | 2011 |  | 101111 | Sampling Sink | [6 empty] | 0 | [9 empty] | 0 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 1000 | IMG_3205 |  |  |  | 0 |  | 0 |  | 0 | good
5921 |  | NRH |  |  |  |  | BM | 2011 |  | 101118 | Vestibule Sink | [6 empty] | 0 | [9 empty] | 0 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 1000 | IMG_3125 |  |  |  | 0 |  | 0 |  | 0 | good
5922 |  | NRH |  |  |  |  | HSS | 2011 |  |  | Elevated Tank Anchor Point (Platform Level) | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 2500 | IMG_9100 |  |  |  | 0 |  | 0 |  | 0 | good
5923 |  | NRH |  |  |  |  | HSS | 2011 |  | 101119 | Elevated Tank Davit Socket Base (Roof Level) | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 4500 | IMG_9109 |  |  |  | 0 |  | 0 |  | 0 | good
5924 | 00040958 | NRH | NRETCR_TWR_HTRC1 |  |  |  | ES | 2011 | Elevated Tank Pedestal | 101111 | Inlet Pipe Heat Trace Panel | [6 empty] | 0 |  | Central | W - Storage Elevated Tank | Building Mechanical | 24901 |  |  | OPERATING | W-WW | 2 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 10000 | PXL_20210929_132951242 |  |  |  | 0 |  | 0 |  | 0 | good
5925 | 00040959 | NRH | NRETCR_TWR_HTRC3 |  |  |  | ES | 2011 | Valve Room | 101111 | Outlet Heat Trace Panel | [6 empty] | 0 |  | Central | W - Storage Elevated Tank | Building Mechanical | 24901 |  |  | OPERATING | W-WW | 0 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 5000 | PXL_20210929_132958677 |  |  |  | 0 |  | 0 |  | 0 | good
5926 | 00040975 | NRH | 600V, 250A, 36CCT, 200kA SPD |  |  |  | ES | 2010 | Electrical and SCADA Room | 101114 | Distribution Panel DPA | M00044 | [5 empty] | 0 |  | Central | W - Storage Elevated Tank | Electrical System | 85-624342 |  |  | OPERATING | W-WW | 0 | 2 |  |  |  |  | 0 | 2023 | 0 | 0 | 16000 | PXL_20210929_131301523 |  |  |  | 0 | Review arc flash label and replace if necessary. | 500 |  | 0 | good | arc flash label to be reviewed and replaced if necessary
5927 | 00040976 | NRH | 120/208V, 150A, 60CCT |  |  |  | ES | 2011 | Electrical and SCADA Room | 101114 | Lighting Panel LPA | M00044 | [5 empty] | 0 |  | Central | W - Storage Elevated Tank | Electrical System | 85-624342 |  |  | OPERATING | W-WW | 0 | 2 |  |  |  |  | 0 | 2023 | 0 | 0 | 10000 | PXL_20210929_130857780 |  |  |  | 0 | Review arc flash label and replace if necessary. | 500 |  | 0 | good | arc flash label to be reviewed and replaced if necessary
5928 | 00040978 | NRH | NRETCR_ELEC_TX1 |  |  |  | ES | 2011 | Electrical and SCADA Room | 101114 | Transformer #1 | M00488 | [5 empty] | 0 |  | Central | W - Storage Elevated Tank | Siteworks | NMK045PBC |  |  | OPERATING | W-WW | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 9000 | PXL_20210929_131216304 |  |  |  | 0 |  | 0 |  | 0 | good
5929 | 00040979 | NRH | NRETCR_ELEC_TX2, 45kVA, 600-208V |  |  |  | ES | 2011 | Electrical and SCADA Room | 101114 | Transformer #2 | M00488 | [5 empty] | 0 |  | Central | W - Storage Elevated Tank | Siteworks | NMK030PBCN |  |  | OPERATING | W-WW | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 11000 | PXL_20210929_131245455 |  |  |  | 0 |  | 0 |  | 0 | good
5930 | 00040985 | NRH |  |  |  |  | ES | 2010 |  | 101114 | Fan Control Panel 2 | [6 empty] | 0 | [9 empty] | 0 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 5000 | PXL_20210929_131759973 |  |  |  | 0 |  | 0 |  | 0 | good
5931 | 00040986 | NRH |  |  |  |  | ES | 2010 |  | 101111 | Fan Control Panel 2 | [6 empty] | 0 | [9 empty] | 0 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 5000 | PXL_20210929_133006471 |  |  |  | 0 |  | 0 |  | 0 | good
5932 | 00040987 | NRH |  |  |  |  | ES | 2010 |  | 101118 | Fan Control Panel 3 | [6 empty] | 0 | [9 empty] | 0 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 5000 | PXL_20210929_133955195 |  |  |  | 0 |  | 0 |  | 0 | good
5933 | 00040988 | NRH |  |  |  |  | ES | 2010 |  | 101118 | Fan Control Panel 4 | [6 empty] | 0 | [9 empty] | 0 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 5000 | PXL_20210929_134029516 |  |  |  | 0 |  | 0 |  | 0 | good
5934 | 00040989 | NRH |  |  |  |  | ES | 2010 |  | 101118 | Fan Control Panel 5 | [6 empty] | 0 | [9 empty] | 0 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 5000 | PXL_20210929_134115354 |  |  |  | 0 |  | 0 |  | 0 | good
5935 | 00086792 | NRH | with manual transfer switch, NRETCR_GEN_MTS1, 30A, 120/240V |  |  |  | ES | 2011 | Vestibule | 101114 | Generator Transfer Panel | [6 empty] | 0 |  | Central | W - Storage Elevated Tank |  |  |  |  | OPERATING | W-WW | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 5000 | PXL_20210929_131918544 |  |  |  | 0 |  | 0 |  | 0 | good
5937 |  | NRH |  |  |  |  | ES | 2010 |  | 101119 | Elevated Tank Lightning Protection System | [6 empty] | 25 | [9 empty] | 3 | 3 | One of the lightning rods were not erected. |  |  | The asset was observed to be in fair condition. Reinstall the lightning rod to the highest point of the elevated tank . | 500 |  | 0 |  | 7000 | IMG_9125 |  | King City Fisher ET Capital Project 1 |  | 2019 |  |  |  | 0 | good
5938 |  | NRH |  |  |  |  | ES | 2010 |  | 101119 | Elevated Tank Grounding | [6 empty] | 25 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. |  |  |  |  | 10000 | IMG_9062 |  |  |  | 0 |  |  |  |  | good
5939 |  | NRH |  |  |  |  | ES | 2010 |  | 101119 | Electrical Duct System and Conduit System | [6 empty] | 25 | [9 empty] | 4 | 3 | The cables installed in the access tube poses safety concern as cable cluster prevents safe and effective rescue. |  |  | The asset was observed to be in poor condition. Install cable messenger or a dedicated communication cable chute to access tube for better cable organization. Two options were recommended. They cost around $110k to $200k. $200k is included in the capital | 200000 |  | 0 |  | 75000 | IMG_9068 |  | King City Fisher ET Capital Project 1 |  | 2019 |  |  |  | 0 | good
5940 |  | NRH | Two warning lights, assumed installation year: 2010 |  |  |  | ES | 2010 |  | 101119 | Aircraft Obstruction Lights | [6 empty] | 5 | [9 empty] | 3 | 3 | The incandescent fixture was not working after the bulbs were replaced. It is recommended to replace the unit with LED fixture controller. |  |  | The asset was observed to be in fair condition. |  |  |  |  | 2000 | IMG_9116 | King City Fisher ET Capital Project 1 |  |  | 2019 |  |  |  |  | Good
5941 | 00043008 | NRH |  |  |  |  | ES | 2010 |  | 101119 | Elevated Tank Piping Heat Tracing | [6 empty] | 15 |  |  |  |  | R1-050-DP |  |  |  |  | 2 | 3 |  |  |  | The asset was observed to be in good condition. Asset to be replaced in the long term. |  |  |  |  | 30000 | IMG_3277 | King City Fisher ET Capital Project 2 |  |  | 0 |  |  |  |  | good
5942 |  | NRH | 450mm CCP watermain. Approx. total length 60 meters |  |  |  | SW | 2011 |  | 101117 | Watermain | [6 empty] | 25 | [9 empty] | 3 | 5 |  |  |  | The asset was assumed to be in fair condition. |  |  |  |  | 85000 |  |  |  |  | 0 |  |  |  |  | good
5943 |  | NRH |  |  |  |  | SW | 2011 |  | 101117 | Valve Chamber No. 1 Concrete Structure | [6 empty] | 50 | [9 empty] | 2 | 3 | Minor rust spots on wall and roof was observed. |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. |  |  |  |  | 65000 | IMG_9071 |  |  |  | 0 |  |  |  |  | good
5944 |  | NRH |  |  |  |  | SW | 2011 |  | 17512 | Valve Chamber No. 1 Ladder | [6 empty] | 50 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. |  |  |  |  | 3000 | IMG_9071 |  |  |  | 0 |  |  |  |  | good
5945 |  | NRH |  |  |  |  | SW | 2011 |  | 17512 | Valve Chamber No. 1 Access Hatch | [6 empty] | 50 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. |  |  |  |  | 5000 | IMG_9075 |  |  |  | 0 |  |  |  |  | good
5946 |  | NRH | Approximate 200m 250mm PVC Sanitary pipe |  |  |  | SW | 2011 |  | 17512 | Sanitary Service | [6 empty] | 50 | [9 empty] | 1 | 4 |  |  |  | The asset was assumed to be in very good condition based on its age. Asset to be replaced at the end of their service life. |  |  |  |  | 150000 |  |  |  |  | 0 |  |  |  |  | good
5947 |  | NRH | 450mm PCV, length: 200 meters |  |  |  | SW | 1984 |  | 17512 | Overflow Pipe | [6 empty] | 25 | [9 empty] | 3 | 4 |  |  |  | The asset was assumed to be in fair condition. Asset to be replaced at the end of their service life. |  |  |  |  | 280000 |  |  |  |  | 0 |  |  |  |  | good
5948 |  | NRH |  |  |  |  | SW | 2011 |  | 101117 | Valve Chamber No.2 Concrete Structure | [6 empty] | 50 | [9 empty] | 1 | 3 |  |  |  | The asset was observed to be in very good condition. Asset to be replaced at the end of its service life. |  |  |  |  | 10000 | IMG_3106 |  |  |  | 0 |  |  |  |  | good
5949 |  | NRH |  |  |  |  | SW | 2011 |  | 101117 | Valve Chamber No.2 Concrete Structure | [6 empty] | 50 | [9 empty] | 1 | 2 |  |  |  | The asset was observed to be in very good condition. Asset to be replaced at the end of its service life. |  |  |  |  | 2000 | IMG_9077 |  |  |  | 0 |  |  |  |  | good
5950 |  | NRH |  |  |  |  | SW | 2011 |  | 101117 | Valve Chamber No.2 Access Hatch | [6 empty] | 50 | [9 empty] | 1 | 2 |  |  |  | The asset was observed to be in very good condition. Asset to be replaced at the end of its service life. |  |  |  |  | 5000 | IMG_3106 |  |  |  | 0 |  |  |  |  | good
5952 |  | NRH | 3 in total |  |  |  | SW | 2011 |  | 17512 | Concrete Pads (at entrance) | [6 empty] | 25 | [9 empty] | 3 | 1 | Minor damage was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of its service life. |  |  |  |  | 6000 | IMG_3115 |  |  |  | 0 |  |  |  |  | good
5953 |  | NRH | 1.8m hight chainlink fence around site. Approx. length 230m |  |  |  | SW | 2011 |  | 101117 | Chainlink Fence | [6 empty] | 20 | [9 empty] | 3 | 2 | Minor corrosion was noted on the north, west, and south sids of the fence. The esat side of the fence is new. |  |  | The asset was observed to be in fair condition. Minor corrosion was noted on the north, west, and south sids of the fence. The esat side of the fence is new. Asset to be replaced in the long term. |  |  |  |  | 23000 | IMG_3086 | King City Fisher ET Capital Project 2 |  |  | 0 |  |  |  |  | good
5954 |  | NRH | Asphalt driveway |  |  |  | SW | 2011 |  | 101117 | Asphalt Driveway | [6 empty] | 16 | [9 empty] | 3 | 2 | Cracks were observed at various locations of driveway. |  |  | The asset was observed to be in fair condition. Repave top surface of asphalt. Asset to be replaced in the intermediate term. | 7500 |  | 0 |  | 50000 | IMG_3097 | King City Fisher ET Capital Project 2 | King City Fisher ET Capital Project 1 |  | 0 |  |  |  | 0 | Minor surface cracks
5955 | 00008866 | NRH |  |  |  |  | SW | 2010 | King City Fisher Elevated Tank | 101117 | Double Lockable Swing Gate | [6 empty] | 20 |  | Area 1S Linear Water & Wells | W - Storage Elevated Tank | Siteworks |  |  |  |  | W-WW | 1 | 1 |  |  |  | The asset was observed to be in very good condition. Asset to be replaced in the long term. |  |  |  |  | 4000 | IMG_3103 | King City Fisher ET Capital Project 2 |  |  | 0 |  |  |  |  | Good
5956 | 00008870 | NRH | including swale |  |  |  | SW | 2011 | King City FS ET Valve Room | 17512 | Site Drainage (soft surfaces) | [6 empty] | 25 |  | Area 2N Linear Water & Wells |  | Siteworks |  |  |  |  | W-WW | 3 | 1 | Low spots adjacent to concrete pads was observed. | Exposed top soil was observed in various locations around site. |  | The asset was observed to be in fair condition. Place more granular/top soil adjacent to pad to ensure drainage away from pads. Asset to be replaced in the intermediate term. | 7000 |  |  |  | 75000 | IMG_3097 | King City Fisher ET Capital Project 1 | King City Fisher ET Capital Project 1 |  | 0 |  |  |  |  | good
5957 |  | NRH | diameter: 450mm |  |  |  | PM | 1997 |  | 101117 | Valve Chamber No. 1 Butterfly Valve | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 10000 | IMG_9072 |  |  |  | 0 |  | 0 |  | 0 | surface corrosion
5958 |  | NRH | diameter: 100mm |  |  |  | PM | 1997 |  | 101117 | Valve Chamber No. 1 Watermain Drain Valve | [6 empty] | 0 | [9 empty] | 0 | 3 |  |  |  |  | 0 | 0 | 0 | 0 | 2000 | IMG_9074 |  |  |  | 0 |  | 0 |  | 0 | surface corrosion
5959 |  | NRH |  |  |  |  | SW | 2011 |  | 101117 | PRV Valve Chamber Ladder | [6 empty] | 50 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. |  |  |  |  | 3000 | IMG_9132 |  |  |  | 0 |  |  |  |  | good
5960 |  | NRH |  |  |  |  | SW | 2011 |  | 101117 | PRV Valve Chamber Concrete Structure | [6 empty] | 50 | [9 empty] | 2 | 3 | Minor rust spots on wall and roof was observed. |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. |  |  |  |  | 65000 | IMG_9132 |  |  |  | 0 |  |  |  |  | good
5961 |  | NRH |  |  |  |  | SW | 2011 |  | 101117 | PRV Valve Chamber Access Hatch | [6 empty] | 50 | [9 empty] | 2 | 2 |  |  |  | The asset was observed to be in good condition. Asset to be replaced at the end of its service life. |  |  |  |  | 5000 | IMG_9138 |  |  |  | 0 |  |  |  |  | good
5962 |  | NRH | 4 in total |  |  |  | SW | 2011 |  | 17512 | Bollards | [6 empty] | 0 | [9 empty] | 0 | 1 |  |  |  |  | 0 |  | 0 |  | 2000 | IMG_3115 |  |  |  | 0 |  |  |  |  | good
5963 |  | NRH | 450mm ss, approximate length: 15 meters |  |  |  | PM | 2011 | King City FS ET Valve Room | 00002335 | Elevated Tank Inlet/Outlet Line | [6 empty] | 32 | [9 empty] | 2 | 5 |  |  |  | The asset was observed to be in good condition. |  |  |  |  | 10000 | IMG_3214 |  |  |  | 0 |  |  |  |  | good
5964 |  | NRH | Diameter: 200mm, with a gate valve |  |  |  | PM | 2011 | King City FS ET Valve Room | 00017520 | Elevated Tank Bypass Line | [6 empty] | 28 | [9 empty] | 1 | 3 |  |  |  | The asset was observed to be in very good condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | 5000 | IMG_3273 |  |  |  | 0 |  |  |  |  | Good
5966 |  | NRH | Diameter: 450mm, approximate length: 40 meters |  |  |  | PM | 2011 | King City FS ET Valve Room | 00002335 | Elevated Tank Inlet Line | [6 empty] | 32 | [9 empty] | 2 | 5 |  |  |  | The asset was observed to be in good condition. |  |  |  |  | 66000 | IMG_3234 |  |  |  | 0 |  |  |  |  | good
5967 |  | NRH | Diameter: 450mm, approximate length: 25 meters |  |  |  | PM | 2011 | King City FS ET Valve Room | 00002335 | Elevated Tank Outlet Line | [6 empty] | 32 | [9 empty] | 2 | 5 |  |  |  | The asset was observed to be in good condition. |  |  |  |  | 41000 | IMG_3263 |  |  |  | 0 |  |  |  |  | good
5968 |  | NRH | Diameter: 100mm, approximate length: 20 meters |  |  |  | PM | 2011 | King City FS ET Valve Room | 00002335 | Elevated Tank Circulation Line | [6 empty] | 32 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. |  |  |  |  | 7000 | DSCN4033 |  |  |  | 0 |  |  |  |  | good
5969 |  | NRH | Diameter: 400mm, approximate length: 50 meters |  |  |  | PM | 2011 | King City FS ET Valve Room | 00002335 | Elevated Tank Overflow Line | [6 empty] | 32 | [9 empty] | 2 | 4 |  |  |  | The asset was observed to be in good condition. |  |  |  |  | 73000 | IMG_3262 |  |  |  | 0 |  |  |  |  | good
5970 |  | NRH | Two PRV valves |  |  |  | PM | 2011 | King City FS ET Valve Room | 00002335 | PRV Valve Chamber Process Mechanical Equipment | [6 empty] | 32 | [9 empty] | 2 | 3 |  |  |  | The asset was observed to be in good condition. |  |  |  |  | 30000 | IMG_9133 |  |  |  | 0 |  |  |  |  | minor surface corrosion
5971 |  | NRH |  |  |  |  | PM | 2011 |  | 00002335 | Elevated Tank Mixing System | [6 empty] | 25 | [9 empty] | 2 | 3 |  |  |  | The elevated tank mixing system was observed to be in good condition. | 0 |  | 0 |  | 85000 |  |  |  |  | 2019 |  | 0 |  | 0 | good
5972 |  | NRH |  |  |  |  | PM | 2011 | King City FS ET Valve Room | 00002335 | Elevated Tank Frostproof Vent/Vacuum Relief Unit | [6 empty] | 21 | [9 empty] | 3 | 3 | Minor surface corrosion was observed. |  |  | The asset was observed to be in fair condition. Asset to be replaced at the end of remaining service life. |  |  |  |  | 6000 | IMG_9108 |  |  |  | 2019 |  |  |  |  | good
5973 |  | NRH | total of 3 |  |  |  | SW | 2011 |  |  | Sanitary Manholes | [6 empty] | 0 | [9 empty] | 0 | 2 |  |  |  |  | 0 | 0 | 0 | 0 | 50000 | IMG_9085 |  |  |  | 0 |  | 0 |  | 0 | good